PONCE | 2021-09-05 08:13 | 2021-09-05 10:23 | 18 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN TRANSFORMADOR CRUCE DE FASE POR IGUANA | P21090500003 | New_Event |  |  | Include | Wildlife | 130 | 2021-09-05 | 2340 | keep | 0 | Sep | 2021 | 0.0015938 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2021-09-05 08:20 | 2021-09-05 08:21 | 464 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR | P21090500006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-05 | 464 | keep | 0 | Sep | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2021-09-05 08:21 | 2021-09-05 10:23 | 100 | 002:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | P21090500007 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 122 | 2021-09-05 | 12200 | keep | 0 | Sep | 2021 | 0.0083094 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-05 08:23 | 2021-09-05 14:33 | 5 | 006:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO EN EL FID:1000325127 / MARCA GE / #SERIE 1855110063 / CAPACIDAD 37.5KVA / VOLTAJES 7.62/13.2KV - 120/240V POR LO MISMO | A21090500016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 370 | 2021-09-05 | 1850 | keep | 0 | Sep | 2021 | 0.00126 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-05 08:28 | 2021-09-07 17:27 | 60 | 056:59 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | C21090500017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3419 | 2021-09-05 | 205140 | keep | 0 | Sep | 2021 | 0.13972 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-05 08:31 | 2021-09-05 15:27 | 13 | 006:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50 KVA | A21090500017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 416 | 2021-09-05 | 5408 | keep | 0 | Sep | 2021 | 0.0036834 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-09-05 08:33 | 2021-09-05 17:35 | 10 | 009:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B21090500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 542 | 2021-09-05 | 5420 | keep | 0 | Sep | 2021 | 0.0036915 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-09-05 08:35 | 2021-09-05 13:27 | 40 | 004:52 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 EN SU - 1 CONTAMINACION | R21090400013 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 292 | 2021-09-05 | 11680 | keep | 0 | Sep | 2021 | 0.0079552 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-09-05 08:50 | 2021-09-05 13:15 | 20 | 004:25 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REMPLAZO POSTE PARTIDO | P21090500018 | New_Event | Defective Pole | Include | Include | Equipment | 265 | 2021-09-05 | 5300 | keep | 0 | Sep | 2021 | 0.0036098 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-05 09:21 | 2021-09-05 14:21 | 30 | 005:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REEMPLAZO AISLADOR | R21090500010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 300 | 2021-09-05 | 9000 | keep | 0 | Sep | 2021 | 0.0061299 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-05 09:21 | 2021-09-05 09:22 | 1510 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECERRO INTERRUPTOR | C21090500029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-09-05 | 1510 | keep | 0 | Sep | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-09-05 09:22 | 2021-09-05 16:50 | 23 | 007:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZAR 100 PIES DE SECUNDARIA | C21090400063 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 448 | 2021-09-05 | 10304 | keep | 0 | Sep | 2021 | 0.007018 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2021-09-05 09:30 | 2021-09-05 11:39 | 10 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | S21090500090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2021-09-05 | 1290 | keep | 0 | Sep | 2021 | 0.00087861 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-05 09:42 | 2021-09-05 12:55 | 1 | 003:13 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | B21090500030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-09-05 | 193 | keep | 0 | Sep | 2021 | 0.00013145 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-05 09:57 | 2021-09-05 14:14 | 50 | 004:17 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE REALIZO DESGANCHE | A21090500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2021-09-05 | 12850 | keep | 0 | Sep | 2021 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-05 10:09 | 2021-09-06 12:33 | 4 | 026:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | B21090500033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1584 | 2021-09-05 | 6336 | keep | 0 | Sep | 2021 | 0.0043154 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-09-05 10:13 | 2021-09-05 17:35 | 150 | 007:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR DE REMPLAZO PORTAFUSIBLES EN TRANSFORMADOR | A21090500028 | New_Event | Cutout Failure | Include | Include | Equipment | 442 | 2021-09-05 | 66300 | keep | 0 | Sep | 2021 | 0.045157 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-05 10:16 | 2021-09-05 14:35 | 5 | 004:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES | A21090500029 | New_Event | Cutout Failure | Include | Include | Equipment | 259 | 2021-09-05 | 1295 | keep | 0 | Sep | 2021 | 0.00088202 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-05 10:41 | 2021-09-05 23:30 | 53 | 012:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B21090500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 769 | 2021-09-05 | 40757 | keep | 0 | Sep | 2021 | 0.027759 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
BAYAMON | 2021-09-05 10:45 | 2021-09-05 10:46 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 6136 | keep | 0 | Sep | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
SAN JUAN | 2021-09-05 10:46 | 2021-09-05 13:44 | 40 | 002:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2021-09-05 | 7120 | keep | 0 | Sep | 2021 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-05 10:49 | 2021-09-05 10:50 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1717-05 | B21090500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 4533 | keep | 0 | Sep | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-09-05 10:49 | 2021-09-05 10:50 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1717-01 | B21090500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2021-09-05 11:02 | 2021-09-05 11:03 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1717-05 | B21090600019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 4533 | keep | 0 | Sep | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-09-05 11:02 | 2021-09-05 11:03 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1717-01 | B21090600019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2021-09-05 11:07 | 2021-09-05 17:14 | 100 | 006:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2021-09-05 | 36700 | keep | 0 | Sep | 2021 | 0.024996 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-05 11:21 | 2021-09-05 11:22 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1717-01 | B21090600020 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
CAGUAS | 2021-09-05 11:22 | 2021-09-05 12:18 | 5 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090400057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-09-05 | 280 | keep | 0 | Sep | 2021 | 0.00019071 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-05 11:31 | 2021-09-05 15:50 | 75 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21090500045 | New_Event | Wire Down | Include | Include | Equipment | 259 | 2021-09-05 | 19425 | keep | 0 | Sep | 2021 | 0.01323 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-05 11:31 | 2021-09-05 11:32 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1717-01 | B21090600021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
ARECIBO | 2021-09-05 11:31 | 2021-09-05 21:38 | 20 | 010:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A21090500034 | New_Event | Wire Down | Include | Include | Equipment | 607 | 2021-09-05 | 12140 | keep | 0 | Sep | 2021 | 0.0082685 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-05 11:34 | 2021-09-05 12:35 | 1681 | 001:01 | T | DESGANCHE | SE RETIRO BAMBUA CRUZANDO LINEAS CARGA POR 1303 04 | S21090500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-09-05 | 102541 | keep | 0 | Sep | 2021 | 0.06984 | 0.0011449 | Sustained | FALSE | TRUE | Not_TMED_Event | 1681
SAN JUAN | 2021-09-05 11:34 | 2021-09-05 12:35 | 1598 | 001:01 | T | DESGANCHE | SE RETIRO BAMBUA CRUZANDO LINEAS CARGA POR 1303 04 | S21090500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-09-05 | 97478 | keep | 0 | Sep | 2021 | 0.066392 | 0.0010884 | Sustained | FALSE | TRUE | Not_TMED_Event | 1598
CAGUAS | 2021-09-05 12:10 | 2021-09-05 12:11 | 3131 | 000:01 | T | SECUNDARIA/DESGANCHE | RECERRO INTERRUPTOR | C21090500038 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1 | 2021-09-05 | 3131 | keep | 0 | Sep | 2021 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
CAGUAS | 2021-09-05 12:11 | 2021-09-06 11:53 | 7 | 023:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21090500057 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 1422 | 2021-09-05 | 9954 | keep | 0 | Sep | 2021 | 0.0067796 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-05 12:13 | 2021-09-05 13:43 | 726 | 001:30 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO LLEVA CARGA 1346 04 | S21090500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 90 | 2021-09-05 | 65340 | keep | 0 | Sep | 2021 | 0.044503 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-09-05 12:13 | 2021-09-05 13:43 | 3932 | 001:30 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO CARGA POR 1303 03 | S21090500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 90 | 2021-09-05 | 353880 | keep | 0 | Sep | 2021 | 0.24103 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
AGUADILLA | 2021-09-05 12:25 | 2021-09-05 15:00 | 100 | 002:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21090500044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-09-05 | 15500 | keep | 0 | Sep | 2021 | 0.010557 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-09-05 12:32 | 2021-09-05 14:19 | 10 | 001:47 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | R21090500027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 107 | 2021-09-05 | 1070 | keep | 0 | Sep | 2021 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-05 12:44 | 2021-09-06 15:47 | 45 | 027:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S21090500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1623 | 2021-09-05 | 73035 | keep | 0 | Sep | 2021 | 0.049744 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-09-05 12:45 | 2021-09-05 14:35 | 50 | 001:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | C21090500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-09-05 | 5500 | keep | 0 | Sep | 2021 | 0.003746 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-05 12:46 | 2021-09-05 13:30 | 13 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | M21090500057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-09-05 | 572 | keep | 0 | Sep | 2021 | 0.00038959 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-09-05 12:48 | 2021-09-05 19:29 | 75 | 006:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B21090500058 | New_Event | Wire Down | Include | Include | Equipment | 401 | 2021-09-05 | 30075 | keep | 0 | Sep | 2021 | 0.020484 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-05 12:51 | 2021-09-05 17:28 | 9 | 004:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD EN EL FID33576203 / MARCA ERMCO / #SERIE 82011973985 / VOLTAJE 2.4KV A 120/240V | A21090500040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 277 | 2021-09-05 | 2493 | keep | 0 | Sep | 2021 | 0.001698 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-09-05 12:59 | 2021-09-05 15:09 | 1 | 002:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21090500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-09-05 | 130 | keep | 0 | Sep | 2021 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-05 13:02 | 2021-09-05 17:13 | 12 | 004:11 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21090500154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2021-09-05 | 3012 | keep | 0 | Sep | 2021 | 0.0020515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-05 13:11 | 2021-09-05 13:13 | 1420 | 000:02 | T | OTRAS CAUSAS | SE CERRO POR SCADA CARGA POR 1530-06 | S21090500155 | New_Event | Other Causes | Include | Include | Other | 2 | 2021-09-05 | 2840 | keep | 0 | Sep | 2021 | 0.0019343 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-05 13:11 | 2021-09-05 13:13 | 437 | 000:02 | T | OTRAS CAUSAS | SE CERRO POR SCADA LLEVA 1526 02 DESBALANCE | S21090500155 | New_Event | Other Causes | Include | Include | Other | 2 | 2021-09-05 | 874 | keep | 0 | Sep | 2021 | 0.00059528 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2021-09-05 13:25 | 2021-09-05 13:27 | 3387 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL | B21090500061 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-09-05 | 6774 | keep | 0 | Sep | 2021 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
CAGUAS | 2021-09-05 14:00 | 2021-09-05 18:44 | 181 | 004:44 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTES DE LINEA DESGANCHE | C21090500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-09-05 | 51404 | keep | 0 | Sep | 2021 | 0.035011 | 0.00012328 | Sustained | FALSE | TRUE | Not_TMED_Event | 181
BAYAMON | 2021-09-05 14:16 | 2021-09-05 14:17 | 1399 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090500067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 1399 | keep | 0 | Sep | 2021 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-09-05 14:16 | 2021-09-05 14:17 | 302 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090500067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 302 | keep | 0 | Sep | 2021 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
ARECIBO | 2021-09-05 14:20 | 2021-09-06 15:17 | 5 | 024:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFROMADOR Y SE REPARO SECUNDARIA | A21090500060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1497 | 2021-09-05 | 7485 | keep | 0 | Sep | 2021 | 0.005098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-09-05 14:46 | 2021-09-05 14:47 | 3387 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL | B21090500071 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-09-05 | 3387 | keep | 0 | Sep | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-09-05 14:47 | 2021-09-05 15:11 | 30 | 000:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | B21090500077 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 24 | 2021-09-05 | 720 | keep | 0 | Sep | 2021 | 0.00049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-05 15:11 | 2021-09-05 17:28 | 3387 | 002:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | B21090500077 | Additional_clients | Wire Down | Include | Include | Equipment | 137 | 2021-09-05 | 464019 | keep | 0 | Sep | 2021 | 0.31604 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-05 15:25 | 2021-09-05 18:42 | 170 | 003:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA | S21090500179 | New_Event | Wire Down | Include | Include | Equipment | 197 | 2021-09-05 | 33490 | keep | 0 | Sep | 2021 | 0.02281 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
CAGUAS | 2021-09-05 15:34 | 2021-09-05 17:02 | 57 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21090500055 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-09-05 | 5016 | keep | 0 | Sep | 2021 | 0.0034164 | 3.8822e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 57
SAN JUAN | 2021-09-05 15:36 | 2021-09-06 13:07 | 15 | 021:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21090500180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1291 | 2021-09-05 | 19365 | keep | 0 | Sep | 2021 | 0.013189 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-05 15:49 | 2021-09-05 16:50 | 15 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | B21090500060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-09-05 | 915 | keep | 0 | Sep | 2021 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-09-05 15:51 | 2021-09-05 18:12 | 100 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21090500055 | New_Event |  |  | Include | Wildlife | 141 | 2021-09-05 | 14100 | keep | 0 | Sep | 2021 | 0.0096034 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-05 15:51 | 2021-09-05 17:13 | 100 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE Y RETEZO LINEA | R21090500043 | New_Event |  |  | Include | Wildlife | 82 | 2021-09-05 | 8200 | keep | 0 | Sep | 2021 | 0.005585 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-05 15:51 | 2021-09-05 16:26 | 9 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090300093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-09-05 | 315 | keep | 0 | Sep | 2021 | 0.00021455 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-09-05 15:53 | 2021-09-05 18:16 | 20 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21090500046 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2021-09-05 | 2860 | keep | 0 | Sep | 2021 | 0.0019479 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-05 16:08 | 2021-09-05 16:09 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LCARGA TRANSFERIDA AL 1717-01 | B21090600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
MAYAGÃœEZ | 2021-09-05 16:15 | 2021-09-05 18:10 | 3 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21090500071 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-09-05 | 345 | keep | 0 | Sep | 2021 | 0.00023498 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-09-05 16:16 | 2021-09-05 19:10 | 50 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21090500072 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-09-05 | 8700 | keep | 0 | Sep | 2021 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-05 16:45 | 2021-09-05 18:45 | 5 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21090500051 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-09-05 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-05 16:47 | 2021-09-05 16:48 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 2617 | keep | 0 | Sep | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
ARECIBO | 2021-09-05 16:49 | 2021-09-05 22:20 | 6 | 005:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | A21090400119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 331 | 2021-09-05 | 1986 | keep | 0 | Sep | 2021 | 0.0013527 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-09-05 16:51 | 2021-09-05 16:53 | 327 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-05 | 654 | keep | 0 | Sep | 2021 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2021-09-05 17:17 | 2021-09-05 17:47 | 3941 | 000:30 | T | ESTRUCTURA AVERIADA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B21090500000 | New_Event | Defective Pole | Include | Include | Equipment | 30 | 2021-09-05 | 118230 | keep | 0 | Sep | 2021 | 0.080526 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-09-05 17:38 | 2021-09-07 17:12 | 25 | 047:34 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO | B21090500099 | New_Event | UG Cable Fault | Include | Include | Equipment | 2854 | 2021-09-05 | 71350 | keep | 0 | Sep | 2021 | 0.048596 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-09-05 17:58 | 2021-09-05 19:22 | 70 | 001:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN RISER | A21090500055 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2021-09-05 | 5880 | keep | 0 | Sep | 2021 | 0.0040048 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2021-09-05 18:17 | 2021-09-06 10:48 | 40 | 016:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21090500067 | New_Event |  |  | Include | Wildlife | 991 | 2021-09-05 | 39640 | keep | 0 | Sep | 2021 | 0.026999 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-05 18:21 | 2021-09-06 11:16 | 75 | 016:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1015 | 2021-09-05 | 76125 | keep | 0 | Sep | 2021 | 0.051848 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-09-05 18:29 | 2021-09-05 20:40 | 40 | 002:11 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21090500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-09-05 | 5240 | keep | 0 | Sep | 2021 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-05 18:40 | 2021-09-05 18:41 | 776 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090500107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 776 | keep | 0 | Sep | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-09-05 18:41 | 2021-09-05 20:02 | 75 | 001:21 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B21090500112 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-09-05 | 6075 | keep | 0 | Sep | 2021 | 0.0041377 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-09-05 18:52 | 2021-09-06 10:32 | 80 | 015:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21090500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 940 | 2021-09-05 | 75200 | keep | 0 | Sep | 2021 | 0.051218 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-09-05 19:00 | 2021-09-06 11:15 | 5 | 016:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21090500090 | New_Event | Bad Weather | Include | Include | Weather | 975 | 2021-09-05 | 4875 | keep | 0 | Sep | 2021 | 0.0033203 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-09-05 19:05 | 2021-09-06 10:49 | 8 | 015:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21090500075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 944 | 2021-09-05 | 7552 | keep | 0 | Sep | 2021 | 0.0051436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-09-05 19:47 | 2021-09-06 15:59 | 150 | 020:12 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21090500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1212 | 2021-09-05 | 181800 | keep | 0 | Sep | 2021 | 0.12382 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-05 20:05 | 2021-09-06 11:40 | 40 | 015:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA QUEMADA SE ABRIO CORTE DE LINEA PARA REMPLAZARLA | M21090500098 | New_Event | Cutout Failure | Include | Include | Equipment | 935 | 2021-09-05 | 37400 | keep | 0 | Sep | 2021 | 0.025473 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-05 20:16 | 2021-09-06 09:31 | 168 | 013:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R21090500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 795 | 2021-09-05 | 133560 | keep | 0 | Sep | 2021 | 0.090967 | 0.00011442 | Sustained | FALSE | TRUE | Not_TMED_Event | 168
SAN JUAN | 2021-09-05 20:45 | 2021-09-06 17:21 | 45 | 020:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA DE CORTE DE LINEA | S21090500199 | New_Event | Cutout Failure | Include | Include | Equipment | 1236 | 2021-09-05 | 55620 | keep | 0 | Sep | 2021 | 0.037883 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-09-05 20:46 | 2021-09-06 14:41 | 10 | 017:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE CERRO PUENTE DE LINEA A CAJA | S21090500200 | New_Event | Wire Down | Include | Include | Equipment | 1075 | 2021-09-05 | 10750 | keep | 0 | Sep | 2021 | 0.0073218 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-05 20:46 | 2021-09-06 10:00 | 12 | 013:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21090500107 | New_Event | Bad Weather | Include | Include | Weather | 794 | 2021-09-05 | 9528 | keep | 0 | Sep | 2021 | 0.0064895 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-09-05 20:46 | 2021-09-06 12:20 | 30 | 015:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEAS SECUNDARIAS AVERIADAS | M21090500092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 934 | 2021-09-05 | 28020 | keep | 0 | Sep | 2021 | 0.019084 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-05 20:54 | 2021-09-06 14:54 | 8 | 018:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | A21090500062 | New_Event | Wire Down | Include | Include | Equipment | 1080 | 2021-09-05 | 8640 | keep | 0 | Sep | 2021 | 0.0058847 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-05 20:57 | 2021-09-05 20:58 | 1420 | 000:01 | T | OTRAS CAUSAS | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LA CARGA SE ENCUENTRA POR EL 1530-06 | S21090500202 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-05 20:57 | 2021-09-05 20:58 | 437 | 000:01 | T | OTRAS CAUSAS | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1526-02 DESBALANCE | S21090500202 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-05 21:15 | 2021-09-05 21:52 | 12 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR PUENTE SECUNDARIO | S21090500095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-09-05 | 444 | keep | 0 | Sep | 2021 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-05 21:31 | 2021-09-06 09:07 | 60 | 011:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21090500109 | New_Event | Bad Weather | Include | Include | Weather | 696 | 2021-09-05 | 41760 | keep | 0 | Sep | 2021 | 0.028443 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-05 21:34 | 2021-09-05 21:35 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO EL 1530-06 LA CARGA DEL 1526-02 SE ENCUENTRA POR EL 1530-06 DESBALANCE | S21090500000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-05 21:34 | 2021-09-05 21:35 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-02 DESBALANCE | S21090500000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-05 21:39 | 2021-09-05 21:40 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO EL 1530-06 LA CARGA DEL 1526-02 SE ENCUENTRA POR EL 1530-06 | S21090500000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-05 21:39 | 2021-09-05 21:40 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-02 DESBALANCE | S21090500000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-05 21:51 | 2021-09-05 21:52 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO EL 1530-06 LA CARGA DEL 1526-02 SE ENCUENTRA POR EL 1530-06 | S21090500000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-05 21:51 | 2021-09-05 21:52 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-02 DESBALANCE | S21090500000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-05 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
MAYAGÃœEZ | 2021-09-05 22:00 | 2021-09-06 11:00 | 250 | 013:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21090500114 | New_Event | Bad Weather | Include | Include | Weather | 780 | 2021-09-05 | 195000 | keep | 0 | Sep | 2021 | 0.13281 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
PONCE | 2021-09-05 22:02 | 2021-09-06 09:29 | 40 | 011:27 | P | NO SE REPORTO CAUSA | 1X65 EN CORTE DE LINEA. NO SE REPORTA CAUSA | P21090500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 687 | 2021-09-05 | 27480 | keep | 0 | Sep | 2021 | 0.018717 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-05 22:13 | 2021-09-06 12:46 | 10 | 014:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA DE TRANSFORMADOR AVERIADA Y BAJANTE SECUNDARIO | C21090500088 | New_Event | Cutout Failure | Include | Include | Equipment | 873 | 2021-09-05 | 8730 | keep | 0 | Sep | 2021 | 0.005946 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-05 22:40 | 2021-09-05 22:41 | 3012 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF PERMANENTE | R21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 3012 | keep | 0 | Sep | 2021 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
BAYAMON | 2021-09-05 22:40 | 2021-09-06 09:25 | 10 | 010:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090500129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 645 | 2021-09-05 | 6450 | keep | 0 | Sep | 2021 | 0.0043931 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-09-05 22:41 | 2021-09-06 06:55 | 15 | 008:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR AVE | P21090500030 | New_Event |  |  | Include | Wildlife | 494 | 2021-09-05 | 7410 | keep | 0 | Sep | 2021 | 0.0050469 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-09-05 23:02 | 2021-09-06 10:22 | 12 | 011:20 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21090500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 680 | 2021-09-05 | 8160 | keep | 0 | Sep | 2021 | 0.0055577 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-09-06 00:06 | 2021-09-06 16:47 | 250 | 016:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZARON 3 CAJAS PRIMARIAS | S21090600003 | New_Event | Cutout Failure | Include | Include | Equipment | 1001 | 2021-09-06 | 250250 | keep | 0 | Sep | 2021 | 0.17044 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-09-06 00:29 | 2021-09-06 02:55 | 893 | 002:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO POR SCADA | S21090600000 | New_Event | Wire Down | Include | Include | Equipment | 146 | 2021-09-06 | 130378 | keep | 0 | Sep | 2021 | 0.0888 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2021-09-06 00:29 | 2021-09-06 00:30 | 602 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 602 | keep | 0 | Sep | 2021 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2021-09-06 00:29 | 2021-09-06 00:30 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 2203 | keep | 0 | Sep | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2021-09-06 01:08 | 2021-09-06 12:53 | 80 | 011:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21090600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 705 | 2021-09-06 | 56400 | keep | 0 | Sep | 2021 | 0.038414 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-06 01:10 | 2021-09-06 10:05 | 40 | 008:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21090600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 535 | 2021-09-06 | 21400 | keep | 0 | Sep | 2021 | 0.014575 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-06 01:48 | 2021-09-06 04:12 | 2203 | 002:24 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE PARTIDO POR ACCIDENTE VEHICULAR Y SE CERRO POR SCADA | S21090600021 | New_Event |  |  | Include | Wildlife | 144 | 2021-09-06 | 317232 | keep | 0 | Sep | 2021 | 0.21607 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2021-09-06 02:24 | 2021-09-06 02:25 | 602 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO POR ACCIDENTE VEHICULAR | S21090600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-06 | 602 | keep | 0 | Sep | 2021 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
MAYAGÃœEZ | 2021-09-06 03:36 | 2021-09-06 13:29 | 25 | 009:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090600085 | New_Event | Bad Weather | Include | Include | Weather | 593 | 2021-09-06 | 14825 | keep | 0 | Sep | 2021 | 0.010097 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
GUAYAMA | 2021-09-06 04:18 | 2021-09-06 09:17 | 20 | 004:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN CORTE DE LINEA POR CONTACTO DE AVE | P21090600005 | New_Event |  |  | Include | Wildlife | 299 | 2021-09-06 | 5980 | keep | 0 | Sep | 2021 | 0.004073 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-06 04:18 | 2021-09-06 09:03 | 1 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 12 NX EN SWITCH UNIT/ NO REPORTAN CAUSA | P21090600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2021-09-06 | 285 | keep | 0 | Sep | 2021 | 0.00019411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-06 04:35 | 2021-09-06 09:17 | 65 | 004:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21090600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2021-09-06 | 18330 | keep | 0 | Sep | 2021 | 0.012484 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-09-06 05:54 | 2021-09-06 05:55 | 2302 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21090600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-06 | 2302 | keep | 0 | Sep | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-09-06 05:55 | 2021-09-06 09:37 | 65 | 003:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21090600011 | 1st_after_momentary |  |  | Include | Wildlife | 222 | 2021-09-06 | 14430 | keep | 0 | Sep | 2021 | 0.0098282 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-09-06 06:14 | 2021-09-06 08:18 | 12 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21090600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-09-06 | 1488 | keep | 0 | Sep | 2021 | 0.0010135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-06 06:57 | 2021-09-06 06:58 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 108 | keep | 0 | Sep | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
FAJARDO | 2021-09-06 07:00 | 2021-09-06 10:45 | 15 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR IGUANA | R21090600002 | New_Event |  |  | Include | Wildlife | 225 | 2021-09-06 | 3375 | keep | 0 | Sep | 2021 | 0.0022987 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-06 07:27 | 2021-09-06 10:40 | 80 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21090600002 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-09-06 | 15440 | keep | 0 | Sep | 2021 | 0.010516 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-06 07:44 | 2021-09-06 13:07 | 50 | 005:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21090600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2021-09-06 | 16150 | keep | 0 | Sep | 2021 | 0.011 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-06 07:49 | 2021-09-06 11:00 | 60 | 003:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21090600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-09-06 | 11460 | keep | 0 | Sep | 2021 | 0.0078054 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-06 07:51 | 2021-09-06 10:30 | 5 | 002:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 37.5 KVA | A21090500049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 159 | 2021-09-06 | 795 | keep | 0 | Sep | 2021 | 0.00054147 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-06 07:59 | 2021-09-06 13:36 | 75 | 005:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA SE REEMPLAZO AISLACION ROTA | A21090600007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 337 | 2021-09-06 | 25275 | keep | 0 | Sep | 2021 | 0.017215 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-09-06 08:36 | 2021-09-06 10:29 | 30 | 001:53 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA PARARRAYO | C21090600023 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 113 | 2021-09-06 | 3390 | keep | 0 | Sep | 2021 | 0.0023089 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-06 08:51 | 2021-09-06 15:44 | 50 | 006:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21090600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2021-09-06 | 20650 | keep | 0 | Sep | 2021 | 0.014065 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-06 08:51 | 2021-09-06 11:02 | 100 | 002:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR CANTACTO DE AVE | P21090600006 | New_Event |  |  | Include | Wildlife | 131 | 2021-09-06 | 13100 | keep | 0 | Sep | 2021 | 0.0089224 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-06 08:52 | 2021-09-06 09:40 | 2 | 000:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 Y 1 X 15 EN TRANSFORMADORES CRUCE POR AVE | R21090600008 | New_Event |  |  | Include | Wildlife | 48 | 2021-09-06 | 96 | keep | 0 | Sep | 2021 | 6.5385e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-09-06 08:53 | 2021-09-06 10:21 | 194 | 001:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO 2 DISCOS | R21090600009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 88 | 2021-09-06 | 17072 | keep | 0 | Sep | 2021 | 0.011628 | 0.00013213 | Sustained | FALSE | TRUE | Not_TMED_Event | 194
SAN JUAN | 2021-09-06 08:54 | 2021-09-06 11:36 | 35 | 002:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S21090600052 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2021-09-06 | 5670 | keep | 0 | Sep | 2021 | 0.0038618 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-09-06 09:00 | 2021-09-06 10:13 | 50 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090500085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2021-09-06 | 3650 | keep | 0 | Sep | 2021 | 0.002486 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-09-06 09:10 | 2021-09-06 09:11 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1839 | keep | 0 | Sep | 2021 | 0.0012525 | 0.0012525 | Momentary | FALSE | TRUE | Not_TMED_Event | 1839
FAJARDO | 2021-09-06 09:10 | 2021-09-06 09:11 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1778 | keep | 0 | Sep | 2021 | 0.001211 | 0.001211 | Momentary | FALSE | TRUE | Not_TMED_Event | 1778
FAJARDO | 2021-09-06 09:10 | 2021-09-06 09:11 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1376 | keep | 0 | Sep | 2021 | 0.00093719 | 0.00093719 | Momentary | FALSE | TRUE | Not_TMED_Event | 1376
HUMACAO | 2021-09-06 09:10 | 2021-09-06 09:11 | 3701 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 3701 | keep | 0 | Sep | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | TRUE | Not_TMED_Event | 3701
HUMACAO | 2021-09-06 09:10 | 2021-09-06 09:11 | 989 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 989 | keep | 0 | Sep | 2021 | 0.0006736 | 0.0006736 | Momentary | FALSE | TRUE | Not_TMED_Event | 989
HUMACAO | 2021-09-06 09:10 | 2021-09-06 09:11 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1467 | keep | 0 | Sep | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
FAJARDO | 2021-09-06 09:10 | 2021-09-06 09:11 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 293 | keep | 0 | Sep | 2021 | 0.00019956 | 0.00019956 | Momentary | FALSE | TRUE | Not_TMED_Event | 293
FAJARDO | 2021-09-06 09:10 | 2021-09-06 09:11 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1215 | keep | 0 | Sep | 2021 | 0.00082753 | 0.00082753 | Momentary | FALSE | TRUE | Not_TMED_Event | 1215
FAJARDO | 2021-09-06 09:48 | 2021-09-06 09:49 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1839 | keep | 0 | Sep | 2021 | 0.0012525 | 0.0012525 | Momentary | FALSE | TRUE | Not_TMED_Event | 1839
FAJARDO | 2021-09-06 09:48 | 2021-09-06 09:49 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1778 | keep | 0 | Sep | 2021 | 0.001211 | 0.001211 | Momentary | FALSE | TRUE | Not_TMED_Event | 1778
FAJARDO | 2021-09-06 09:48 | 2021-09-06 09:49 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1376 | keep | 0 | Sep | 2021 | 0.00093719 | 0.00093719 | Momentary | FALSE | TRUE | Not_TMED_Event | 1376
HUMACAO | 2021-09-06 09:48 | 2021-09-06 09:49 | 3701 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 3701 | keep | 0 | Sep | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | TRUE | Not_TMED_Event | 3701
HUMACAO | 2021-09-06 09:48 | 2021-09-06 09:49 | 989 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 989 | keep | 0 | Sep | 2021 | 0.0006736 | 0.0006736 | Momentary | FALSE | TRUE | Not_TMED_Event | 989
HUMACAO | 2021-09-06 09:48 | 2021-09-06 09:49 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1467 | keep | 0 | Sep | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
FAJARDO | 2021-09-06 09:48 | 2021-09-06 09:49 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 293 | keep | 0 | Sep | 2021 | 0.00019956 | 0.00019956 | Momentary | FALSE | TRUE | Not_TMED_Event | 293
FAJARDO | 2021-09-06 09:48 | 2021-09-06 09:49 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1215 | keep | 0 | Sep | 2021 | 0.00082753 | 0.00082753 | Momentary | FALSE | TRUE | Not_TMED_Event | 1215
FAJARDO | 2021-09-06 10:04 | 2021-09-06 11:11 | 1 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE POR IGUANA | R21090600016 | New_Event |  |  | Include | Wildlife | 67 | 2021-09-06 | 67 | keep | 0 | Sep | 2021 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-09-06 10:15 | 2021-09-06 11:55 | 1 | 001:40 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO | C21090600037 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 100 | 2021-09-06 | 100 | keep | 0 | Sep | 2021 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-06 10:21 | 2021-09-07 10:41 | 1 | 024:20 | P | DESGANCHE | 1 X 30 DE RISER HACIA PM | B21090600013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1460 | 2021-09-06 | 1460 | keep | 0 | Sep | 2021 | 0.0009944 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-06 10:33 | 2021-09-06 10:34 | 1145 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090600038 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-06 | 1145 | keep | 0 | Sep | 2021 | 0.00077985 | 0.00077985 | Momentary | FALSE | FALSE | Not_TMED_Event | 1145
MAYAGÃœEZ | 2021-09-06 10:34 | 2021-09-06 13:20 | 75 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M21090600041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 166 | 2021-09-06 | 12450 | keep | 0 | Sep | 2021 | 0.0084796 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2021-09-06 10:35 | 2021-09-06 18:40 | 30 | 008:05 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA TRABAJOS DE PREPARATIVOS DE FUTURA VIA LIBRE | M21090600035 | New_Event | Other Causes | Include | Include | Other | 485 | 2021-09-06 | 14550 | keep | 0 | Sep | 2021 | 0.0099099 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-09-06 10:57 | 2021-09-06 11:00 | 1839 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 5517 | keep | 0 | Sep | 2021 | 0.0037576 | 0.0012525 | Momentary | FALSE | TRUE | Not_TMED_Event | 1839
FAJARDO | 2021-09-06 10:57 | 2021-09-06 11:00 | 1778 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 5334 | keep | 0 | Sep | 2021 | 0.003633 | 0.001211 | Momentary | FALSE | TRUE | Not_TMED_Event | 1778
FAJARDO | 2021-09-06 10:57 | 2021-09-06 11:00 | 1376 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 4128 | keep | 0 | Sep | 2021 | 0.0028116 | 0.00093719 | Momentary | FALSE | TRUE | Not_TMED_Event | 1376
HUMACAO | 2021-09-06 10:57 | 2021-09-06 11:00 | 3701 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 11103 | keep | 0 | Sep | 2021 | 0.0075622 | 0.0025207 | Momentary | FALSE | TRUE | Not_TMED_Event | 3701
HUMACAO | 2021-09-06 10:57 | 2021-09-06 11:00 | 989 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 2967 | keep | 0 | Sep | 2021 | 0.0020208 | 0.0006736 | Momentary | FALSE | TRUE | Not_TMED_Event | 989
HUMACAO | 2021-09-06 10:57 | 2021-09-06 11:00 | 1467 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21090600043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 4401 | keep | 0 | Sep | 2021 | 0.0029975 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
FAJARDO | 2021-09-06 10:57 | 2021-09-06 11:00 | 293 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 879 | keep | 0 | Sep | 2021 | 0.00059868 | 0.00019956 | Momentary | FALSE | TRUE | Not_TMED_Event | 293
FAJARDO | 2021-09-06 10:57 | 2021-09-06 11:00 | 1215 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A VIEQUES | R21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 3645 | keep | 0 | Sep | 2021 | 0.0024826 | 0.00082753 | Momentary | FALSE | TRUE | Not_TMED_Event | 1215
UTUADO | 2021-09-06 10:58 | 2021-09-06 11:00 | 650 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO LA CAUSA | A21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-06 | 1300 | keep | 0 | Sep | 2021 | 0.00088542 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
ARECIBO | 2021-09-06 11:15 | 2021-09-06 14:29 | 20 | 003:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | A21090600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-09-06 | 3880 | keep | 0 | Sep | 2021 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-06 11:21 | 2021-09-06 11:22 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1717-05 | B21090600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 4533 | keep | 0 | Sep | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
VEGA BAJA | 2021-09-06 11:22 | 2021-09-06 12:11 | 25 | 000:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y DESGANCHE | B21090600018 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2021-09-06 | 1225 | keep | 0 | Sep | 2021 | 0.00083434 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-09-06 11:24 | 2021-09-06 17:15 | 30 | 005:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21090600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2021-09-06 | 10530 | keep | 0 | Sep | 2021 | 0.0071719 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-06 11:25 | 2021-09-06 18:14 | 8 | 006:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE SECUNDARIO Y LEVANTO FASE DE LINEA DE 38 KV FUERA DE SERVICIO | C21090600058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 409 | 2021-09-06 | 3272 | keep | 0 | Sep | 2021 | 0.0022285 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-09-06 11:31 | 2021-09-06 11:32 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1717-05 | B21090600021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 4533 | keep | 0 | Sep | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
SAN JUAN | 2021-09-06 11:34 | 2021-09-06 11:35 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 | S21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 5290 | keep | 0 | Sep | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-09-06 11:34 | 2021-09-06 11:35 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 Y SE CERRO POR SCADA. ADEMAS LA CARGA ESTA POR EL 1336-08 | S21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 207 | keep | 0 | Sep | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2021-09-06 11:38 | 2021-09-07 10:35 | 70 | 022:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1377 | 2021-09-06 | 96390 | keep | 0 | Sep | 2021 | 0.065651 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-06 11:40 | 2021-09-06 12:30 | 60 | 000:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN EL CORTE DE LINEA SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA PRIMARIA QUEMADA | M21090600047 | Additional_clients | Cutout Failure | Include | Include | Equipment | 50 | 2021-09-06 | 3000 | keep | 0 | Sep | 2021 | 0.0020433 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-06 11:47 | 2021-09-06 14:25 | 4 | 002:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO NEUTRAL PRIMARIO Y ABRIO TRANSFORMADOR PARA REGULARLO | C21090600054 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2021-09-06 | 632 | keep | 0 | Sep | 2021 | 0.00043045 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-06 11:51 | 2021-09-06 19:48 | 8 | 007:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21090400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 477 | 2021-09-06 | 3816 | keep | 0 | Sep | 2021 | 0.0025991 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-09-06 11:55 | 2021-09-06 14:23 | 30 | 002:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21090600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-09-06 | 4440 | keep | 0 | Sep | 2021 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-06 11:55 | 2021-09-06 19:25 | 60 | 007:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21090600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 450 | 2021-09-06 | 27000 | keep | 0 | Sep | 2021 | 0.01839 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-09-06 11:55 | 2021-09-06 21:59 | 30 | 010:04 | P | ESTRUCTURA AVERIADA | 2 X 30 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO EN EL FID1000487425 POR POSTE DE 45' DE METAL | M21090600136 | New_Event | Defective Pole | Include | Include | Equipment | 604 | 2021-09-06 | 18120 | keep | 0 | Sep | 2021 | 0.012341 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-06 12:05 | 2021-09-06 15:25 | 75 | 003:20 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21090600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-09-06 | 15000 | keep | 0 | Sep | 2021 | 0.010216 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-09-06 12:11 | 2021-09-06 13:56 | 2216 | 001:45 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES Y SE CERRO INTERRUPTOR | B21090600048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2021-09-06 | 232680 | keep | 0 | Sep | 2021 | 0.15848 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
CAGUAS | 2021-09-06 12:27 | 2021-09-06 12:29 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21090600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-06 | 2002 | keep | 0 | Sep | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
BAYAMON | 2021-09-06 12:34 | 2021-09-06 12:35 | 353 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21090600080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 353 | keep | 0 | Sep | 2021 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2021-09-06 12:36 | 2021-09-06 14:47 | 60 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21090600059 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-09-06 | 7860 | keep | 0 | Sep | 2021 | 0.0053534 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-06 12:37 | 2021-09-06 12:40 | 3701 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | C21090600055 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 11103 | keep | 0 | Sep | 2021 | 0.0075622 | 0.0025207 | Momentary | FALSE | TRUE | Not_TMED_Event | 3701
HUMACAO | 2021-09-06 12:37 | 2021-09-06 12:40 | 989 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | C21090600055 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 2967 | keep | 0 | Sep | 2021 | 0.0020208 | 0.0006736 | Momentary | FALSE | TRUE | Not_TMED_Event | 989
HUMACAO | 2021-09-06 12:37 | 2021-09-06 12:40 | 1467 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | C21090600055 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-06 | 4401 | keep | 0 | Sep | 2021 | 0.0029975 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2021-09-06 12:52 | 2021-09-06 12:53 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-06 12:52 | 2021-09-06 12:53 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-06 12:52 | 2021-09-06 12:53 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-06 12:52 | 2021-09-06 12:53 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 863 | keep | 0 | Sep | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-06 12:52 | 2021-09-06 12:53 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 309 | keep | 0 | Sep | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-06 12:52 | 2021-09-06 12:53 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 176 | keep | 0 | Sep | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-09-06 12:55 | 2021-09-06 17:18 | 70 | 004:23 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M21090600065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-09-06 | 18410 | keep | 0 | Sep | 2021 | 0.012539 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-06 13:00 | 2021-09-07 12:00 | 35 | 023:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M2109070068 | New_Event | Bad Weather | Include | Include | Weather | 1380 | 2021-09-06 | 48300 | keep | 0 | Sep | 2021 | 0.032897 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-09-06 13:04 | 2021-09-06 13:05 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 2608 | keep | 0 | Sep | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
SAN JUAN | 2021-09-06 13:05 | 2021-09-07 16:30 | 1 | 027:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 RVA DE 30 EN SU-5 TERMINACION AVERIADA | R21090600024 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1645 | 2021-09-06 | 1645 | keep | 0 | Sep | 2021 | 0.0011204 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-06 13:05 | 2021-09-06 17:30 | 50 | 004:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21090600069 | New_Event | Bad Weather | Include | Include | Weather | 265 | 2021-09-06 | 13250 | keep | 0 | Sep | 2021 | 0.0090245 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-06 13:07 | 2021-09-06 13:08 | 1533 | 000:01 | T | DESGANCHE | RECERRO | S21090600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-06 | 1533 | keep | 0 | Sep | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-09-06 13:08 | 2021-09-06 14:43 | 50 | 001:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21090600042 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-09-06 | 4750 | keep | 0 | Sep | 2021 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-06 13:08 | 2021-09-06 17:22 | 7 | 004:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO NEUTRAL SECUNDARIO CRUZADO | C21090600072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 254 | 2021-09-06 | 1778 | keep | 0 | Sep | 2021 | 0.001211 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-06 13:08 | 2021-09-06 23:34 | 6 | 010:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M21090600072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 626 | 2021-09-06 | 3756 | keep | 0 | Sep | 2021 | 0.0025582 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-06 13:14 | 2021-09-06 13:15 | 4369 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 4369 | keep | 0 | Sep | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | TRUE | Not_TMED_Event | 4369
CAGUAS | 2021-09-06 13:14 | 2021-09-06 13:15 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 676 | keep | 0 | Sep | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | TRUE | Not_TMED_Event | 676
CAGUAS | 2021-09-06 13:14 | 2021-09-06 13:15 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1606 | keep | 0 | Sep | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | TRUE | Not_TMED_Event | 1606
CAGUAS | 2021-09-06 13:14 | 2021-09-06 13:15 | 725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 725 | keep | 0 | Sep | 2021 | 0.00049379 | 0.00049379 | Momentary | FALSE | TRUE | Not_TMED_Event | 725
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 591 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 591 | keep | 0 | Sep | 2021 | 0.00040253 | 0.00040253 | Momentary | FALSE | TRUE | Not_TMED_Event | 591
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1924 | keep | 0 | Sep | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 968 | keep | 0 | Sep | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 680 | keep | 0 | Sep | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2246 | keep | 0 | Sep | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2011 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2011 | keep | 0 | Sep | 2021 | 0.0013697 | 0.0013697 | Momentary | FALSE | TRUE | Not_TMED_Event | 2011
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 339 | keep | 0 | Sep | 2021 | 0.00023089 | 0.00023089 | Momentary | FALSE | TRUE | Not_TMED_Event | 339
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2470 | keep | 0 | Sep | 2021 | 0.0016823 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1182 | keep | 0 | Sep | 2021 | 0.00080505 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2340 | keep | 0 | Sep | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1637 | keep | 0 | Sep | 2021 | 0.001115 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 1475 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 661 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 661 | keep | 0 | Sep | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1569 | keep | 0 | Sep | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2309 | keep | 0 | Sep | 2021 | 0.0015726 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2440 | keep | 0 | Sep | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 3973 | keep | 0 | Sep | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-09-06 13:14 | 2021-09-06 13:15 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P21090600024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2484 | keep | 0 | Sep | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
CAGUAS | 2021-09-06 13:20 | 2021-09-06 13:21 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 1307 | keep | 0 | Sep | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
AGUADILLA | 2021-09-06 13:24 | 2021-09-06 17:21 | 40 | 003:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21090600078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-09-06 | 9480 | keep | 0 | Sep | 2021 | 0.0064568 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-06 13:25 | 2021-09-06 17:11 | 15 | 003:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | R21090600026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 226 | 2021-09-06 | 3390 | keep | 0 | Sep | 2021 | 0.0023089 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-09-06 13:25 | 2021-09-06 14:02 | 8 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21090500052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-09-06 | 296 | keep | 0 | Sep | 2021 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-06 13:28 | 2021-09-06 13:29 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090600087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 1097 | keep | 0 | Sep | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-09-06 13:29 | 2021-09-06 13:30 | 1417 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21090600091 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-06 | 1417 | keep | 0 | Sep | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-09-06 13:30 | 2021-09-06 20:02 | 25 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090600085 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 392 | 2021-09-06 | 9800 | keep | 0 | Sep | 2021 | 0.0066747 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1339 | keep | 0 | Sep | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 470 | keep | 0 | Sep | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | TRUE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2483 | keep | 0 | Sep | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | TRUE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 2190 | keep | 0 | Sep | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | TRUE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 3006 | keep | 0 | Sep | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | TRUE | Not_TMED_Event | 179
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 107 | keep | 0 | Sep | 2021 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1666 | keep | 0 | Sep | 2021 | 0.0011347 | 0.0011347 | Momentary | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 4387 | keep | 0 | Sep | 2021 | 0.002988 | 0.002988 | Momentary | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-09-06 13:47 | 2021-09-06 13:48 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 4304 | keep | 0 | Sep | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
CANOVANAS | 2021-09-06 13:53 | 2021-09-06 15:13 | 105 | 001:20 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21090600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-09-06 | 8400 | keep | 0 | Sep | 2021 | 0.0057212 | 7.1515e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 105
VEGA BAJA | 2021-09-06 13:56 | 2021-09-06 15:30 | 25 | 001:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y DESGANCHE | B21090600018 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 94 | 2021-09-06 | 2350 | keep | 0 | Sep | 2021 | 0.0016006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-06 13:57 | 2021-09-06 17:30 | 80 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-09-06 | 17040 | keep | 0 | Sep | 2021 | 0.011606 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-06 13:57 | 2021-09-06 19:12 | 7 | 005:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA POR VEHICULO QUE IMPACTO POSTE | M21090600093 | New_Event |  |  | Include | Wildlife | 315 | 2021-09-06 | 2205 | keep | 0 | Sep | 2021 | 0.0015018 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-06 13:58 | 2021-09-06 14:00 | 4533 | 000:02 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1717-05 | B21090600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-09-06 | 9066 | keep | 0 | Sep | 2021 | 0.0061748 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-09-06 13:58 | 2021-09-06 14:00 | 341 | 000:02 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA CARGA TRANSFERIDA AL 1717-01 | B21090600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-09-06 | 682 | keep | 0 | Sep | 2021 | 0.00046451 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
MAYAGÃœEZ | 2021-09-06 14:01 | 2021-09-06 19:40 | 100 | 005:39 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTES DE LINEA SE REALIZO DESGANCHE | M21090600094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-09-06 | 33900 | keep | 0 | Sep | 2021 | 0.023089 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-06 14:03 | 2021-09-06 18:46 | 100 | 004:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21090600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-09-06 | 28300 | keep | 0 | Sep | 2021 | 0.019275 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-06 14:07 | 2021-09-06 16:58 | 10 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21090600083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-09-06 | 1710 | keep | 0 | Sep | 2021 | 0.0011647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-06 14:08 | 2021-09-06 16:25 | 200 | 002:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21090600084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-09-06 | 27400 | keep | 0 | Sep | 2021 | 0.018662 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-06 14:17 | 2021-09-06 14:18 | 4533 | 000:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 1717-05 | B21090600000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-06 | 4533 | keep | 0 | Sep | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-09-06 14:17 | 2021-09-06 14:18 | 341 | 000:01 | T | DESGANCHE | RECIERRE CARGA TRANSFERIDA AL 1717-05 | B21090600000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-06 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
MAYAGÃœEZ | 2021-09-06 14:27 | 2021-09-06 16:38 | 75 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21090600100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-09-06 | 9825 | keep | 0 | Sep | 2021 | 0.0066918 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-06 14:38 | 2021-09-06 15:39 | 36 | 001:01 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21090600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-09-06 | 2196 | keep | 0 | Sep | 2021 | 0.0014957 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
ARECIBO | 2021-09-06 14:55 | 2021-09-06 19:50 | 60 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTE PARA SECCIONALIZAR AVERIA DE LINEA PARTIDA Y SE CERRO CORTE DE LINEA | A21090600050 | New_Event | Wire Down | Include | Include | Equipment | 295 | 2021-09-06 | 17700 | keep | 0 | Sep | 2021 | 0.012055 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-09-06 15:26 | 2021-09-06 15:27 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21090600032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-09-06 15:28 | 2021-09-06 17:08 | 50 | 001:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21090600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2021-09-06 | 5000 | keep | 0 | Sep | 2021 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-06 15:36 | 2021-09-06 17:22 | 15 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21090600110 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-09-06 | 1590 | keep | 0 | Sep | 2021 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-06 15:39 | 2021-09-06 19:23 | 70 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA VIENTO LLUVIA Y DESCARGAS ELECTRICAS | M21090600111 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-09-06 | 15680 | keep | 0 | Sep | 2021 | 0.01068 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-09-06 15:43 | 2021-09-06 17:42 | 50 | 001:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21090600097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-09-06 | 5950 | keep | 0 | Sep | 2021 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-06 15:46 | 2021-09-06 19:44 | 15 | 003:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21090600053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 238 | 2021-09-06 | 3570 | keep | 0 | Sep | 2021 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-06 16:01 | 2021-09-06 16:02 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090600000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-06 16:01 | 2021-09-06 16:02 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO EL 1526-02 DESBALANACE | S21090600000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-06 16:12 | 2021-09-06 18:07 | 8 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21090600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-09-06 | 920 | keep | 0 | Sep | 2021 | 0.00062661 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-06 16:22 | 2021-09-06 16:23 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-06 16:22 | 2021-09-06 16:23 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO EL 1526-02 DESBALANCE | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2021-09-06 16:33 | 2021-09-06 16:35 | 52 | 000:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE | C21090600101 | New_Event |  |  | Include | Wildlife | 2 | 2021-09-06 | 104 | keep | 0 | Sep | 2021 | 7.0834e-05 | 3.5417e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 52
CAGUAS | 2021-09-06 16:35 | 2021-09-06 19:05 | 50 | 002:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21090600102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-09-06 | 7500 | keep | 0 | Sep | 2021 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-06 16:45 | 2021-09-06 22:29 | 70 | 005:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21090600132 | New_Event | Bad Weather | Include | Include | Weather | 344 | 2021-09-06 | 24080 | keep | 0 | Sep | 2021 | 0.016401 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
FAJARDO | 2021-09-06 16:56 | 2021-09-06 17:17 | 40 | 000:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR GLOBO | R21090600036 | New_Event |  |  | Include | Wildlife | 21 | 2021-09-06 | 840 | keep | 0 | Sep | 2021 | 0.00057212 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-06 17:00 | 2021-09-06 18:18 | 10 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | A21090600031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-09-06 | 780 | keep | 0 | Sep | 2021 | 0.00053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-06 17:22 | 2021-09-06 17:23 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 2782 | keep | 0 | Sep | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2021-09-06 17:28 | 2021-09-06 18:54 | 50 | 001:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21090600068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2021-09-06 | 4300 | keep | 0 | Sep | 2021 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-06 17:32 | 2021-09-07 12:46 | 8 | 019:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA CRUZADA | B21090600069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1154 | 2021-09-06 | 9232 | keep | 0 | Sep | 2021 | 0.0062879 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-09-06 17:36 | 2021-09-06 21:24 | 5 | 003:48 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | R21090600037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 228 | 2021-09-06 | 1140 | keep | 0 | Sep | 2021 | 0.00077645 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-06 18:23 | 2021-09-07 10:06 | 140 | 015:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21090600112 | New_Event |  |  | Include | Wildlife | 943 | 2021-09-06 | 132020 | keep | 0 | Sep | 2021 | 0.089918 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
CAGUAS | 2021-09-06 18:26 | 2021-09-06 19:55 | 4 | 001:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C21090600113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-09-06 | 356 | keep | 0 | Sep | 2021 | 0.00024247 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
AGUADILLA | 2021-09-06 18:52 | 2021-09-06 18:53 | 2493 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 2493 | keep | 0 | Sep | 2021 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
ARECIBO | 2021-09-06 18:53 | 2021-09-07 18:00 | 5 | 023:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 50 KVA POR UNO MARCA MOLONEY DE 50KVA A 13.2KV 120/240V SERIE# A3130-5 Y UN POSTE DE 40' METAL EN EL FID19911852 TAMBIEN SE REMPLAZO OTRO POSTE DE METAL 40' EN FID19911842 | A21090600061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1387 | 2021-09-06 | 6935 | keep | 0 | Sep | 2021 | 0.0047234 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-06 18:58 | 2021-09-06 21:20 | 8 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CERRO PUENTE ABIERTO EN TRANSFORMADOR | B21090600071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-09-06 | 1136 | keep | 0 | Sep | 2021 | 0.00077372 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-06 19:44 | 2021-09-06 19:45 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 281 | keep | 0 | Sep | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-06 19:44 | 2021-09-06 19:45 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 1252 | keep | 0 | Sep | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-09-06 19:44 | 2021-09-06 19:45 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 595 | keep | 0 | Sep | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-09-06 19:44 | 2021-09-06 19:45 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 51 | keep | 0 | Sep | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-09-06 19:44 | 2021-09-06 19:45 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21090600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-06 | 721 | keep | 0 | Sep | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-09-06 19:50 | 2021-09-07 19:00 | 20 | 023:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21090600050 | Partial_restoration | Wire Down | Include | Include | Equipment | 1390 | 2021-09-06 | 27800 | keep | 0 | Sep | 2021 | 0.018934 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
FAJARDO | 2021-09-06 20:14 | 2021-09-07 08:42 | 30 | 012:28 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | R21090600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 748 | 2021-09-06 | 22440 | keep | 0 | Sep | 2021 | 0.015284 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-06 21:01 | 2021-09-06 21:02 | 2053 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R21090600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 2053 | keep | 0 | Sep | 2021 | 0.0013983 | 0.0013983 | Momentary | FALSE | FALSE | Not_TMED_Event | 2053
BAYAMON | 2021-09-06 21:22 | 2021-09-06 21:23 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090600000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-06 21:22 | 2021-09-06 21:23 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO EL 1526-02 DESBALANCE | S21090600000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2021-09-06 21:28 | 2021-09-06 21:29 | 418 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21090600165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 418 | keep | 0 | Sep | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
CAGUAS | 2021-09-06 21:33 | 2021-09-07 12:17 | 4 | 014:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C21090600113 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 884 | 2021-09-06 | 3536 | keep | 0 | Sep | 2021 | 0.0024084 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-06 21:40 | 2021-09-07 10:35 | 25 | 012:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090600085 | Partial_restoration | Bad Weather | Include | Include | Weather | 775 | 2021-09-06 | 19375 | keep | 0 | Sep | 2021 | 0.013196 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-06 21:41 | 2021-09-07 11:44 | 50 | 014:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21090600179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 843 | 2021-09-06 | 42150 | keep | 0 | Sep | 2021 | 0.028708 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-06 21:42 | 2021-09-06 21:43 | 418 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21090600165 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 418 | keep | 0 | Sep | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
MAYAGÃœEZ | 2021-09-06 21:42 | 2021-09-07 12:28 | 200 | 014:46 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21090600235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 886 | 2021-09-06 | 177200 | keep | 0 | Sep | 2021 | 0.12069 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-09-06 21:58 | 2021-09-06 21:59 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-09-06 22:00 | 2021-09-07 11:15 | 45 | 013:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090600103 | New_Event | Bad Weather | Include | Include | Weather | 795 | 2021-09-06 | 35775 | keep | 0 | Sep | 2021 | 0.024366 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-09-06 22:09 | 2021-09-07 11:28 | 4 | 013:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTES DEL TRANSFORMADOR Y LINEAS SECUNDARIAS | A21090700030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 799 | 2021-09-06 | 3196 | keep | 0 | Sep | 2021 | 0.0021768 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-09-06 22:21 | 2021-09-06 22:22 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-06 22:21 | 2021-09-06 22:22 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO EL 1526-02 DESBALANCE | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2021-09-06 22:33 | 2021-09-06 22:34 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-06 22:35 | 2021-09-06 22:36 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-06 22:35 | 2021-09-06 22:36 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO EL 1526-02 DESBALANCE | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-06 22:45 | 2021-09-06 22:46 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-06 22:45 | 2021-09-06 22:46 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO EL 1526-02 DESBALANCE | S21090600000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-06 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
MAYAGÃœEZ | 2021-09-06 23:04 | 2021-09-07 10:00 | 85 | 010:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090600265 | New_Event | Bad Weather | Include | Include | Weather | 656 | 2021-09-06 | 55760 | keep | 0 | Sep | 2021 | 0.037978 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
MAYAGÃœEZ | 2021-09-06 23:26 | 2021-09-07 16:20 | 100 | 016:54 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | M21090600268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1014 | 2021-09-06 | 101400 | keep | 0 | Sep | 2021 | 0.069063 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-06 23:34 | 2021-09-07 17:21 | 50 | 017:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21090600270 | New_Event | Bad Weather | Include | Include | Weather | 1067 | 2021-09-06 | 53350 | keep | 0 | Sep | 2021 | 0.036336 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-06 23:57 | 2021-09-06 23:58 | 200 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21090700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-06 | 200 | keep | 0 | Sep | 2021 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-09-06 23:59 | 2021-09-07 13:00 | 50 | 013:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21090600262 | New_Event | Wire Down | Include | Include | Equipment | 781 | 2021-09-06 | 39050 | keep | 0 | Sep | 2021 | 0.026597 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-07 00:10 | 2021-09-07 16:25 | 100 | 016:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21090700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 975 | 2021-09-07 | 97500 | keep | 0 | Sep | 2021 | 0.066407 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-07 00:18 | 2021-09-07 18:03 | 80 | 017:45 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21090700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1065 | 2021-09-07 | 85200 | keep | 0 | Sep | 2021 | 0.058029 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-07 00:18 | 2021-09-07 12:17 | 4 | 011:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON 75 PIES DE SECUNDARIA | C21090700003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 719 | 2021-09-07 | 2876 | keep | 0 | Sep | 2021 | 0.0019588 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-09-07 01:16 | 2021-09-07 11:24 | 100 | 010:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | R21090700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 608 | 2021-09-07 | 60800 | keep | 0 | Sep | 2021 | 0.041411 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-09-07 01:19 | 2021-09-07 13:15 | 450 | 011:56 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA SOBRECARGA EN UNA FASE, SE BALANCEO LAS CARGAS DEL CORTE DE LINEA | A21090700002 | New_Event | Trip Due To Overload | Include | Include | Other | 716 | 2021-09-07 | 322200 | keep | 0 | Sep | 2021 | 0.21945 | 0.00030649 | Sustained | FALSE | TRUE | Not_TMED_Event | 450
SAN JUAN | 2021-09-07 01:41 | 2021-09-07 15:35 | 20 | 013:54 | P | CABLE SOTERRADO AVERIADO | SE DEJO SECCIONALIZADO DE RISER @ T-6 Y SE CERRO N/O DE T-7 @ T-6 | S21090700008 | New_Event | UG Cable Fault | Include | Include | Equipment | 834 | 2021-09-07 | 16680 | keep | 0 | Sep | 2021 | 0.011361 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-07 02:06 | 2021-09-07 02:09 | 1 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1002-01 | S21090800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-07 | 3 | keep | 0 | Sep | 2021 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-07 02:06 | 2021-09-07 02:09 | 47 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1002-01 | S21090800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-07 | 141 | keep | 0 | Sep | 2021 | 9.6034e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2021-09-07 02:06 | 2021-09-07 02:09 | 245 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1002-01 | S21090800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-07 | 735 | keep | 0 | Sep | 2021 | 0.00050061 | 0.00016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 245
BAYAMON | 2021-09-07 02:06 | 2021-09-07 02:09 | 35 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA EL 1001-01, 1001-02 Y EL 101-03 | S21090800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-07 | 105 | keep | 0 | Sep | 2021 | 7.1515e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2021-09-07 03:29 | 2021-09-07 10:18 | 60 | 006:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21090700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2021-09-07 | 24540 | keep | 0 | Sep | 2021 | 0.016714 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-07 03:36 | 2021-09-07 11:20 | 50 | 007:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21090700004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 464 | 2021-09-07 | 23200 | keep | 0 | Sep | 2021 | 0.015801 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-07 04:28 | 2021-09-07 04:29 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-07 | 990 | keep | 0 | Sep | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2021-09-07 04:31 | 2021-09-07 13:20 | 12 | 008:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CULEBRA CRUZO LINEAS | A21090700005 | New_Event |  |  | Include | Wildlife | 529 | 2021-09-07 | 6348 | keep | 0 | Sep | 2021 | 0.0043236 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-09-07 05:14 | 2021-09-07 05:15 | 635 | 000:01 | T | OTRAS CAUSAS | RECIERRE | R21090700000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 635 | keep | 0 | Sep | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2021-09-07 05:15 | 2021-09-07 18:52 | 1 | 013:37 | P | OTRAS CAUSAS | 3 X 10 EN BANCO DE TRANSFORMADORES MAIN BREAKER QUEMADO | R21090700077 | 1st_after_momentary | Other Causes | Include | Include | Other | 817 | 2021-09-07 | 817 | keep | 0 | Sep | 2021 | 0.00055645 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-07 05:17 | 2021-09-07 18:45 | 13 | 013:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA | B21090700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 808 | 2021-09-07 | 10504 | keep | 0 | Sep | 2021 | 0.0071542 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
BAYAMON | 2021-09-07 05:17 | 2021-09-08 10:48 | 25 | 029:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21090700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1771 | 2021-09-07 | 44275 | keep | 0 | Sep | 2021 | 0.030156 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-09-07 05:21 | 2021-09-07 10:10 | 8 | 004:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21090700007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 289 | 2021-09-07 | 2312 | keep | 0 | Sep | 2021 | 0.0015747 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-09-07 05:28 | 2021-09-07 09:12 | 10 | 003:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21090700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2021-09-07 | 2240 | keep | 0 | Sep | 2021 | 0.0015257 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-07 07:06 | 2021-09-07 12:20 | 16 | 005:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090700009 | New_Event | Bad Weather | Include | Include | Weather | 314 | 2021-09-07 | 5024 | keep | 0 | Sep | 2021 | 0.0034218 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-09-07 07:22 | 2021-09-07 12:35 | 25 | 005:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090600021 | New_Event | Bad Weather | Include | Include | Weather | 313 | 2021-09-07 | 7825 | keep | 0 | Sep | 2021 | 0.0053296 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-09-07 07:49 | 2021-09-07 10:20 | 54 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21090700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-09-07 | 8154 | keep | 0 | Sep | 2021 | 0.0055537 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
ARECIBO | 2021-09-07 07:50 | 2021-09-07 11:30 | 8 | 003:40 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21090700013 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 220 | 2021-09-07 | 1760 | keep | 0 | Sep | 2021 | 0.0011987 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-09-07 07:51 | 2021-09-07 15:09 | 40 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2021-09-07 | 17520 | keep | 0 | Sep | 2021 | 0.011933 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-07 08:07 | 2021-09-07 08:08 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
PONCE | 2021-09-07 08:07 | 2021-09-07 17:38 | 100 | 009:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO NO SE REPUSO FUSIBLE | P21090700009 | New_Event | Wire Down | Include | Include | Equipment | 571 | 2021-09-07 | 57100 | keep | 0 | Sep | 2021 | 0.038891 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-09-07 08:09 | 2021-09-07 09:29 | 4 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | FIJO BAJANTE SECUNDARIO NO FUNDIO | R21090700024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-09-07 | 320 | keep | 0 | Sep | 2021 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-09-07 08:09 | 2021-09-07 11:30 | 20 | 003:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21090700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-09-07 | 4020 | keep | 0 | Sep | 2021 | 0.002738 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-09-07 08:28 | 2021-09-07 14:14 | 100 | 005:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | C21090700017 | New_Event | Cutout Failure | Include | Include | Equipment | 346 | 2021-09-07 | 34600 | keep | 0 | Sep | 2021 | 0.023566 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-07 08:28 | 2021-09-07 12:21 | 100 | 003:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M2109070039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-09-07 | 23300 | keep | 0 | Sep | 2021 | 0.01587 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-07 08:33 | 2021-09-07 12:23 | 80 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090700034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2021-09-07 | 18400 | keep | 0 | Sep | 2021 | 0.012532 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-09-07 08:42 | 2021-09-07 10:50 | 12 | 002:08 | P | PARARRAYOS DEFECTUOSO | SE CAMBIARON 2 PARARRAYOS | P21090700012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 128 | 2021-09-07 | 1536 | keep | 0 | Sep | 2021 | 0.0010462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-07 08:49 | 2021-09-08 11:11 | 8 | 026:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090700021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1582 | 2021-09-07 | 12656 | keep | 0 | Sep | 2021 | 0.0086199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-09-07 08:52 | 2021-09-07 14:46 | 100 | 005:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO | A21090700029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 354 | 2021-09-07 | 35400 | keep | 0 | Sep | 2021 | 0.024111 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-09-07 09:04 | 2021-09-07 09:05 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-07 | 5961 | keep | 0 | Sep | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
CANOVANAS | 2021-09-07 09:13 | 2021-09-07 15:42 | 12 | 006:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21090700022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 389 | 2021-09-07 | 4668 | keep | 0 | Sep | 2021 | 0.0031794 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-07 09:25 | 2021-09-07 09:57 | 1 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21090700014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-09-07 | 32 | keep | 0 | Sep | 2021 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-07 09:29 | 2021-09-07 14:28 | 25 | 004:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA FUERTE VIENTO | A21090700032 | New_Event | Bad Weather | Include | Include | Weather | 299 | 2021-09-07 | 7475 | keep | 0 | Sep | 2021 | 0.0050912 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-09-07 09:33 | 2021-09-07 13:49 | 10 | 004:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A TRANSFORMADOR | M21090600140 | New_Event | Wire Down | Include | Include | Equipment | 256 | 2021-09-07 | 2560 | keep | 0 | Sep | 2021 | 0.0017436 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-07 09:46 | 2021-09-07 17:14 | 3 | 007:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | M21090700073 | New_Event | Wire Down | Include | Include | Equipment | 448 | 2021-09-07 | 1344 | keep | 0 | Sep | 2021 | 0.00091539 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2021-09-07 09:51 | 2021-09-07 12:00 | 2 | 002:09 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN BANCO DE TRANSFORMADORES DESGANCHE | R21090700034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 129 | 2021-09-07 | 258 | keep | 0 | Sep | 2021 | 0.00017572 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-09-07 09:58 | 2021-09-07 13:11 | 6 | 003:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZAR BUSHING SECUNDARIO Y REPARAR BAJANTE | C21090700024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 193 | 2021-09-07 | 1158 | keep | 0 | Sep | 2021 | 0.00078871 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-07 10:03 | 2021-09-07 16:30 | 40 | 006:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21090700079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2021-09-07 | 15480 | keep | 0 | Sep | 2021 | 0.010543 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-07 10:06 | 2021-09-07 14:02 | 7 | 003:56 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21090700026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 236 | 2021-09-07 | 1652 | keep | 0 | Sep | 2021 | 0.0011252 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-07 10:10 | 2021-09-07 21:30 | 10 | 011:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 50 X 50KVA | S21090700059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 680 | 2021-09-07 | 6800 | keep | 0 | Sep | 2021 | 0.0046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-07 10:12 | 2021-09-07 10:41 | 1 | 000:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO ENCONTRARON NADA | C21090700028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2021-09-07 | 29 | keep | 0 | Sep | 2021 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-07 10:17 | 2021-09-07 10:18 | 25 | 000:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21090700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-07 | 25 | keep | 0 | Sep | 2021 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-07 10:17 | 2021-09-07 11:15 | 50 | 000:58 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21090700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-09-07 | 2900 | keep | 0 | Sep | 2021 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-07 10:41 | 2021-09-08 15:15 | 30 | 028:34 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 20 EN SU SE DIO MANTENIMIENTO EN SU | B21090700032 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1714 | 2021-09-07 | 51420 | keep | 0 | Sep | 2021 | 0.035022 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-09-07 10:50 | 2021-09-07 12:49 | 12 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE AJUSTARON Y LIMPIARON BARRAS DEL PEDESTAL SECUNDARIO. | P21090700012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-09-07 | 1428 | keep | 0 | Sep | 2021 | 0.0009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-09-07 10:55 | 2021-09-07 13:48 | 8 | 002:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR REPTIL | R21090700044 | New_Event |  |  | Include | Wildlife | 173 | 2021-09-07 | 1384 | keep | 0 | Sep | 2021 | 0.00094264 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
PONCE | 2021-09-07 11:01 | 2021-09-07 12:57 | 10 | 001:56 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR DE 37.5 KVA A UNO DE 50 KVA A 2.4KV | P21090700028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 116 | 2021-09-07 | 1160 | keep | 0 | Sep | 2021 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-07 11:01 | 2021-09-07 14:05 | 10 | 003:04 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE EN LA COLINDANCIA CON LA OTRA REGION POR ESO LA LETRA C DEL EVENTO | A21090700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-09-07 | 1840 | keep | 0 | Sep | 2021 | 0.0012532 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-09-07 11:02 | 2021-09-07 12:50 | 40 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090700044 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-09-07 | 4320 | keep | 0 | Sep | 2021 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-09-07 11:05 | 2021-09-07 14:30 | 50 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21090700046 | New_Event |  |  | Include | Wildlife | 205 | 2021-09-07 | 10250 | keep | 0 | Sep | 2021 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-07 11:06 | 2021-09-08 10:41 | 12 | 023:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANFORMADOR PARA REPARAR SECUNDARIA | S21090600069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1415 | 2021-09-07 | 16980 | keep | 0 | Sep | 2021 | 0.011565 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-07 11:08 | 2021-09-07 17:48 | 10 | 006:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA X 25 KVA | M21090700000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 400 | 2021-09-07 | 4000 | keep | 0 | Sep | 2021 | 0.0027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-07 11:10 | 2021-09-07 16:17 | 30 | 005:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21090700093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-09-07 | 9210 | keep | 0 | Sep | 2021 | 0.0062729 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-09-07 11:12 | 2021-09-07 17:12 | 30 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21090700094 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-09-07 | 10800 | keep | 0 | Sep | 2021 | 0.0073558 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-07 11:15 | 2021-09-07 16:22 | 45 | 005:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REEMPLAZARON DOS CAJAS QUEMADAS | S21090700074 | New_Event | Cutout Failure | Include | Include | Equipment | 307 | 2021-09-07 | 13815 | keep | 0 | Sep | 2021 | 0.0094093 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-09-07 11:21 | 2021-09-07 16:08 | 80 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 60 Y 1 X 100 EN CORTE DE LINEA | M21090700096 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2021-09-07 | 22960 | keep | 0 | Sep | 2021 | 0.015638 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-07 11:29 | 2021-09-08 13:31 | 15 | 026:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090700080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1562 | 2021-09-07 | 23430 | keep | 0 | Sep | 2021 | 0.015958 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-09-07 11:33 | 2021-09-07 13:20 | 2 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090700025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-09-07 | 214 | keep | 0 | Sep | 2021 | 0.00014575 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-09-07 11:53 | 2021-09-07 11:54 | 71 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21090700038 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-07 | 71 | keep | 0 | Sep | 2021 | 4.8358e-05 | 4.8358e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2021-09-07 12:07 | 2021-09-07 18:39 | 50 | 006:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA VECINOS DESGANCHANDO Y SE REMPLAZO CAJA | C21090700041 | New_Event |  |  | Include | Wildlife | 392 | 2021-09-07 | 19600 | keep | 0 | Sep | 2021 | 0.013349 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-07 12:23 | 2021-09-07 12:24 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 12:23 | 2021-09-07 12:24 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-07 12:27 | 2021-09-07 14:34 | 1382 | 002:07 | T | DESGANCHE | SE ABRIO EL AMARRE Y SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 1706-03 Y DEL 1715-03 | B21090700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-09-07 | 175514 | keep | 0 | Sep | 2021 | 0.11954 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-09-07 12:27 | 2021-09-07 17:36 | 663 | 005:09 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO N/O TRANSFIRIENDO SU CARGA AL 1706-02 | B21090700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-09-07 | 204867 | keep | 0 | Sep | 2021 | 0.13953 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-09-07 12:27 | 2021-09-07 14:34 | 74 | 002:07 | T | DESGANCHE | SE ABRIO EL AMARRE Y SE CERRO INTERRUPTOR CARGA TRANSFERIDA AL 1706-02 | B21090700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-09-07 | 9398 | keep | 0 | Sep | 2021 | 0.0064009 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
CAGUAS | 2021-09-07 12:34 | 2021-09-07 17:09 | 6 | 004:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21090700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2021-09-07 | 1650 | keep | 0 | Sep | 2021 | 0.0011238 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-07 12:52 | 2021-09-07 12:53 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 12:52 | 2021-09-07 12:53 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BARRANQUITAS | 2021-09-07 13:07 | 2021-09-07 16:04 | 90 | 002:57 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | C21090700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-09-07 | 15930 | keep | 0 | Sep | 2021 | 0.01085 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BARRANQUITAS | 2021-09-07 13:18 | 2021-09-07 15:22 | 30 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21090700048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-09-07 | 3720 | keep | 0 | Sep | 2021 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-07 13:28 | 2021-09-07 14:30 | 15 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES | M21090700081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2021-09-07 | 930 | keep | 0 | Sep | 2021 | 0.00063342 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-07 13:30 | 2021-09-07 13:31 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 13:30 | 2021-09-07 13:31 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
HUMACAO | 2021-09-07 13:30 | 2021-09-07 15:01 | 9 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090700050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-09-07 | 819 | keep | 0 | Sep | 2021 | 0.00055782 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-09-07 13:34 | 2021-09-07 15:38 | 30 | 002:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A21090700058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-09-07 | 3720 | keep | 0 | Sep | 2021 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-07 13:35 | 2021-09-07 13:38 | 1408 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1714-03 Y SE CERRO POR SCADA LLEVA 1714-02 | B21090700059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-07 | 4224 | keep | 0 | Sep | 2021 | 0.0028769 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-09-07 13:35 | 2021-09-07 13:38 | 455 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA 1714-02 | B21090700059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-07 | 1365 | keep | 0 | Sep | 2021 | 0.0009297 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
MAYAGÃœEZ | 2021-09-07 13:42 | 2021-09-07 14:39 | 1097 | 000:57 | T | DESGANCHE | SE ABRIO INTERRUPTOR SE RETIRO BAMBÃšS SOBRE LINEA | M21090700127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-09-07 | 62529 | keep | 0 | Sep | 2021 | 0.042588 | 0.00074716 | Sustained | FALSE | TRUE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-09-07 14:02 | 2021-09-07 14:03 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-07 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-07 14:02 | 2021-09-07 14:03 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-07 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-07 14:02 | 2021-09-07 14:03 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-07 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
AGUADILLA | 2021-09-07 14:15 | 2021-09-07 15:04 | 150 | 000:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21090700132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2021-09-07 | 7350 | keep | 0 | Sep | 2021 | 0.0050061 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-07 14:15 | 2021-09-07 14:16 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-07 | 4176 | keep | 0 | Sep | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-09-07 14:16 | 2021-09-07 18:33 | 80 | 004:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090700073 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 257 | 2021-09-07 | 20560 | keep | 0 | Sep | 2021 | 0.014003 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-09-07 14:26 | 2021-09-08 15:51 | 30 | 025:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LEVANTO NEUTRAL PRIMARIO | C21090700056 | New_Event | Wire Down | Include | Include | Equipment | 1525 | 2021-09-07 | 45750 | keep | 0 | Sep | 2021 | 0.03116 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-07 14:28 | 2021-09-07 15:51 | 12 | 001:23 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON DERRAME DE 37.5KVA X 37.5KVA | C21090700057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 83 | 2021-09-07 | 996 | keep | 0 | Sep | 2021 | 0.00067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-07 14:30 | 2021-09-07 16:48 | 70 | 002:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21090700144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2021-09-07 | 9660 | keep | 0 | Sep | 2021 | 0.0065794 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-09-07 14:46 | 2021-09-08 12:10 | 80 | 021:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21090700067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1284 | 2021-09-07 | 102720 | keep | 0 | Sep | 2021 | 0.069962 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-07 14:49 | 2021-09-07 15:01 | 40 | 000:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | R21090700054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2021-09-07 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-09-07 14:52 | 2021-09-07 14:53 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 14:52 | 2021-09-07 14:53 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
AGUADILLA | 2021-09-07 14:58 | 2021-09-07 21:24 | 200 | 006:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE | M21090700153 | New_Event | Wire Down | Include | Include | Equipment | 386 | 2021-09-07 | 77200 | keep | 0 | Sep | 2021 | 0.052581 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-07 15:07 | 2021-09-07 16:06 | 1 | 000:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C21090700061 | New_Event |  |  | Include | Wildlife | 59 | 2021-09-07 | 59 | keep | 0 | Sep | 2021 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-09-07 15:11 | 2021-09-07 17:54 | 40 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21090700159 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-09-07 | 6520 | keep | 0 | Sep | 2021 | 0.0044407 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-07 15:13 | 2021-09-08 19:41 | 4 | 028:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y BARRA DE PEDESTAL | C21090700063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1708 | 2021-09-07 | 6832 | keep | 0 | Sep | 2021 | 0.0046532 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-07 15:21 | 2021-09-07 15:22 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
MAYAGÃœEZ | 2021-09-07 15:27 | 2021-09-07 21:29 | 100 | 006:02 | P | DESGANCHE | 3 X 40 Y 3 X 50 EN CORTE DE LINEA | M21090700170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2021-09-07 | 36200 | keep | 0 | Sep | 2021 | 0.024656 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-07 15:29 | 2021-09-07 17:18 | 3025 | 001:49 | T | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO FASE DE LA LINEA 3700 SOBRE LA DISTRIBUCION | C21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-09-07 | 329725 | keep | 0 | Sep | 2021 | 0.22457 | 0.0020603 | Sustained | FALSE | TRUE | Not_TMED_Event | 3025
UTUADO | 2021-09-07 15:31 | 2021-09-07 15:32 | 1241 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21090700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-07 | 1241 | keep | 0 | Sep | 2021 | 0.00084524 | 0.00084524 | Momentary | FALSE | TRUE | Not_TMED_Event | 1241
BAYAMON | 2021-09-07 15:32 | 2021-09-07 15:33 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 15:32 | 2021-09-07 15:33 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-07 15:40 | 2021-09-07 15:41 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 15:40 | 2021-09-07 15:41 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
UTUADO | 2021-09-07 15:41 | 2021-09-07 17:02 | 10 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21090700081 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2021-09-07 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-09-07 15:45 | 2021-09-07 16:55 | 2011 | 001:10 | T | NO SE REPORTO CAUSA | SE CERRO BREAKER NO SE REPORTO CAUSA | P21090700079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-09-07 | 140770 | keep | 0 | Sep | 2021 | 0.095878 | 0.0013697 | Sustained | FALSE | FALSE | Not_TMED_Event | 2011
BAYAMON | 2021-09-07 15:48 | 2021-09-07 15:49 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 15:48 | 2021-09-07 15:49 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
AGUADILLA | 2021-09-07 15:48 | 2021-09-07 23:55 | 200 | 008:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PROTAFUSIBLE AVERIADO | M21090700256 | New_Event | Cutout Failure | Include | Include | Equipment | 487 | 2021-09-07 | 97400 | keep | 0 | Sep | 2021 | 0.066339 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-09-07 15:52 | 2021-09-08 12:40 | 70 | 020:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 50 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P21090700160 | New_Event | Bad Weather | Include | Include | Weather | 1248 | 2021-09-07 | 87360 | keep | 0 | Sep | 2021 | 0.0595 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-09-07 15:56 | 2021-09-07 18:19 | 80 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21090700086 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2021-09-07 | 11440 | keep | 0 | Sep | 2021 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-09-07 15:58 | 2021-09-07 18:39 | 7 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REGULARLO QUEDO EN 124V | C21090700085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2021-09-07 | 1127 | keep | 0 | Sep | 2021 | 0.00076759 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-09-07 15:58 | 2021-09-07 18:36 | 250 | 002:38 | P | DESGANCHE | 4 X 15 EN TRES TRANSFORMADORES DISTINTOS 3 X 50 EN CORTES DE LINEA SE REALIZO DESGANCHE | A21090700088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-09-07 | 39500 | keep | 0 | Sep | 2021 | 0.026903 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
HUMACAO | 2021-09-07 16:04 | 2021-09-07 16:05 | 9 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21090600115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-09-07 | 9 | keep | 0 | Sep | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-09-07 16:07 | 2021-09-07 18:10 | 30 | 002:03 | P | ESTRUCTURA AVERIADA | SE PASO TRANSFORMADOR A POSTE NUEVO METAL 35 CLASE 3 | M21090700189 | New_Event | Defective Pole | Include | Include | Equipment | 123 | 2021-09-07 | 3690 | keep | 0 | Sep | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-07 16:16 | 2021-09-08 15:20 | 50 | 023:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21090700195 | New_Event | Bad Weather | Include | Include | Weather | 1384 | 2021-09-07 | 69200 | keep | 0 | Sep | 2021 | 0.047132 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-07 16:39 | 2021-09-07 18:32 | 30 | 001:53 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | M21090700202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-09-07 | 3390 | keep | 0 | Sep | 2021 | 0.0023089 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-07 16:43 | 2021-09-07 16:44 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSA | P210907000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-07 | 1945 | keep | 0 | Sep | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2021-09-07 16:46 | 2021-09-07 16:47 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 16:46 | 2021-09-07 16:47 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-09-07 16:46 | 2021-09-07 17:51 | 30 | 001:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A21090700058 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-09-07 | 1950 | keep | 0 | Sep | 2021 | 0.0013281 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-07 16:47 | 2021-09-07 17:24 | 40 | 000:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21090700099 | New_Event | Bad Weather | Include | Include | Weather | 37 | 2021-09-07 | 1480 | keep | 0 | Sep | 2021 | 0.001008 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-07 16:48 | 2021-09-07 16:53 | 3718 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21090700181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-07 | 18590 | keep | 0 | Sep | 2021 | 0.012662 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-09-07 16:50 | 2021-09-08 17:20 | 1 | 024:30 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 RVA DE 30 EN SU-5 TERMINACION AVERIADA | R21090600024 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 1470 | 2021-09-07 | 1470 | keep | 0 | Sep | 2021 | 0.0010012 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-07 16:52 | 2021-09-07 20:50 | 7 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A21090700101 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2021-09-07 | 1666 | keep | 0 | Sep | 2021 | 0.0011347 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-07 17:14 | 2021-09-07 18:40 | 90 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA | M21090700213 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-09-07 | 7740 | keep | 0 | Sep | 2021 | 0.0052717 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-09-07 17:16 | 2021-09-07 17:23 | 1891 | 000:07 | S | LINEA DE TRANSMISION 38KV | ABRIERON LINEA 3700 PARA SECCIONALIZAR CONDUCTOR SOBRE LA DISTRIBUCION | C21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-07 | 13237 | keep | 0 | Sep | 2021 | 0.0090157 | 0.001288 | Sustained | FALSE | TRUE | Not_TMED_Event | 1891
HUMACAO | 2021-09-07 17:16 | 2021-09-07 17:23 | 1250 | 000:07 | S | LINEA DE TRANSMISION 38KV | ABRIERON LINEA 3700 PARA SECCIONALIZAR CONDUCTOR SOBRE LA DISTRIBUCION | C21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-07 | 8750 | keep | 0 | Sep | 2021 | 0.0059596 | 0.00085137 | Sustained | FALSE | TRUE | Not_TMED_Event | 1250
HUMACAO | 2021-09-07 17:16 | 2021-09-07 17:23 | 2141 | 000:07 | S | LINEA DE TRANSMISION 38KV | ABRIERON LINEA 3700 PARA SECCIONALIZAR CONDUCTOR SOBRE LA DISTRIBUCION | C21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-07 | 14987 | keep | 0 | Sep | 2021 | 0.010208 | 0.0014582 | Sustained | FALSE | TRUE | Not_TMED_Event | 2141
HUMACAO | 2021-09-07 17:16 | 2021-09-07 17:23 | 1827 | 000:07 | S | LINEA DE TRANSMISION 38KV | ABRIERON LINEA 3700 PARA SECCIONALIZAR CONDUCTOR SOBRE LA DISTRIBUCION | C21090700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-07 | 12789 | keep | 0 | Sep | 2021 | 0.0087105 | 0.0012444 | Sustained | FALSE | TRUE | Not_TMED_Event | 1827
HUMACAO | 2021-09-07 17:18 | 2021-09-07 20:14 | 907 | 002:56 | P | LINEA DE TRANSMISION 38KV | SE LEVANTO FASE DE LA LINEA 3700 QUE ESTABA SOBRE LA DISTRIBUCION | C21090700071 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 176 | 2021-09-07 | 159632 | keep | 0 | Sep | 2021 | 0.10872 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-09-07 17:29 | 2021-09-08 11:55 | 30 | 018:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA REPARO LINEA | P21090800101 | New_Event | Wire Down | Include | Include | Equipment | 1106 | 2021-09-07 | 33180 | keep | 0 | Sep | 2021 | 0.022599 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-07 17:31 | 2021-09-07 20:32 | 80 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090700204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-09-07 | 14480 | keep | 0 | Sep | 2021 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-07 17:38 | 2021-09-08 13:00 | 50 | 019:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21090700107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1162 | 2021-09-07 | 58100 | keep | 0 | Sep | 2021 | 0.039572 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-07 17:42 | 2021-09-07 19:41 | 548 | 001:59 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO POR CONTINGENCIA | C21090700139 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 119 | 2021-09-07 | 65212 | keep | 0 | Sep | 2021 | 0.044416 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
SAN JUAN | 2021-09-07 18:14 | 2021-09-08 08:53 | 15 | 014:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21090600104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 879 | 2021-09-07 | 13185 | keep | 0 | Sep | 2021 | 0.0089802 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-09-07 18:28 | 2021-09-07 19:34 | 4 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090700098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-09-07 | 264 | keep | 0 | Sep | 2021 | 0.00017981 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-09-07 18:33 | 2021-09-07 21:01 | 776 | 002:28 | T | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA AL 2601-02 INTERRUPTOR CON OLOR A QUEMADO | C21090700208 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 148 | 2021-09-07 | 114848 | keep | 0 | Sep | 2021 | 0.078222 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
ARECIBO | 2021-09-07 18:43 | 2021-09-07 21:14 | 50 | 002:31 | P | SOBRECARGA | 1 X 65 EN CORTE DE LINEA CAUSA CARGA | A21090700123 | New_Event | Trip Due To Overload | Include | Include | Other | 151 | 2021-09-07 | 7550 | keep | 0 | Sep | 2021 | 0.0051423 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-07 19:41 | 2021-09-08 18:21 | 52 | 022:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE | C21090600101 | New_Event |  |  | Include | Wildlife | 1360 | 2021-09-07 | 70720 | keep | 0 | Sep | 2021 | 0.048167 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
HUMACAO | 2021-09-07 20:02 | 2021-09-07 20:30 | 1891 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21090700071 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-09-07 | 52948 | keep | 0 | Sep | 2021 | 0.036063 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-07 20:02 | 2021-09-07 20:30 | 1250 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21090700071 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-09-07 | 35000 | keep | 0 | Sep | 2021 | 0.023838 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-07 20:02 | 2021-09-07 20:30 | 2141 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21090700071 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-09-07 | 59948 | keep | 0 | Sep | 2021 | 0.04083 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-07 20:02 | 2021-09-07 20:30 | 1827 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21090700071 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-09-07 | 51156 | keep | 0 | Sep | 2021 | 0.034842 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 2100 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 4200 | keep | 0 | Sep | 2021 | 0.0028606 | 0.0014303 | Momentary | FALSE | TRUE | Not_TMED_Event | 2100
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 922 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 1844 | keep | 0 | Sep | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | TRUE | Not_TMED_Event | 922
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 1676 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 3352 | keep | 0 | Sep | 2021 | 0.002283 | 0.0011415 | Momentary | FALSE | TRUE | Not_TMED_Event | 1676
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 2844 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 5688 | keep | 0 | Sep | 2021 | 0.0038741 | 0.001937 | Momentary | FALSE | TRUE | Not_TMED_Event | 2844
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 2775 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 5550 | keep | 0 | Sep | 2021 | 0.0037801 | 0.00189 | Momentary | FALSE | TRUE | Not_TMED_Event | 2775
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 1457 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 2914 | keep | 0 | Sep | 2021 | 0.0019847 | 0.00099236 | Momentary | FALSE | TRUE | Not_TMED_Event | 1457
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 1086 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 2172 | keep | 0 | Sep | 2021 | 0.0014793 | 0.00073967 | Momentary | FALSE | TRUE | Not_TMED_Event | 1086
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 2134 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 4268 | keep | 0 | Sep | 2021 | 0.0029069 | 0.0014535 | Momentary | FALSE | TRUE | Not_TMED_Event | 2134
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 1464 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 2928 | keep | 0 | Sep | 2021 | 0.0019942 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 1833 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 3666 | keep | 0 | Sep | 2021 | 0.0024969 | 0.0012484 | Momentary | FALSE | TRUE | Not_TMED_Event | 1833
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 3130 | keep | 0 | Sep | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
GUAYAMA | 2021-09-07 20:02 | 2021-09-07 20:04 | 977 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-07 | 1954 | keep | 0 | Sep | 2021 | 0.0013309 | 0.00066543 | Momentary | FALSE | TRUE | Not_TMED_Event | 977
GUAYAMA | 2021-09-07 20:08 | 2021-09-08 07:55 | 47 | 011:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P21090700122 | New_Event |  |  | Include | Wildlife | 707 | 2021-09-07 | 33229 | keep | 0 | Sep | 2021 | 0.022632 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
PONCE | 2021-09-07 20:19 | 2021-09-07 22:50 | 1863 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 281313 | keep | 0 | Sep | 2021 | 0.1916 | 0.0012689 | Sustained | FALSE | TRUE | Not_TMED_Event | 1863
PONCE | 2021-09-07 20:19 | 2021-09-07 22:50 | 708 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 106908 | keep | 0 | Sep | 2021 | 0.072815 | 0.00048222 | Sustained | FALSE | TRUE | Not_TMED_Event | 708
YAUCO | 2021-09-07 20:19 | 2021-09-07 22:50 | 502 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 75802 | keep | 0 | Sep | 2021 | 0.051628 | 0.00034191 | Sustained | FALSE | TRUE | Not_TMED_Event | 502
YAUCO | 2021-09-07 20:19 | 2021-09-07 22:50 | 2747 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 414797 | keep | 0 | Sep | 2021 | 0.28252 | 0.001871 | Sustained | FALSE | TRUE | Not_TMED_Event | 2747
YAUCO | 2021-09-07 20:19 | 2021-09-07 22:50 | 1587 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 239637 | keep | 0 | Sep | 2021 | 0.16322 | 0.0010809 | Sustained | FALSE | TRUE | Not_TMED_Event | 1587
YAUCO | 2021-09-07 20:19 | 2021-09-07 22:50 | 2671 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 403321 | keep | 0 | Sep | 2021 | 0.2747 | 0.0018192 | Sustained | FALSE | TRUE | Not_TMED_Event | 2671
YAUCO | 2021-09-07 20:19 | 2021-09-07 22:50 | 508 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 76708 | keep | 0 | Sep | 2021 | 0.052245 | 0.000346 | Sustained | FALSE | TRUE | Not_TMED_Event | 508
YAUCO | 2021-09-07 20:19 | 2021-09-07 22:50 | 64 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210906000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2021-09-07 | 9664 | keep | 0 | Sep | 2021 | 0.0065821 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
UTUADO | 2021-09-07 20:43 | 2021-09-08 16:10 | 50 | 019:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21090700152 | New_Event | Bad Weather | Include | Include | Weather | 1167 | 2021-09-07 | 58350 | keep | 0 | Sep | 2021 | 0.039742 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-07 20:46 | 2021-09-08 10:55 | 20 | 014:09 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | M21090700244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 849 | 2021-09-07 | 16980 | keep | 0 | Sep | 2021 | 0.011565 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-09-07 20:59 | 2021-09-07 21:01 | 181 | 000:02 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO INTERRUPTOR PARA CERRAR N/O DEL 2601-02 Y 2601-04 QUE TIENE OLOR A QUEMADO | C21090700208 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2021-09-07 | 362 | keep | 0 | Sep | 2021 | 0.00024656 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
ARECIBO | 2021-09-07 21:02 | 2021-09-08 11:05 | 6 | 014:03 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21090700154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 843 | 2021-09-07 | 5058 | keep | 0 | Sep | 2021 | 0.003445 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-07 21:15 | 2021-09-07 21:16 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 21:15 | 2021-09-07 21:16 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-07 21:20 | 2021-09-07 21:22 | 1420 | 000:02 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 2 | 2021-09-07 | 2840 | keep | 0 | Sep | 2021 | 0.0019343 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 21:20 | 2021-09-07 21:21 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
HUMACAO | 2021-09-07 21:26 | 2021-09-08 13:40 | 80 | 016:14 | P | DESGANCHE | DESGANCHO CRUCE POR REPTIL Y LEVANTO CONDUCTOR | C21090700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 974 | 2021-09-07 | 77920 | keep | 0 | Sep | 2021 | 0.053071 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-07 21:26 | 2021-09-08 09:59 | 1491 | 012:33 | T | NO SE REPORTO CAUSA | INTERRUPTOR DA INDICACION DE CERRADO EN SCADA CUANDO SE DISPARA SE CERRO EN LA SUBESTACION | M21090700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 753 | 2021-09-07 | 1122723 | keep | 0 | Sep | 2021 | 0.76468 | 0.0010155 | Sustained | FALSE | FALSE | Not_TMED_Event | 1491
BAYAMON | 2021-09-07 21:31 | 2021-09-07 21:32 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-07 21:31 | 2021-09-07 21:32 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1530-06 QUE A SU VEZ LLEVA LA CARGA DEL 1526-02 DESBALANCE | S21090700000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-07 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-07 21:34 | 2021-09-08 10:12 | 12 | 012:38 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | B21090700170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 758 | 2021-09-07 | 9096 | keep | 0 | Sep | 2021 | 0.0061952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-07 21:41 | 2021-09-07 21:42 | 2720 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21090700156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-07 | 2720 | keep | 0 | Sep | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
CAGUAS | 2021-09-07 21:46 | 2021-09-08 11:33 | 10 | 013:47 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR DESGANCHE | C21090700217 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 827 | 2021-09-07 | 8270 | keep | 0 | Sep | 2021 | 0.0056327 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-07 21:54 | 2021-09-08 17:24 | 60 | 019:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21090700219 | New_Event | Wire Down | Include | Include | Equipment | 1170 | 2021-09-07 | 70200 | keep | 0 | Sep | 2021 | 0.047813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-09-07 21:55 | 2021-09-07 23:31 | 155 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | R21090700107 | New_Event |  |  | Include | Wildlife | 96 | 2021-09-07 | 14880 | keep | 0 | Sep | 2021 | 0.010135 | 0.00010557 | Sustained | FALSE | TRUE | Not_TMED_Event | 155
MAYAGÃœEZ | 2021-09-07 22:00 | 2021-09-08 13:00 | 125 | 015:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA PORTAFUSIBLE QUEMADO | M21090700261 | New_Event | Cutout Failure | Include | Include | Equipment | 900 | 2021-09-07 | 112500 | keep | 0 | Sep | 2021 | 0.076623 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-09-07 22:22 | 2021-09-08 11:28 | 10 | 013:06 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO CAUSA | C21090700226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 786 | 2021-09-07 | 7860 | keep | 0 | Sep | 2021 | 0.0053534 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-07 22:32 | 2021-09-08 10:47 | 50 | 012:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21090700229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 735 | 2021-09-07 | 36750 | keep | 0 | Sep | 2021 | 0.02503 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-07 22:35 | 2021-09-08 12:32 | 100 | 013:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA FIJO FASE | C21090700230 | New_Event | Wire Down | Include | Include | Equipment | 837 | 2021-09-07 | 83700 | keep | 0 | Sep | 2021 | 0.057008 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-07 22:55 | 2021-09-08 11:16 | 55 | 012:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA DEFECTUOSA | S21090700019 | New_Event | Cutout Failure | Include | Include | Equipment | 741 | 2021-09-07 | 40755 | keep | 0 | Sep | 2021 | 0.027758 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-09-07 22:55 | 2021-09-08 11:16 | 55 | 012:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y SE REEMPLAZO CAJA DEFECTUOSA | S21090700019 | New_Event | Cutout Failure | Include | Include | Equipment | 741 | 2021-09-07 | 40755 | keep | 0 | Sep | 2021 | 0.027758 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CAGUAS | 2021-09-07 23:07 | 2021-09-08 09:38 | 200 | 010:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21090700233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 631 | 2021-09-07 | 126200 | keep | 0 | Sep | 2021 | 0.085954 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-07 23:08 | 2021-09-08 11:18 | 100 | 012:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C21090700235 | New_Event | Cutout Failure | Include | Include | Equipment | 730 | 2021-09-07 | 73000 | keep | 0 | Sep | 2021 | 0.04972 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-09-07 23:10 | 2021-09-08 14:27 | 100 | 015:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21090700236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 917 | 2021-09-07 | 91700 | keep | 0 | Sep | 2021 | 0.062456 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-07 23:16 | 2021-09-08 11:33 | 50 | 012:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO PODA | S21090700278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 737 | 2021-09-07 | 36850 | keep | 0 | Sep | 2021 | 0.025098 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-07 23:41 | 2021-09-08 06:45 | 200 | 007:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS SE REMPLAZO CRUCETA Y SE REALIZO DESGANCHE | M21090700273 | New_Event | Wire Down | Include | Include | Equipment | 424 | 2021-09-07 | 84800 | keep | 0 | Sep | 2021 | 0.057757 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-09-08 00:01 | 2021-09-08 10:00 | 4 | 009:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE POR AVE | R21090800001 | New_Event |  |  | Include | Wildlife | 599 | 2021-09-08 | 2396 | keep | 0 | Sep | 2021 | 0.0016319 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-09-08 00:03 | 2021-09-08 06:57 | 65 | 006:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21090800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2021-09-08 | 26910 | keep | 0 | Sep | 2021 | 0.018328 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
GUAYAMA | 2021-09-08 00:26 | 2021-09-08 07:05 | 54 | 006:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REMPLAZO CAJA | P21090800001 | New_Event | Cutout Failure | Include | Include | Equipment | 399 | 2021-09-08 | 21546 | keep | 0 | Sep | 2021 | 0.014675 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
BAYAMON | 2021-09-08 01:02 | 2021-09-08 10:59 | 40 | 009:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 597 | 2021-09-08 | 23880 | keep | 0 | Sep | 2021 | 0.016265 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-08 01:03 | 2021-09-08 08:23 | 20 | 007:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 440 | 2021-09-08 | 8800 | keep | 0 | Sep | 2021 | 0.0059936 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-08 01:24 | 2021-09-08 11:48 | 50 | 010:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 624 | 2021-09-08 | 31200 | keep | 0 | Sep | 2021 | 0.02125 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-08 02:06 | 2021-09-08 02:10 | 948 | 000:04 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR Y SE CERRO POR SCADA | S21090800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-08 | 3792 | keep | 0 | Sep | 2021 | 0.0025827 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
BAYAMON | 2021-09-08 02:07 | 2021-09-08 10:06 | 15 | 007:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21090800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 479 | 2021-09-08 | 7185 | keep | 0 | Sep | 2021 | 0.0048937 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-08 02:53 | 2021-09-08 02:55 | 4702 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-08 | 9404 | keep | 0 | Sep | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-09-08 04:02 | 2021-09-08 10:59 | 90 | 006:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 80 EN OTRO CORTE DE LINEA | B21090800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2021-09-08 | 37530 | keep | 0 | Sep | 2021 | 0.025562 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-09-08 04:23 | 2021-09-08 04:24 | 817 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21090800006 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-08 | 817 | keep | 0 | Sep | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2021-09-08 04:24 | 2021-09-08 16:26 | 10 | 012:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR GLOBO | C21090800108 | 1st_after_momentary |  |  | Include | Wildlife | 722 | 2021-09-08 | 7220 | keep | 0 | Sep | 2021 | 0.0049175 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-09-08 04:42 | 2021-09-08 11:10 | 3 | 006:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21090800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2021-09-08 | 1164 | keep | 0 | Sep | 2021 | 0.0007928 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-09-08 05:00 | 2021-09-08 13:45 | 60 | 008:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21090800011 | New_Event | Bad Weather | Include | Include | Weather | 525 | 2021-09-08 | 31500 | keep | 0 | Sep | 2021 | 0.021455 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-08 05:16 | 2021-09-08 12:32 | 80 | 007:16 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTES DE LINEA Y 1 X 20 EN RISER DE BOMBA DE AAA | C21090800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 436 | 2021-09-08 | 34880 | keep | 0 | Sep | 2021 | 0.023757 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-08 06:22 | 2021-09-08 06:23 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 312 | keep | 0 | Sep | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2021-09-08 06:24 | 2021-09-08 09:55 | 100 | 003:31 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A21090800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-09-08 | 21100 | keep | 0 | Sep | 2021 | 0.014371 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-08 06:46 | 2021-09-08 14:41 | 100 | 007:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA SE INSPECCIONO | R21090800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 475 | 2021-09-08 | 47500 | keep | 0 | Sep | 2021 | 0.032352 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-08 06:47 | 2021-09-08 15:41 | 10 | 008:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21090800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 534 | 2021-09-08 | 5340 | keep | 0 | Sep | 2021 | 0.003637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-08 06:57 | 2021-09-08 06:58 | 2708 | 000:01 | T | DESGANCHE | RECIERRE | R21090800007 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-08 | 2708 | keep | 0 | Sep | 2021 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-08 06:58 | 2021-09-08 09:24 | 65 | 002:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21090800002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-09-08 | 9490 | keep | 0 | Sep | 2021 | 0.0064636 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
UTUADO | 2021-09-08 07:01 | 2021-09-09 20:44 | 30 | 037:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21090800107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2263 | 2021-09-08 | 67890 | keep | 0 | Sep | 2021 | 0.04624 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-08 07:02 | 2021-09-08 09:45 | 75 | 002:43 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTE DE LINEA | P21090800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-09-08 | 12225 | keep | 0 | Sep | 2021 | 0.0083264 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-09-08 07:21 | 2021-09-08 07:22 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2021-09-08 07:26 | 2021-09-08 15:09 | 4 | 007:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21090800019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 463 | 2021-09-08 | 1852 | keep | 0 | Sep | 2021 | 0.0012614 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-08 07:29 | 2021-09-08 13:42 | 60 | 006:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA SE RETIRO IGUANA CRUZANDO LINEAS | B21090800035 | New_Event |  |  | Include | Wildlife | 373 | 2021-09-08 | 22380 | keep | 0 | Sep | 2021 | 0.015243 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-09-08 07:45 | 2021-09-08 11:10 | 30 | 003:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090800036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-09-08 | 6150 | keep | 0 | Sep | 2021 | 0.0041887 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-08 07:53 | 2021-09-08 11:30 | 60 | 003:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21090800026 | New_Event | Bad Weather | Include | Include | Weather | 217 | 2021-09-08 | 13020 | keep | 0 | Sep | 2021 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-08 08:00 | 2021-09-08 14:10 | 1 | 006:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADAS | A21090800079 | New_Event | Cutout Failure | Include | Include | Equipment | 370 | 2021-09-08 | 370 | keep | 0 | Sep | 2021 | 0.00025201 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-08 08:12 | 2021-09-08 10:50 | 50 | 002:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21090800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-09-08 | 7900 | keep | 0 | Sep | 2021 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-08 08:19 | 2021-09-08 11:35 | 7 | 003:16 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21090800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-09-08 | 1372 | keep | 0 | Sep | 2021 | 0.00093446 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-08 08:21 | 2021-09-08 11:35 | 35 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA EN MACHETE | S21090700019 | New_Event | Wire Down | Include | Include | Equipment | 194 | 2021-09-08 | 6790 | keep | 0 | Sep | 2021 | 0.0046246 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-09-08 08:47 | 2021-09-09 10:54 | 1 | 026:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21090800045 | New_Event |  |  | Include | Wildlife | 1567 | 2021-09-08 | 1567 | keep | 0 | Sep | 2021 | 0.0010673 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-08 08:48 | 2021-09-08 17:45 | 154 | 008:57 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTES DE LINEA | C21090800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 537 | 2021-09-08 | 82698 | keep | 0 | Sep | 2021 | 0.056325 | 0.00010489 | Sustained | FALSE | TRUE | Not_TMED_Event | 154
CAGUAS | 2021-09-08 08:51 | 2021-09-08 13:11 | 10 | 004:20 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR CON DERRAME DE 50 KVA X 50 KVA | C21090800028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 260 | 2021-09-08 | 2600 | keep | 0 | Sep | 2021 | 0.0017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-08 08:51 | 2021-09-08 11:45 | 15 | 002:54 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REPARO PARARRAYO CRUZADO | A21090800027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 174 | 2021-09-08 | 2610 | keep | 0 | Sep | 2021 | 0.0017777 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-09-08 08:55 | 2021-09-08 20:13 | 200 | 011:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA | R21090800053 | New_Event | Cutout Failure | Include | Include | Equipment | 678 | 2021-09-08 | 135600 | keep | 0 | Sep | 2021 | 0.092357 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-09-08 08:58 | 2021-09-08 11:01 | 35 | 002:03 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA Y 2 X 15 CORTE DE LINEA | S21090600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-09-08 | 4305 | keep | 0 | Sep | 2021 | 0.0029321 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-09-08 09:44 | 2021-09-08 12:59 | 150 | 003:15 | P | DESGANCHE | 1 X 100 Y 1 X 40 EN CORTES DE LINEA | C21090800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-09-08 | 29250 | keep | 0 | Sep | 2021 | 0.019922 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-09-08 09:50 | 2021-09-08 11:17 | 100 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21090800071 | New_Event |  |  | Include | Wildlife | 87 | 2021-09-08 | 8700 | keep | 0 | Sep | 2021 | 0.0059255 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-08 09:57 | 2021-09-09 13:39 | 20 | 027:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1662 | 2021-09-08 | 33240 | keep | 0 | Sep | 2021 | 0.02264 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-09-08 09:57 | 2021-09-08 19:35 | 75 | 009:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | A21090800039 | New_Event | Wire Down | Include | Include | Equipment | 578 | 2021-09-08 | 43350 | keep | 0 | Sep | 2021 | 0.029525 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-08 10:01 | 2021-09-08 11:30 | 20 | 001:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21090800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-09-08 | 1780 | keep | 0 | Sep | 2021 | 0.0012123 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-08 10:04 | 2021-09-08 13:40 | 10 | 003:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | M21090800068 | New_Event | Bad Weather | Include | Include | Weather | 216 | 2021-09-08 | 2160 | keep | 0 | Sep | 2021 | 0.0014712 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-08 10:05 | 2021-09-15 10:49 | 2 | 168:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE FIJO BAJANTE PRIMARIO SAFADO | P21090800036 | New_Event | Wire Down | Include | Include | Equipment | 10124 | 2021-09-08 | 20248 | keep | 0 | Sep | 2021 | 0.013791 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
AGUADILLA | 2021-09-08 10:48 | 2021-09-08 16:20 | 1 | 005:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DE RISER | M21090800074 | New_Event | Cutout Failure | Include | Include | Equipment | 332 | 2021-09-08 | 332 | keep | 0 | Sep | 2021 | 0.00022612 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-09-08 10:50 | 2021-09-08 15:12 | 50 | 004:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETESO LINEA | P21090800043 | New_Event | Wire Down | Include | Include | Equipment | 262 | 2021-09-08 | 13100 | keep | 0 | Sep | 2021 | 0.0089224 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-08 10:55 | 2021-09-08 15:15 | 9 | 004:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37.5 X 37.5KVA CON ESCAPE DE ACEITE | A21090800044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 260 | 2021-09-08 | 2340 | keep | 0 | Sep | 2021 | 0.0015938 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-09-08 10:56 | 2021-09-08 18:46 | 20 | 007:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA SE REMPLAZO SECUNDARIA QUEMADA | B21090800067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 470 | 2021-09-08 | 9400 | keep | 0 | Sep | 2021 | 0.0064023 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-09-08 10:59 | 2021-09-08 11:01 | 2450 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21090800084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-08 | 4900 | keep | 0 | Sep | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
MAYAGÃœEZ | 2021-09-08 11:02 | 2021-09-09 14:04 | 200 | 027:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO | M21090800085 | New_Event | Bad Weather | Include | Include | Weather | 1622 | 2021-09-08 | 324400 | keep | 0 | Sep | 2021 | 0.22095 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-08 11:04 | 2021-09-09 11:01 | 150 | 023:57 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090800073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1437 | 2021-09-08 | 215550 | keep | 0 | Sep | 2021 | 0.14681 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-09-08 11:17 | 2021-09-08 18:40 | 300 | 007:23 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA X DESGANCHE | P21090800054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 443 | 2021-09-08 | 132900 | keep | 0 | Sep | 2021 | 0.090518 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-09-08 11:18 | 2021-09-08 17:06 | 36 | 005:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON CAJAS PRIMARIAS Y PARARRAYOS EN TRANSFORMADOR TRASPATIO SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | B21090800054 | New_Event | Cutout Failure | Include | Include | Equipment | 348 | 2021-09-08 | 12528 | keep | 0 | Sep | 2021 | 0.0085328 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2021-09-08 11:20 | 2021-09-08 15:50 | 100 | 004:30 | P | HERRAJE ROTO O PODRIDO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CRUCETA PARTIDA | M21090800090 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 270 | 2021-09-08 | 27000 | keep | 0 | Sep | 2021 | 0.01839 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-08 11:21 | 2021-09-08 11:22 | 1825 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR EN PRUEBA CON FUSIBLE EN RISER. SE REPORTA CAJA QUEMADA CARGA POR EL 1118-09 | S21090800000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-08 | 1825 | keep | 0 | Sep | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2021-09-08 11:21 | 2021-09-08 11:22 | 4398 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR EN PRUEBA CON FUSIBLE EN RISER. SE REPORTA CAJA QUEMADA LLEVA EL 118-08 | S21090800000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-08 | 4398 | keep | 0 | Sep | 2021 | 0.0029955 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2021-09-08 11:22 | 2021-09-08 13:46 | 80 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPLAZARON DOS CAJAS QUEMADAS | S21090800055 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 144 | 2021-09-08 | 11520 | keep | 0 | Sep | 2021 | 0.0078462 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-08 11:30 | 2021-09-08 13:40 | 10 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21090800071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-09-08 | 1300 | keep | 0 | Sep | 2021 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-08 11:52 | 2021-09-08 12:05 | 2 | 000:13 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 RISER HACIA SU - D CONTAMINACION | R21090800023 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 13 | 2021-09-08 | 26 | keep | 0 | Sep | 2021 | 1.7708e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-09-08 12:06 | 2021-09-08 15:18 | 120 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 80 EN CORTES DE LINEA CRUCE CON AVE | R21090800025 | New_Event |  |  | Include | Wildlife | 192 | 2021-09-08 | 23040 | keep | 0 | Sep | 2021 | 0.015692 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-09-08 12:08 | 2021-09-08 21:15 | 30 | 009:07 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO | M21090800104 | New_Event | Defective Pole | Include | Include | Equipment | 547 | 2021-09-08 | 16410 | keep | 0 | Sep | 2021 | 0.011177 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-08 12:11 | 2021-09-08 12:12 | 11 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21090800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-08 | 11 | keep | 0 | Sep | 2021 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-09-08 12:12 | 2021-09-09 14:26 | 5 | 026:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | M21090800184 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1574 | 2021-09-08 | 7870 | keep | 0 | Sep | 2021 | 0.0053602 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-08 12:17 | 2021-09-08 16:42 | 20 | 004:25 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE PASO CARGA DE TRANSFORMADOR AVERIADO A EXISTENTE FALTA REMPLAZAR TRANSFORMADOR TODOS EN SERVICIO | B21090800087 | New_Event | Defective Pole | Include | Include | Equipment | 265 | 2021-09-08 | 5300 | keep | 0 | Sep | 2021 | 0.0036098 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-09-08 12:20 | 2021-09-08 12:35 | 1 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | M21090800110 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2021-09-08 | 15 | keep | 0 | Sep | 2021 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-08 12:25 | 2021-09-08 12:40 | 8 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21090800064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-09-08 | 120 | keep | 0 | Sep | 2021 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-08 12:26 | 2021-09-08 12:27 | 2366 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 2366 | keep | 0 | Sep | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2021-09-08 12:34 | 2021-09-08 15:57 | 45 | 003:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | B21090800093 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2021-09-08 | 9135 | keep | 0 | Sep | 2021 | 0.0062218 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-08 12:48 | 2021-09-08 21:03 | 12 | 008:15 | P | ERROR HUMANO | PERSONAL QUE TRABAJO EN AVERIA DIA ANTERIOR DEJO TRANSFORMADOR FUERA AL DEJAR CABLE SOTERRADO ENERGIZADO EN PARKING BUSHING DE TRANSFORMADOR | B21090800097 | New_Event | Human Error | Include | Include | Other | 495 | 2021-09-08 | 5940 | keep | 0 | Sep | 2021 | 0.0040457 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-09-08 12:58 | 2021-09-08 17:00 | 15 | 004:02 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO CLASE#3 35 PIES | M21090800124 | New_Event | Defective Pole | Include | Include | Equipment | 242 | 2021-09-08 | 3630 | keep | 0 | Sep | 2021 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-09-08 13:01 | 2021-09-08 15:51 | 10 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21090800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2021-09-08 | 1700 | keep | 0 | Sep | 2021 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-08 13:08 | 2021-09-08 19:14 | 75 | 006:06 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21090800102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 366 | 2021-09-08 | 27450 | keep | 0 | Sep | 2021 | 0.018696 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-09-08 13:18 | 2021-09-08 13:34 | 10 | 000:16 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA SE INSPECCIONO WR 5929158 | R21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2021-09-08 | 160 | keep | 0 | Sep | 2021 | 0.00010898 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-09-08 13:28 | 2021-09-08 17:25 | 40 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21090800110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2021-09-08 | 9480 | keep | 0 | Sep | 2021 | 0.0064568 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-08 13:33 | 2021-09-08 13:34 | 1394 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21090800000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-08 | 1394 | keep | 0 | Sep | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2021-09-08 13:34 | 2021-09-08 16:19 | 100 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R21090800039 | 1st_after_momentary |  |  | Include | Wildlife | 165 | 2021-09-08 | 16500 | keep | 0 | Sep | 2021 | 0.011238 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-08 13:41 | 2021-09-08 16:22 | 100 | 002:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | R21090800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-09-08 | 16100 | keep | 0 | Sep | 2021 | 0.010966 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-08 13:43 | 2021-09-08 20:50 | 250 | 007:07 | P | NO SE REPORTO CAUSA | 3 X 80 Y 2 X 40 EN CORTES DE LINEAS, TAMBIEN 1 X 10 Y 1 X 8 EN TRANSFORMADORES | C21090800111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 427 | 2021-09-08 | 106750 | keep | 0 | Sep | 2021 | 0.072707 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-09-08 13:47 | 2021-09-08 13:48 | 829 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO EL 60% DE LA CARGA SE ENCUENTRA POR EL 1206-04 | S21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 829 | keep | 0 | Sep | 2021 | 0.00056463 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2021-09-08 13:47 | 2021-09-08 13:48 | 1978 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO EL 40% DE LA CARGA SE ENCUENTRA POR EL 1206-04 | S21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 1978 | keep | 0 | Sep | 2021 | 0.0013472 | 0.0013472 | Momentary | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2021-09-08 13:47 | 2021-09-08 13:48 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 40% DEL 1204-04 Y 60% DEL 1204-03 | S21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 1799 | keep | 0 | Sep | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
CANOVANAS | 2021-09-08 13:55 | 2021-09-08 16:51 | 1 | 002:56 | P | OTRAS CAUSAS | 1 X 20 EN BANCO DE TRANSFORMADORES PROBLEMA DEL CLIENTE | R21090800034 | New_Event | Other Causes | Include | Include | Other | 176 | 2021-09-08 | 176 | keep | 0 | Sep | 2021 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-08 14:04 | 2021-09-08 16:15 | 30 | 002:11 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B21090800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-09-08 | 3930 | keep | 0 | Sep | 2021 | 0.0026767 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-08 14:04 | 2021-09-08 17:01 | 80 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21090800116 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-08 | 14160 | keep | 0 | Sep | 2021 | 0.0096443 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-08 14:09 | 2021-09-08 14:10 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-08 14:09 | 2021-09-08 14:10 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-08 14:14 | 2021-09-08 17:31 | 20 | 003:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B21090800115 | New_Event |  |  | Include | Wildlife | 197 | 2021-09-08 | 3940 | keep | 0 | Sep | 2021 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-08 14:23 | 2021-09-09 16:25 | 20 | 026:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21090800075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1562 | 2021-09-08 | 31240 | keep | 0 | Sep | 2021 | 0.021277 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-08 14:30 | 2021-09-08 17:10 | 4 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR MAL TIEMPO | M21090800145 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-09-08 | 640 | keep | 0 | Sep | 2021 | 0.0004359 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-09-08 14:34 | 2021-09-08 19:34 | 25 | 005:00 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 30 EN AEREOS PROVISIONALES | B21090800119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2021-09-08 | 7500 | keep | 0 | Sep | 2021 | 0.0051082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-08 14:34 | 2021-09-09 11:44 | 120 | 021:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | M21090800149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1270 | 2021-09-08 | 152400 | keep | 0 | Sep | 2021 | 0.1038 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-08 14:39 | 2021-09-08 14:40 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-08 14:39 | 2021-09-08 14:40 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-08 14:40 | 2021-09-08 17:42 | 1 | 003:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN BANCO DE TRANSFORMADORES | B21090800122 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2021-09-08 | 182 | keep | 0 | Sep | 2021 | 0.00012396 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-08 14:55 | 2021-09-09 20:30 | 1 | 029:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | M21090800159 | New_Event | Bad Weather | Include | Include | Weather | 1775 | 2021-09-08 | 1775 | keep | 0 | Sep | 2021 | 0.0012089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-09-08 14:56 | 2021-09-08 20:40 | 100 | 005:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELCTRICAS | A21090800088 | New_Event | Bad Weather | Include | Include | Weather | 344 | 2021-09-08 | 34400 | keep | 0 | Sep | 2021 | 0.02343 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-08 14:58 | 2021-09-10 18:22 | 9 | 051:24 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 37.5 KVA 4160/7200V 120/240V HOWARD INDUSTRIES SER:HI1767091218 | A21090800089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3084 | 2021-09-08 | 27756 | keep | 0 | Sep | 2021 | 0.018904 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2021-09-08 14:59 | 2021-09-08 15:00 | 978 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 978 | keep | 0 | Sep | 2021 | 0.00066611 | 0.00066611 | Momentary | FALSE | TRUE | Not_TMED_Event | 978
PONCE | 2021-09-08 14:59 | 2021-09-08 15:00 | 1730 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1730 | keep | 0 | Sep | 2021 | 0.0011783 | 0.0011783 | Momentary | FALSE | TRUE | Not_TMED_Event | 1730
PONCE | 2021-09-08 14:59 | 2021-09-08 15:00 | 891 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 891 | keep | 0 | Sep | 2021 | 0.00060686 | 0.00060686 | Momentary | FALSE | TRUE | Not_TMED_Event | 891
PONCE | 2021-09-08 14:59 | 2021-09-08 15:00 | 527 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 527 | keep | 0 | Sep | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | TRUE | Not_TMED_Event | 527
PONCE | 2021-09-08 14:59 | 2021-09-08 15:00 | 542 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 542 | keep | 0 | Sep | 2021 | 0.00036915 | 0.00036915 | Momentary | FALSE | TRUE | Not_TMED_Event | 542
CAGUAS | 2021-09-08 15:05 | 2021-09-08 16:02 | 4 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090800129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-09-08 | 228 | keep | 0 | Sep | 2021 | 0.00015529 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-09-08 15:13 | 2021-09-08 15:14 | 1093 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1093 | keep | 0 | Sep | 2021 | 0.00074444 | 0.00074444 | Momentary | FALSE | TRUE | Not_TMED_Event | 1093
PONCE | 2021-09-08 15:13 | 2021-09-08 15:14 | 1067 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1067 | keep | 0 | Sep | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | TRUE | Not_TMED_Event | 1067
PONCE | 2021-09-08 15:13 | 2021-09-08 15:14 | 836 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 836 | keep | 0 | Sep | 2021 | 0.0005694 | 0.0005694 | Momentary | FALSE | TRUE | Not_TMED_Event | 836
PONCE | 2021-09-08 15:13 | 2021-09-08 15:14 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1339 | keep | 0 | Sep | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
PONCE | 2021-09-08 15:13 | 2021-09-08 15:14 | 1295 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1295 | keep | 0 | Sep | 2021 | 0.00088202 | 0.00088202 | Momentary | FALSE | TRUE | Not_TMED_Event | 1295
MAYAGÃœEZ | 2021-09-08 15:13 | 2021-09-08 15:16 | 1253 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21090800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-08 | 3759 | keep | 0 | Sep | 2021 | 0.0025602 | 0.00085341 | Momentary | FALSE | TRUE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2021-09-08 15:13 | 2021-09-08 15:16 | 1266 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21090800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-08 | 3798 | keep | 0 | Sep | 2021 | 0.0025868 | 0.00086227 | Momentary | FALSE | TRUE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-09-08 15:13 | 2021-09-08 15:16 | 411 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21090800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-08 | 1233 | keep | 0 | Sep | 2021 | 0.00083979 | 0.00027993 | Momentary | FALSE | TRUE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-09-08 15:13 | 2021-09-08 15:16 | 108 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21090800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-08 | 324 | keep | 0 | Sep | 2021 | 0.00022067 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
PONCE | 2021-09-08 15:16 | 2021-09-08 15:17 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21090000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2021-09-08 15:19 | 2021-09-08 17:20 | 75 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21090800170 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-09-08 | 9075 | keep | 0 | Sep | 2021 | 0.0061809 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-08 15:27 | 2021-09-08 18:35 | 6285 | 003:08 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115KV SAN SEBASTIAN | M21090800174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 188 | 2021-09-08 | 1181580 | keep | 0 | Sep | 2021 | 0.80477 | 0.0042807 | Sustained | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-09-08 15:27 | 2021-09-08 18:36 | 2225 | 003:09 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115KV SAN SEBASTIAN | M21090800175 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 189 | 2021-09-08 | 420525 | keep | 0 | Sep | 2021 | 0.28642 | 0.0015154 | Sustained | FALSE | FALSE | Not_TMED_Event | 2225
BAYAMON | 2021-09-08 15:28 | 2021-09-08 18:30 | 1420 | 003:02 | T | OTRAS CAUSAS | DISPARO Y SE ENVIO A PATRULLAR NUEVAMENTE. SE COORDINO CON JUAN CARLOS PARA TRANSFERIR MAÃ‘ANA LA CARGA 1526-02 HACIA OTRO ALIMENTADOR PARA IDENTIFICAR MEJOR HACIA DONDE ESTA LA CONDICION. DESBALANCE | S21090800000 | 1st_after_momentary | Other Causes | Include | Include | Other | 182 | 2021-09-08 | 258440 | keep | 0 | Sep | 2021 | 0.17602 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-08 15:28 | 2021-09-08 18:30 | 437 | 003:02 | T | OTRAS CAUSAS | DISPARO Y SE ENVIO A PATRULLAR NUEVAMENTE. SE COORDINO CON JUAN CARLOS PARA TRANSFERIR MAÃ‘ANA LA CARGA 1526-02 HACIA OTRO ALIMENTADOR PARA IDENTIFICAR MEJOR HACIA DONDE ESTA LA CONDICION. DESBALANCE | S21090800000 | 1st_after_momentary | Other Causes | Include | Include | Other | 182 | 2021-09-08 | 79534 | keep | 0 | Sep | 2021 | 0.05417 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
PONCE | 2021-09-08 15:30 | 2021-09-08 15:31 | 1067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210908000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 1067 | keep | 0 | Sep | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2021-09-08 15:35 | 2021-09-08 15:36 | 2751 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210908000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 2751 | keep | 0 | Sep | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
MAYAGÃœEZ | 2021-09-08 15:37 | 2021-09-09 13:20 | 100 | 021:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21090800191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1303 | 2021-09-08 | 130300 | keep | 0 | Sep | 2021 | 0.088747 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-08 15:40 | 2021-09-08 23:40 | 80 | 008:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21090800196 | New_Event | Wire Down | Include | Include | Equipment | 480 | 2021-09-08 | 38400 | keep | 0 | Sep | 2021 | 0.026154 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-09-08 15:41 | 2021-09-08 16:13 | 1 | 000:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CAJAS PRIMARIAS SE DESPEGO CONDUCTOR DE CRUCETA | R21090800043 | New_Event | Wire Down | Include | Include | Equipment | 32 | 2021-09-08 | 32 | keep | 0 | Sep | 2021 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-09-08 15:48 | 2021-09-08 17:23 | 5 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21090800100 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-09-08 | 475 | keep | 0 | Sep | 2021 | 0.00032352 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-09-08 15:50 | 2021-09-08 15:51 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
ARECIBO | 2021-09-08 15:50 | 2021-09-08 18:25 | 75 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21090800102 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-09-08 | 11625 | keep | 0 | Sep | 2021 | 0.0079177 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-09-08 15:56 | 2021-09-08 22:20 | 60 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800103 | New_Event | Bad Weather | Include | Include | Weather | 384 | 2021-09-08 | 23040 | keep | 0 | Sep | 2021 | 0.015692 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-08 15:57 | 2021-09-08 21:35 | 10 | 005:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21090800104 | New_Event | Bad Weather | Include | Include | Weather | 338 | 2021-09-08 | 3380 | keep | 0 | Sep | 2021 | 0.0023021 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-08 15:57 | 2021-09-08 18:43 | 50 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21090800138 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2021-09-08 | 8300 | keep | 0 | Sep | 2021 | 0.0056531 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-08 16:02 | 2021-09-08 16:27 | 5 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIA | C21090800000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-09-08 | 125 | keep | 0 | Sep | 2021 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-09-08 16:03 | 2021-09-08 16:59 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21090800087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-09-08 | 560 | keep | 0 | Sep | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 1924 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPAO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 3848 | keep | 0 | Sep | 2021 | 0.0026209 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 968 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPAO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 1936 | keep | 0 | Sep | 2021 | 0.0013186 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 680 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPAO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 1360 | keep | 0 | Sep | 2021 | 0.00092629 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 2246 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPAO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 4492 | keep | 0 | Sep | 2021 | 0.0030595 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 2470 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 4940 | keep | 0 | Sep | 2021 | 0.0033646 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 1182 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 2364 | keep | 0 | Sep | 2021 | 0.0016101 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 2340 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 4680 | keep | 0 | Sep | 2021 | 0.0031875 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 1637 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 3274 | keep | 0 | Sep | 2021 | 0.0022299 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 1475 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 2950 | keep | 0 | Sep | 2021 | 0.0020092 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 661 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 1322 | keep | 0 | Sep | 2021 | 0.00090041 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 1352 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 2704 | keep | 0 | Sep | 2021 | 0.0018417 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 3973 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 7946 | keep | 0 | Sep | 2021 | 0.005412 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-09-08 16:05 | 2021-09-08 16:07 | 2484 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-08 | 4968 | keep | 0 | Sep | 2021 | 0.0033837 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-09-08 16:16 | 2021-09-09 13:45 | 40 | 021:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21090800228 | New_Event | Bad Weather | Include | Include | Weather | 1289 | 2021-09-08 | 51560 | keep | 0 | Sep | 2021 | 0.035117 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-08 16:18 | 2021-09-09 20:23 | 10 | 028:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 37.5 KVA 4160/7200V 120/240V HOWARD INDUSTRIES SER:HI1809821318 | A21090800107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1685 | 2021-09-08 | 16850 | keep | 0 | Sep | 2021 | 0.011476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-08 16:20 | 2021-09-09 14:12 | 15 | 021:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21090800109 | New_Event | Bad Weather | Include | Include | Weather | 1312 | 2021-09-08 | 19680 | keep | 0 | Sep | 2021 | 0.013404 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-09-08 16:26 | 2021-09-08 22:15 | 80 | 005:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21090800238 | New_Event | Bad Weather | Include | Include | Weather | 349 | 2021-09-08 | 27920 | keep | 0 | Sep | 2021 | 0.019016 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-09-08 16:29 | 2021-09-08 16:30 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1569 | keep | 0 | Sep | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-09-08 16:29 | 2021-09-08 16:30 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2309 | keep | 0 | Sep | 2021 | 0.0015726 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-09-08 16:29 | 2021-09-08 16:30 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-09-08 16:29 | 2021-09-08 16:30 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210908000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2440 | keep | 0 | Sep | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
UTUADO | 2021-09-08 16:31 | 2021-09-08 20:40 | 30 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21090800111 | New_Event | Wire Down | Include | Include | Equipment | 249 | 2021-09-08 | 7470 | keep | 0 | Sep | 2021 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2021-09-08 16:34 | 2021-09-08 16:35 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1924 | keep | 0 | Sep | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-09-08 16:34 | 2021-09-08 16:35 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 968 | keep | 0 | Sep | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-09-08 16:34 | 2021-09-08 16:35 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 680 | keep | 0 | Sep | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-09-08 16:34 | 2021-09-08 16:35 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2246 | keep | 0 | Sep | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
HUMACAO | 2021-09-08 16:36 | 2021-09-08 20:14 | 4 | 003:38 | P | SECUNDARIA/ESTRUCTURA AVERIADA | REMPLAZO BARRA EN PEDESTAL | C21090800142 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 218 | 2021-09-08 | 872 | keep | 0 | Sep | 2021 | 0.00059392 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-08 16:42 | 2021-09-08 18:16 | 30 | 001:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090800149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-09-08 | 2820 | keep | 0 | Sep | 2021 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-08 16:48 | 2021-09-09 18:13 | 30 | 025:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y PUENTE ABIERTO TRASPATIO | S21090800106 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1525 | 2021-09-08 | 45750 | keep | 0 | Sep | 2021 | 0.03116 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-08 16:52 | 2021-09-08 18:18 | 80 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR MAL TIEMPO | M21090800252 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-09-08 | 6880 | keep | 0 | Sep | 2021 | 0.0046859 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-09-08 16:56 | 2021-09-08 19:14 | 30 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21090800148 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-09-08 | 4140 | keep | 0 | Sep | 2021 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-08 16:58 | 2021-09-09 10:20 | 2 | 017:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090800115 | New_Event | Bad Weather | Include | Include | Weather | 1042 | 2021-09-08 | 2084 | keep | 0 | Sep | 2021 | 0.0014194 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2470 | keep | 0 | Sep | 2021 | 0.0016823 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1182 | keep | 0 | Sep | 2021 | 0.00080505 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2340 | keep | 0 | Sep | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1637 | keep | 0 | Sep | 2021 | 0.001115 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 1475 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 661 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 661 | keep | 0 | Sep | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1569 | keep | 0 | Sep | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2309 | keep | 0 | Sep | 2021 | 0.0015726 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-09-08 17:00 | 2021-09-08 17:01 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2440 | keep | 0 | Sep | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
MAYAGÃœEZ | 2021-09-08 17:05 | 2021-09-09 14:50 | 30 | 021:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21090800257 | New_Event | Bad Weather | Include | Include | Weather | 1305 | 2021-09-08 | 39150 | keep | 0 | Sep | 2021 | 0.026665 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-08 17:09 | 2021-09-08 18:47 | 30 | 001:38 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA PODER ELIMINAR PELIGRO DE ARBOL HACIENDO CONTACTO CON LINEAS Y EN FUEGO | B21090800142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-09-08 | 2940 | keep | 0 | Sep | 2021 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-08 17:11 | 2021-09-08 18:40 | 1 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21090800119 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-09-08 | 89 | keep | 0 | Sep | 2021 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-08 17:12 | 2021-09-09 11:50 | 50 | 018:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21090800262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1118 | 2021-09-08 | 55900 | keep | 0 | Sep | 2021 | 0.038073 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-08 17:20 | 2021-09-08 18:04 | 331 | 000:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR AVERIA DE NEUTRAL DEL 1619-03 COLGADO Y CERCA DEL 1618-01 | R21090800049 | New_Event | Wire Down | Include | Include | Equipment | 44 | 2021-09-08 | 14564 | keep | 0 | Sep | 2021 | 0.0099195 | 0.00022544 | Sustained | FALSE | FALSE | Not_TMED_Event | 331
HUMACAO | 2021-09-08 17:21 | 2021-09-09 08:46 | 1 | 015:25 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN BANCO DE TRANSFORMADORES BEJUCOS | C21090800149 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 925 | 2021-09-08 | 925 | keep | 0 | Sep | 2021 | 0.00063001 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-09-08 17:27 | 2021-09-08 17:28 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-09-08 17:27 | 2021-09-08 17:28 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 3973 | keep | 0 | Sep | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-09-08 17:27 | 2021-09-08 17:28 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21090800089 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-08 | 2484 | keep | 0 | Sep | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
UTUADO | 2021-09-08 17:36 | 2021-09-09 14:55 | 50 | 021:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800122 | New_Event | Bad Weather | Include | Include | Weather | 1279 | 2021-09-08 | 63950 | keep | 0 | Sep | 2021 | 0.043556 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-08 17:39 | 2021-09-10 16:23 | 5 | 046:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA 4160/7200V 120/240V SN. HI1723681218 HOWARD INDUSTRIES | A21090800123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2804 | 2021-09-08 | 14020 | keep | 0 | Sep | 2021 | 0.009549 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-09-08 17:40 | 2021-09-09 11:30 | 175 | 017:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21090800125 | New_Event | Cutout Failure | Include | Include | Equipment | 1070 | 2021-09-08 | 187250 | keep | 0 | Sep | 2021 | 0.12754 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
UTUADO | 2021-09-08 17:40 | 2021-09-08 21:55 | 7 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800125 | New_Event | Bad Weather | Include | Include | Weather | 255 | 2021-09-08 | 1785 | keep | 0 | Sep | 2021 | 0.0012158 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
ARECIBO | 2021-09-08 17:45 | 2021-09-08 19:50 | 15 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21090800127 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-09-08 | 1875 | keep | 0 | Sep | 2021 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-09-08 17:47 | 2021-09-08 22:53 | 1 | 005:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800128 | New_Event | Bad Weather | Include | Include | Weather | 306 | 2021-09-08 | 306 | keep | 0 | Sep | 2021 | 0.00020842 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-09-08 18:02 | 2021-09-11 10:05 | 8 | 064:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR REPARO SECUNDARIA | P21090800092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3843 | 2021-09-08 | 30744 | keep | 0 | Sep | 2021 | 0.02094 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-09-08 18:02 | 2021-09-09 11:49 | 52 | 017:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21090800158 | New_Event | Bad Weather | Include | Include | Weather | 1067 | 2021-09-08 | 55484 | keep | 0 | Sep | 2021 | 0.03779 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
SAN JUAN | 2021-09-08 18:04 | 2021-09-09 17:00 | 1 | 022:56 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 RVA DE 30 EN SU-5 TERMINACION AVERIADA | R21090600024 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 1376 | 2021-09-08 | 1376 | keep | 0 | Sep | 2021 | 0.00093719 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-08 18:18 | 2021-09-08 19:35 | 10 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21090800162 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-09-08 | 770 | keep | 0 | Sep | 2021 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-08 18:24 | 2021-09-08 18:26 | 2466 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-08 | 4932 | keep | 0 | Sep | 2021 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
VEGA BAJA | 2021-09-08 18:41 | 2021-09-09 19:26 | 1 | 024:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21090800164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1485 | 2021-09-08 | 1485 | keep | 0 | Sep | 2021 | 0.0010114 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-09-08 18:51 | 2021-09-08 18:52 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210908000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-09-08 19:00 | 2021-09-08 19:01 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL # 10 | P210908000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-08 19:00 | 2021-09-08 19:01 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL # 10 | P210908000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-08 19:00 | 2021-09-08 19:01 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL # 10 | P210908000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
CAGUAS | 2021-09-08 19:02 | 2021-09-08 19:03 | 3005 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | C21090800169 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-08 | 3005 | keep | 0 | Sep | 2021 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2021-09-08 19:07 | 2021-09-08 21:03 | 20 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR SE INSPECCIONO | R21090800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-08 | 2320 | keep | 0 | Sep | 2021 | 0.0015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-08 19:08 | 2021-09-09 12:25 | 30 | 017:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090800133 | New_Event | Bad Weather | Include | Include | Weather | 1037 | 2021-09-08 | 31110 | keep | 0 | Sep | 2021 | 0.021189 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-08 19:19 | 2021-09-08 19:20 | 3957 | 000:01 | T | DESGANCHE | RECERRO | S21090800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-08 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
MAYAGÃœEZ | 2021-09-08 19:20 | 2021-09-09 11:14 | 100 | 015:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21090800312 | New_Event | Bad Weather | Include | Include | Weather | 954 | 2021-09-08 | 95400 | keep | 0 | Sep | 2021 | 0.064977 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-08 19:21 | 2021-09-08 20:36 | 60 | 001:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | S21090800115 | New_Event | Wire Down | Include | Include | Equipment | 75 | 2021-09-08 | 4500 | keep | 0 | Sep | 2021 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-08 19:29 | 2021-09-08 19:30 | 2203 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21090800189 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-08 | 2203 | keep | 0 | Sep | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2021-09-08 19:30 | 2021-09-08 20:33 | 8 | 001:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE CERRO BAJANTE | C21090800209 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 63 | 2021-09-08 | 504 | keep | 0 | Sep | 2021 | 0.00034327 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-08 19:53 | 2021-09-08 20:18 | 30 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21090800171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2021-09-08 | 750 | keep | 0 | Sep | 2021 | 0.00051082 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-08 19:53 | 2021-09-08 19:54 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 2201 | keep | 0 | Sep | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-09-08 19:57 | 2021-09-09 10:30 | 20 | 014:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090800135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 873 | 2021-09-08 | 17460 | keep | 0 | Sep | 2021 | 0.011892 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-08 20:01 | 2021-09-08 20:02 | 1070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-08 | 1070 | keep | 0 | Sep | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
CAGUAS | 2021-09-08 20:04 | 2021-09-08 20:05 | 2276 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21090800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-08 | 2276 | keep | 0 | Sep | 2021 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2021-09-08 20:05 | 2021-09-09 01:00 | 300 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REEMPLAZARON CAJAS PRIMARIAS Y BAJANTES QUEMADOS POR AVERIA DE CONDUCTOR ROTO DEL 3006-05 SOBRE EL 3014-01 Y SE CERRO EL CORTE DE LINEA | C21090800237 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 295 | 2021-09-08 | 88500 | keep | 0 | Sep | 2021 | 0.060277 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-09-08 20:19 | 2021-09-08 20:20 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | Partial_restoration | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-08 20:19 | 2021-09-08 20:20 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | Partial_restoration | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-08 20:23 | 2021-09-10 13:00 | 8 | 040:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA | A21090800136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2437 | 2021-09-08 | 19496 | keep | 0 | Sep | 2021 | 0.013279 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-08 20:29 | 2021-09-08 22:30 | 3957 | 002:01 | T | DESGANCHE | SE RETIRO RAMA CRUZANDO FASE EN LA CARRETERA 873 FRENTE A URBANIZACION ALBERNIA SE CERRO POR CONTROL Y QUEDO EN SERVICIO 100% | S21090800121 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-09-08 | 478797 | keep | 0 | Sep | 2021 | 0.32611 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
VEGA BAJA | 2021-09-08 20:29 | 2021-09-09 10:49 | 80 | 014:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090800180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2021-09-08 | 68800 | keep | 0 | Sep | 2021 | 0.046859 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-08 20:33 | 2021-09-08 20:34 | 2203 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21090800189 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-08 | 2203 | keep | 0 | Sep | 2021 | 0.0015005 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-08 20:34 | 2021-09-09 13:32 | 8 | 016:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE CERRO BAJANTE | C21090800209 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1018 | 2021-09-08 | 8144 | keep | 0 | Sep | 2021 | 0.0055468 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-08 20:52 | 2021-09-08 21:17 | 3005 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C21090800225 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 25 | 2021-09-08 | 75125 | keep | 0 | Sep | 2021 | 0.051167 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
BAYAMON | 2021-09-08 21:01 | 2021-09-08 21:02 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-08 21:01 | 2021-09-08 21:02 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 DESBALANCE | S21090800000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-08 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-08 21:14 | 2021-09-09 11:15 | 20 | 014:01 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21090800139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 841 | 2021-09-08 | 16820 | keep | 0 | Sep | 2021 | 0.011456 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-08 21:17 | 2021-09-09 01:00 | 1349 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO MACHETES | C21090800225 | Partial_restoration | Wire Down | Include | Include | Equipment | 223 | 2021-09-08 | 300827 | keep | 0 | Sep | 2021 | 0.20489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-08 21:17 | 2021-09-09 08:43 | 1701 | 011:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTELLIRRUPTER 3006-05D CERRADO EN EL CAMPO | C21090800225 | New_Event | Wire Down | Include | Include | Equipment | 686 | 2021-09-08 | 1166886 | keep | 0 | Sep | 2021 | 0.79476 | 0.0011585 | Sustained | FALSE | FALSE | Not_TMED_Event | 1701
BAYAMON | 2021-09-08 21:32 | 2021-09-09 14:05 | 100 | 016:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 40 EN CORTES DE LINEA | B21090800189 | New_Event |  |  | Include | Wildlife | 993 | 2021-09-08 | 99300 | keep | 0 | Sep | 2021 | 0.067633 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-08 21:38 | 2021-09-09 13:30 | 20 | 015:52 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21090800353 | New_Event | Bad Weather | Include | Include | Weather | 952 | 2021-09-08 | 19040 | keep | 0 | Sep | 2021 | 0.012968 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-08 21:56 | 2021-09-09 12:54 | 76 | 014:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21090800246 | New_Event | Bad Weather | Include | Include | Weather | 898 | 2021-09-08 | 68248 | keep | 0 | Sep | 2021 | 0.046483 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
ARECIBO | 2021-09-08 22:03 | 2021-09-09 11:30 | 65 | 013:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21090800144 | New_Event | Cutout Failure | Include | Include | Equipment | 807 | 2021-09-08 | 52455 | keep | 0 | Sep | 2021 | 0.035727 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BARRANQUITAS | 2021-09-08 22:41 | 2021-09-09 13:19 | 25 | 014:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21090800254 | New_Event | Bad Weather | Include | Include | Weather | 878 | 2021-09-08 | 21950 | keep | 0 | Sep | 2021 | 0.01495 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-09 00:46 | 2021-09-10 09:31 | 80 | 032:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA Y SE REPORTA AVERIA POR DESGANCHE | S21091000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1965 | 2021-09-09 | 157200 | keep | 0 | Sep | 2021 | 0.10707 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-09 00:52 | 2021-09-09 00:53 | 325 | 000:01 | T | DESGANCHE | RECERRO | B21090900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-09 | 325 | keep | 0 | Sep | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-09-09 00:56 | 2021-09-09 00:57 | 325 | 000:01 | T | DESGANCHE | RECERRO | B21090900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-09 | 325 | keep | 0 | Sep | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-09-09 00:58 | 2021-09-09 00:59 | 325 | 000:01 | T | DESGANCHE | RECERRO | B21090900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-09 | 325 | keep | 0 | Sep | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-09-09 00:59 | 2021-09-09 01:00 | 325 | 000:01 | T | DESGANCHE | RECERRO | B21090900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-09 | 325 | keep | 0 | Sep | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-09-09 01:00 | 2021-09-09 13:10 | 325 | 012:10 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | B21090900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 730 | 2021-09-09 | 237250 | keep | 0 | Sep | 2021 | 0.16159 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
FAJARDO | 2021-09-09 01:39 | 2021-09-09 09:32 | 55 | 007:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO DISCO PARTIDO | R21090900001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 473 | 2021-09-09 | 26015 | keep | 0 | Sep | 2021 | 0.017719 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
HUMACAO | 2021-09-09 01:43 | 2021-09-09 11:07 | 42 | 009:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21090900005 | New_Event | Cutout Failure | Include | Include | Equipment | 564 | 2021-09-09 | 23688 | keep | 0 | Sep | 2021 | 0.016134 | 2.8606e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 42
CAGUAS | 2021-09-09 03:20 | 2021-09-09 03:21 | 1922 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1922 | keep | 0 | Sep | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
BAYAMON | 2021-09-09 03:24 | 2021-09-09 09:21 | 1501 | 005:57 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | B21090900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-09-09 | 535857 | keep | 0 | Sep | 2021 | 0.36497 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
VEGA BAJA | 2021-09-09 04:12 | 2021-09-09 09:49 | 80 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2021-09-09 | 26960 | keep | 0 | Sep | 2021 | 0.018362 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-09 04:17 | 2021-09-09 11:30 | 200 | 007:13 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | M21090900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2021-09-09 | 86600 | keep | 0 | Sep | 2021 | 0.058983 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-09 05:37 | 2021-09-09 11:48 | 40 | 006:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2021-09-09 | 14840 | keep | 0 | Sep | 2021 | 0.010107 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-09 06:03 | 2021-09-09 10:15 | 20 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090900004 | New_Event | Bad Weather | Include | Include | Weather | 252 | 2021-09-09 | 5040 | keep | 0 | Sep | 2021 | 0.0034327 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-09 06:39 | 2021-09-09 06:40 | 817 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21090900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 817 | keep | 0 | Sep | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
SAN JUAN | 2021-09-09 07:11 | 2021-09-09 13:04 | 25 | 005:53 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA | S21090800013 | New_Event | Other Causes | Include | Include | Other | 353 | 2021-09-09 | 8825 | keep | 0 | Sep | 2021 | 0.0060107 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-09-09 07:52 | 2021-09-09 07:53 | 7621 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | R21090900000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-09 | 7621 | keep | 0 | Sep | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2021-09-09 07:53 | 2021-09-09 11:45 | 148 | 003:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CAMION IMPACTO ALAMBRES | R21090900007 | 1st_after_momentary |  |  | Include | Wildlife | 232 | 2021-09-09 | 34336 | keep | 0 | Sep | 2021 | 0.023386 | 0.0001008 | Sustained | FALSE | TRUE | Not_TMED_Event | 148
MAYAGÃœEZ | 2021-09-09 07:53 | 2021-09-09 14:55 | 100 | 007:02 | P | HERRAJE ROTO O PODRIDO | 2 X 100 EN CORTE DE LINEA SE REMPLAZARON CRUCETAS | M21090900022 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 422 | 2021-09-09 | 42200 | keep | 0 | Sep | 2021 | 0.028742 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-09 08:09 | 2021-09-09 21:10 | 200 | 013:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21090900024 | New_Event | Wire Down | Include | Include | Equipment | 781 | 2021-09-09 | 156200 | keep | 0 | Sep | 2021 | 0.10639 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-09-09 08:18 | 2021-09-09 10:38 | 1 | 002:20 | P | SOBRECARGA | 1 X 40 EN CORTE DE LINEA POR CARGA | R21090900004 | New_Event | Trip Due To Overload | Include | Include | Other | 140 | 2021-09-09 | 140 | keep | 0 | Sep | 2021 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-09 08:18 | 2021-09-09 16:07 | 7 | 007:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO BAJANTE SECUNDARIO | C21090900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 469 | 2021-09-09 | 3283 | keep | 0 | Sep | 2021 | 0.002236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-09 08:28 | 2021-09-09 14:49 | 100 | 006:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090900023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2021-09-09 | 38100 | keep | 0 | Sep | 2021 | 0.02595 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-09 08:39 | 2021-09-09 16:34 | 50 | 007:55 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO DEFECTUOSO | P21090900003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 475 | 2021-09-09 | 23750 | keep | 0 | Sep | 2021 | 0.016176 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-09 08:41 | 2021-09-09 17:00 | 100 | 008:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21090900040 | New_Event | Bad Weather | Include | Include | Weather | 499 | 2021-09-09 | 49900 | keep | 0 | Sep | 2021 | 0.033987 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-09-09 08:46 | 2021-09-09 12:00 | 20 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR CRUCE DE FASES POR AVE | P21090900004 | New_Event |  |  | Include | Wildlife | 194 | 2021-09-09 | 3880 | keep | 0 | Sep | 2021 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-09 09:10 | 2021-09-09 14:16 | 30 | 005:06 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21090900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2021-09-09 | 9180 | keep | 0 | Sep | 2021 | 0.0062525 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-09 09:14 | 2021-09-09 18:57 | 50 | 009:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21090900022 | New_Event | Wire Down | Include | Include | Equipment | 583 | 2021-09-09 | 29150 | keep | 0 | Sep | 2021 | 0.019854 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-09 09:20 | 2021-09-09 14:34 | 30 | 005:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21090900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-09-09 | 9420 | keep | 0 | Sep | 2021 | 0.0064159 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-09 09:21 | 2021-09-09 10:30 | 750 | 001:09 | P | DESGANCHE | SE SECCIONALIZO EN CARR. 174 Y SE CERRO MACHETES EN LOMAS VERDES | B21090900006 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-09-09 | 51750 | keep | 0 | Sep | 2021 | 0.035247 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-09 09:32 | 2021-09-09 20:49 | 35 | 011:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S21090900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 677 | 2021-09-09 | 23695 | keep | 0 | Sep | 2021 | 0.016139 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-09-09 09:34 | 2021-09-09 19:15 | 20 | 009:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO NO FUNDIO | B21090900023 | New_Event | Wire Down | Include | Include | Equipment | 581 | 2021-09-09 | 11620 | keep | 0 | Sep | 2021 | 0.0079143 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-09 09:43 | 2021-09-09 18:28 | 200 | 008:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP Y AISLADOR | R21090900007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 525 | 2021-09-09 | 105000 | keep | 0 | Sep | 2021 | 0.071515 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-09 09:57 | 2021-09-09 14:03 | 31 | 004:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21090900032 | New_Event |  |  | Include | Wildlife | 246 | 2021-09-09 | 7626 | keep | 0 | Sep | 2021 | 0.005194 | 2.1114e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 31
PONCE | 2021-09-09 09:59 | 2021-09-10 17:02 | 200 | 031:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P21090900015 | New_Event | Wire Down | Include | Include | Equipment | 1863 | 2021-09-09 | 372600 | keep | 0 | Sep | 2021 | 0.25378 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-09-09 10:26 | 2021-09-09 10:54 | 44 | 000:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21090900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2021-09-09 | 1232 | keep | 0 | Sep | 2021 | 0.00083911 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
BAYAMON | 2021-09-09 10:30 | 2021-09-09 11:34 | 300 | 001:04 | P | DESGANCHE | SE DESGANCHO Y SE CERRO EN CARR. 174 MACHETES | B21090900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-09-09 | 19200 | keep | 0 | Sep | 2021 | 0.013077 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-09-09 10:35 | 2021-09-09 18:52 | 11 | 008:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21090900010 | New_Event |  |  | Include | Wildlife | 497 | 2021-09-09 | 5467 | keep | 0 | Sep | 2021 | 0.0037235 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2021-09-09 10:35 | 2021-09-09 18:00 | 1 | 007:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21090900036 | New_Event | Wire Down | Include | Include | Equipment | 445 | 2021-09-09 | 445 | keep | 0 | Sep | 2021 | 0.00030309 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-09-09 11:08 | 2021-09-09 16:30 | 20 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON LINEAS PRIMARIAS CRUZADAS | A21090900040 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2021-09-09 | 6440 | keep | 0 | Sep | 2021 | 0.0043863 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-09 11:10 | 2021-09-09 22:30 | 15 | 011:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M21090900112 | New_Event | Cutout Failure | Include | Include | Equipment | 680 | 2021-09-09 | 10200 | keep | 0 | Sep | 2021 | 0.0069472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-09 11:11 | 2021-09-09 13:10 | 2926 | 001:59 | T | DESGANCHE | SE ABRIO PARA REALIZAR DESGANCHE EN 9206-10 | B21090900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-09-09 | 348194 | keep | 0 | Sep | 2021 | 0.23715 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
ARECIBO | 2021-09-09 11:20 | 2021-09-09 12:30 | 6 | 001:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 KVA X 37.5 KVA CON ESCAPE DE ACEITE | A21090900042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 70 | 2021-09-09 | 420 | keep | 0 | Sep | 2021 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-09 11:27 | 2021-09-09 17:10 | 80 | 005:43 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21090900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2021-09-09 | 27440 | keep | 0 | Sep | 2021 | 0.018689 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-09 11:28 | 2021-09-09 17:52 | 40 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P21090900025 | New_Event | Bad Weather | Include | Include | Weather | 384 | 2021-09-09 | 15360 | keep | 0 | Sep | 2021 | 0.010462 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-09 11:31 | 2021-09-09 13:48 | 18 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21090900044 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-09-09 | 2466 | keep | 0 | Sep | 2021 | 0.0016796 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
ARECIBO | 2021-09-09 11:49 | 2021-09-09 16:15 | 75 | 004:26 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A21090900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-09-09 | 19950 | keep | 0 | Sep | 2021 | 0.013588 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-09 11:50 | 2021-09-09 14:40 | 20 | 002:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LA LINEA PRIMARIA | A21090900052 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-09-09 | 3400 | keep | 0 | Sep | 2021 | 0.0023157 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-09-09 11:52 | 2021-09-09 12:28 | 1 | 000:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN BANCO DE TRANSFORMADORES SE ELIMINO TENSOR | R21090900015 | New_Event |  |  | Include | Wildlife | 36 | 2021-09-09 | 36 | keep | 0 | Sep | 2021 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-09 11:55 | 2021-09-09 11:56 | 3157 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-09 | 3157 | keep | 0 | Sep | 2021 | 0.0021502 | 0.0021502 | Momentary | FALSE | TRUE | Not_TMED_Event | 3157
ARECIBO | 2021-09-09 11:55 | 2021-09-09 11:56 | 35 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-09 | 35 | keep | 0 | Sep | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-09 11:55 | 2021-09-09 11:56 | 2916 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-09 | 2916 | keep | 0 | Sep | 2021 | 0.0019861 | 0.0019861 | Momentary | FALSE | TRUE | Not_TMED_Event | 2916
FAJARDO | 2021-09-09 12:00 | 2021-09-09 14:29 | 12 | 002:29 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | R21090900016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-09-09 | 1788 | keep | 0 | Sep | 2021 | 0.0012178 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
ARECIBO | 2021-09-09 12:08 | 2021-09-09 17:26 | 70 | 005:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21090900056 | New_Event | Bad Weather | Include | Include | Weather | 318 | 2021-09-09 | 22260 | keep | 0 | Sep | 2021 | 0.015161 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-09 12:17 | 2021-09-09 15:45 | 200 | 003:28 | P | DESGANCHE | 1 X 100, 1 X 80 EN CORTE DE LINEA DESGANCHE | M21090900147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-09-09 | 41600 | keep | 0 | Sep | 2021 | 0.028334 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-09 12:17 | 2021-09-09 15:03 | 45 | 002:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090900087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-09-09 | 7470 | keep | 0 | Sep | 2021 | 0.0050878 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-09-09 12:24 | 2021-09-10 16:35 | 3 | 028:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA 100AMP. HOOVER FID: 18407772 | M21090900149 | New_Event | Cutout Failure | Include | Include | Equipment | 1691 | 2021-09-09 | 5073 | keep | 0 | Sep | 2021 | 0.0034552 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-09-09 12:27 | 2021-09-09 19:06 | 12 | 006:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21090800093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 399 | 2021-09-09 | 4788 | keep | 0 | Sep | 2021 | 0.0032611 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-09-09 12:43 | 2021-09-09 22:33 | 100 | 009:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21090900160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 590 | 2021-09-09 | 59000 | keep | 0 | Sep | 2021 | 0.040185 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-09 12:50 | 2021-09-09 18:55 | 10 | 006:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | S21090900037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 365 | 2021-09-09 | 3650 | keep | 0 | Sep | 2021 | 0.002486 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-09-09 12:51 | 2021-09-09 14:36 | 500 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN CORTE DE LINEA SECUNDARIA SE CRUZO CON LA PRIMARIA | R21090900023 | New_Event | Wire Down | Include | Include | Equipment | 105 | 2021-09-09 | 52500 | keep | 0 | Sep | 2021 | 0.035758 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
UTUADO | 2021-09-09 12:55 | 2021-09-09 21:46 | 20 | 008:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LA LINEA | A21090900064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 531 | 2021-09-09 | 10620 | keep | 0 | Sep | 2021 | 0.0072332 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-09 12:57 | 2021-09-09 16:03 | 1320 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 100 | P21090900038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-09 | 245520 | keep | 0 | Sep | 2021 | 0.16722 | 0.00089905 | Sustained | FALSE | TRUE | Not_TMED_Event | 1320
PONCE | 2021-09-09 12:57 | 2021-09-09 16:03 | 274 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 100 | P21090900038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-09 | 50964 | keep | 0 | Sep | 2021 | 0.034711 | 0.00018662 | Sustained | FALSE | TRUE | Not_TMED_Event | 274
CAGUAS | 2021-09-09 12:59 | 2021-09-10 12:59 | 6 | 024:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y 2 TOMAS | C21090900051 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1440 | 2021-09-09 | 8640 | keep | 0 | Sep | 2021 | 0.0058847 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-09-09 13:10 | 2021-09-09 18:48 | 40 | 005:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090900066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2021-09-09 | 13520 | keep | 0 | Sep | 2021 | 0.0092084 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-09 13:10 | 2021-09-09 13:12 | 165 | 000:02 | P | DESGANCHE | HACIENDO OPERACIONES DISPARO | B21090900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-09-09 | 330 | keep | 0 | Sep | 2021 | 0.00022476 | 0.00011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 165
VEGA BAJA | 2021-09-09 13:12 | 2021-09-09 13:23 | 325 | 000:11 | T | DESGANCHE | SE REALIZO DESGANCHE SE SECCIONALIZO Y SE CERRO POR SCADA | B21090900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 11 | 2021-09-09 | 3575 | keep | 0 | Sep | 2021 | 0.0024349 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2021-09-09 13:14 | 2021-09-09 21:39 | 65 | 008:25 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B21090900073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 505 | 2021-09-09 | 32825 | keep | 0 | Sep | 2021 | 0.022357 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-09-09 13:23 | 2021-09-09 14:18 | 165 | 000:55 | P | DESGANCHE | SE NORMALIZO CARGA APARENTE CONTAMINACIONES EN SU DE URBANIZACION | B21090900000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-09-09 | 9075 | keep | 0 | Sep | 2021 | 0.0061809 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-09 13:25 | 2021-09-09 14:08 | 100 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA AVERIADA | M21090900188 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2021-09-09 | 4300 | keep | 0 | Sep | 2021 | 0.0029287 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-09 13:31 | 2021-09-09 18:40 | 30 | 005:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21090900194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-09-09 | 9270 | keep | 0 | Sep | 2021 | 0.0063138 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-09 13:40 | 2021-09-09 13:41 | 1131 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21090900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-09 | 1131 | keep | 0 | Sep | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BARRANQUITAS | 2021-09-09 13:41 | 2021-09-09 14:18 | 100 | 000:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZARON TRAMO DE CONDUCTOR ROTO DEL 9703-02 POR MONTE ABRIENDO PUENTES Y TRANSFIRIO PARTE DE LA CARGA DEL 9703-02 AL 9605-02 | C21090900126 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 37 | 2021-09-09 | 3700 | keep | 0 | Sep | 2021 | 0.0025201 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-09-09 13:42 | 2021-09-09 14:44 | 25 | 001:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R21090900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-09-09 | 1550 | keep | 0 | Sep | 2021 | 0.0010557 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-09 13:58 | 2021-09-10 17:20 | 45 | 027:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21091000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1642 | 2021-09-09 | 73890 | keep | 0 | Sep | 2021 | 0.050326 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-09-09 14:08 | 2021-09-09 14:46 | 1617 | 000:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETIRAR PELIGRO LINEA PRIMARIA ROTA | M21090900222 | Additional_clients | Wire Down | Include | Include | Equipment | 38 | 2021-09-09 | 61446 | keep | 0 | Sep | 2021 | 0.041851 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-09 14:18 | 2021-09-09 14:19 | 1604 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE COMERIO A BARRANQUITAS | C21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-09 | 1604 | keep | 0 | Sep | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | TRUE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-09-09 14:18 | 2021-09-09 14:19 | 1131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE COMERIO A BARRANQUITAS | C21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-09 | 1131 | keep | 0 | Sep | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | TRUE | Not_TMED_Event | 1131
BARRANQUITAS | 2021-09-09 14:18 | 2021-09-09 14:19 | 2362 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE COMERIO A BARRANQUITAS | C21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-09 | 2362 | keep | 0 | Sep | 2021 | 0.0016087 | 0.0016087 | Momentary | FALSE | TRUE | Not_TMED_Event | 2362
BARRANQUITAS | 2021-09-09 14:19 | 2021-09-10 00:52 | 100 | 010:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZARON TRAMO DE CONDUCTOR ROTO DEL 9703-02 POR MONTE ABRIENDO PUENTES Y TRANSFIRIO PARTE DE LA CARGA DEL 9703-02 AL 9605-02 | C21090900126 | Partial_restoration | Wire Down | Include | Include | Equipment | 633 | 2021-09-09 | 63300 | keep | 0 | Sep | 2021 | 0.043113 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-09 14:25 | 2021-09-10 14:26 | 500 | 024:01 | P | ESTRUCTURA AVERIADA | SE TRANSFIRIERON LINEAS DE POSTE PARTIDO A POSTE NUEVO YA INSTALADO PREVIAMENTE EN EL LUGAR | B21090900069 | New_Event | Defective Pole | Include | Include | Equipment | 1441 | 2021-09-09 | 720500 | keep | 0 | Sep | 2021 | 0.49073 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
MAYAGÃœEZ | 2021-09-09 14:26 | 2021-09-09 17:21 | 11 | 002:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO Y SE CERRO INTERRUPTOR | M21090900238 | Additional_clients | Wire Down | Include | Include | Equipment | 175 | 2021-09-09 | 1925 | keep | 0 | Sep | 2021 | 0.0013111 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-09 14:32 | 2021-09-09 14:35 | 1408 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO 1714-03 QUE LLEVA 1714-02 | B21090900081 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2021-09-09 | 4224 | keep | 0 | Sep | 2021 | 0.0028769 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-09-09 14:32 | 2021-09-09 14:35 | 455 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO Y SE CERRO POR SCADA LLEVA 1714-02 | B21090900081 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2021-09-09 | 1365 | keep | 0 | Sep | 2021 | 0.0009297 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
CAGUAS | 2021-09-09 14:44 | 2021-09-09 16:08 | 1 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090900066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-09-09 | 84 | keep | 0 | Sep | 2021 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-09 14:46 | 2021-09-09 15:50 | 100 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M21090900188 | Partial_restoration | Wire Down | Include | Include | Equipment | 64 | 2021-09-09 | 6400 | keep | 0 | Sep | 2021 | 0.004359 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-09-09 14:47 | 2021-09-09 16:45 | 5 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR IGUANA | R21090900033 | New_Event |  |  | Include | Wildlife | 118 | 2021-09-09 | 590 | keep | 0 | Sep | 2021 | 0.00040185 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BARRANQUITAS | 2021-09-09 14:52 | 2021-09-10 00:14 | 110 | 009:22 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | C21090900070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2021-09-09 | 61820 | keep | 0 | Sep | 2021 | 0.042105 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
UTUADO | 2021-09-09 14:55 | 2021-09-09 14:59 | 1054 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR FUERTES LLUVIAS | A21090900082 | Additional_clients | Bad Weather | Include | Include | Weather | 4 | 2021-09-09 | 4216 | keep | 0 | Sep | 2021 | 0.0028715 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-09 14:58 | 2021-09-09 16:58 | 8 | 002:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21090900067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2021-09-09 | 960 | keep | 0 | Sep | 2021 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-09-09 14:59 | 2021-09-14 14:54 | 50 | 119:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800122 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 7195 | 2021-09-09 | 359750 | keep | 0 | Sep | 2021 | 0.24502 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-09 15:01 | 2021-09-09 15:03 | 2658 | 000:02 | T | NO SE REPORTO CAUSA | OPERACION DE INTERRUPTOR | M21090900259 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-09 | 5316 | keep | 0 | Sep | 2021 | 0.0036207 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
MAYAGÃœEZ | 2021-09-09 15:05 | 2021-09-09 18:15 | 10 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 8 EN TRANSFORMADOR MAL TIEMPO | M21090900262 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-09-09 | 1900 | keep | 0 | Sep | 2021 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-09 15:13 | 2021-09-09 15:14 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 2617 | keep | 0 | Sep | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2021-09-09 15:13 | 2021-09-09 15:14 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 3511 | keep | 0 | Sep | 2021 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
UTUADO | 2021-09-09 15:15 | 2021-09-10 10:25 | 10 | 019:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090900101 | New_Event | Bad Weather | Include | Include | Weather | 1150 | 2021-09-09 | 11500 | keep | 0 | Sep | 2021 | 0.0078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-09 15:17 | 2021-09-09 15:52 | 959 | 000:35 | T | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO ABRIENDO MACHETES EN CALLE NOGAL Y SE CONTINUA PATRULLANDO. FUERTES LLUVIAS Y TRUENOS | B21090900092 | New_Event | Bad Weather | Include | Include | Weather | 35 | 2021-09-09 | 33565 | keep | 0 | Sep | 2021 | 0.022861 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
CAGUAS | 2021-09-09 15:18 | 2021-09-10 16:20 | 14 | 025:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21090900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1502 | 2021-09-09 | 21028 | keep | 0 | Sep | 2021 | 0.014322 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
BAYAMON | 2021-09-09 15:19 | 2021-09-09 15:20 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 3941 | keep | 0 | Sep | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-09-09 15:19 | 2021-09-09 15:20 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 2617 | keep | 0 | Sep | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2021-09-09 15:21 | 2021-09-09 15:22 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 3941 | keep | 0 | Sep | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-09-09 15:24 | 2021-09-09 15:25 | 5191 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1710-05 LLEVANDO LA CARGA DEL 1719-15 Y SE CERRO POR SCADA | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 5191 | keep | 0 | Sep | 2021 | 0.0035356 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2021-09-09 15:24 | 2021-09-09 15:25 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1710-05 LLEVANDO LA CARGA DEL 1719-15 Y SE CERRO POR SCADA | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 3597 | keep | 0 | Sep | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-09-09 15:25 | 2021-09-09 23:32 | 100 | 008:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090900166 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 487 | 2021-09-09 | 48700 | keep | 0 | Sep | 2021 | 0.033169 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-09 15:26 | 2021-09-09 18:59 | 1 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR SUMERGIBLE | S21090900051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-09-09 | 213 | keep | 0 | Sep | 2021 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-09-09 15:26 | 2021-09-09 16:44 | 2635 | 001:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A OROCOVIS SE SECCIONALIZO POSTE VACANTE SOBRE LINEA | C21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2021-09-09 | 205530 | keep | 0 | Sep | 2021 | 0.13999 | 0.0017947 | Sustained | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-09 15:26 | 2021-09-09 16:44 | 2280 | 001:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A OROCOVIS SE SECCIONALIZO POSTE VACANTE SOBRE LINEA | C21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2021-09-09 | 177840 | keep | 0 | Sep | 2021 | 0.12113 | 0.0015529 | Sustained | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-09-09 15:26 | 2021-09-09 16:44 | 1617 | 001:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A OROCOVIS SE SECCIONALIZO POSTE VACANTE SOBRE LINEA | C21090900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2021-09-09 | 126126 | keep | 0 | Sep | 2021 | 0.085904 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
BAYAMON | 2021-09-09 15:27 | 2021-09-10 13:30 | 1408 | 022:03 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA SOTERRADA CASI A LA SALIDA DEL 1714-03. SE TRANSFIRIO 70% DEL 1714-02 AL 1707-04 ABRIENDO MACHETES EN CALLE 35 URB. SANTA ROSA Y CERRANDO N/O EN CARR 177 DETRAS COSTCO | B21090900099 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1323 | 2021-09-09 | 1862784 | keep | 0 | Sep | 2021 | 1.2687 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-09-09 15:27 | 2021-09-09 21:50 | 455 | 006:23 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA SOTERRADA CASI A LA SALIDA DEL 1714-03. SE TRANSFIRIO 95% DEL 1714-03 AL 1715-05 Y SE DEJO FUERA EL 1714-02. | B21090900099 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 383 | 2021-09-09 | 174265 | keep | 0 | Sep | 2021 | 0.11869 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
BAYAMON | 2021-09-09 15:27 | 2021-09-11 14:00 | 40 | 046:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090900097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2793 | 2021-09-09 | 111720 | keep | 0 | Sep | 2021 | 0.076092 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-09 15:28 | 2021-09-09 15:29 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 LLEVANDO LA CARGA DEL 1711-05 Y SE CERRO POR SCADA | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 723 | keep | 0 | Sep | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-09-09 15:28 | 2021-09-09 15:29 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 LLEVANDO LA CARGA DEL 1711-05 Y SE CERRO POR SCADA | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1976 | keep | 0 | Sep | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-09-09 15:28 | 2021-09-09 15:29 | 878 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1903-05 LLEVANDO LA CARGA DEL 1714-05 Y SE CERRO POR SCADA | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 878 | keep | 0 | Sep | 2021 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2021-09-09 15:28 | 2021-09-09 15:29 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1903-05 LLEVANDO LA CARGA DEL 1714-05 Y SE CERRO POR SCADA | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1310 | keep | 0 | Sep | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-09-09 15:29 | 2021-09-09 19:47 | 1399 | 004:18 | T | DESGANCHE | SE DISPARO INTERRUPTOR POR AVERIA FRENTE A LA SUBESTACION SE ABRIO RISER DE SALIDA SE TRABAJO DESENREDADO LINEAS Y SE REEMPLAZO MACHETE SE CERRO RISER DE SALIDA Y SE CERRO INTERRUPTOR POR SCADA 100% EN SERVICIO | B21090900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2021-09-09 | 360942 | keep | 0 | Sep | 2021 | 0.24584 | 0.00095285 | Sustained | FALSE | TRUE | Not_TMED_Event | 1399
BAYAMON | 2021-09-09 15:30 | 2021-09-09 15:31 | 573 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1704-04 LLEVANDO LA CARGA DEL 1704-05 | B21090900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 573 | keep | 0 | Sep | 2021 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-09-09 15:30 | 2021-09-09 15:31 | 1313 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1704-04 LLEVANDO LA CARGA DEL 1704-05 | B21090900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1313 | keep | 0 | Sep | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
CAGUAS | 2021-09-09 15:31 | 2021-09-09 15:32 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21090900079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1879 | keep | 0 | Sep | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2021-09-09 15:33 | 2021-09-09 15:34 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1717-02 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 5961 | keep | 0 | Sep | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-09-09 15:33 | 2021-09-09 15:34 | 911 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO LA CARGA DEL 1717-02 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 911 | keep | 0 | Sep | 2021 | 0.00062048 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
SAN JUAN | 2021-09-09 15:34 | 2021-09-09 17:31 | 10 | 001:57 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA DESGANCHAR ENREDADERA EN SECUNDARIA ABIERTA | S21090900043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 117 | 2021-09-09 | 1170 | keep | 0 | Sep | 2021 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-09 15:35 | 2021-09-09 15:36 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1909-08 LA CARGA DEL 1907-05 SE ENCUENTRA POR EL 1909-08 | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 2435 | keep | 0 | Sep | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-09-09 15:35 | 2021-09-09 15:36 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1909-08 LLEVANDO LA CARGA DEL 1907-05 | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 2956 | keep | 0 | Sep | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-09-09 15:36 | 2021-09-09 15:39 | 1310 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | EVENTO DE LLUVIA FUERTE Y RAYOS | S21090900059 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2021-09-09 | 3930 | keep | 0 | Sep | 2021 | 0.0026767 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-09-09 15:36 | 2021-09-09 17:30 | 20 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA MARCA-ABB 100AMP. | A21090900108 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2021-09-09 | 2280 | keep | 0 | Sep | 2021 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-09 15:37 | 2021-09-09 15:38 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1706-03 Y 1715-03 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-09-09 15:37 | 2021-09-09 15:38 | 663 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1706-03 Y 1715-03 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 663 | keep | 0 | Sep | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-09-09 15:37 | 2021-09-09 15:38 | 74 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1706-03 Y 1715-03 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 74 | keep | 0 | Sep | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2021-09-09 15:37 | 2021-09-09 15:38 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1717-05 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 4533 | keep | 0 | Sep | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-09-09 15:37 | 2021-09-09 15:38 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1717-01 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 341 | keep | 0 | Sep | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2021-09-09 15:38 | 2021-09-09 15:39 | 1587 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 1587 | keep | 0 | Sep | 2021 | 0.0010809 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
CAGUAS | 2021-09-09 15:43 | 2021-09-10 16:01 | 1 | 024:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C21090900083 | New_Event |  |  | Include | Wildlife | 1458 | 2021-09-09 | 1458 | keep | 0 | Sep | 2021 | 0.00099304 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-09 15:44 | 2021-09-09 15:46 | 170 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR 1345-02 | S21090900067 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-09 | 340 | keep | 0 | Sep | 2021 | 0.00023157 | 0.00011579 | Momentary | FALSE | FALSE | Not_TMED_Event | 170
SAN JUAN | 2021-09-09 15:44 | 2021-09-09 15:46 | 291 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR 1345-02 | S21090900067 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-09 | 582 | keep | 0 | Sep | 2021 | 0.0003964 | 0.0001982 | Momentary | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2021-09-09 15:44 | 2021-09-09 15:46 | 435 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | EVENTO DE LLUVIA FUERTE Y RAYOS LLEVA CARGA 1342-05 Y PARTE 1330-04 | S21090900067 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-09 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2021-09-09 15:50 | 2021-09-09 15:51 | 10211 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR EL 1206-03 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-09-09 15:50 | 2021-09-09 15:51 | 4133 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS LLEVA EL 1204-05 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-09-09 15:52 | 2021-09-09 16:14 | 400 | 000:22 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRARON MACHETES NUEVAMENTE Y SE QUEDO EN SERVICIO. FUERTES LLUVIAS Y TRUENOS | B21090900092 | Partial_restoration | Bad Weather | Include | Include | Weather | 22 | 2021-09-09 | 8800 | keep | 0 | Sep | 2021 | 0.0059936 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-09 15:57 | 2021-09-09 17:00 | 1382 | 001:03 | T | DESGANCHE | SE SECCIONALIZO AVERIA DE ARBOL SOBRE LINEAS. SE DEJO FUERA EL 1706-03 Y 1715-03 | B21090900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2021-09-09 | 87066 | keep | 0 | Sep | 2021 | 0.0593 | 0.00094127 | Sustained | FALSE | TRUE | Not_TMED_Event | 1382
BAYAMON | 2021-09-09 15:57 | 2021-09-09 17:56 | 663 | 001:59 | T | DESGANCHE | SE CERRARON MACHETES CONTRA EL 1706-02 DESPUES DE DESGANCHAR ARBOL SOBRE LINEAS. CARGA POR EL 1706-02 | B21090900092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-09-09 | 78897 | keep | 0 | Sep | 2021 | 0.053736 | 0.00045157 | Sustained | FALSE | TRUE | Not_TMED_Event | 663
BAYAMON | 2021-09-09 15:57 | 2021-09-09 17:56 | 74 | 001:59 | T | DESGANCHE | SE CERRARON MACHETES CONTRA EL 1706-02 DESPUES DE DESGANCHAR ARBOL SOBRE LINEAS. CARGA POR EL 1706-02 | B21090900092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-09-09 | 8806 | keep | 0 | Sep | 2021 | 0.0059977 | 5.0401e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 74
CAGUAS | 2021-09-09 15:57 | 2021-09-09 19:11 | 116 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21090900088 | New_Event |  |  | Include | Wildlife | 194 | 2021-09-09 | 22504 | keep | 0 | Sep | 2021 | 0.015327 | 7.9007e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 116
MAYAGÃœEZ | 2021-09-09 15:57 | 2021-09-09 20:30 | 4 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21090900291 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2021-09-09 | 1092 | keep | 0 | Sep | 2021 | 0.00074376 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-09-09 15:58 | 2021-09-09 17:00 | 150 | 001:02 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21090900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-09-09 | 9300 | keep | 0 | Sep | 2021 | 0.0063342 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-09 16:01 | 2021-09-09 16:02 | 271 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 271 | keep | 0 | Sep | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2021-09-09 16:01 | 2021-09-09 16:08 | 1271 | 000:07 | T | DESGANCHE | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21090900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 7 | 2021-09-09 | 8897 | keep | 0 | Sep | 2021 | 0.0060597 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2021-09-09 16:01 | 2021-09-09 23:00 | 12 | 006:59 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | C21090900091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 419 | 2021-09-09 | 5028 | keep | 0 | Sep | 2021 | 0.0034245 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-09 16:02 | 2021-09-09 16:10 | 433 | 000:08 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EVENTO DE LLUVIA FUERTE Y RAYOS | S21090900085 | New_Event | Cutout Failure | Include | Include | Equipment | 8 | 2021-09-09 | 3464 | keep | 0 | Sep | 2021 | 0.0023593 | 0.00029491 | Sustained | FALSE | FALSE | Not_TMED_Event | 433
CAGUAS | 2021-09-09 16:02 | 2021-09-09 18:44 | 86 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE POSTE PRIMARIO IMPACTADO Y RETEZAR LINEA PRIMARIA AL ALCANCE DE LA MANO | C21090900101 | New_Event |  |  | Include | Wildlife | 162 | 2021-09-09 | 13932 | keep | 0 | Sep | 2021 | 0.009489 | 5.8574e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 86
BAYAMON | 2021-09-09 16:03 | 2021-09-09 18:07 | 514 | 002:04 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR POR SCADA ABRIENDO MACHETES DE AMARRE EN BARRA DE INSPECCION CONTRA 1520-04 CARGA POR 1520-05 | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-09-09 | 63736 | keep | 0 | Sep | 2021 | 0.04341 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-09-09 16:03 | 2021-09-09 18:52 | 752 | 002:49 | T | NO SE REPORTO CAUSA | SE CERRO MACHETES DE AMARRE EN BARRA DE INSPECCION CONTRA 1520 05 NO SE ENCONTRO CAUSA | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2021-09-09 | 127088 | keep | 0 | Sep | 2021 | 0.086559 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-09-09 16:03 | 2021-09-09 18:07 | 68 | 002:04 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR POR SCADA ABRIENDO MACHETES DE AMARRE EN BARRA DE INSPECCION CONTRA 1520-04 LLEVA CARGA 1520-01 | S21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-09-09 | 8432 | keep | 0 | Sep | 2021 | 0.005743 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
VEGA BAJA | 2021-09-09 16:03 | 2021-09-09 21:19 | 35 | 005:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 316 | 2021-09-09 | 11060 | keep | 0 | Sep | 2021 | 0.0075329 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-09-09 16:04 | 2021-09-09 16:05 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 2147 | keep | 0 | Sep | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2021-09-09 16:05 | 2021-09-09 16:09 | 506 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR 1118-10 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-09-09 | 2024 | keep | 0 | Sep | 2021 | 0.0013785 | 0.00034463 | Momentary | FALSE | FALSE | Not_TMED_Event | 506
SAN JUAN | 2021-09-09 16:05 | 2021-09-09 16:09 | 2782 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EVENTO DE LLUVIA FUERTE Y RAYOS LLEVA PARTE DE LA CARGA 1111-01 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-09-09 | 11128 | keep | 0 | Sep | 2021 | 0.0075792 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2021-09-09 16:09 | 2021-09-09 22:13 | 250 | 006:04 | P | DESGANCHE | SE ABRE INTERRUPTOR PARA REPARAR PUENTE ABIERTO PASANTE Y REALIZAR DESGANCHE | S21090900094 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 364 | 2021-09-09 | 91000 | keep | 0 | Sep | 2021 | 0.06198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-09 16:10 | 2021-09-09 16:11 | 5290 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR EL 1424-06 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 5290 | keep | 0 | Sep | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-09-09 16:10 | 2021-09-09 16:11 | 1001 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS EL 80% DE LA CARGA DEL 1348-06 ESTA POR EL 1424-06 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 1001 | keep | 0 | Sep | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2021-09-09 16:10 | 2021-09-09 16:11 | 278 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR EL 1424-06 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 278 | keep | 0 | Sep | 2021 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-09-09 16:10 | 2021-09-09 16:11 | 2203 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR EVENTO DE LLUVIA FUERTE Y RAYOS LLEVA EL 80% 1348-06, EL 1348-07 Y PARTE DEL 1336-08 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-09 | 2203 | keep | 0 | Sep | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2021-09-09 16:10 | 2021-09-09 19:27 | 15 | 003:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE PRIMARIO TRASPATIO | S21090900166 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 197 | 2021-09-09 | 2955 | keep | 0 | Sep | 2021 | 0.0020126 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-09 16:14 | 2021-09-10 13:19 | 200 | 021:05 | P | DESGANCHE | 3 X 100 Y 2 X 80 EN CORTES DE LINEA | C21090900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1265 | 2021-09-09 | 253000 | keep | 0 | Sep | 2021 | 0.17232 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-09-09 16:18 | 2021-09-09 16:19 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR SPARE 9001-03 LLEVANDO 40% DEL 9002-03 | B21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 3332 | keep | 0 | Sep | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
SAN JUAN | 2021-09-09 16:26 | 2021-09-09 16:30 | 314 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EVENTO DE LLUVIA FUERTE Y RAYOS | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-09-09 | 1256 | keep | 0 | Sep | 2021 | 0.00085546 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
BAYAMON | 2021-09-09 16:30 | 2021-09-09 16:31 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21090900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 3941 | keep | 0 | Sep | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2021-09-09 16:30 | 2021-09-09 19:45 | 100 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21090900301 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2021-09-09 | 19500 | keep | 0 | Sep | 2021 | 0.013281 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-09 16:31 | 2021-09-09 19:04 | 10 | 002:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21090900050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 153 | 2021-09-09 | 1530 | keep | 0 | Sep | 2021 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-09 16:35 | 2021-09-10 16:22 | 20 | 023:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | B21090900157 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1427 | 2021-09-09 | 28540 | keep | 0 | Sep | 2021 | 0.019438 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-09 16:38 | 2021-09-09 17:40 | 60 | 001:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21090900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-09-09 | 3720 | keep | 0 | Sep | 2021 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-09 16:42 | 2021-09-10 13:48 | 15 | 021:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | M21090900306 | New_Event | Bad Weather | Include | Include | Weather | 1266 | 2021-09-09 | 18990 | keep | 0 | Sep | 2021 | 0.012934 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-09 16:52 | 2021-09-10 20:36 | 60 | 027:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21091000166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1664 | 2021-09-09 | 99840 | keep | 0 | Sep | 2021 | 0.068001 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-09 16:54 | 2021-09-10 10:45 | 60 | 017:51 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBÃšS SOBRE LAS LINEAS | A21090900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1071 | 2021-09-09 | 64260 | keep | 0 | Sep | 2021 | 0.043767 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-09 16:56 | 2021-09-09 19:00 | 75 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A21090900121 | New_Event | Wire Down | Include | Include | Equipment | 124 | 2021-09-09 | 9300 | keep | 0 | Sep | 2021 | 0.0063342 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-09 16:57 | 2021-09-09 21:11 | 1097 | 004:14 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REMPLAZARON AISLADORES | M21090900313 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 254 | 2021-09-09 | 278638 | keep | 0 | Sep | 2021 | 0.18978 | 0.00074716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1097
HUMACAO | 2021-09-09 17:00 | 2021-09-09 20:50 | 16 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEL TRANSFORMADOR | C21090900113 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2021-09-09 | 3680 | keep | 0 | Sep | 2021 | 0.0025064 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2021-09-09 17:02 | 2021-09-09 17:04 | 36 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EVENTO DE LLUVIA FUERTE Y RAYOS CARGA POR 1620-04 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-09 | 72 | keep | 0 | Sep | 2021 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-09-09 17:02 | 2021-09-09 17:04 | 172 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EVENTO DE LLUVIA FUERTE Y RAYOS LLEVA 1620-01 | S21090900000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-09 | 344 | keep | 0 | Sep | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-09-09 17:03 | 2021-09-09 21:21 | 15 | 004:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE SECUNDARIO IMPACTADO POR CAMION | B21090900175 | New_Event |  |  | Include | Wildlife | 258 | 2021-09-09 | 3870 | keep | 0 | Sep | 2021 | 0.0026358 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-09 17:04 | 2021-09-10 17:59 | 50 | 024:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091000039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1495 | 2021-09-09 | 74750 | keep | 0 | Sep | 2021 | 0.050912 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-09 17:10 | 2021-09-09 17:11 | 1420 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR AL NORMALIZAR RELE DE GROUND CARGA POR 1530-06 DESBALANCE | S21090900000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-09 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-09 17:10 | 2021-09-09 17:11 | 437 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE ALIMENTADOR AL HACER PRUEBA DE NORMALIZAR RELE DE GROUND LLEVA CARGA 1526-02 DESBALANCE | S21090900000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-09 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-09-09 17:19 | 2021-09-09 22:22 | 60 | 005:03 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090900129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2021-09-09 | 18180 | keep | 0 | Sep | 2021 | 0.012382 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-09 17:28 | 2021-09-09 18:30 | 2 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21090900132 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2021-09-09 | 124 | keep | 0 | Sep | 2021 | 8.4456e-05 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CANOVANAS | 2021-09-09 17:33 | 2021-09-09 18:04 | 7 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21090900046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-09-09 | 217 | keep | 0 | Sep | 2021 | 0.0001478 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-09-09 17:39 | 2021-09-09 19:45 | 20 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21090900133 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-09-09 | 2520 | keep | 0 | Sep | 2021 | 0.0017164 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-09 17:47 | 2021-09-09 19:21 | 300 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE DE FASE POR AVE | P21090900084 | New_Event |  |  | Include | Wildlife | 94 | 2021-09-09 | 28200 | keep | 0 | Sep | 2021 | 0.019207 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-09-09 17:50 | 2021-09-09 17:51 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21090900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2021-09-09 17:51 | 2021-09-09 19:09 | 40 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21090900343 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-09-09 | 3120 | keep | 0 | Sep | 2021 | 0.002125 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-09 18:14 | 2021-09-09 19:13 | 15 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | B21090900204 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-09-09 | 885 | keep | 0 | Sep | 2021 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-09-09 18:20 | 2021-09-10 13:00 | 8 | 018:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21090900140 | New_Event | Cutout Failure | Include | Include | Equipment | 1120 | 2021-09-09 | 8960 | keep | 0 | Sep | 2021 | 0.0061026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-09 18:37 | 2021-09-10 12:30 | 50 | 017:53 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | M21090900338 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1073 | 2021-09-09 | 53650 | keep | 0 | Sep | 2021 | 0.036541 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-09 18:38 | 2021-09-09 21:00 | 8 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090900145 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-09-09 | 1136 | keep | 0 | Sep | 2021 | 0.00077372 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-09 18:42 | 2021-09-10 13:34 | 10 | 018:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR SOTERRADO NO CAUSA | C21090900122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1132 | 2021-09-09 | 11320 | keep | 0 | Sep | 2021 | 0.00771 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-09 18:46 | 2021-09-09 21:44 | 50 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE LINEA MAL TIEMPO | M21090800304 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-09-09 | 8900 | keep | 0 | Sep | 2021 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-09 18:49 | 2021-09-09 20:46 | 50 | 001:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21090900086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-09-09 | 5850 | keep | 0 | Sep | 2021 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-09 18:52 | 2021-09-09 19:40 | 60 | 000:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21090900349 | New_Event | Bad Weather | Include | Include | Weather | 48 | 2021-09-09 | 2880 | keep | 0 | Sep | 2021 | 0.0019616 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-09 18:55 | 2021-09-09 19:39 | 10 | 000:44 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARARON BARRAS SECUNDARIAS EN PEDESTAL | S21090900154 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 44 | 2021-09-09 | 440 | keep | 0 | Sep | 2021 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-09 18:59 | 2021-09-10 15:16 | 20 | 020:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21090900158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1217 | 2021-09-09 | 24340 | keep | 0 | Sep | 2021 | 0.016578 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-09-09 19:15 | 2021-09-10 10:49 | 8 | 015:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR CONEXION EN PEDESTAL | R21090900052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 934 | 2021-09-09 | 7472 | keep | 0 | Sep | 2021 | 0.0050891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-09 19:27 | 2021-09-09 20:22 | 433 | 000:55 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REMPLAZAR CAJA PRIMARIA QUEMADA Y REPARAR PUENTE PRIMARIO ABIERTO | S21090900091 | Additional_clients | Cutout Failure | Include | Include | Equipment | 55 | 2021-09-09 | 23815 | keep | 0 | Sep | 2021 | 0.01622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-09 19:36 | 2021-09-09 20:25 | 325 | 000:49 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 9206-10 PARA ABRIR MACHETE QUEMADO POR SEGURIDAD. | B21090900000 | New_Event | Switch Failure | Include | Include | Equipment | 49 | 2021-09-09 | 15925 | keep | 0 | Sep | 2021 | 0.010846 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
ARECIBO | 2021-09-09 19:42 | 2021-09-10 11:18 | 50 | 015:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21090900157 | New_Event | Wire Down | Include | Include | Equipment | 936 | 2021-09-09 | 46800 | keep | 0 | Sep | 2021 | 0.031875 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-09-09 19:43 | 2021-09-09 22:09 | 25 | 002:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | P21090900088 | New_Event |  |  | Include | Wildlife | 146 | 2021-09-09 | 3650 | keep | 0 | Sep | 2021 | 0.002486 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
GUAYAMA | 2021-09-09 19:53 | 2021-09-09 22:09 | 50 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEAS AVE CRUZO LINEAS | P21090900089 | New_Event |  |  | Include | Wildlife | 136 | 2021-09-09 | 6800 | keep | 0 | Sep | 2021 | 0.0046314 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-09 20:02 | 2021-09-10 19:09 | 100 | 023:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090900259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1387 | 2021-09-09 | 138700 | keep | 0 | Sep | 2021 | 0.094468 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-09 20:10 | 2021-09-11 14:12 | 6 | 042:02 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 15 KVA | C21090900129 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2522 | 2021-09-09 | 15132 | keep | 0 | Sep | 2021 | 0.010306 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-09-09 20:17 | 2021-09-10 11:30 | 80 | 015:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21090900368 | New_Event | Bad Weather | Include | Include | Weather | 913 | 2021-09-09 | 73040 | keep | 0 | Sep | 2021 | 0.049747 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-09 20:25 | 2021-09-09 21:15 | 100 | 000:50 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES QUEMADOS Y SE CERRARON | B21090900000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 50 | 2021-09-09 | 5000 | keep | 0 | Sep | 2021 | 0.0034055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-09 20:30 | 2021-09-09 21:50 | 7 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21090900115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-09-09 | 560 | keep | 0 | Sep | 2021 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-09 20:47 | 2021-09-10 12:00 | 300 | 015:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CORTE DE LINEA Y SE CERRO CORTE DE LINEA | M21090900372 | New_Event | Cutout Failure | Include | Include | Equipment | 913 | 2021-09-09 | 273900 | keep | 0 | Sep | 2021 | 0.18655 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
GUAYAMA | 2021-09-09 20:55 | 2021-09-09 20:56 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21090900094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
UTUADO | 2021-09-09 21:05 | 2021-09-10 13:00 | 15 | 015:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090900169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 955 | 2021-09-09 | 14325 | keep | 0 | Sep | 2021 | 0.0097567 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
PONCE | 2021-09-09 21:10 | 2021-09-10 19:00 | 50 | 021:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21090900095 | New_Event | Bad Weather | Include | Include | Weather | 1310 | 2021-09-09 | 65500 | keep | 0 | Sep | 2021 | 0.044612 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-09 21:11 | 2021-09-10 19:36 | 200 | 022:25 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO | P21091000096 | New_Event | Defective Pole | Include | Include | Equipment | 1345 | 2021-09-09 | 269000 | keep | 0 | Sep | 2021 | 0.18321 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-09-09 21:14 | 2021-09-09 22:43 | 200 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21090900139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-09-09 | 17800 | keep | 0 | Sep | 2021 | 0.012123 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-09 21:20 | 2021-09-10 00:18 | 199 | 002:58 | T | PARARRAYOS DEFECTUOSO | SE RETIRO PARARRAYO QUEMADO Y SE CERRO INTERRUPTOR | M21090900000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 178 | 2021-09-09 | 35422 | keep | 0 | Sep | 2021 | 0.024126 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2021-09-09 21:24 | 2021-09-09 22:41 | 1097 | 001:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS SE CERRO INTERRUPTOR | M21090900382 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 77 | 2021-09-09 | 84469 | keep | 0 | Sep | 2021 | 0.057531 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-09 21:30 | 2021-09-10 18:31 | 30 | 021:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA PRIMARIA QUEMADA EN TRANSFORMADOR TRASPATIO | S21090900178 | New_Event | Cutout Failure | Include | Include | Equipment | 1261 | 2021-09-09 | 37830 | keep | 0 | Sep | 2021 | 0.025766 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-09 21:42 | 2021-09-09 23:31 | 75 | 001:49 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21090900281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-09-09 | 8175 | keep | 0 | Sep | 2021 | 0.005568 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-09 21:50 | 2021-09-10 10:48 | 50 | 012:58 | P | CABLE SOTERRADO AVERIADO | SE CERRARON MACHETES DETRAS DE BURLINGTON TRANSFIRIENDO CARGA RESTANTE DEL 1714-03 AL 1715-05 | B21090900099 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 778 | 2021-09-09 | 38900 | keep | 0 | Sep | 2021 | 0.026495 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-09 21:52 | 2021-09-10 11:49 | 50 | 013:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21090900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 837 | 2021-09-09 | 41850 | keep | 0 | Sep | 2021 | 0.028504 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-09 22:13 | 2021-09-09 23:56 | 1271 | 001:43 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA RETIRAR ARBOL SOBRE LINEAS Y REPARAR PUENTE ABIERTO EN TRONCAL | R21090900183 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-09-09 | 130913 | keep | 0 | Sep | 2021 | 0.089164 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-09 22:20 | 2021-09-09 23:00 | 50 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090900287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-09-09 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-09 22:26 | 2021-09-10 15:24 | 35 | 016:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S290900184 | New_Event | Cutout Failure | Include | Include | Equipment | 1018 | 2021-09-09 | 35630 | keep | 0 | Sep | 2021 | 0.024267 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
FAJARDO | 2021-09-09 22:44 | 2021-09-09 22:45 | 1394 | 000:01 | T | DESGANCHE | RECIERRE | R21090900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-09 | 1394 | keep | 0 | Sep | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2021-09-09 22:45 | 2021-09-10 08:55 | 40 | 010:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21090900056 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 610 | 2021-09-09 | 24400 | keep | 0 | Sep | 2021 | 0.016619 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-09 22:56 | 2021-09-09 22:57 | 693 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-09 | 693 | keep | 0 | Sep | 2021 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
ARECIBO | 2021-09-09 23:00 | 2021-09-10 12:30 | 10 | 013:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21090900138 | New_Event | Wire Down | Include | Include | Equipment | 810 | 2021-09-09 | 8100 | keep | 0 | Sep | 2021 | 0.0055169 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-09 23:51 | 2021-09-10 16:00 | 40 | 016:09 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | M21090900396 | New_Event | Vegetation Contact | Include | Include | Vegetation | 969 | 2021-09-09 | 38760 | keep | 0 | Sep | 2021 | 0.026399 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-09 23:56 | 2021-09-10 10:26 | 50 | 010:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B21090900293 | New_Event | Cutout Failure | Include | Include | Equipment | 630 | 2021-09-09 | 31500 | keep | 0 | Sep | 2021 | 0.021455 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-10 00:07 | 2021-09-10 10:10 | 6 | 010:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR ROEDOR CRUZO LINEAS | A21091000001 | New_Event |  |  | Include | Wildlife | 603 | 2021-09-10 | 3618 | keep | 0 | Sep | 2021 | 0.0024642 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
AGUADILLA | 2021-09-10 00:08 | 2021-09-10 11:50 | 40 | 011:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091000001 | New_Event | Bad Weather | Include | Include | Weather | 702 | 2021-09-10 | 28080 | keep | 0 | Sep | 2021 | 0.019125 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-10 00:52 | 2021-09-10 01:10 | 1131 | 000:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA QUE PERSONAL PUDIERA ABRIR PUENTES HACIA AVERIA DE CONDUCTOR ROTO EN MONTE | C21091000000 | New_Event | Wire Down | Include | Include | Equipment | 18 | 2021-09-10 | 20358 | keep | 0 | Sep | 2021 | 0.013866 | 0.00077032 | Sustained | FALSE | FALSE | Not_TMED_Event | 1131
AGUADILLA | 2021-09-10 00:53 | 2021-09-10 10:50 | 40 | 009:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091000003 | New_Event | Bad Weather | Include | Include | Weather | 597 | 2021-09-10 | 23880 | keep | 0 | Sep | 2021 | 0.016265 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-10 03:28 | 2021-09-10 03:29 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 1494 | keep | 0 | Sep | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
MAYAGÃœEZ | 2021-09-10 03:53 | 2021-09-10 09:53 | 2999 | 006:00 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES PARA SECCIONALIZAR AISLADORES AVERIADOS | M21091000008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 360 | 2021-09-10 | 1079640 | keep | 0 | Sep | 2021 | 0.73534 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-09-10 03:53 | 2021-09-10 09:53 | 1597 | 006:00 | T | AISLADOR ROTO, PARTIDO O SAFADO | LA CARGA ESTA TRANSFERIDA AL 6406-02 | M21091000008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 360 | 2021-09-10 | 574920 | keep | 0 | Sep | 2021 | 0.39158 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
BAYAMON | 2021-09-10 03:58 | 2021-09-10 16:17 | 100 | 012:19 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 739 | 2021-09-10 | 73900 | keep | 0 | Sep | 2021 | 0.050333 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-10 04:26 | 2021-09-10 04:27 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL CON R/R OFF Y QUEDO EN SERVICIO | B21091000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 3295 | keep | 0 | Sep | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
ARECIBO | 2021-09-10 04:47 | 2021-09-10 11:00 | 70 | 006:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21091000003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 373 | 2021-09-10 | 26110 | keep | 0 | Sep | 2021 | 0.017783 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
YAUCO | 2021-09-10 06:24 | 2021-09-10 06:25 | 1352 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR CARGA POR 5602-02 | P21091000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-10 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-09-10 06:24 | 2021-09-10 06:25 | 3973 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | P21091000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-10 | 3973 | keep | 0 | Sep | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-09-10 06:25 | 2021-09-10 08:55 | 200 | 002:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21091000003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-09-10 | 30000 | keep | 0 | Sep | 2021 | 0.020433 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-09-10 06:40 | 2021-09-10 12:01 | 10 | 005:21 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEANDO 50 KVA X 50 KVA | C21091000011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 321 | 2021-09-10 | 3210 | keep | 0 | Sep | 2021 | 0.0021863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-10 07:07 | 2021-09-10 19:46 | 21 | 012:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR UNO DE 50 KVA | B21091000021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 759 | 2021-09-10 | 15939 | keep | 0 | Sep | 2021 | 0.010856 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2021-09-10 07:18 | 2021-09-10 12:41 | 230 | 005:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100, 1 X 65, 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE RETIRO IGUANA | B21091000024 | New_Event |  |  | Include | Wildlife | 323 | 2021-09-10 | 74290 | keep | 0 | Sep | 2021 | 0.050599 | 0.00015665 | Sustained | FALSE | TRUE | Not_TMED_Event | 230
HUMACAO | 2021-09-10 07:39 | 2021-09-10 12:01 | 6 | 004:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091000015 | New_Event | Bad Weather | Include | Include | Weather | 262 | 2021-09-10 | 1572 | keep | 0 | Sep | 2021 | 0.0010707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-10 07:41 | 2021-09-10 07:42 | 436 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO | C21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 436 | keep | 0 | Sep | 2021 | 0.00029696 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
ARECIBO | 2021-09-10 07:45 | 2021-09-10 07:46 | 2231 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 2231 | keep | 0 | Sep | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2021-09-10 07:52 | 2021-09-10 10:00 | 100 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A21091000006 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-09-10 | 12800 | keep | 0 | Sep | 2021 | 0.008718 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-10 08:06 | 2021-09-10 16:52 | 1 | 008:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C21091000016 | New_Event |  |  | Include | Wildlife | 526 | 2021-09-10 | 526 | keep | 0 | Sep | 2021 | 0.00035826 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-10 08:08 | 2021-09-10 18:40 | 80 | 010:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21091000052 | New_Event | Bad Weather | Include | Include | Weather | 632 | 2021-09-10 | 50560 | keep | 0 | Sep | 2021 | 0.034436 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-10 08:18 | 2021-09-10 18:00 | 200 | 009:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21091000055 | New_Event | Bad Weather | Include | Include | Weather | 582 | 2021-09-10 | 116400 | keep | 0 | Sep | 2021 | 0.07928 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-09-10 08:20 | 2021-09-10 13:00 | 250 | 004:40 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-09-10 | 70000 | keep | 0 | Sep | 2021 | 0.047677 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
GUAYAMA | 2021-09-10 08:24 | 2021-09-10 10:18 | 4132 | 001:54 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR SE REMPLAZO CAJA PRIMARIA EN TRONCAL | P21091000006 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2021-09-10 | 471048 | keep | 0 | Sep | 2021 | 0.32083 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
BAYAMON | 2021-09-10 08:25 | 2021-09-10 08:26 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1909-08 CARGA DEL 1907-05 POR EL 1909-08 | S21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 2435 | keep | 0 | Sep | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-09-10 08:25 | 2021-09-10 08:26 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1909-08 LLEVANDO EL 1907-05 | S21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 2956 | keep | 0 | Sep | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2021-09-10 08:26 | 2021-09-10 12:35 | 100 | 004:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21091000010 | New_Event | Cutout Failure | Include | Include | Equipment | 249 | 2021-09-10 | 24900 | keep | 0 | Sep | 2021 | 0.016959 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-10 08:30 | 2021-09-10 19:45 | 15 | 011:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21091000059 | New_Event | Wire Down | Include | Include | Equipment | 675 | 2021-09-10 | 10125 | keep | 0 | Sep | 2021 | 0.0068961 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-09-10 08:33 | 2021-09-10 10:53 | 5 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091000011 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-09-10 | 700 | keep | 0 | Sep | 2021 | 0.00047677 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-10 08:37 | 2021-09-11 09:35 | 75 | 024:58 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21091000036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1498 | 2021-09-10 | 112350 | keep | 0 | Sep | 2021 | 0.076521 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-10 09:09 | 2021-09-10 09:41 | 10 | 000:32 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRANSFORMADOR | B21090900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2021-09-10 | 320 | keep | 0 | Sep | 2021 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-10 09:11 | 2021-09-10 15:07 | 6 | 005:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21091000044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 356 | 2021-09-10 | 2136 | keep | 0 | Sep | 2021 | 0.0014548 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-09-10 09:18 | 2021-09-10 09:19 | 215 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 215 | keep | 0 | Sep | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
AGUADILLA | 2021-09-10 09:20 | 2021-09-10 13:19 | 50 | 003:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21091000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-09-10 | 11950 | keep | 0 | Sep | 2021 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-10 09:25 | 2021-09-10 13:59 | 115 | 004:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21091000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2021-09-10 | 31510 | keep | 0 | Sep | 2021 | 0.021461 | 7.8326e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 115
CANOVANAS | 2021-09-10 09:26 | 2021-09-10 10:00 | 80 | 000:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21091000005 | New_Event |  |  | Include | Wildlife | 34 | 2021-09-10 | 2720 | keep | 0 | Sep | 2021 | 0.0018526 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-10 09:41 | 2021-09-10 12:14 | 100 | 002:33 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21091000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-09-10 | 15300 | keep | 0 | Sep | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-10 09:49 | 2021-09-11 16:00 | 12 | 030:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA | B21091000053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1811 | 2021-09-10 | 21732 | keep | 0 | Sep | 2021 | 0.014802 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-09-10 09:51 | 2021-09-10 20:52 | 30 | 011:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21091000054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 661 | 2021-09-10 | 19830 | keep | 0 | Sep | 2021 | 0.013506 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-10 09:53 | 2021-09-10 11:10 | 200 | 001:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON AISLADORES Y SE CERRO MACHETES | M21091000008 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 77 | 2021-09-10 | 15400 | keep | 0 | Sep | 2021 | 0.010489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-10 09:53 | 2021-09-10 15:27 | 1 | 005:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21091000055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 334 | 2021-09-10 | 334 | keep | 0 | Sep | 2021 | 0.00022749 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-10 10:08 | 2021-09-10 12:51 | 1 | 002:43 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21091000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 163 | 2021-09-10 | 163 | keep | 0 | Sep | 2021 | 0.00011102 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-10 10:08 | 2021-09-10 12:51 | 2266 | 002:43 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21091000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 163 | 2021-09-10 | 369358 | keep | 0 | Sep | 2021 | 0.25157 | 0.0015434 | Sustained | FALSE | TRUE | Not_TMED_Event | 2266
ARECIBO | 2021-09-10 10:08 | 2021-09-10 12:51 | 1399 | 002:43 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21091000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 163 | 2021-09-10 | 228037 | keep | 0 | Sep | 2021 | 0.15531 | 0.00095285 | Sustained | FALSE | TRUE | Not_TMED_Event | 1399
ARECIBO | 2021-09-10 10:22 | 2021-09-10 11:40 | 5 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091000026 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-09-10 | 390 | keep | 0 | Sep | 2021 | 0.00026563 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-09-10 10:26 | 2021-09-10 10:41 | 3 | 000:15 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21091000059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-10 | 45 | keep | 0 | Sep | 2021 | 3.0649e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-09-10 10:26 | 2021-09-10 10:41 | 3957 | 000:15 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21091000059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-10 | 59355 | keep | 0 | Sep | 2021 | 0.040426 | 0.0026951 | Sustained | FALSE | TRUE | Not_TMED_Event | 3957
BAYAMON | 2021-09-10 10:26 | 2021-09-10 10:41 | 58 | 000:15 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21091000059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-10 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
SAN JUAN | 2021-09-10 10:26 | 2021-09-10 10:41 | 386 | 000:15 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21091000059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-10 | 5790 | keep | 0 | Sep | 2021 | 0.0039435 | 0.0002629 | Sustained | FALSE | TRUE | Not_TMED_Event | 386
BAYAMON | 2021-09-10 10:34 | 2021-09-10 17:14 | 100 | 006:40 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B21091000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2021-09-10 | 40000 | keep | 0 | Sep | 2021 | 0.027244 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-10 10:50 | 2021-09-10 16:34 | 3 | 005:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21091000065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 344 | 2021-09-10 | 1032 | keep | 0 | Sep | 2021 | 0.00070289 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2021-09-10 11:00 | 2021-09-10 13:27 | 50 | 002:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA VEHICULO IMPACTO POSTE PRIMARIO | M21091000121 | New_Event |  |  | Include | Wildlife | 147 | 2021-09-10 | 7350 | keep | 0 | Sep | 2021 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-10 11:02 | 2021-09-10 15:43 | 30 | 004:41 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B21091000081 | New_Event | Defective Pole | Include | Include | Equipment | 281 | 2021-09-10 | 8430 | keep | 0 | Sep | 2021 | 0.0057416 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-10 11:14 | 2021-09-10 12:23 | 4 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BARRA EN PEDESTAL | R21090800051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-09-10 | 276 | keep | 0 | Sep | 2021 | 0.00018798 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-09-10 11:15 | 2021-09-10 15:27 | 50 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2021-09-10 | 12600 | keep | 0 | Sep | 2021 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-10 11:16 | 2021-09-10 16:22 | 15 | 005:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21090900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2021-09-10 | 4590 | keep | 0 | Sep | 2021 | 0.0031262 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-10 11:20 | 2021-09-11 10:33 | 250 | 023:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21091000131 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1393 | 2021-09-10 | 348250 | keep | 0 | Sep | 2021 | 0.23719 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-09-10 11:26 | 2021-09-10 18:29 | 300 | 007:03 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | M21091000134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2021-09-10 | 126900 | keep | 0 | Sep | 2021 | 0.086431 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
VEGA BAJA | 2021-09-10 11:32 | 2021-09-10 16:33 | 8 | 005:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21091000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2021-09-10 | 2408 | keep | 0 | Sep | 2021 | 0.0016401 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-10 11:46 | 2021-09-10 13:32 | 1587 | 001:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO ALIMENTADOR PARA CERRAR PUENTE ABIERTO EN TRONCAL | S21091000000 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-09-10 | 168222 | keep | 0 | Sep | 2021 | 0.11458 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
AGUADILLA | 2021-09-10 12:01 | 2021-09-10 14:24 | 325 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA POR LINEA PRIMARIA PARTIDA SE SECCIONALIZO LA AVERIA | M21091000190 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2021-09-10 | 46475 | keep | 0 | Sep | 2021 | 0.031654 | 0.00022136 | Sustained | FALSE | TRUE | Not_TMED_Event | 325
BAYAMON | 2021-09-10 12:08 | 2021-09-10 12:09 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | RECIRRE DE INTERRUPTOR | S21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 1085 | keep | 0 | Sep | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
ARECIBO | 2021-09-10 12:08 | 2021-09-10 16:30 | 5 | 004:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | A21091000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2021-09-10 | 1310 | keep | 0 | Sep | 2021 | 0.00089224 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-09-10 12:10 | 2021-09-10 15:44 | 15 | 003:34 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-09-10 | 3210 | keep | 0 | Sep | 2021 | 0.0021863 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-10 12:21 | 2021-09-10 18:35 | 100 | 006:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | M21091000189 | New_Event | Bad Weather | Include | Include | Weather | 374 | 2021-09-10 | 37400 | keep | 0 | Sep | 2021 | 0.025473 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-10 12:27 | 2021-09-10 20:24 | 1399 | 007:57 | S | BREAKER DEFECTUOSO O NO OPERA | EN DISPARO DE BREAKER SE CERRO Y FUNDIO 2 FUSIBLES STANDARD SPEED 125 SE ABRIO RISER Y SE TRANSFIRIO AL 1704-02 | B21091000089 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 477 | 2021-09-10 | 667323 | keep | 0 | Sep | 2021 | 0.45451 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-09-10 12:27 | 2021-09-10 19:13 | 302 | 006:46 | S | BREAKER DEFECTUOSO O NO OPERA | EN DISPARO DE BREAKER SE CERRO Y FUNDIO 2 FUSIBLES STANDARD SPEED 125 SE SECCIONALIZO Y SE CERRO POR SCADA | B21091000089 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 406 | 2021-09-10 | 122612 | keep | 0 | Sep | 2021 | 0.08351 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-09-10 12:27 | 2021-09-10 18:55 | 1048 | 006:28 | S | BREAKER DEFECTUOSO O NO OPERA | EN DISPARO DE BREAKER SE CERRO Y FUNDIO 2 FUSIBLES STANDARD SPEED 125 | B21091000089 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 388 | 2021-09-10 | 406624 | keep | 0 | Sep | 2021 | 0.27695 | 0.00071379 | Sustained | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2021-09-10 12:27 | 2021-09-10 18:55 | 573 | 006:28 | S | BREAKER DEFECTUOSO O NO OPERA | EN DISPARO DE BREAKER SE CERRO Y FUNDIO 2 FUSIBLES STANDARD SPEED 125 | B21091000089 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 388 | 2021-09-10 | 222324 | keep | 0 | Sep | 2021 | 0.15142 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-09-10 12:27 | 2021-09-10 18:55 | 1313 | 006:28 | S | BREAKER DEFECTUOSO O NO OPERA | EN DISPARO DE BREAKER SE CERRO Y FUNDIO 2 FUSIBLES STANDARD SPEED 125 | B21091000089 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 388 | 2021-09-10 | 509444 | keep | 0 | Sep | 2021 | 0.34698 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
HUMACAO | 2021-09-10 12:30 | 2021-09-10 12:31 | 3420 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21091000000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-10 | 3420 | keep | 0 | Sep | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-09-10 12:31 | 2021-09-10 15:08 | 25 | 002:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21091000042 | 1st_after_momentary |  |  | Include | Wildlife | 157 | 2021-09-10 | 3925 | keep | 0 | Sep | 2021 | 0.0026733 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-10 12:32 | 2021-09-10 12:59 | 8 | 000:27 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO TRANSFORMADOR PARA REMPLAZAR 2 PEDESTALES | C21091000035 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 27 | 2021-09-10 | 216 | keep | 0 | Sep | 2021 | 0.00014712 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-10 12:35 | 2021-09-10 12:36 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2021-09-10 12:43 | 2021-09-10 12:44 | 554 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA EL 30% DE LA CARGA POR EL 1529-15 | S21091000103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 554 | keep | 0 | Sep | 2021 | 0.00037733 | 0.00037733 | Momentary | FALSE | FALSE | Not_TMED_Event | 554
BAYAMON | 2021-09-10 12:43 | 2021-09-10 12:44 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 30% DEL 1346-02 | S21091000103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 1802 | keep | 0 | Sep | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-09-10 12:45 | 2021-09-11 10:06 | 79 | 021:21 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21091000104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1281 | 2021-09-10 | 101199 | keep | 0 | Sep | 2021 | 0.068926 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
HUMACAO | 2021-09-10 12:50 | 2021-09-10 16:27 | 40 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21091000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2021-09-10 | 8680 | keep | 0 | Sep | 2021 | 0.0059119 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-10 12:54 | 2021-09-10 14:35 | 3400 | 001:41 | T | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL 22 | S21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-09-10 | 343400 | keep | 0 | Sep | 2021 | 0.23389 | 0.0023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 3400
SAN JUAN | 2021-09-10 12:54 | 2021-09-10 14:35 | 520 | 001:41 | T | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL 22 | S21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-09-10 | 52520 | keep | 0 | Sep | 2021 | 0.035771 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
CANOVANAS | 2021-09-10 13:02 | 2021-09-10 13:03 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 7621 | keep | 0 | Sep | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
FAJARDO | 2021-09-10 13:11 | 2021-09-10 17:07 | 200 | 003:56 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE POSTE PARTIDO | R21091000016 | New_Event | Defective Pole | Include | Include | Equipment | 236 | 2021-09-10 | 47200 | keep | 0 | Sep | 2021 | 0.032148 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-10 13:30 | 2021-09-10 13:56 | 340 | 000:26 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA SOTERRADA CASI A LA SALIDA DEL 1714-03. SE TRANSFIRIO 30% DEL 1714-02 AL 1707-05 ABRIENDO RISER SALIDO Y CERRANDO EN CALLE 25 SANTA ROSA | B21090900000 | New_Event | UG Cable Fault | Include | Include | Equipment | 26 | 2021-09-10 | 8840 | keep | 0 | Sep | 2021 | 0.0060209 | 0.00023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 340
SAN JUAN | 2021-09-10 13:39 | 2021-09-10 17:12 | 2 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RELOCALIZO LINEA PRIMARIA AVERIADA | S21091000000 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-09-10 | 426 | keep | 0 | Sep | 2021 | 0.00029015 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-09-10 13:54 | 2021-09-10 14:07 | 10 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21091000121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-09-10 | 130 | keep | 0 | Sep | 2021 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-10 14:01 | 2021-09-10 14:02 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 3431 | keep | 0 | Sep | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CANOVANAS | 2021-09-10 14:02 | 2021-09-10 14:24 | 14 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA AJUSTAR BAJANTE SECUNDARIO | R21091000020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2021-09-10 | 308 | keep | 0 | Sep | 2021 | 0.00020978 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2021-09-10 14:20 | 2021-09-10 16:26 | 20 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21091000082 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-09-10 | 2520 | keep | 0 | Sep | 2021 | 0.0017164 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-10 14:21 | 2021-09-10 16:30 | 100 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE POR AVE | P21091000039 | New_Event |  |  | Include | Wildlife | 129 | 2021-09-10 | 12900 | keep | 0 | Sep | 2021 | 0.0087861 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-10 14:21 | 2021-09-10 15:30 | 75 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21091000083 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2021-09-10 | 5175 | keep | 0 | Sep | 2021 | 0.0035247 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-10 14:21 | 2021-09-10 16:20 | 7 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21091000083 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2021-09-10 | 833 | keep | 0 | Sep | 2021 | 0.00056735 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
AGUADILLA | 2021-09-10 14:24 | 2021-09-10 20:00 | 100 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA POR LINEA PRIMARIA PARTIDA SE SECCIONALIZO LA AVERIA | M21091000190 | Partial_restoration | Wire Down | Include | Include | Equipment | 336 | 2021-09-10 | 33600 | keep | 0 | Sep | 2021 | 0.022885 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-10 14:25 | 2021-09-11 00:57 | 50 | 010:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN CONVERTIDOR | B21091000115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 632 | 2021-09-10 | 31600 | keep | 0 | Sep | 2021 | 0.021523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-09-10 14:28 | 2021-09-11 13:47 | 11 | 023:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 POR 37.5 KVA EN EL FID33798174 / MARCA GE / #SERIE E211683Y378 / CAPACIDAD / VOLTAJE 8320/14200V 120/240V | A21091000084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1399 | 2021-09-10 | 15389 | keep | 0 | Sep | 2021 | 0.010481 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2021-09-10 14:38 | 2021-09-10 17:15 | 60 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21091000201 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-09-10 | 9420 | keep | 0 | Sep | 2021 | 0.0064159 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-10 14:47 | 2021-09-10 17:57 | 1 | 003:10 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25 AMP. EN SU-1 NO ENCONTRO CAUSA | C21091000056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2021-09-10 | 190 | keep | 0 | Sep | 2021 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-09-10 14:49 | 2021-09-10 16:34 | 25 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE POR AVE | P21091000041 | New_Event |  |  | Include | Wildlife | 105 | 2021-09-10 | 2625 | keep | 0 | Sep | 2021 | 0.0017879 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-10 14:50 | 2021-09-10 15:39 | 25 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090900068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-09-10 | 1225 | keep | 0 | Sep | 2021 | 0.00083434 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-10 14:51 | 2021-09-11 09:12 | 15 | 018:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21091000119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1101 | 2021-09-10 | 16515 | keep | 0 | Sep | 2021 | 0.011248 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-10 15:07 | 2021-09-10 16:24 | 1 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | B21091000126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-09-10 | 77 | keep | 0 | Sep | 2021 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-10 15:16 | 2021-09-10 19:31 | 3 | 004:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21091000128 | New_Event | Cutout Failure | Include | Include | Equipment | 255 | 2021-09-10 | 765 | keep | 0 | Sep | 2021 | 0.00052104 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-09-10 15:19 | 2021-09-11 11:40 | 146 | 020:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P21091000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1221 | 2021-09-10 | 178266 | keep | 0 | Sep | 2021 | 0.12142 | 9.944e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 146
BAYAMON | 2021-09-10 15:21 | 2021-09-10 18:21 | 80 | 003:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091000132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-09-10 | 14400 | keep | 0 | Sep | 2021 | 0.0098078 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-10 15:24 | 2021-09-10 23:26 | 150 | 008:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21091000223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2021-09-10 | 72300 | keep | 0 | Sep | 2021 | 0.049243 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-09-10 15:29 | 2021-09-10 19:12 | 200 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P21091000052 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-09-10 | 44600 | keep | 0 | Sep | 2021 | 0.030377 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-09-10 15:40 | 2021-09-10 18:00 | 125 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21091000230 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-09-10 | 17500 | keep | 0 | Sep | 2021 | 0.011919 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-09-10 15:46 | 2021-09-10 18:05 | 25 | 002:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M21091000234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-09-10 | 3475 | keep | 0 | Sep | 2021 | 0.0023668 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-10 15:47 | 2021-09-11 16:50 | 50 | 025:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TRANSFIRIO LA CARGA DE ESTOS CLIENTES A OTRO TRANSFORMADOR | B21091000139 | New_Event | Wire Down | Include | Include | Equipment | 1503 | 2021-09-10 | 75150 | keep | 0 | Sep | 2021 | 0.051184 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-09-10 15:49 | 2021-09-10 19:00 | 60 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21091000104 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2021-09-10 | 11460 | keep | 0 | Sep | 2021 | 0.0078054 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-10 15:53 | 2021-09-10 18:58 | 200 | 003:05 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | A21091000107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-09-10 | 37000 | keep | 0 | Sep | 2021 | 0.025201 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-10 15:55 | 2021-09-11 11:02 | 75 | 019:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21091000242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1147 | 2021-09-10 | 86025 | keep | 0 | Sep | 2021 | 0.058591 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-10 15:56 | 2021-09-10 21:22 | 12 | 005:26 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21091000143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-09-10 | 3912 | keep | 0 | Sep | 2021 | 0.0026644 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-10 16:03 | 2021-09-11 09:40 | 60 | 017:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS | M21091000243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1057 | 2021-09-10 | 63420 | keep | 0 | Sep | 2021 | 0.043195 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-10 16:07 | 2021-09-10 18:49 | 20 | 002:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETIRAR LINEAS CRUZADAS EN CRUZETA | S21090900044 | New_Event | Wire Down | Include | Include | Equipment | 162 | 2021-09-10 | 3240 | keep | 0 | Sep | 2021 | 0.0022067 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-09-10 16:07 | 2021-09-10 17:45 | 120 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE POR AVE | P21091000055 | New_Event |  |  | Include | Wildlife | 98 | 2021-09-10 | 11760 | keep | 0 | Sep | 2021 | 0.0080097 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
CAGUAS | 2021-09-10 16:08 | 2021-09-11 09:55 | 7 | 017:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR TOMA | C21091000060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1067 | 2021-09-10 | 7469 | keep | 0 | Sep | 2021 | 0.0050871 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-09-10 16:09 | 2021-09-10 17:31 | 13 | 001:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21091000059 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2021-09-10 | 1066 | keep | 0 | Sep | 2021 | 0.00072605 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-09-10 16:10 | 2021-09-10 17:10 | 5 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO SAFADO | M21091000246 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-09-10 | 300 | keep | 0 | Sep | 2021 | 0.00020433 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-10 16:11 | 2021-09-12 11:55 | 15 | 043:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091000110 | New_Event | Bad Weather | Include | Include | Weather | 2624 | 2021-09-10 | 39360 | keep | 0 | Sep | 2021 | 0.026808 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-09-10 16:24 | 2021-09-10 21:12 | 45 | 004:48 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21091000156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2021-09-10 | 12960 | keep | 0 | Sep | 2021 | 0.008827 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-09-10 16:29 | 2021-09-11 17:51 | 60 | 025:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091000153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1522 | 2021-09-10 | 91320 | keep | 0 | Sep | 2021 | 0.062198 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-09-10 16:33 | 2021-09-10 18:43 | 80 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21091000165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-09-10 | 10400 | keep | 0 | Sep | 2021 | 0.0070834 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-10 16:46 | 2021-09-10 21:40 | 100 | 004:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21091000256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2021-09-10 | 29400 | keep | 0 | Sep | 2021 | 0.020024 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-10 16:53 | 2021-09-10 21:59 | 80 | 005:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21091000165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2021-09-10 | 24480 | keep | 0 | Sep | 2021 | 0.016673 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-10 16:53 | 2021-09-11 10:13 | 50 | 017:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REMPLAZO AISLADOR | C21091000063 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1040 | 2021-09-10 | 52000 | keep | 0 | Sep | 2021 | 0.035417 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-10 17:10 | 2021-09-10 18:31 | 10 | 001:21 | P | SECUNDARIA/DESGANCHE | 2 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | S21090900098 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 81 | 2021-09-10 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-10 17:22 | 2021-09-10 19:13 | 8 | 001:51 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21091000064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 111 | 2021-09-10 | 888 | keep | 0 | Sep | 2021 | 0.00060481 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-09-10 17:43 | 2021-09-11 10:12 | 50 | 016:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21091000126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 989 | 2021-09-10 | 49450 | keep | 0 | Sep | 2021 | 0.03368 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-10 17:51 | 2021-09-11 11:11 | 80 | 017:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21091000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1040 | 2021-09-10 | 83200 | keep | 0 | Sep | 2021 | 0.056667 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-10 18:18 | 2021-09-10 20:32 | 80 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 65 1 X 30 EN CORTES DE LINEA | B21091000179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2021-09-10 | 10720 | keep | 0 | Sep | 2021 | 0.0073013 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-09-10 18:18 | 2021-09-10 20:23 | 365 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 30 EN CORTES DE LINEA CRUCE POR AVE | R21091000032 | New_Event |  |  | Include | Wildlife | 125 | 2021-09-10 | 45625 | keep | 0 | Sep | 2021 | 0.031075 | 0.0002486 | Sustained | FALSE | TRUE | Not_TMED_Event | 365
HUMACAO | 2021-09-10 18:23 | 2021-09-10 18:24 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21091000068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 2126 | keep | 0 | Sep | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-09-10 18:41 | 2021-09-10 22:37 | 50 | 003:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | A21091000131 | New_Event | Bad Weather | Include | Include | Weather | 236 | 2021-09-10 | 11800 | keep | 0 | Sep | 2021 | 0.0080369 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-10 18:55 | 2021-09-11 00:20 | 60 | 005:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21091000186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2021-09-10 | 19500 | keep | 0 | Sep | 2021 | 0.013281 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-10 18:59 | 2021-09-11 11:50 | 30 | 016:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21091000135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1011 | 2021-09-10 | 30330 | keep | 0 | Sep | 2021 | 0.020658 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-10 19:07 | 2021-09-10 20:57 | 30 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21091000139 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-09-10 | 3300 | keep | 0 | Sep | 2021 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-10 19:13 | 2021-09-10 20:21 | 150 | 001:08 | P | BREAKER DEFECTUOSO O NO OPERA | EN DISPARO DE BREAKER SE CERRO Y FUNDIO 2 FUSIBLES STANDARD SPEED 125 SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 1704-01 | B21091000089 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 68 | 2021-09-10 | 10200 | keep | 0 | Sep | 2021 | 0.0069472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-10 19:21 | 2021-09-10 23:32 | 2708 | 004:11 | S | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE LA SUBESTACION A LOCK OUT SE REEMPLAZO CONECTOR DE BARRA FASE C DEL 2302-01 | R21091000036 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 251 | 2021-09-10 | 679708 | keep | 0 | Sep | 2021 | 0.46295 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-09-10 19:21 | 2021-09-10 23:32 | 2524 | 004:11 | S | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE LA SUBESTACION A LOCK OUT SE REEMPLAZO CONECTOR DE BARRA FASE C DEL 2302-01 | R21091000036 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 251 | 2021-09-10 | 633524 | keep | 0 | Sep | 2021 | 0.43149 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2021-09-10 19:21 | 2021-09-10 23:32 | 1648 | 004:11 | S | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE LA SUBESTACION A LOCK OUT SE REEMPLAZO CONECTOR DE BARRA FASE C DEL 2302-01 | R21091000036 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 251 | 2021-09-10 | 413648 | keep | 0 | Sep | 2021 | 0.28173 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
ARECIBO | 2021-09-10 19:29 | 2021-09-10 19:33 | 3157 | 000:04 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO | A21091000142 | New_Event | Defective Pole | Include | Include | Equipment | 4 | 2021-09-10 | 12628 | keep | 0 | Sep | 2021 | 0.0086009 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
CAGUAS | 2021-09-10 19:32 | 2021-09-12 13:06 | 10 | 041:34 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21091000074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2494 | 2021-09-10 | 24940 | keep | 0 | Sep | 2021 | 0.016987 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-10 19:33 | 2021-09-11 18:30 | 1000 | 022:57 | P | ESTRUCTURA AVERIADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO POR UNO DE 45' MADERA | A21091000157 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 1377 | 2021-09-10 | 1377000 | keep | 0 | Sep | 2021 | 0.93787 | 0.0006811 | Sustained | FALSE | TRUE | Not_TMED_Event | 1000
CAGUAS | 2021-09-10 19:38 | 2021-09-11 17:31 | 80 | 021:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REMPLAZO AISLADOR | C21091000075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1313 | 2021-09-10 | 105040 | keep | 0 | Sep | 2021 | 0.071542 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-10 19:52 | 2021-09-11 10:50 | 80 | 014:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21091000147 | New_Event | Bad Weather | Include | Include | Weather | 898 | 2021-09-10 | 71840 | keep | 0 | Sep | 2021 | 0.04893 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-10 20:01 | 2021-09-15 11:50 | 15 | 111:49 | P | NO SE REPORTO CAUSA | SE REPARO BAJANTE SECUNDARIO NO FUNDIO FISIBLE | P21091000074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6709 | 2021-09-10 | 100635 | keep | 0 | Sep | 2021 | 0.068542 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-10 20:15 | 2021-09-11 10:25 | 50 | 014:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091000201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2021-09-10 | 42500 | keep | 0 | Sep | 2021 | 0.028947 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-10 20:26 | 2021-09-10 20:27 | 490 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 3007-04 CERRADO POR CONTROL | C21091000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-10 | 490 | keep | 0 | Sep | 2021 | 0.00033374 | 0.00033374 | Momentary | FALSE | FALSE | Not_TMED_Event | 490
CAGUAS | 2021-09-10 20:26 | 2021-09-10 20:27 | 906 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR LLEVA CARGA DEL 3005-01 CERRADO POR CONTROL | C21091000082 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-10 | 906 | keep | 0 | Sep | 2021 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2021-09-10 20:28 | 2021-09-11 15:43 | 116 | 019:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA LEVANTO CONDUCTOR Y REMPLAZO 2 CAJAS EN MAL ESTADO | C21091000083 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1155 | 2021-09-10 | 133980 | keep | 0 | Sep | 2021 | 0.091253 | 7.9007e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 116
SAN JUAN | 2021-09-10 21:12 | 2021-09-12 22:22 | 15 | 049:10 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21091000169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2950 | 2021-09-10 | 44250 | keep | 0 | Sep | 2021 | 0.030138 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-10 21:13 | 2021-09-11 09:40 | 50 | 012:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | A21091000151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 747 | 2021-09-10 | 37350 | keep | 0 | Sep | 2021 | 0.025439 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-10 21:22 | 2021-09-10 21:38 | 600 | 000:16 | P | ERROR HUMANO | PERSONAL DESGANCHANDO EN 1708-03 QUE LLEVA PARTE DEL 1708-02 DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO 1708-03 | B21091000000 | New_Event | Human Error | Include | Include | Other | 16 | 2021-09-10 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-09-10 21:22 | 2021-09-10 21:38 | 1498 | 000:16 | T | ERROR HUMANO | PERSONAL DESGANCHANDO OCASIONO DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | B21091000000 | New_Event | Human Error | Include | Include | Other | 16 | 2021-09-10 | 23968 | keep | 0 | Sep | 2021 | 0.016324 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
HUMACAO | 2021-09-10 21:28 | 2021-09-11 01:00 | 136 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21091000090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-09-10 | 28832 | keep | 0 | Sep | 2021 | 0.019637 | 9.2629e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 136
AGUADILLA | 2021-09-10 21:33 | 2021-09-10 21:34 | 1192 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR | M21091000000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-10 | 1192 | keep | 0 | Sep | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-09-10 21:40 | 2021-09-10 21:41 | 1192 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR | M21091000000 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-10 | 1192 | keep | 0 | Sep | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-09-10 21:41 | 2021-09-12 05:26 | 500 | 031:45 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO CONVERTIDOR | M21091000355 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1905 | 2021-09-10 | 952500 | keep | 0 | Sep | 2021 | 0.64874 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2021-09-10 21:54 | 2021-09-10 23:24 | 4702 | 001:30 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO Y SE CERRO POR SCADA | B21091000219 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 90 | 2021-09-10 | 423180 | keep | 0 | Sep | 2021 | 0.28823 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
CAGUAS | 2021-09-10 22:34 | 2021-09-11 17:46 | 10 | 019:12 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA Y REPARO SECUNDARIA | C21091000095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1152 | 2021-09-10 | 11520 | keep | 0 | Sep | 2021 | 0.0078462 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-10 22:43 | 2021-09-11 11:01 | 200 | 012:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE LEVANTO PRIMARIA | S21091000199 | New_Event | Wire Down | Include | Include | Equipment | 738 | 2021-09-10 | 147600 | keep | 0 | Sep | 2021 | 0.10053 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-09-10 22:52 | 2021-09-11 11:55 | 200 | 013:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091000344 | New_Event | Bad Weather | Include | Include | Weather | 783 | 2021-09-10 | 156600 | keep | 0 | Sep | 2021 | 0.10666 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-09-10 22:55 | 2021-09-11 17:30 | 40 | 018:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21091000096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1115 | 2021-09-10 | 44600 | keep | 0 | Sep | 2021 | 0.030377 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-10 22:56 | 2021-09-11 10:50 | 70 | 011:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091000345 | New_Event | Bad Weather | Include | Include | Weather | 714 | 2021-09-10 | 49980 | keep | 0 | Sep | 2021 | 0.034041 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-09-10 23:24 | 2021-09-11 00:34 | 1700 | 001:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA CERRAR MACHETES INCOMODOS | B21091000219 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 70 | 2021-09-10 | 119000 | keep | 0 | Sep | 2021 | 0.08105 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-10 23:58 | 2021-09-11 10:13 | 40 | 010:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | B21091000257 | New_Event | Cutout Failure | Include | Include | Equipment | 615 | 2021-09-10 | 24600 | keep | 0 | Sep | 2021 | 0.016755 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-10 23:58 | 2021-09-11 13:58 | 50 | 014:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091000097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 840 | 2021-09-10 | 42000 | keep | 0 | Sep | 2021 | 0.028606 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-11 00:01 | 2021-09-11 10:00 | 9 | 009:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | P21091100001 | New_Event | Wire Down | Include | Include | Equipment | 599 | 2021-09-11 | 5391 | keep | 0 | Sep | 2021 | 0.0036718 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-09-11 00:34 | 2021-09-11 00:39 | 4702 | 000:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO ALIMENTADOR PARA HACER OPERACIONES PROBO MALO Y SE SECCIONALIZO PARA REMPLAZO DE AISLADOR PARTIDO | B21091000219 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2021-09-11 | 23510 | keep | 0 | Sep | 2021 | 0.016013 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-11 00:39 | 2021-09-11 02:24 | 1700 | 001:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA CERRAR MACHETES INCOMODOS | B21091000219 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2021-09-11 | 178500 | keep | 0 | Sep | 2021 | 0.12158 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-11 01:54 | 2021-09-11 02:05 | 2704 | 000:11 | T | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZANDO AISLADOR EN EL 9004-10 QUE PASA POR ENCIMA DISPARO Y SE CERRO LUEGO DE CONFIRMAR PERSONAL FUERA | B21091100008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2021-09-11 | 29744 | keep | 0 | Sep | 2021 | 0.020259 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
CAGUAS | 2021-09-11 01:55 | 2021-09-11 17:11 | 130 | 015:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C21091100003 | New_Event | Wire Down | Include | Include | Equipment | 916 | 2021-09-11 | 119080 | keep | 0 | Sep | 2021 | 0.081105 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2021-09-11 02:24 | 2021-09-11 02:28 | 4702 | 000:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO ALIMENTADOR PARA CERRAR MACHETES CON SEGURIDAD YA QUE ESTABAN INCOMODOS LUEGO DE HABER REMPLAZADO AISLADOR PARTIDO | B21091000219 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2021-09-11 | 18808 | keep | 0 | Sep | 2021 | 0.01281 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-11 02:52 | 2021-09-11 11:03 | 2713 | 008:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE ABRIO MACHETES CONTINUA PATRULLANDO | M21091100371 | New_Event | Wire Down | Include | Include | Equipment | 491 | 2021-09-11 | 1332083 | keep | 0 | Sep | 2021 | 0.90728 | 0.0018478 | Sustained | FALSE | FALSE | Not_TMED_Event | 2713
BAYAMON | 2021-09-11 03:07 | 2021-09-11 11:53 | 50 | 008:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B21091100011 | New_Event | Wire Down | Include | Include | Equipment | 526 | 2021-09-11 | 26300 | keep | 0 | Sep | 2021 | 0.017913 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-11 03:21 | 2021-09-11 03:22 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 325 | keep | 0 | Sep | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
GUAYAMA | 2021-09-11 04:24 | 2021-09-11 09:40 | 50 | 005:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE ELIMINO TENSOR | P21091100003 | New_Event |  |  | Include | Wildlife | 316 | 2021-09-11 | 15800 | keep | 0 | Sep | 2021 | 0.010761 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 06:20 | 2021-09-11 11:23 | 50 | 005:03 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2021-09-11 | 15150 | keep | 0 | Sep | 2021 | 0.010319 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-11 06:57 | 2021-09-11 10:39 | 184 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21091100006 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2021-09-11 | 40848 | keep | 0 | Sep | 2021 | 0.027821 | 0.00012532 | Sustained | FALSE | TRUE | Not_TMED_Event | 184
PONCE | 2021-09-11 07:12 | 2021-09-11 16:41 | 25 | 009:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR RAMA | P21091100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 569 | 2021-09-11 | 14225 | keep | 0 | Sep | 2021 | 0.0096886 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-09-11 07:29 | 2021-09-11 15:42 | 35 | 008:13 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21091100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2021-09-11 | 17255 | keep | 0 | Sep | 2021 | 0.011752 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-11 07:30 | 2021-09-11 11:14 | 30 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21091100006 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-09-11 | 6720 | keep | 0 | Sep | 2021 | 0.004577 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-11 07:36 | 2021-09-11 11:27 | 54 | 003:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA | S21091100007 | New_Event | Wire Down | Include | Include | Equipment | 231 | 2021-09-11 | 12474 | keep | 0 | Sep | 2021 | 0.008496 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2021-09-11 07:41 | 2021-09-11 07:45 | 922 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1401-08 | S21091100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-11 | 3688 | keep | 0 | Sep | 2021 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-09-11 07:41 | 2021-09-11 07:45 | 135 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1346-05 | S21091100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-11 | 540 | keep | 0 | Sep | 2021 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-09-11 07:44 | 2021-09-11 14:41 | 40 | 006:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | B21091100022 | New_Event | Cutout Failure | Include | Include | Equipment | 417 | 2021-09-11 | 16680 | keep | 0 | Sep | 2021 | 0.011361 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-11 07:45 | 2021-09-11 09:44 | 3 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21091100007 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2021-09-11 | 357 | keep | 0 | Sep | 2021 | 0.00024315 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-09-11 07:48 | 2021-09-11 07:49 | 351 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 351 | keep | 0 | Sep | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
VEGA BAJA | 2021-09-11 07:50 | 2021-09-11 12:59 | 40 | 005:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2021-09-11 | 12360 | keep | 0 | Sep | 2021 | 0.0084183 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-11 07:53 | 2021-09-11 12:28 | 40 | 004:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21091100011 | New_Event | Wire Down | Include | Include | Equipment | 275 | 2021-09-11 | 11000 | keep | 0 | Sep | 2021 | 0.007492 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-09-11 07:56 | 2021-09-11 11:20 | 30 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA ABB / 100 AMP FID-33776945 | A21091100009 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2021-09-11 | 6120 | keep | 0 | Sep | 2021 | 0.0041683 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-11 08:07 | 2021-09-11 12:07 | 7 | 004:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21091100012 | New_Event | Bad Weather | Include | Include | Weather | 240 | 2021-09-11 | 1680 | keep | 0 | Sep | 2021 | 0.0011442 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-11 08:09 | 2021-09-11 15:44 | 8 | 007:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21091100021 | New_Event | Bad Weather | Include | Include | Weather | 455 | 2021-09-11 | 3640 | keep | 0 | Sep | 2021 | 0.0024792 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-11 08:15 | 2021-09-11 10:04 | 24 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y SE LEVANTO NEUTRAL | S21090900125 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2021-09-11 | 2616 | keep | 0 | Sep | 2021 | 0.0017817 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
ARECIBO | 2021-09-11 08:20 | 2021-09-11 10:25 | 50 | 002:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A21091100017 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2021-09-11 | 6250 | keep | 0 | Sep | 2021 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-11 08:20 | 2021-09-11 18:21 | 10 | 010:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN RISER SE REPARO LINEA SECUNDARIA QUEMADA EN PEDESTAL | A21091100018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 601 | 2021-09-11 | 6010 | keep | 0 | Sep | 2021 | 0.0040934 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-11 08:28 | 2021-09-11 13:20 | 50 | 004:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21091100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2021-09-11 | 14600 | keep | 0 | Sep | 2021 | 0.009944 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 08:30 | 2021-09-11 10:32 | 51 | 002:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21091100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-09-11 | 6222 | keep | 0 | Sep | 2021 | 0.0042378 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
CANOVANAS | 2021-09-11 08:36 | 2021-09-11 09:12 | 10 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21091100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-09-11 | 360 | keep | 0 | Sep | 2021 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-11 08:39 | 2021-09-11 18:50 | 50 | 010:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37.5KVA X 37.5KVA | S21091100010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 611 | 2021-09-11 | 30550 | keep | 0 | Sep | 2021 | 0.020807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-09-11 08:42 | 2021-09-11 11:25 | 40 | 002:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHO Y REEMPLAZO AISLADOR | R21091100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-09-11 | 6520 | keep | 0 | Sep | 2021 | 0.0044407 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-11 08:47 | 2021-09-13 19:15 | 10 | 058:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50KVA | M21091100037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3508 | 2021-09-11 | 35080 | keep | 0 | Sep | 2021 | 0.023893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-11 08:48 | 2021-09-12 09:47 | 6 | 024:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE EN TRANSFORMADOR | M21091100038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1499 | 2021-09-11 | 8994 | keep | 0 | Sep | 2021 | 0.0061258 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-09-11 09:16 | 2021-09-11 15:50 | 5 | 006:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REGULARLO QUEDO 124V | C21091100024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 394 | 2021-09-11 | 1970 | keep | 0 | Sep | 2021 | 0.0013418 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-09-11 09:18 | 2021-09-11 15:13 | 40 | 005:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21091100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-09-11 | 14200 | keep | 0 | Sep | 2021 | 0.0096716 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-11 09:19 | 2021-09-11 15:32 | 50 | 006:13 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21091100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 373 | 2021-09-11 | 18650 | keep | 0 | Sep | 2021 | 0.012702 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-11 09:26 | 2021-09-11 09:46 | 1 | 000:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER CRUCE POR AVE | R21091100005 | New_Event |  |  | Include | Wildlife | 20 | 2021-09-11 | 20 | keep | 0 | Sep | 2021 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-09-11 09:46 | 2021-09-11 13:58 | 7 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091100034 | New_Event | Bad Weather | Include | Include | Weather | 252 | 2021-09-11 | 1764 | keep | 0 | Sep | 2021 | 0.0012015 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-11 10:04 | 2021-09-11 15:10 | 45 | 005:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21091000040 | New_Event | Wire Down | Include | Include | Equipment | 306 | 2021-09-11 | 13770 | keep | 0 | Sep | 2021 | 0.0093787 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-09-11 10:05 | 2021-09-11 10:06 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-09-11 10:05 | 2021-09-11 10:06 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1204-05 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
CAGUAS | 2021-09-11 10:14 | 2021-09-11 15:22 | 100 | 005:08 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | C21091100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2021-09-11 | 30800 | keep | 0 | Sep | 2021 | 0.020978 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-11 10:15 | 2021-09-11 10:16 | 922 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1401-08 | S21091100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 922 | keep | 0 | Sep | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-09-11 10:15 | 2021-09-11 10:16 | 135 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1346-05 | S21091100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 135 | keep | 0 | Sep | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-09-11 10:22 | 2021-09-11 12:13 | 40 | 001:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-09-11 | 4440 | keep | 0 | Sep | 2021 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-11 10:30 | 2021-09-11 14:12 | 20 | 003:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21091100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2021-09-11 | 4440 | keep | 0 | Sep | 2021 | 0.0030241 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-11 10:33 | 2021-09-11 10:34 | 2483 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | M21091100000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-11 | 2483 | keep | 0 | Sep | 2021 | 0.0016912 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-11 10:34 | 2021-09-11 15:34 | 20 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SEPARARON LINEAS ENTRELAZADAS | S21091100026 | New_Event | Wire Down | Include | Include | Equipment | 300 | 2021-09-11 | 6000 | keep | 0 | Sep | 2021 | 0.0040866 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-11 10:34 | 2021-09-11 12:15 | 250 | 001:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21091000131 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2021-09-11 | 25250 | keep | 0 | Sep | 2021 | 0.017198 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
ARECIBO | 2021-09-11 10:37 | 2021-09-12 10:55 | 3 | 024:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091100038 | New_Event | Bad Weather | Include | Include | Weather | 1458 | 2021-09-11 | 4374 | keep | 0 | Sep | 2021 | 0.0029791 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-09-11 10:38 | 2021-09-11 22:53 | 100 | 012:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21091100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 735 | 2021-09-11 | 73500 | keep | 0 | Sep | 2021 | 0.050061 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-11 10:49 | 2021-09-11 13:00 | 45 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21091100066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-09-11 | 5895 | keep | 0 | Sep | 2021 | 0.0040151 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-09-11 11:00 | 2021-09-11 12:55 | 10 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | S21091100000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-09-11 | 1150 | keep | 0 | Sep | 2021 | 0.00078326 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-11 11:03 | 2021-09-11 18:28 | 550 | 007:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21091100344 | New_Event | Wire Down | Include | Include | Equipment | 445 | 2021-09-11 | 244750 | keep | 0 | Sep | 2021 | 0.1667 | 0.0003746 | Sustained | FALSE | TRUE | Not_TMED_Event | 550
BAYAMON | 2021-09-11 11:11 | 2021-09-11 13:24 | 50 | 002:13 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | B21091100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-09-11 | 6650 | keep | 0 | Sep | 2021 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 11:30 | 2021-09-11 17:23 | 20 | 005:53 | P | TRANSFORMADOR AVERIADO | SE INSTALO TRANSFORMADOR Y SE DIVIDIO CARGA PROBLEMA DE MARIA WR-5919732 | B21091100000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 353 | 2021-09-11 | 7060 | keep | 0 | Sep | 2021 | 0.0048085 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-11 11:32 | 2021-09-11 14:14 | 15 | 002:42 | P | OTRAS CAUSAS | 2 X 15 EN UN TRANSFORMADOR Y 1 X 15 EN OTRO TRANSFORMADOR SE RETIRO CLIENTE CON PROBLEMA INTERNO | A21091100040 | New_Event | Other Causes | Include | Include | Other | 162 | 2021-09-11 | 2430 | keep | 0 | Sep | 2021 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-11 11:40 | 2021-09-11 14:11 | 75 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21091100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-09-11 | 11325 | keep | 0 | Sep | 2021 | 0.0077134 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
YAUCO | 2021-09-11 11:40 | 2021-09-11 11:41 | 64 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 64 | keep | 0 | Sep | 2021 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
HUMACAO | 2021-09-11 11:48 | 2021-09-11 15:29 | 100 | 003:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21091100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-09-11 | 22100 | keep | 0 | Sep | 2021 | 0.015052 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-11 11:56 | 2021-09-11 12:31 | 7621 | 000:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR | R21091100017 | New_Event | Wire Down | Include | Include | Equipment | 35 | 2021-09-11 | 266735 | keep | 0 | Sep | 2021 | 0.18167 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2021-09-11 12:04 | 2021-09-11 12:06 | 297 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA EL 40% DE LA CARGA ESTA POR EL 1335-05 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-11 | 594 | keep | 0 | Sep | 2021 | 0.00040457 | 0.00020229 | Momentary | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2021-09-11 12:04 | 2021-09-11 12:06 | 1397 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1335-05 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-11 | 2794 | keep | 0 | Sep | 2021 | 0.001903 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
SAN JUAN | 2021-09-11 12:04 | 2021-09-11 12:06 | 314 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA 1301-04 Y 40% DEL 1301-02 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-11 | 628 | keep | 0 | Sep | 2021 | 0.00042773 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
MAYAGÃœEZ | 2021-09-11 12:05 | 2021-09-13 14:45 | 50 | 050:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091100094 | New_Event | Bad Weather | Include | Include | Weather | 3040 | 2021-09-11 | 152000 | keep | 0 | Sep | 2021 | 0.10353 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 12:14 | 2021-09-11 17:45 | 20 | 005:31 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | S21091100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2021-09-11 | 6620 | keep | 0 | Sep | 2021 | 0.0045089 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-11 12:15 | 2021-09-11 12:16 | 418 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 418 | keep | 0 | Sep | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2021-09-11 12:16 | 2021-09-11 12:17 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-11 12:18 | 2021-09-11 12:19 | 1860 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21091100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 1860 | keep | 0 | Sep | 2021 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2021-09-11 12:21 | 2021-09-11 19:22 | 80 | 007:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE DESGANCHO | B21091100087 | New_Event | Cutout Failure | Include | Include | Equipment | 421 | 2021-09-11 | 33680 | keep | 0 | Sep | 2021 | 0.022939 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-11 12:30 | 2021-09-11 16:48 | 35 | 004:18 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21091100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2021-09-11 | 9030 | keep | 0 | Sep | 2021 | 0.0061503 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-09-11 12:31 | 2021-09-11 17:43 | 150 | 005:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | R21091100017 | Partial_restoration | Wire Down | Include | Include | Equipment | 312 | 2021-09-11 | 46800 | keep | 0 | Sep | 2021 | 0.031875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-11 12:36 | 2021-09-11 16:46 | 30 | 004:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21091100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-09-11 | 7500 | keep | 0 | Sep | 2021 | 0.0051082 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-11 12:46 | 2021-09-11 15:22 | 1 | 002:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | A21091100044 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2021-09-11 | 156 | keep | 0 | Sep | 2021 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-11 12:46 | 2021-09-11 17:55 | 75 | 005:09 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21091100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2021-09-11 | 23175 | keep | 0 | Sep | 2021 | 0.015784 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-11 12:48 | 2021-09-11 16:10 | 35 | 003:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21091100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-09-11 | 7070 | keep | 0 | Sep | 2021 | 0.0048153 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-11 12:58 | 2021-09-11 12:59 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 1606 | keep | 0 | Sep | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2021-09-11 13:00 | 2021-09-11 21:55 | 50 | 008:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEAS DESGANCHE | P21091100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 535 | 2021-09-11 | 26750 | keep | 0 | Sep | 2021 | 0.018219 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-11 13:00 | 2021-09-11 18:16 | 90 | 005:16 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA PRIMARIA | M21091100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-09-11 | 28440 | keep | 0 | Sep | 2021 | 0.01937 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-09-11 13:05 | 2021-09-11 19:16 | 30 | 006:11 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA | B21091100104 | New_Event | Bad Weather | Include | Include | Weather | 371 | 2021-09-11 | 11130 | keep | 0 | Sep | 2021 | 0.0075806 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-11 13:18 | 2021-09-11 16:41 | 50 | 003:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-09-11 | 10150 | keep | 0 | Sep | 2021 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-11 13:22 | 2021-09-11 14:57 | 40 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21091100074 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-09-11 | 3800 | keep | 0 | Sep | 2021 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-11 13:27 | 2021-09-11 17:38 | 75 | 004:11 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-09-11 | 18825 | keep | 0 | Sep | 2021 | 0.012822 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-09-11 13:29 | 2021-09-11 13:38 | 1952 | 000:09 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR FUERTES VIENTOS | P21091100023 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-09-11 | 17568 | keep | 0 | Sep | 2021 | 0.011965 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
PONCE | 2021-09-11 13:30 | 2021-09-11 14:58 | 349 | 001:28 | T | DESGANCHE | DISPARO INTERRUPTOR SE ABRE MACHETES EN CALLE POWER ESQUINA CONCORDIA Y SE COLOCA INTERRUPTOR EN SERVICIO | P21091100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-09-11 | 30712 | keep | 0 | Sep | 2021 | 0.020918 | 0.0002377 | Sustained | FALSE | FALSE | Not_TMED_Event | 349
MAYAGÃœEZ | 2021-09-11 13:30 | 2021-09-11 14:14 | 3147 | 000:44 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE RETIRO RAMA Y SE REALIZO PRUEBA QUEDO EN SERVICIO | M21091100069 | New_Event | Bad Weather | Include | Include | Weather | 44 | 2021-09-11 | 138468 | keep | 0 | Sep | 2021 | 0.09431 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
PONCE | 2021-09-11 13:34 | 2021-09-11 13:35 | 595 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR FUERTES VIENTOS | P21091100024 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-11 | 595 | keep | 0 | Sep | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
PONCE | 2021-09-11 13:36 | 2021-09-11 13:37 | 1157 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR FUERTES VIENTOS | P21091100031 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-11 | 1157 | keep | 0 | Sep | 2021 | 0.00078803 | 0.00078803 | Momentary | FALSE | FALSE | Not_TMED_Event | 1157
PONCE | 2021-09-11 13:36 | 2021-09-11 13:37 | 595 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR FUERTES VIENTOS | P21091100030 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-09-11 | 595 | keep | 0 | Sep | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
PONCE | 2021-09-11 13:36 | 2021-09-11 13:37 | 969 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR FUERTES VIENTOS | P21091100036 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-11 | 969 | keep | 0 | Sep | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
PONCE | 2021-09-11 13:37 | 2021-09-11 13:38 | 1078 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR FUERTES VIENTOS | P21091100037 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-11 | 1078 | keep | 0 | Sep | 2021 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
PONCE | 2021-09-11 13:38 | 2021-09-11 14:06 | 475 | 000:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES | P21091100112 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 28 | 2021-09-11 | 13300 | keep | 0 | Sep | 2021 | 0.0090586 | 0.00032352 | Sustained | FALSE | TRUE | Not_TMED_Event | 475
PONCE | 2021-09-11 13:39 | 2021-09-12 09:39 | 58 | 020:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA CALLE AVILA, 1 X 65 EN CALLE NAVARRA | P21091100038 | New_Event | Bad Weather | Include | Include | Weather | 1200 | 2021-09-11 | 69600 | keep | 0 | Sep | 2021 | 0.047404 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
PONCE | 2021-09-11 13:42 | 2021-09-11 17:06 | 2689 | 003:24 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PATRULLO ALIMENTADOR Y NO SE ENCONTRO CAUSA | P21091100042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-09-11 | 548556 | keep | 0 | Sep | 2021 | 0.37362 | 0.0018315 | Sustained | FALSE | FALSE | Not_TMED_Event | 2689
UTUADO | 2021-09-11 13:47 | 2021-09-11 14:08 | 1241 | 000:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21091100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-09-11 | 26061 | keep | 0 | Sep | 2021 | 0.01775 | 0.00084524 | Sustained | FALSE | TRUE | Not_TMED_Event | 1241
UTUADO | 2021-09-11 13:47 | 2021-09-11 14:09 | 650 | 000:22 | T | TRANSFORMADOR AVERIADO | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21091100048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 22 | 2021-09-11 | 14300 | keep | 0 | Sep | 2021 | 0.0097397 | 0.00044271 | Sustained | FALSE | TRUE | Not_TMED_Event | 650
VEGA BAJA | 2021-09-11 13:54 | 2021-09-12 16:13 | 20 | 026:19 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21091100112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1579 | 2021-09-11 | 31580 | keep | 0 | Sep | 2021 | 0.021509 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-11 13:55 | 2021-09-11 19:45 | 150 | 005:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2021-09-11 | 52500 | keep | 0 | Sep | 2021 | 0.035758 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-09-11 13:58 | 2021-09-11 13:59 | 1382 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-11 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-11 13:58 | 2021-09-11 13:59 | 654 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-11 | 654 | keep | 0 | Sep | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
UTUADO | 2021-09-11 13:59 | 2021-09-11 14:17 | 7 | 000:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091100034 | New_Event | Bad Weather | Include | Include | Weather | 18 | 2021-09-11 | 126 | keep | 0 | Sep | 2021 | 8.5818e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-09-11 14:03 | 2021-09-11 14:04 | 1979 | 000:01 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SUB PORTATIL 10 | P21091100076 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-11 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-11 14:03 | 2021-09-11 14:04 | 5069 | 000:01 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SUB PORTATIL 10 | P21091100076 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-11 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-11 14:03 | 2021-09-11 14:04 | 5063 | 000:01 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SUB PORTATIL 10 | P21091100076 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-11 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2021-09-11 14:04 | 2021-09-11 18:15 | 200 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE PROCEDIO A SECCIONALIZAR Y SE TRANSFIRIO CARGA AL 5011-05 | P21091100077 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 251 | 2021-09-11 | 50200 | keep | 0 | Sep | 2021 | 0.034191 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-09-11 14:06 | 2021-09-11 14:52 | 1078 | 000:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR DEBIDO A LINEA PRIMARIA PARTIDA EN EL SUELO INFORMADO POR MANUEL ACOSTA | P21091100071 | Additional_clients | Wire Down | Include | Include | Equipment | 46 | 2021-09-11 | 49588 | keep | 0 | Sep | 2021 | 0.033774 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-11 14:07 | 2021-09-11 16:01 | 16 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 Y 1 X 10 EN 2 TRANSFORMADORES LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091100052 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2021-09-11 | 1824 | keep | 0 | Sep | 2021 | 0.0012423 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-09-11 14:08 | 2021-09-11 17:21 | 60 | 003:13 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA | S21091100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-09-11 | 11580 | keep | 0 | Sep | 2021 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-11 14:08 | 2021-09-11 15:02 | 11 | 000:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR EN EL FID33798174 / MARCA GE / #SERIE E211683Y378 / CAPACIDAD 37.5KVG / VOLTAJE 8320/14200V 120/240V | A21091000084 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 54 | 2021-09-11 | 594 | keep | 0 | Sep | 2021 | 0.00040457 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-09-11 14:11 | 2021-09-12 18:12 | 25 | 028:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1681 | 2021-09-11 | 42025 | keep | 0 | Sep | 2021 | 0.028623 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-11 14:12 | 2021-09-11 15:07 | 1825 | 000:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2021-09-11 | 100375 | keep | 0 | Sep | 2021 | 0.068365 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-09-11 14:12 | 2021-09-11 15:07 | 47 | 000:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2021-09-11 | 2585 | keep | 0 | Sep | 2021 | 0.0017606 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-09-11 14:12 | 2021-09-11 15:07 | 315 | 000:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2021-09-11 | 17325 | keep | 0 | Sep | 2021 | 0.0118 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-09-11 14:12 | 2021-09-11 15:07 | 2 | 000:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2021-09-11 | 110 | keep | 0 | Sep | 2021 | 7.492e-05 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-09-11 14:12 | 2021-09-11 15:07 | 2391 | 000:55 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2021-09-11 | 131505 | keep | 0 | Sep | 2021 | 0.089567 | 0.0016285 | Sustained | FALSE | TRUE | Not_TMED_Event | 2391
BAYAMON | 2021-09-11 14:12 | 2021-09-11 14:13 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
ARECIBO | 2021-09-11 14:12 | 2021-09-11 18:12 | 1500 | 004:00 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO EL AUXILIAR DE LINEA FASE B QUE SE AVERIO POR UNO MARCA COOPER DE 900AMP Y SE CERRO EL INTERRUPTOR | A21091100055 | New_Event | Switch Failure | Include | Include | Equipment | 240 | 2021-09-11 | 360000 | keep | 0 | Sep | 2021 | 0.24519 | 0.0010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 1500
BAYAMON | 2021-09-11 14:14 | 2021-09-11 19:23 | 50 | 005:09 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-09-11 | 15450 | keep | 0 | Sep | 2021 | 0.010523 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-11 14:16 | 2021-09-11 18:41 | 150 | 004:25 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHO Y REMPLAZO PIN POLE TOP | C21091100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2021-09-11 | 39750 | keep | 0 | Sep | 2021 | 0.027074 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-11 14:16 | 2021-09-11 22:57 | 1352 | 008:41 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE DE TIERRA PEGANDO A LINEA | M21091100307 | New_Event | Wire Down | Include | Include | Equipment | 521 | 2021-09-11 | 704392 | keep | 0 | Sep | 2021 | 0.47976 | 0.00092084 | Sustained | FALSE | TRUE | Not_TMED_Event | 1352
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:24 | 1984 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1911-07 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-09-11 | 11904 | keep | 0 | Sep | 2021 | 0.0081078 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:20 | 878 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE L-4300 LLEVA EL 1714-05 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-11 | 1756 | keep | 0 | Sep | 2021 | 0.001196 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:20 | 293 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-4300 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-11 | 586 | keep | 0 | Sep | 2021 | 0.00039912 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:20 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-4300 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-11 | 630 | keep | 0 | Sep | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:20 | 216 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-4300 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-11 | 432 | keep | 0 | Sep | 2021 | 0.00029423 | 0.00014712 | Momentary | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:20 | 1310 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-4300 LLEVA EL 1714-05 | S21091100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-11 | 2620 | keep | 0 | Sep | 2021 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-09-11 14:18 | 2021-09-11 14:24 | 577 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LA CARGA ESTA POR EL 1529-12 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-09-11 | 3462 | keep | 0 | Sep | 2021 | 0.002358 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2021-09-11 14:26 | 2021-09-11 14:27 | 1633 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21091100117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 1633 | keep | 0 | Sep | 2021 | 0.0011122 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2021-09-11 14:27 | 2021-09-11 19:16 | 25 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091100148 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 289 | 2021-09-11 | 7225 | keep | 0 | Sep | 2021 | 0.0049209 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-09-11 14:27 | 2021-09-11 18:30 | 45 | 004:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-09-11 | 10935 | keep | 0 | Sep | 2021 | 0.0074478 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-09-11 14:29 | 2021-09-12 15:22 | 80 | 024:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1493 | 2021-09-11 | 119440 | keep | 0 | Sep | 2021 | 0.08135 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-11 14:34 | 2021-09-11 20:45 | 40 | 006:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21091100120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2021-09-11 | 14840 | keep | 0 | Sep | 2021 | 0.010107 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-11 14:35 | 2021-09-11 16:04 | 6 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR SUMERGIBLE PARA REPARAR CONEXIONES SECUNDARIAS | S21090900008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2021-09-11 | 534 | keep | 0 | Sep | 2021 | 0.0003637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-11 14:37 | 2021-09-11 15:58 | 12 | 001:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 4.16KV AVERIADO X 37.5KVA | P21091100178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2021-09-11 | 972 | keep | 0 | Sep | 2021 | 0.00066202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-11 14:37 | 2021-09-11 17:43 | 1617 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21091100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-11 | 300762 | keep | 0 | Sep | 2021 | 0.20485 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-11 14:37 | 2021-09-11 17:43 | 1017 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21091100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-11 | 189162 | keep | 0 | Sep | 2021 | 0.12884 | 0.00069267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-11 14:37 | 2021-09-11 17:43 | 828 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21091100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-11 | 154008 | keep | 0 | Sep | 2021 | 0.10489 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-11 14:37 | 2021-09-11 17:43 | 863 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21091100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-11 | 160518 | keep | 0 | Sep | 2021 | 0.10933 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-11 14:37 | 2021-09-11 17:43 | 309 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21091100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-11 | 57474 | keep | 0 | Sep | 2021 | 0.039145 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-11 14:37 | 2021-09-11 17:43 | 176 | 003:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21091100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 186 | 2021-09-11 | 32736 | keep | 0 | Sep | 2021 | 0.022296 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
FAJARDO | 2021-09-11 14:45 | 2021-09-11 15:41 | 40 | 000:56 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21091100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-09-11 | 2240 | keep | 0 | Sep | 2021 | 0.0015257 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-11 14:45 | 2021-09-11 14:46 | 1131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 1131 | keep | 0 | Sep | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BAYAMON | 2021-09-11 14:46 | 2021-09-11 14:47 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21091100130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 3295 | keep | 0 | Sep | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
PONCE | 2021-09-11 14:52 | 2021-09-11 16:31 | 475 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES | P21091100112 | Partial_restoration | Wire Down | Include | Include | Equipment | 99 | 2021-09-11 | 47025 | keep | 0 | Sep | 2021 | 0.032029 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-11 14:55 | 2021-09-12 10:18 | 54 | 019:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21091100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1163 | 2021-09-11 | 62802 | keep | 0 | Sep | 2021 | 0.042774 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
PONCE | 2021-09-11 14:58 | 2021-09-11 17:10 | 154 | 002:12 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | P21091100116 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-09-11 | 20328 | keep | 0 | Sep | 2021 | 0.013845 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-11 15:01 | 2021-09-11 17:55 | 30 | 002:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-09-11 | 5220 | keep | 0 | Sep | 2021 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-11 15:01 | 2021-09-11 18:11 | 50 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | P21091100109 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-09-11 | 9500 | keep | 0 | Sep | 2021 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-09-11 15:01 | 2021-09-11 17:03 | 80 | 002:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P31091100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-09-11 | 9760 | keep | 0 | Sep | 2021 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-11 15:01 | 2021-09-12 18:01 | 20 | 027:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA PRINCIPAL Y 1 X 30 EN CORTE DE LINEA INTERMEDIO | B21091100135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1620 | 2021-09-11 | 32400 | keep | 0 | Sep | 2021 | 0.022067 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-11 15:02 | 2021-09-11 21:15 | 3147 | 006:13 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR | M21091100153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 373 | 2021-09-11 | 1173831 | keep | 0 | Sep | 2021 | 0.79949 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
ARECIBO | 2021-09-11 15:02 | 2021-09-11 20:45 | 300 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091100064 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2021-09-11 | 102900 | keep | 0 | Sep | 2021 | 0.070085 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BARRANQUITAS | 2021-09-11 15:03 | 2021-09-11 17:16 | 50 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091100079 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-09-11 | 6650 | keep | 0 | Sep | 2021 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-11 15:05 | 2021-09-11 15:06 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
BAYAMON | 2021-09-11 15:06 | 2021-09-12 10:30 | 60 | 019:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1164 | 2021-09-11 | 69840 | keep | 0 | Sep | 2021 | 0.047568 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-11 15:07 | 2021-09-11 15:09 | 143 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S21091100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-11 | 286 | keep | 0 | Sep | 2021 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2021-09-11 15:09 | 2021-09-11 23:35 | 20 | 008:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21091100142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 506 | 2021-09-11 | 10120 | keep | 0 | Sep | 2021 | 0.0068927 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-11 15:10 | 2021-09-11 18:24 | 50 | 003:14 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-09-11 | 9700 | keep | 0 | Sep | 2021 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-11 15:10 | 2021-09-12 17:34 | 50 | 026:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21091100082 | New_Event | Bad Weather | Include | Include | Weather | 1584 | 2021-09-11 | 79200 | keep | 0 | Sep | 2021 | 0.053943 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 15:11 | 2021-09-11 19:40 | 30 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2021-09-11 | 8070 | keep | 0 | Sep | 2021 | 0.0054964 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-11 15:14 | 2021-09-11 18:55 | 100 | 003:41 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-09-11 | 22100 | keep | 0 | Sep | 2021 | 0.015052 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-11 15:14 | 2021-09-11 15:15 | 1066 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 1066 | keep | 0 | Sep | 2021 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
MAYAGÃœEZ | 2021-09-11 15:15 | 2021-09-12 11:08 | 7 | 019:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21091100247 | New_Event | Bad Weather | Include | Include | Weather | 1193 | 2021-09-11 | 8351 | keep | 0 | Sep | 2021 | 0.0056878 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-09-11 15:15 | 2021-09-12 09:05 | 15 | 017:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091100065 | New_Event | Bad Weather | Include | Include | Weather | 1070 | 2021-09-11 | 16050 | keep | 0 | Sep | 2021 | 0.010932 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-11 15:21 | 2021-09-12 15:20 | 80 | 023:59 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091100254 | New_Event | Bad Weather | Include | Include | Weather | 1439 | 2021-09-11 | 115120 | keep | 0 | Sep | 2021 | 0.078408 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-11 15:21 | 2021-09-11 19:23 | 100 | 004:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REPARO AISLACION | B21091100151 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 242 | 2021-09-11 | 24200 | keep | 0 | Sep | 2021 | 0.016483 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-11 15:29 | 2021-09-11 20:40 | 140 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN SALIDA DE CONVERTIDOR FUERTES VIENTOS | P21091100120 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2021-09-11 | 43540 | keep | 0 | Sep | 2021 | 0.029655 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2021-09-11 15:30 | 2021-09-11 16:20 | 30 | 000:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091100268 | New_Event | Bad Weather | Include | Include | Weather | 50 | 2021-09-11 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-11 15:31 | 2021-09-11 16:15 | 100 | 000:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091100270 | New_Event | Bad Weather | Include | Include | Weather | 44 | 2021-09-11 | 4400 | keep | 0 | Sep | 2021 | 0.0029968 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-11 15:32 | 2021-09-11 15:33 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 478 | keep | 0 | Sep | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-09-11 15:32 | 2021-09-11 15:33 | 900 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 900 | keep | 0 | Sep | 2021 | 0.00061299 | 0.00061299 | Momentary | FALSE | FALSE | Not_TMED_Event | 900
SAN JUAN | 2021-09-11 15:35 | 2021-09-11 16:33 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES QUEMADOS EN SECUNDARIA | S21091100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-09-11 | 580 | keep | 0 | Sep | 2021 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-11 15:35 | 2021-09-12 00:52 | 80 | 009:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTE PARA SECCIONALIZAR AVERIA DE LINEA PARTIDA | A21091100070 | New_Event | Wire Down | Include | Include | Equipment | 557 | 2021-09-11 | 44560 | keep | 0 | Sep | 2021 | 0.03035 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-11 15:38 | 2021-09-11 15:39 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21091100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 2379 | keep | 0 | Sep | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
SAN JUAN | 2021-09-11 15:51 | 2021-09-11 16:40 | 10 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA EN EL PISO Y REPARAR TOMA DE CLIENTE | S21090800146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-09-11 | 490 | keep | 0 | Sep | 2021 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-11 16:06 | 2021-09-11 16:07 | 1076 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | P21091100184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-11 | 1076 | keep | 0 | Sep | 2021 | 0.00073286 | 0.00073286 | Momentary | FALSE | FALSE | Not_TMED_Event | 1076
PONCE | 2021-09-11 16:07 | 2021-09-12 16:32 | 150 | 024:25 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100154 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1465 | 2021-09-11 | 219750 | keep | 0 | Sep | 2021 | 0.14967 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-09-11 16:08 | 2021-09-12 14:22 | 200 | 022:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21091100137 | New_Event | Wire Down | Include | Include | Equipment | 1334 | 2021-09-11 | 266800 | keep | 0 | Sep | 2021 | 0.18172 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-09-11 16:13 | 2021-09-12 17:40 | 60 | 025:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARARON LINEAS PRIMARIAS PARTIDAS | A21091100077 | New_Event | Wire Down | Include | Include | Equipment | 1527 | 2021-09-11 | 91620 | keep | 0 | Sep | 2021 | 0.062402 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-11 16:22 | 2021-09-11 18:59 | 30 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091100081 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-09-11 | 4710 | keep | 0 | Sep | 2021 | 0.003208 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-11 16:26 | 2021-09-11 16:54 | 300 | 000:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2021-09-11 | 8400 | keep | 0 | Sep | 2021 | 0.0057212 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-09-11 16:31 | 2021-09-11 17:33 | 50 | 001:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-09-11 | 3100 | keep | 0 | Sep | 2021 | 0.0021114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-11 16:32 | 2021-09-13 09:36 | 50 | 041:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091100320 | New_Event | Bad Weather | Include | Include | Weather | 2464 | 2021-09-11 | 123200 | keep | 0 | Sep | 2021 | 0.083911 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-11 16:34 | 2021-09-12 12:49 | 150 | 020:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | M21091100327 | New_Event | Bad Weather | Include | Include | Weather | 1215 | 2021-09-11 | 182250 | keep | 0 | Sep | 2021 | 0.12413 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-09-11 16:38 | 2021-09-12 15:30 | 20 | 022:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21091100086 | New_Event | Bad Weather | Include | Include | Weather | 1372 | 2021-09-11 | 27440 | keep | 0 | Sep | 2021 | 0.018689 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-09-11 16:46 | 2021-09-12 12:05 | 100 | 019:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091100087 | New_Event | Bad Weather | Include | Include | Weather | 1159 | 2021-09-11 | 115900 | keep | 0 | Sep | 2021 | 0.078939 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-11 17:09 | 2021-09-11 17:12 | 776 | 000:03 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DEL SUPERVISOR POR MACHETE ARQUEANDO | B21091100000 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2021-09-11 | 2328 | keep | 0 | Sep | 2021 | 0.0015856 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
MAYAGÃœEZ | 2021-09-11 17:23 | 2021-09-12 13:37 | 12 | 020:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | M21091200344 | New_Event | Bad Weather | Include | Include | Weather | 1214 | 2021-09-11 | 14568 | keep | 0 | Sep | 2021 | 0.0099222 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
GUAYAMA | 2021-09-11 17:32 | 2021-09-11 19:03 | 600 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21091100159 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2021-09-11 | 54600 | keep | 0 | Sep | 2021 | 0.037188 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
YAUCO | 2021-09-11 17:34 | 2021-09-11 19:08 | 25 | 001:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-09-11 | 2350 | keep | 0 | Sep | 2021 | 0.0016006 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-11 17:50 | 2021-09-11 20:01 | 6 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | A21091100095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2021-09-11 | 786 | keep | 0 | Sep | 2021 | 0.00053534 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
ARECIBO | 2021-09-11 18:06 | 2021-09-12 10:05 | 8 | 015:59 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21091100097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 959 | 2021-09-11 | 7672 | keep | 0 | Sep | 2021 | 0.0052254 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
PONCE | 2021-09-11 18:12 | 2021-09-12 12:00 | 75 | 017:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 1 X 100 EN CORTE DE LINEA MAL TIEMPO | P21091200017 | New_Event | Bad Weather | Include | Include | Weather | 1068 | 2021-09-11 | 80100 | keep | 0 | Sep | 2021 | 0.054556 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-11 18:12 | 2021-09-12 12:45 | 20 | 018:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21091100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1113 | 2021-09-11 | 22260 | keep | 0 | Sep | 2021 | 0.015161 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-11 18:18 | 2021-09-12 15:11 | 150 | 020:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091100368 | New_Event | Bad Weather | Include | Include | Weather | 1253 | 2021-09-11 | 187950 | keep | 0 | Sep | 2021 | 0.12801 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-09-11 18:36 | 2021-09-12 11:00 | 40 | 016:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | C21091100122 | New_Event | Wire Down | Include | Include | Equipment | 984 | 2021-09-11 | 39360 | keep | 0 | Sep | 2021 | 0.026808 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-11 18:37 | 2021-09-11 18:38 | 3046 | 000:01 | T | DESGANCHE | RECIERRE | R21091100098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-11 | 3046 | keep | 0 | Sep | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-09-11 18:38 | 2021-09-12 18:31 | 80 | 023:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21091100100 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1433 | 2021-09-11 | 114640 | keep | 0 | Sep | 2021 | 0.078081 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-11 18:40 | 2021-09-11 21:56 | 2782 | 003:16 | T | NO SE REPORTO CAUSA | SE DISPARO ALIMENTADOR SE CERRO POR SCADA PROBO MALO | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2021-09-11 | 545272 | keep | 0 | Sep | 2021 | 0.37138 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2021-09-11 18:44 | 2021-09-11 18:45 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 271 | keep | 0 | Sep | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-09-11 18:45 | 2021-09-11 18:46 | 681 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 681 | keep | 0 | Sep | 2021 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
PONCE | 2021-09-11 18:47 | 2021-09-12 15:21 | 110 | 020:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA LINEA PRIMARIA ARRIADA | P21091100175 | New_Event | Wire Down | Include | Include | Equipment | 1234 | 2021-09-11 | 135740 | keep | 0 | Sep | 2021 | 0.092452 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
AGUADILLA | 2021-09-11 18:50 | 2021-09-11 20:03 | 40 | 001:13 | P | HERRAJE ROTO O PODRIDO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CRUZETAS PARTIDAS | M21091000297 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 73 | 2021-09-11 | 2920 | keep | 0 | Sep | 2021 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-11 19:05 | 2021-09-12 09:20 | 30 | 014:15 | P | DESGANCHE | 2 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 855 | 2021-09-11 | 25650 | keep | 0 | Sep | 2021 | 0.01747 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-11 19:11 | 2021-09-11 19:12 | 75 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21091100181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-11 | 75 | keep | 0 | Sep | 2021 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-09-11 19:16 | 2021-09-12 15:30 | 12 | 020:14 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | S21091100127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1214 | 2021-09-11 | 14568 | keep | 0 | Sep | 2021 | 0.0099222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-09-11 19:18 | 2021-09-11 21:30 | 100 | 002:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE Y SE CERRO PUENTE PRIMARIO | P21091100180 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2021-09-11 | 13200 | keep | 0 | Sep | 2021 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-11 19:26 | 2021-09-11 21:43 | 100 | 002:17 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-09-11 | 13700 | keep | 0 | Sep | 2021 | 0.009331 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-11 19:42 | 2021-09-12 05:27 | 1192 | 009:45 | T | TRANSFORMADOR AVERIADO | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE CONVERTIDOR | M21091100399 | New_Event | Service Transformer Failure | Include | Include | Equipment | 585 | 2021-09-11 | 697320 | keep | 0 | Sep | 2021 | 0.47494 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2021-09-11 20:03 | 2021-09-12 12:28 | 50 | 016:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091100414 | New_Event | Bad Weather | Include | Include | Weather | 985 | 2021-09-11 | 49250 | keep | 0 | Sep | 2021 | 0.033544 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 20:04 | 2021-09-12 00:53 | 45 | 004:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | B21091100148 | New_Event | Wire Down | Include | Include | Equipment | 289 | 2021-09-11 | 13005 | keep | 0 | Sep | 2021 | 0.0088576 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BARRANQUITAS | 2021-09-11 20:05 | 2021-09-11 21:25 | 2565 | 001:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO INTERRUPTOR PARA LEVANTAR NEUTRAL PRIMARIO | C21091100142 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2021-09-11 | 205200 | keep | 0 | Sep | 2021 | 0.13976 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
BAYAMON | 2021-09-11 20:08 | 2021-09-12 15:06 | 30 | 018:58 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1138 | 2021-09-11 | 34140 | keep | 0 | Sep | 2021 | 0.023253 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-11 20:13 | 2021-09-12 12:59 | 40 | 016:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA RETEZO LINEA Y REMPLAZO AISLADOR | C21091100144 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1006 | 2021-09-11 | 40240 | keep | 0 | Sep | 2021 | 0.027407 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-11 20:18 | 2021-09-12 19:02 | 40 | 022:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21091100147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1364 | 2021-09-11 | 54560 | keep | 0 | Sep | 2021 | 0.037161 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-11 20:23 | 2021-09-12 10:15 | 50 | 013:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA VECINOS DESGANCHANDO | C21091100149 | New_Event |  |  | Include | Wildlife | 832 | 2021-09-11 | 41600 | keep | 0 | Sep | 2021 | 0.028334 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-11 20:24 | 2021-09-12 19:19 | 50 | 022:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091100190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1375 | 2021-09-11 | 68750 | keep | 0 | Sep | 2021 | 0.046825 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-11 20:58 | 2021-09-12 16:34 | 15 | 019:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21091100118 | New_Event | Bad Weather | Include | Include | Weather | 1176 | 2021-09-11 | 17640 | keep | 0 | Sep | 2021 | 0.012015 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-11 21:28 | 2021-09-12 15:08 | 12 | 017:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21091100177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1060 | 2021-09-11 | 12720 | keep | 0 | Sep | 2021 | 0.0086635 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-09-11 21:30 | 2021-09-13 10:00 | 35 | 036:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21091100198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2190 | 2021-09-11 | 76650 | keep | 0 | Sep | 2021 | 0.052206 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-11 21:30 | 2021-09-12 10:35 | 50 | 013:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21091100120 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 785 | 2021-09-11 | 39250 | keep | 0 | Sep | 2021 | 0.026733 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-11 21:31 | 2021-09-12 13:36 | 35 | 016:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | P21091100199 | New_Event | Wire Down | Include | Include | Equipment | 965 | 2021-09-11 | 33775 | keep | 0 | Sep | 2021 | 0.023004 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-11 21:39 | 2021-09-12 08:50 | 60 | 011:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091100121 | New_Event | Bad Weather | Include | Include | Weather | 671 | 2021-09-11 | 40260 | keep | 0 | Sep | 2021 | 0.027421 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-11 21:44 | 2021-09-12 09:59 | 300 | 012:15 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | M21091100442 | New_Event | Bad Weather | Include | Include | Weather | 735 | 2021-09-11 | 220500 | keep | 0 | Sep | 2021 | 0.15018 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-09-11 21:45 | 2021-09-12 11:50 | 200 | 014:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21091100444 | New_Event | Wire Down | Include | Include | Equipment | 845 | 2021-09-11 | 169000 | keep | 0 | Sep | 2021 | 0.11511 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-09-11 21:56 | 2021-09-11 22:07 | 2642 | 000:11 | P | NO SE REPORTO CAUSA | SE ABRIO MACHETES EN CALLE E. CONDE AL LADO DE LA FUNERARIA CARDONA SE DEJO 5% EN SERVICIO | S21091100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-09-11 | 29062 | keep | 0 | Sep | 2021 | 0.019794 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-11 22:07 | 2021-09-11 23:19 | 514 | 001:12 | T | NO SE REPORTO CAUSA | SE DISPARO ALIMENTADOR SE CERRO POR SCADA PROBO MALO EL 20% DE LA CARGA SE ENCUENTRA POR EL 1118-10 | S21091100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-09-11 | 37008 | keep | 0 | Sep | 2021 | 0.025206 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2021-09-11 22:07 | 2021-09-11 23:19 | 2782 | 001:12 | T | NO SE REPORTO CAUSA | SE DISPARO ALIMENTADOR SE CERRO POR SCADA PROBO MALO LLEVA 20% DEL 1111-01 | S21091100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-09-11 | 200304 | keep | 0 | Sep | 2021 | 0.13643 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-11 22:10 | 2021-09-12 13:41 | 50 | 015:31 | T | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO | M21091100397 | New_Event | Defective Pole | Include | Include | Equipment | 931 | 2021-09-11 | 46550 | keep | 0 | Sep | 2021 | 0.031705 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-09-11 22:13 | 2021-09-11 22:14 | 100 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21091100067 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-11 | 100 | keep | 0 | Sep | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-11 22:25 | 2021-09-12 11:45 | 12 | 013:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21091100228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 800 | 2021-09-11 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-11 22:33 | 2021-09-12 09:25 | 200 | 010:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | C21091100165 | New_Event | Cutout Failure | Include | Include | Equipment | 652 | 2021-09-11 | 130400 | keep | 0 | Sep | 2021 | 0.088815 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-09-11 22:33 | 2021-09-12 18:05 | 50 | 019:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091100446 | New_Event | Bad Weather | Include | Include | Weather | 1172 | 2021-09-11 | 58600 | keep | 0 | Sep | 2021 | 0.039912 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-11 23:29 | 2021-09-12 18:31 | 15 | 019:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN AEREO PROVISIONAL | S21091100233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1142 | 2021-09-11 | 17130 | keep | 0 | Sep | 2021 | 0.011667 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-11 23:36 | 2021-09-14 20:18 | 40 | 068:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | S21091100221 | New_Event | Wire Down | Include | Include | Equipment | 4122 | 2021-09-11 | 164880 | keep | 0 | Sep | 2021 | 0.1123 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-11 23:58 | 2021-09-12 02:17 | 3654 | 002:19 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO CULEBRA EN RISER DE SALIDA | A21091100128 | New_Event |  |  | Include | Wildlife | 139 | 2021-09-11 | 507906 | keep | 0 | Sep | 2021 | 0.34593 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
SAN JUAN | 2021-09-12 00:11 | 2021-09-12 16:10 | 87 | 015:59 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 100 EN CORTE DE LINEA Y 3 X 25 SMU20 EN SU-6 SE REALIZO MANTENIMIENTO A SU-6 | S21091200007 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 959 | 2021-09-12 | 83433 | keep | 0 | Sep | 2021 | 0.056826 | 5.9255e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 87
ARECIBO | 2021-09-12 00:52 | 2021-09-13 11:36 | 25 | 034:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES PRIMARIOS | A21091100070 | Partial_restoration | Wire Down | Include | Include | Equipment | 2084 | 2021-09-12 | 52100 | keep | 0 | Sep | 2021 | 0.035485 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-09-12 02:01 | 2021-09-12 02:02 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210912000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 2379 | keep | 0 | Sep | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
GUAYAMA | 2021-09-12 02:09 | 2021-09-12 13:05 | 45 | 010:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA | P21091200002 | New_Event | Bad Weather | Include | Include | Weather | 656 | 2021-09-12 | 29520 | keep | 0 | Sep | 2021 | 0.020106 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-09-12 03:44 | 2021-09-12 03:45 | 2379 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P210912000XX | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-12 | 2379 | keep | 0 | Sep | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-09-12 03:45 | 2021-09-12 10:00 | 55 | 006:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO CAJA | P21091200004 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 375 | 2021-09-12 | 20625 | keep | 0 | Sep | 2021 | 0.014048 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
HUMACAO | 2021-09-12 03:52 | 2021-09-12 09:47 | 50 | 005:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-09-12 | 17750 | keep | 0 | Sep | 2021 | 0.012089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-12 05:19 | 2021-09-12 05:23 | 723 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE CERRO POR SCADA LLEVA CARGA 1711 05 | B21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-12 | 2892 | keep | 0 | Sep | 2021 | 0.0019697 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
SAN JUAN | 2021-09-12 06:32 | 2021-09-12 12:21 | 54 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21091200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2021-09-12 | 18846 | keep | 0 | Sep | 2021 | 0.012836 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
AGUADILLA | 2021-09-12 06:32 | 2021-09-12 11:15 | 250 | 004:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21091200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-09-12 | 70750 | keep | 0 | Sep | 2021 | 0.048188 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
ARECIBO | 2021-09-12 06:35 | 2021-09-12 17:55 | 40 | 011:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21091200012 | New_Event | Bad Weather | Include | Include | Weather | 680 | 2021-09-12 | 27200 | keep | 0 | Sep | 2021 | 0.018526 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-12 06:41 | 2021-09-12 11:04 | 40 | 004:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-09-12 | 10520 | keep | 0 | Sep | 2021 | 0.0071651 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-09-12 06:43 | 2021-09-12 06:44 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210912000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-09-12 06:44 | 2021-09-12 08:50 | 58 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 65 EN CORTE DE LINEA | P21091200008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-09-12 | 7308 | keep | 0 | Sep | 2021 | 0.0049774 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
ARECIBO | 2021-09-12 06:44 | 2021-09-12 09:40 | 200 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091200013 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-09-12 | 35200 | keep | 0 | Sep | 2021 | 0.023975 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-12 06:47 | 2021-09-12 06:48 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 2107 | keep | 0 | Sep | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
CAGUAS | 2021-09-12 06:49 | 2021-09-12 12:44 | 40 | 005:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21091200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-09-12 | 14200 | keep | 0 | Sep | 2021 | 0.0096716 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-12 06:57 | 2021-09-13 16:44 | 15 | 033:47 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE CERRO PUENTES Y CORTE DE LINEA | B21091200004 | New_Event | Defective Pole | Include | Include | Equipment | 2027 | 2021-09-12 | 30405 | keep | 0 | Sep | 2021 | 0.020709 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-09-12 06:59 | 2021-09-12 10:38 | 52 | 003:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21091100117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-09-12 | 11388 | keep | 0 | Sep | 2021 | 0.0077563 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
AGUADILLA | 2021-09-12 07:00 | 2021-09-12 07:01 | 1827 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE INTERRUPTOR | M21091200000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-09-12 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BARRANQUITAS | 2021-09-12 07:01 | 2021-09-12 10:36 | 90 | 003:35 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21091200019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-09-12 | 19350 | keep | 0 | Sep | 2021 | 0.013179 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
AGUADILLA | 2021-09-12 07:01 | 2021-09-12 18:20 | 8 | 011:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | M21091200099 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 679 | 2021-09-12 | 5432 | keep | 0 | Sep | 2021 | 0.0036997 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
GUAYAMA | 2021-09-12 07:06 | 2021-09-12 08:10 | 27 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | P21091200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2021-09-12 | 1728 | keep | 0 | Sep | 2021 | 0.0011769 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
BAYAMON | 2021-09-12 07:32 | 2021-09-12 07:33 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 4089 | keep | 0 | Sep | 2021 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2021-09-12 07:33 | 2021-09-12 16:25 | 24 | 008:52 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B21091200019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 532 | 2021-09-12 | 12768 | keep | 0 | Sep | 2021 | 0.0086962 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
BARRANQUITAS | 2021-09-12 07:34 | 2021-09-12 16:04 | 40 | 008:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21091200023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 510 | 2021-09-12 | 20400 | keep | 0 | Sep | 2021 | 0.013894 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-12 07:39 | 2021-09-12 11:23 | 100 | 003:44 | P | DESGANCHE | 2 X 50 Y 1 X 25 EN CORTES DE LINEA DESGANCHO Y CERRO PUENTE | R21091200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-09-12 | 22400 | keep | 0 | Sep | 2021 | 0.015257 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-12 07:45 | 2021-09-12 09:38 | 50 | 001:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-09-12 | 5650 | keep | 0 | Sep | 2021 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-12 07:46 | 2021-09-12 14:07 | 50 | 006:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21091200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2021-09-12 | 19050 | keep | 0 | Sep | 2021 | 0.012975 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-12 07:46 | 2021-09-12 10:30 | 8 | 002:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN TRANSFORMADOR CAMION IMPACTO LINEA SECUNDARIA Y HUBO CRUSE SECUNDARIO | P21091200013 | New_Event |  |  | Include | Wildlife | 164 | 2021-09-12 | 1312 | keep | 0 | Sep | 2021 | 0.0008936 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
SAN JUAN | 2021-09-12 07:50 | 2021-09-12 12:39 | 50 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21091200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2021-09-12 | 14450 | keep | 0 | Sep | 2021 | 0.0098418 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-09-12 07:52 | 2021-09-12 07:53 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1234 | keep | 0 | Sep | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-09-12 07:55 | 2021-09-12 07:56 | 1463 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1463 | keep | 0 | Sep | 2021 | 0.00099644 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
FAJARDO | 2021-09-12 07:56 | 2021-09-12 17:00 | 50 | 009:04 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21091200064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 544 | 2021-09-12 | 27200 | keep | 0 | Sep | 2021 | 0.018526 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-09-12 07:57 | 2021-09-12 07:58 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1830 | keep | 0 | Sep | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2021-09-12 07:59 | 2021-09-12 08:00 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091200010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1830 | keep | 0 | Sep | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
CANOVANAS | 2021-09-12 08:02 | 2021-09-12 09:34 | 2106 | 001:32 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | R21091200004 | New_Event | Switch Failure | Include | Include | Equipment | 92 | 2021-09-12 | 193752 | keep | 0 | Sep | 2021 | 0.13196 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
FAJARDO | 2021-09-12 08:04 | 2021-09-12 08:05 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091200010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1830 | keep | 0 | Sep | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2021-09-12 08:06 | 2021-09-12 09:27 | 1830 | 001:21 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO EL ALIMENTADOR | R21091200017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-09-12 | 148230 | keep | 0 | Sep | 2021 | 0.10096 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
SAN JUAN | 2021-09-12 08:09 | 2021-09-12 12:49 | 300 | 004:40 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA | R21091200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-09-12 | 84000 | keep | 0 | Sep | 2021 | 0.057212 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-09-12 08:09 | 2021-09-12 19:18 | 20 | 011:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21091200030 | New_Event | Bad Weather | Include | Include | Weather | 669 | 2021-09-12 | 13380 | keep | 0 | Sep | 2021 | 0.0091131 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-09-12 08:11 | 2021-09-12 12:40 | 100 | 004:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 1 X 30 EN CORTES DE LINEA Y 1 X 10 EN TRANSFORMADOR ELIMINO LINEA VACANTE Y RETEZO LINEA | R21091200014 | New_Event | Wire Down | Include | Include | Equipment | 269 | 2021-09-12 | 26900 | keep | 0 | Sep | 2021 | 0.018321 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-09-12 08:12 | 2021-09-12 15:41 | 25 | 007:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR T - 6 | R21091200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 449 | 2021-09-12 | 11225 | keep | 0 | Sep | 2021 | 0.0076453 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-12 08:20 | 2021-09-12 17:19 | 40 | 008:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091200033 | New_Event | Bad Weather | Include | Include | Weather | 539 | 2021-09-12 | 21560 | keep | 0 | Sep | 2021 | 0.014684 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-12 08:21 | 2021-09-12 13:57 | 25 | 005:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091200028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2021-09-12 | 8400 | keep | 0 | Sep | 2021 | 0.0057212 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-09-12 08:23 | 2021-09-12 14:47 | 100 | 006:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21091200020 | New_Event |  |  | Include | Wildlife | 384 | 2021-09-12 | 38400 | keep | 0 | Sep | 2021 | 0.026154 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-12 08:23 | 2021-09-12 15:00 | 60 | 006:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A21091200019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2021-09-12 | 23820 | keep | 0 | Sep | 2021 | 0.016224 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-09-12 08:26 | 2021-09-12 09:59 | 80 | 001:33 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | R21091200022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-09-12 | 7440 | keep | 0 | Sep | 2021 | 0.0050674 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-12 08:30 | 2021-09-12 08:33 | 297 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA EL 40% DE LA CARGA ESTA POR EL 1335-05 | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-12 | 891 | keep | 0 | Sep | 2021 | 0.00060686 | 0.00020229 | Momentary | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2021-09-12 08:30 | 2021-09-12 08:33 | 1397 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1335-05 | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-12 | 4191 | keep | 0 | Sep | 2021 | 0.0028545 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
SAN JUAN | 2021-09-12 08:30 | 2021-09-12 08:33 | 314 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1301-04 Y EL 40% DEL 1301-02 | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-12 | 942 | keep | 0 | Sep | 2021 | 0.00064159 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2021-09-12 08:34 | 2021-09-13 10:16 | 23 | 025:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21091200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1542 | 2021-09-12 | 35466 | keep | 0 | Sep | 2021 | 0.024156 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
BAYAMON | 2021-09-12 08:35 | 2021-09-12 20:21 | 30 | 011:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21091200014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 706 | 2021-09-12 | 21180 | keep | 0 | Sep | 2021 | 0.014426 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-12 08:35 | 2021-09-12 12:57 | 20 | 004:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA REEMPLAZO AISLADOR | R21091200025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 262 | 2021-09-12 | 5240 | keep | 0 | Sep | 2021 | 0.0035689 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-12 08:39 | 2021-09-12 16:00 | 50 | 007:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C21091200032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 441 | 2021-09-12 | 22050 | keep | 0 | Sep | 2021 | 0.015018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-12 08:41 | 2021-09-12 10:41 | 30 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091200038 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-09-12 | 3600 | keep | 0 | Sep | 2021 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-12 08:43 | 2021-09-12 13:57 | 40 | 005:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21091200033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-09-12 | 12560 | keep | 0 | Sep | 2021 | 0.0085546 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-12 08:44 | 2021-09-13 10:31 | 50 | 025:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21091200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1547 | 2021-09-12 | 77350 | keep | 0 | Sep | 2021 | 0.052683 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-12 08:49 | 2021-09-12 08:50 | 681 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | S21091200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-12 | 681 | keep | 0 | Sep | 2021 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
FAJARDO | 2021-09-12 08:50 | 2021-09-12 10:44 | 40 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA RETEZO NEUTRAL PRIMARIO | R21091200035 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2021-09-12 | 4560 | keep | 0 | Sep | 2021 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-09-12 08:50 | 2021-09-12 09:05 | 58 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 65 EN CORTE DE LINEA | P21091200008 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-09-12 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
YAUCO | 2021-09-12 08:50 | 2021-09-12 08:51 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210912000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
SAN JUAN | 2021-09-12 08:51 | 2021-09-12 21:29 | 62 | 012:38 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21091200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 758 | 2021-09-12 | 46996 | keep | 0 | Sep | 2021 | 0.032009 | 4.2228e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 62
UTUADO | 2021-09-12 08:53 | 2021-09-12 16:55 | 30 | 008:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21091200023 | New_Event | Bad Weather | Include | Include | Weather | 482 | 2021-09-12 | 14460 | keep | 0 | Sep | 2021 | 0.0098486 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-12 08:58 | 2021-09-12 11:36 | 115 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 80 EN CONVERTIDOR | P21091200025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-09-12 | 18170 | keep | 0 | Sep | 2021 | 0.012376 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
UTUADO | 2021-09-12 09:03 | 2021-09-13 11:30 | 2 | 026:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR COOPER 25 KVA X 25 KVA-4160/7200 #1855108031 FID-30736833 | A21091200024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1587 | 2021-09-12 | 3174 | keep | 0 | Sep | 2021 | 0.0021618 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-09-12 09:04 | 2021-09-12 13:33 | 8 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 50 CORTE DE LINEA | S21091200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2021-09-12 | 2152 | keep | 0 | Sep | 2021 | 0.0014657 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
CANOVANAS | 2021-09-12 09:08 | 2021-09-12 17:59 | 100 | 008:51 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21091200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 531 | 2021-09-12 | 53100 | keep | 0 | Sep | 2021 | 0.036166 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-12 09:22 | 2021-09-12 18:35 | 100 | 009:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A21091200025 | New_Event | Bad Weather | Include | Include | Weather | 553 | 2021-09-12 | 55300 | keep | 0 | Sep | 2021 | 0.037665 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-12 09:25 | 2021-09-13 10:08 | 50 | 024:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091200042 | New_Event | Bad Weather | Include | Include | Weather | 1483 | 2021-09-12 | 74150 | keep | 0 | Sep | 2021 | 0.050503 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-09-12 09:27 | 2021-09-12 09:32 | 300 | 000:05 | P | NO SE REPORTO CAUSA | NO SE ENCONTRO CAUSA | R21091200017 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-12 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-12 09:28 | 2021-09-12 12:01 | 54 | 002:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA | S21091200050 | New_Event | Wire Down | Include | Include | Equipment | 153 | 2021-09-12 | 8262 | keep | 0 | Sep | 2021 | 0.0056272 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2021-09-12 09:33 | 2021-09-12 15:22 | 1 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO DE TRANSFORMADORES | S21091200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2021-09-12 | 349 | keep | 0 | Sep | 2021 | 0.0002377 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-12 09:34 | 2021-09-12 09:44 | 200 | 000:10 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO 2 MACHETES QUEMADOS Y 5 DISCOS | R21091200004 | Partial_restoration | Switch Failure | Include | Include | Equipment | 10 | 2021-09-12 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-12 09:35 | 2021-09-12 14:17 | 102 | 004:42 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21091200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2021-09-12 | 28764 | keep | 0 | Sep | 2021 | 0.019591 | 6.9472e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 102
SAN JUAN | 2021-09-12 09:37 | 2021-09-15 13:20 | 43 | 075:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | S21091200053 | New_Event | Wire Down | Include | Include | Equipment | 4543 | 2021-09-12 | 195349 | keep | 0 | Sep | 2021 | 0.13305 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
HUMACAO | 2021-09-12 09:37 | 2021-09-12 12:06 | 50 | 002:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-09-12 | 7450 | keep | 0 | Sep | 2021 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-12 09:44 | 2021-09-12 09:45 | 2106 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL LOCALIZANDO AVERIA | R21091200004 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-09-12 | 2106 | keep | 0 | Sep | 2021 | 0.0014344 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-12 09:45 | 2021-09-12 13:50 | 200 | 004:05 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO 2 MACHETES QUEMADOS Y 5 DISCOS | R21091200004 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 245 | 2021-09-12 | 49000 | keep | 0 | Sep | 2021 | 0.033374 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-12 09:47 | 2021-09-12 21:09 | 100 | 011:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091200053 | New_Event | Bad Weather | Include | Include | Weather | 682 | 2021-09-12 | 68200 | keep | 0 | Sep | 2021 | 0.046451 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-12 09:54 | 2021-09-12 12:55 | 10 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091200029 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-09-12 | 1810 | keep | 0 | Sep | 2021 | 0.0012328 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
PONCE | 2021-09-12 10:07 | 2021-09-12 15:00 | 100 | 004:53 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2021-09-12 | 29300 | keep | 0 | Sep | 2021 | 0.019956 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-12 10:09 | 2021-09-12 11:57 | 10 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21091100027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2021-09-12 | 1080 | keep | 0 | Sep | 2021 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-12 10:21 | 2021-09-12 15:34 | 2302 | 005:13 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA DE LA MEDICION REMOTA QUEMADA | C21091200088 | New_Event | Cutout Failure | Include | Include | Equipment | 313 | 2021-09-12 | 720526 | keep | 0 | Sep | 2021 | 0.49075 | 0.0015679 | Sustained | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-09-12 10:21 | 2021-09-12 15:34 | 1342 | 005:13 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA DE LA MEDICION REMOTA QUEMADA | C21091200088 | New_Event | Cutout Failure | Include | Include | Equipment | 313 | 2021-09-12 | 420046 | keep | 0 | Sep | 2021 | 0.28609 | 0.00091403 | Sustained | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-09-12 10:21 | 2021-09-12 15:34 | 34 | 005:13 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA DE LA MEDICION REMOTA QUEMADA | C21091200088 | New_Event | Cutout Failure | Include | Include | Equipment | 313 | 2021-09-12 | 10642 | keep | 0 | Sep | 2021 | 0.0072482 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2021-09-12 10:21 | 2021-09-12 15:34 | 1742 | 005:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA DE LA MEDICION REMOTA QUEMADA | C21091200088 | New_Event | Cutout Failure | Include | Include | Equipment | 313 | 2021-09-12 | 545246 | keep | 0 | Sep | 2021 | 0.37136 | 0.0011865 | Sustained | FALSE | FALSE | Not_TMED_Event | 1742
SAN JUAN | 2021-09-12 10:23 | 2021-09-12 21:10 | 21 | 010:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA | S21091200056 | New_Event | Wire Down | Include | Include | Equipment | 647 | 2021-09-12 | 13587 | keep | 0 | Sep | 2021 | 0.009254 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2021-09-12 10:30 | 2021-09-12 10:31 | 1979 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER PORTATIL #10 | P21091200033 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-12 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-12 10:30 | 2021-09-12 10:31 | 5069 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER PORTATIL #10 | P21091200033 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-12 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-12 10:30 | 2021-09-12 10:31 | 5063 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER PORTATIL #10 | P21091200033 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-12 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
AGUADILLA | 2021-09-12 10:30 | 2021-09-12 15:56 | 15 | 005:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | M21091100218 | New_Event | Service Transformer Failure | Include | Include | Equipment | 326 | 2021-09-12 | 4890 | keep | 0 | Sep | 2021 | 0.0033306 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-12 10:31 | 2021-09-12 10:45 | 8 | 000:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN TRANSFORMADOR CAMION IMPACTO LINEA SECUNDARIA Y HUBO CRUCE SECUNDARIO | P21091200013 | 1st_after_momentary |  |  | Include | Wildlife | 14 | 2021-09-12 | 112 | keep | 0 | Sep | 2021 | 7.6283e-05 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
FAJARDO | 2021-09-12 10:36 | 2021-09-12 17:28 | 10 | 006:52 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21091200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2021-09-12 | 4120 | keep | 0 | Sep | 2021 | 0.0028061 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-09-12 10:41 | 2021-09-12 13:20 | 150 | 002:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA REEMPLAZO CAJA AVERIADA | R21091200067 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2021-09-12 | 23850 | keep | 0 | Sep | 2021 | 0.016244 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CANOVANAS | 2021-09-12 10:49 | 2021-09-12 17:36 | 20 | 006:47 | P | SECUNDARIA/DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y LEVANTO SECUNDARIA | R21091200069 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 407 | 2021-09-12 | 8140 | keep | 0 | Sep | 2021 | 0.0055441 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-12 10:54 | 2021-09-12 10:55 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091200034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 969 | keep | 0 | Sep | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2021-09-12 11:02 | 2021-09-12 16:00 | 10 | 004:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO PARTIDO | A21091200038 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2021-09-12 | 2980 | keep | 0 | Sep | 2021 | 0.0020297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-12 11:07 | 2021-09-12 18:54 | 1 | 007:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA AVERIADA | P21091200037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 467 | 2021-09-12 | 467 | keep | 0 | Sep | 2021 | 0.00031807 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-12 11:28 | 2021-09-13 16:54 | 10 | 029:26 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SU - 2 AVERIADO CERRO N/O EN T - 15 HACIA T - 14 | C21091200078 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1766 | 2021-09-12 | 17660 | keep | 0 | Sep | 2021 | 0.012028 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-12 11:32 | 2021-09-12 15:45 | 50 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21091200080 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-09-12 | 12650 | keep | 0 | Sep | 2021 | 0.0086159 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-12 12:07 | 2021-09-12 17:02 | 34 | 004:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5900 | S21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 295 | 2021-09-12 | 10030 | keep | 0 | Sep | 2021 | 0.0068314 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
BAYAMON | 2021-09-12 12:07 | 2021-09-12 17:02 | 19 | 004:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5900 | S21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 295 | 2021-09-12 | 5605 | keep | 0 | Sep | 2021 | 0.0038175 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
SAN JUAN | 2021-09-12 12:20 | 2021-09-13 10:47 | 32 | 022:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21091200069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1347 | 2021-09-12 | 43104 | keep | 0 | Sep | 2021 | 0.029358 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
BAYAMON | 2021-09-12 12:21 | 2021-09-12 14:05 | 681 | 001:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR EN EL SUELO | S21091200150 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2021-09-12 | 70824 | keep | 0 | Sep | 2021 | 0.048238 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
FAJARDO | 2021-09-12 12:26 | 2021-09-12 14:41 | 40 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21091200091 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-09-12 | 5400 | keep | 0 | Sep | 2021 | 0.0036779 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-12 12:40 | 2021-09-13 22:52 | 30 | 034:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CREO LINEA AEREA PROVISIONAL | M21091200099 | New_Event | Wire Down | Include | Include | Equipment | 2052 | 2021-09-12 | 61560 | keep | 0 | Sep | 2021 | 0.041928 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-12 12:45 | 2021-09-12 20:49 | 10 | 008:04 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | R21091200093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 484 | 2021-09-12 | 4840 | keep | 0 | Sep | 2021 | 0.0032965 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 9 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 9 | keep | 0 | Sep | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 9
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 6 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 6 | keep | 0 | Sep | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 6
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 12 | keep | 0 | Sep | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
SAN JUAN | 2021-09-12 12:54 | 2021-09-12 12:55 | 5062 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | TRUE | Not_TMED_Event | 5062
MAYAGÃœEZ | 2021-09-12 12:57 | 2021-09-13 15:00 | 6 | 026:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 15 KVA X 15 KVA | M21091200104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1563 | 2021-09-12 | 9378 | keep | 0 | Sep | 2021 | 0.0063873 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-09-12 13:00 | 2021-09-13 16:00 | 1 | 027:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA DEFECTUOSA NO FUNDIO FUSIBLE | R21091200098 | New_Event | Cutout Failure | Include | Include | Equipment | 1620 | 2021-09-12 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-12 13:07 | 2021-09-12 19:34 | 20 | 006:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2021-09-12 | 7740 | keep | 0 | Sep | 2021 | 0.0052717 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-12 13:11 | 2021-09-12 16:22 | 844 | 003:11 | T | NO SE REPORTO CAUSA | SE CERRO EN LA SUBESTACION POR PERSONAL CDS | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-09-12 | 161204 | keep | 0 | Sep | 2021 | 0.1098 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
FAJARDO | 2021-09-12 13:16 | 2021-09-12 15:35 | 40 | 002:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21091200102 | New_Event | Wire Down | Include | Include | Equipment | 139 | 2021-09-12 | 5560 | keep | 0 | Sep | 2021 | 0.0037869 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-09-12 13:18 | 2021-09-12 13:19 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | M21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 3041 | keep | 0 | Sep | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2021-09-12 13:28 | 2021-09-12 18:02 | 57 | 004:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21091200089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2021-09-12 | 15618 | keep | 0 | Sep | 2021 | 0.010637 | 3.8822e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 57
ARECIBO | 2021-09-12 13:36 | 2021-09-12 19:00 | 5 | 005:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON BAJANTES SECUNDARIOS EN TRANSFORMADOR | A21091200110 | New_Event | Wire Down | Include | Include | Equipment | 324 | 2021-09-12 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-09-12 13:40 | 2021-09-12 14:33 | 40 | 000:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21091200109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-09-12 | 2120 | keep | 0 | Sep | 2021 | 0.0014439 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-12 13:41 | 2021-09-12 15:50 | 146 | 002:09 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21091200115 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-09-12 | 18834 | keep | 0 | Sep | 2021 | 0.012828 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
UTUADO | 2021-09-12 13:41 | 2021-09-13 09:50 | 50 | 020:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091200055 | New_Event | Bad Weather | Include | Include | Weather | 1209 | 2021-09-12 | 60450 | keep | 0 | Sep | 2021 | 0.041172 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-12 13:44 | 2021-09-12 17:55 | 100 | 004:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21091200111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-09-12 | 25100 | keep | 0 | Sep | 2021 | 0.017095 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-12 13:46 | 2021-09-12 13:47 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-12 | 3041 | keep | 0 | Sep | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2021-09-12 13:47 | 2021-09-12 14:35 | 10 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL EN BAJANTE SECUNDARIO | S21091200069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-09-12 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-12 13:48 | 2021-09-12 13:49 | 1155 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIRRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-12 | 1155 | keep | 0 | Sep | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
HUMACAO | 2021-09-12 13:49 | 2021-09-12 15:55 | 50 | 002:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091200113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-09-12 | 6300 | keep | 0 | Sep | 2021 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-12 13:49 | 2021-09-12 21:10 | 50 | 007:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21091200112 | New_Event | Wire Down | Include | Include | Equipment | 441 | 2021-09-12 | 22050 | keep | 0 | Sep | 2021 | 0.015018 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-12 13:52 | 2021-09-12 17:06 | 60 | 003:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091200116 | New_Event | Bad Weather | Include | Include | Weather | 194 | 2021-09-12 | 11640 | keep | 0 | Sep | 2021 | 0.007928 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-12 13:52 | 2021-09-13 12:00 | 50 | 022:08 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | A21091200057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1328 | 2021-09-12 | 66400 | keep | 0 | Sep | 2021 | 0.045225 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-12 13:56 | 2021-09-12 13:57 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 6136 | keep | 0 | Sep | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
ARECIBO | 2021-09-12 14:01 | 2021-09-12 20:35 | 20 | 006:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21091200061 | New_Event | Wire Down | Include | Include | Equipment | 394 | 2021-09-12 | 7880 | keep | 0 | Sep | 2021 | 0.005367 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-12 14:01 | 2021-09-12 17:03 | 40 | 003:02 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C21091200114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-09-12 | 7280 | keep | 0 | Sep | 2021 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-12 14:04 | 2021-09-12 16:54 | 40 | 002:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21091100068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-09-12 | 6800 | keep | 0 | Sep | 2021 | 0.0046314 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-12 14:13 | 2021-09-12 18:51 | 45 | 004:38 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2021-09-12 | 12510 | keep | 0 | Sep | 2021 | 0.0085205 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-12 14:17 | 2021-09-13 15:55 | 13 | 025:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR UNO DE IGUAL CAPACIDAD | B21091200051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1538 | 2021-09-12 | 19994 | keep | 0 | Sep | 2021 | 0.013618 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-09-12 14:20 | 2021-09-12 14:21 | 1139 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1139 | keep | 0 | Sep | 2021 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
MAYAGÃœEZ | 2021-09-12 14:20 | 2021-09-12 19:57 | 50 | 005:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091200121 | New_Event | Bad Weather | Include | Include | Weather | 337 | 2021-09-12 | 16850 | keep | 0 | Sep | 2021 | 0.011476 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-12 14:25 | 2021-09-12 14:26 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-12 14:25 | 2021-09-12 14:26 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-12 14:25 | 2021-09-12 14:26 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-12 14:25 | 2021-09-12 14:26 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 863 | keep | 0 | Sep | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-12 14:25 | 2021-09-12 14:26 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 309 | keep | 0 | Sep | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-12 14:25 | 2021-09-12 14:26 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 POR DESCARGAS ELECTRICAS | M21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 176 | keep | 0 | Sep | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
SAN JUAN | 2021-09-12 14:29 | 2021-09-12 14:30 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-12 14:44 | 2021-09-12 22:32 | 300 | 007:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN TRONCAL | B21091200067 | New_Event | Wire Down | Include | Include | Equipment | 468 | 2021-09-12 | 140400 | keep | 0 | Sep | 2021 | 0.095626 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-09-12 14:46 | 2021-09-12 23:12 | 35 | 008:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21091200109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 506 | 2021-09-12 | 17710 | keep | 0 | Sep | 2021 | 0.012062 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-09-12 14:47 | 2021-09-12 15:04 | 681 | 000:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE | S21091200000 | Partial_restoration | Wire Down | Include | Include | Equipment | 17 | 2021-09-12 | 11577 | keep | 0 | Sep | 2021 | 0.007885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-12 14:52 | 2021-09-13 00:44 | 150 | 009:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA | M21091200140 | New_Event | Wire Down | Include | Include | Equipment | 592 | 2021-09-12 | 88800 | keep | 0 | Sep | 2021 | 0.060481 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-12 14:54 | 2021-09-13 16:33 | 20 | 025:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21091200142 | New_Event | Bad Weather | Include | Include | Weather | 1539 | 2021-09-12 | 30780 | keep | 0 | Sep | 2021 | 0.020964 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-12 15:04 | 2021-09-12 17:07 | 27 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 CORTE DE LINEA SE CERRO PUENTE | S21091200040 | Partial_restoration | Wire Down | Include | Include | Equipment | 123 | 2021-09-12 | 3321 | keep | 0 | Sep | 2021 | 0.0022619 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-12 15:07 | 2021-09-12 15:12 | 1812 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-12 | 9060 | keep | 0 | Sep | 2021 | 0.0061707 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2021-09-12 15:08 | 2021-09-12 15:13 | 500 | 000:05 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA POR 1708 03 | B21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-12 | 2500 | keep | 0 | Sep | 2021 | 0.0017027 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-09-12 15:08 | 2021-09-12 15:13 | 1498 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA PARTE CARGA 1708 02 | B21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-12 | 7490 | keep | 0 | Sep | 2021 | 0.0051014 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-09-12 15:08 | 2021-09-12 15:09 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 99% DEL 1909-09 | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 222 | keep | 0 | Sep | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-09-12 15:08 | 2021-09-12 15:09 | 4412 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR EL 99% DE LA CARGA ESTA POR EL 1907-03 | S21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 4412 | keep | 0 | Sep | 2021 | 0.003005 | 0.003005 | Momentary | FALSE | FALSE | Not_TMED_Event | 4412
BAYAMON | 2021-09-12 15:18 | 2021-09-12 19:12 | 35 | 003:54 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA RETIRAR PELIGRO DE TRANSFORMADOR COLGANDO POR CRUCETA PARTIDA CLIENTES DE TRANSFORMADOR SE QUEDARON SIN SERVICIO POR QUE HAY CAMBIAR POSTE | B21091200053 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 234 | 2021-09-12 | 8190 | keep | 0 | Sep | 2021 | 0.0055782 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-09-12 15:20 | 2021-09-12 18:29 | 520 | 003:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21091100158 | New_Event | Wire Down | Include | Include | Equipment | 189 | 2021-09-12 | 98280 | keep | 0 | Sep | 2021 | 0.066938 | 0.00035417 | Sustained | FALSE | TRUE | Not_TMED_Event | 520
ARECIBO | 2021-09-12 15:38 | 2021-09-12 17:15 | 100 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A21091200070 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-09-12 | 9700 | keep | 0 | Sep | 2021 | 0.0066066 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-12 15:38 | 2021-09-13 14:49 | 80 | 023:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091200081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1391 | 2021-09-12 | 111280 | keep | 0 | Sep | 2021 | 0.075792 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-12 15:39 | 2021-09-12 15:40 | 1862 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1862 | keep | 0 | Sep | 2021 | 0.0012682 | 0.0012682 | Momentary | FALSE | TRUE | Not_TMED_Event | 1862
SAN JUAN | 2021-09-12 15:39 | 2021-09-12 15:40 | 1613 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1613 | keep | 0 | Sep | 2021 | 0.0010986 | 0.0010986 | Momentary | FALSE | TRUE | Not_TMED_Event | 1613
SAN JUAN | 2021-09-12 15:39 | 2021-09-12 15:40 | 1448 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-12 | 1448 | keep | 0 | Sep | 2021 | 0.00098623 | 0.00098623 | Momentary | FALSE | TRUE | Not_TMED_Event | 1448
HUMACAO | 2021-09-12 15:40 | 2021-09-12 18:03 | 6 | 002:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21091200132 | New_Event |  |  | Include | Wildlife | 143 | 2021-09-12 | 858 | keep | 0 | Sep | 2021 | 0.00058438 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-12 16:03 | 2021-09-12 18:40 | 10 | 002:37 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21091100303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-09-12 | 1570 | keep | 0 | Sep | 2021 | 0.0010693 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-12 16:16 | 2021-09-12 21:38 | 50 | 005:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21091200079 | New_Event | Bad Weather | Include | Include | Weather | 322 | 2021-09-12 | 16100 | keep | 0 | Sep | 2021 | 0.010966 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-12 16:18 | 2021-09-12 16:20 | 748 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE CERRO POR SCADA LLEVA CARGA 1802 02 | B21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-12 | 1496 | keep | 0 | Sep | 2021 | 0.0010189 | 0.00050946 | Momentary | FALSE | FALSE | Not_TMED_Event | 748
BAYAMON | 2021-09-12 16:18 | 2021-09-12 16:20 | 33 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE CERRO POR SCADA CARGA POR 1802 01 | B21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-12 | 66 | keep | 0 | Sep | 2021 | 4.4952e-05 | 2.2476e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2021-09-12 16:21 | 2021-09-12 16:24 | 748 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE CERRO POR SCADA LLEVA CARGA 1802 02 | B21091200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-12 | 2244 | keep | 0 | Sep | 2021 | 0.0015284 | 0.00050946 | Momentary | FALSE | FALSE | Not_TMED_Event | 748
BAYAMON | 2021-09-12 16:21 | 2021-09-12 16:24 | 33 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE CERRO POR SCADA CARGA POR 1802 01 | B21091200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-12 | 99 | keep | 0 | Sep | 2021 | 6.7428e-05 | 2.2476e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2021-09-12 16:23 | 2021-09-13 14:30 | 60 | 022:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21091200163 | New_Event | Bad Weather | Include | Include | Weather | 1327 | 2021-09-12 | 79620 | keep | 0 | Sep | 2021 | 0.054229 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-12 16:23 | 2021-09-16 11:00 | 250 | 090:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400219 | New_Event | Bad Weather | Include | Include | Weather | 5437 | 2021-09-12 | 1359250 | keep | 0 | Sep | 2021 | 0.92578 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
FAJARDO | 2021-09-12 17:02 | 2021-09-12 17:03 | 1394 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 1394 | keep | 0 | Sep | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
ARECIBO | 2021-09-12 17:08 | 2021-09-12 21:30 | 150 | 004:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21091200090 | New_Event | Wire Down | Include | Include | Equipment | 262 | 2021-09-12 | 39300 | keep | 0 | Sep | 2021 | 0.026767 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-12 17:09 | 2021-09-12 18:12 | 25 | 001:03 | P | DESGANCHE | 1 X 25 EN AEREO PROVISIONAL SE REALIZO DESGANCHE | B21091200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2021-09-12 | 1575 | keep | 0 | Sep | 2021 | 0.0010727 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-12 17:32 | 2021-09-13 16:46 | 50 | 023:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1394 | 2021-09-12 | 69700 | keep | 0 | Sep | 2021 | 0.047472 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-12 17:47 | 2021-09-13 11:00 | 60 | 017:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091200184 | New_Event | Bad Weather | Include | Include | Weather | 1033 | 2021-09-12 | 61980 | keep | 0 | Sep | 2021 | 0.042214 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-12 17:59 | 2021-09-12 20:44 | 50 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21091200186 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2021-09-12 | 8250 | keep | 0 | Sep | 2021 | 0.005619 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-12 18:09 | 2021-09-12 20:56 | 35 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21091200108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-09-12 | 5845 | keep | 0 | Sep | 2021 | 0.003981 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-12 18:09 | 2021-09-12 21:06 | 200 | 002:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-09-12 | 35400 | keep | 0 | Sep | 2021 | 0.024111 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-12 18:39 | 2021-09-13 17:55 | 4 | 023:16 | P | HERRAJE ROTO O PODRIDO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091200194 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1396 | 2021-09-12 | 5584 | keep | 0 | Sep | 2021 | 0.0038032 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
CANOVANAS | 2021-09-12 18:50 | 2021-09-13 10:16 | 6 | 015:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21091200123 | New_Event |  |  | Include | Wildlife | 926 | 2021-09-12 | 5556 | keep | 0 | Sep | 2021 | 0.0037842 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-09-12 19:05 | 2021-09-12 21:06 | 20 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR CALZADO DEPORTIVO | C21091200144 | New_Event |  |  | Include | Wildlife | 121 | 2021-09-12 | 2420 | keep | 0 | Sep | 2021 | 0.0016483 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-12 19:09 | 2021-09-13 13:32 | 40 | 018:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091200145 | New_Event | Bad Weather | Include | Include | Weather | 1103 | 2021-09-12 | 44120 | keep | 0 | Sep | 2021 | 0.03005 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-12 19:12 | 2021-09-13 13:58 | 1 | 018:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA REMPLAZO BAJANTE PRIMARIO CRUZADO | R21091200124 | New_Event | Wire Down | Include | Include | Equipment | 1126 | 2021-09-12 | 1126 | keep | 0 | Sep | 2021 | 0.00076691 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-09-12 19:32 | 2021-09-13 10:25 | 30 | 014:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO UNA CAJA MARCA CHIN DE 100AMP EN EL FID1001925207 | A21091200098 | New_Event | Cutout Failure | Include | Include | Equipment | 893 | 2021-09-12 | 26790 | keep | 0 | Sep | 2021 | 0.018247 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-12 19:38 | 2021-09-12 23:29 | 70 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21091200148 | New_Event |  |  | Include | Wildlife | 231 | 2021-09-12 | 16170 | keep | 0 | Sep | 2021 | 0.011013 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-12 20:24 | 2021-09-13 15:30 | 50 | 019:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091200215 | New_Event | Bad Weather | Include | Include | Weather | 1146 | 2021-09-12 | 57300 | keep | 0 | Sep | 2021 | 0.039027 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-12 20:30 | 2021-09-13 09:39 | 50 | 013:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091200167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 789 | 2021-09-12 | 39450 | keep | 0 | Sep | 2021 | 0.026869 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-12 20:34 | 2021-09-13 20:04 | 60 | 023:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091200218 | New_Event | Bad Weather | Include | Include | Weather | 1410 | 2021-09-12 | 84600 | keep | 0 | Sep | 2021 | 0.057621 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-12 20:35 | 2021-09-13 09:25 | 80 | 012:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091200219 | New_Event | Bad Weather | Include | Include | Weather | 770 | 2021-09-12 | 61600 | keep | 0 | Sep | 2021 | 0.041955 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-09-12 20:37 | 2021-09-13 12:05 | 100 | 015:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21091200221 | New_Event | Cutout Failure | Include | Include | Equipment | 928 | 2021-09-12 | 92800 | keep | 0 | Sep | 2021 | 0.063206 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-12 20:44 | 2021-09-13 23:13 | 30 | 026:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091200223 | New_Event | Bad Weather | Include | Include | Weather | 1589 | 2021-09-12 | 47670 | keep | 0 | Sep | 2021 | 0.032468 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-12 20:45 | 2021-09-12 21:32 | 238 | 000:47 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO CAUSA | C21091200171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2021-09-12 | 11186 | keep | 0 | Sep | 2021 | 0.0076187 | 0.0001621 | Sustained | FALSE | TRUE | Not_TMED_Event | 238
ARECIBO | 2021-09-12 20:45 | 2021-09-14 15:03 | 20 | 042:18 | P | PARARRAYOS DEFECTUOSO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A21091200104 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2538 | 2021-09-12 | 50760 | keep | 0 | Sep | 2021 | 0.034572 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-12 21:15 | 2021-09-13 17:49 | 40 | 020:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21091200228 | New_Event | Wire Down | Include | Include | Equipment | 1234 | 2021-09-12 | 49360 | keep | 0 | Sep | 2021 | 0.033619 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-12 22:02 | 2021-09-12 22:03 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21091200175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 5630 | keep | 0 | Sep | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2021-09-12 23:02 | 2021-09-13 18:14 | 9 | 019:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REEMPLAZAR 120 PIES DE SECUNDARIA AVERIADA | R21091200130 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1152 | 2021-09-12 | 10368 | keep | 0 | Sep | 2021 | 0.0070616 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-09-12 23:56 | 2021-09-12 23:57 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21091200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-12 | 4431 | keep | 0 | Sep | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
VEGA BAJA | 2021-09-13 00:47 | 2021-09-13 12:57 | 75 | 012:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 730 | 2021-09-13 | 54750 | keep | 0 | Sep | 2021 | 0.03729 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-09-13 01:17 | 2021-09-13 11:54 | 50 | 010:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA Y 1 SMU 20 DE 25A EN EL SU - 1C CRUCE POR RATON | R21091300002 | New_Event |  |  | Include | Wildlife | 637 | 2021-09-13 | 31850 | keep | 0 | Sep | 2021 | 0.021693 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-13 01:43 | 2021-09-13 01:47 | 1615 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-13 | 6460 | keep | 0 | Sep | 2021 | 0.0043999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-09-13 01:57 | 2021-09-13 01:58 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1206-03 | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-09-13 01:57 | 2021-09-13 01:58 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA CARGA 1204-05 | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-09-13 01:58 | 2021-09-13 10:07 | 102 | 008:09 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA | S21091300001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 489 | 2021-09-13 | 49878 | keep | 0 | Sep | 2021 | 0.033972 | 6.9472e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 102
CAGUAS | 2021-09-13 03:29 | 2021-09-13 03:30 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21091300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 1879 | keep | 0 | Sep | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
HUMACAO | 2021-09-13 03:32 | 2021-09-13 13:42 | 40 | 010:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN RISER MAL TIEMPO | C21091300005 | New_Event | Bad Weather | Include | Include | Weather | 610 | 2021-09-13 | 24400 | keep | 0 | Sep | 2021 | 0.016619 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-13 04:07 | 2021-09-13 04:08 | 2410 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21090600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-13 | 2410 | keep | 0 | Sep | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-09-13 04:08 | 2021-09-13 11:42 | 40 | 007:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21091300020 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 454 | 2021-09-13 | 18160 | keep | 0 | Sep | 2021 | 0.012369 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-13 05:19 | 2021-09-13 05:23 | 1976 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1711 03 | B21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-13 | 7904 | keep | 0 | Sep | 2021 | 0.0053834 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-09-13 05:20 | 2021-09-13 05:24 | 293 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4300 | S21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-09-13 | 1172 | keep | 0 | Sep | 2021 | 0.00079824 | 0.00019956 | Momentary | FALSE | TRUE | Not_TMED_Event | 293
BAYAMON | 2021-09-13 05:20 | 2021-09-13 05:24 | 315 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4300 | S21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-09-13 | 1260 | keep | 0 | Sep | 2021 | 0.00085818 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
BAYAMON | 2021-09-13 05:20 | 2021-09-13 05:24 | 216 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4300 | S21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-09-13 | 864 | keep | 0 | Sep | 2021 | 0.00058847 | 0.00014712 | Momentary | FALSE | TRUE | Not_TMED_Event | 216
BAYAMON | 2021-09-13 05:20 | 2021-09-13 05:24 | 1310 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4300 | S21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-09-13 | 5240 | keep | 0 | Sep | 2021 | 0.0035689 | 0.00089224 | Momentary | FALSE | TRUE | Not_TMED_Event | 1310
MAYAGÃœEZ | 2021-09-13 06:19 | 2021-09-13 12:40 | 200 | 006:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091200007 | New_Event | Bad Weather | Include | Include | Weather | 381 | 2021-09-13 | 76200 | keep | 0 | Sep | 2021 | 0.051899 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-09-13 06:23 | 2021-09-13 06:24 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210913000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-09-13 06:24 | 2021-09-13 10:09 | 186 | 003:45 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | P21091300002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 225 | 2021-09-13 | 41850 | keep | 0 | Sep | 2021 | 0.028504 | 0.00012668 | Sustained | FALSE | TRUE | Not_TMED_Event | 186
CAGUAS | 2021-09-13 06:27 | 2021-09-13 11:44 | 100 | 005:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA FIJO CONDUCTOR | C21091300012 | New_Event | Wire Down | Include | Include | Equipment | 317 | 2021-09-13 | 31700 | keep | 0 | Sep | 2021 | 0.021591 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-13 06:29 | 2021-09-13 11:11 | 40 | 004:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHO Y ABRIO PUENTES HACIA BANCO DE TRANSFORMADORES VACANTE | R21091300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2021-09-13 | 11280 | keep | 0 | Sep | 2021 | 0.0076828 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-13 06:34 | 2021-09-13 16:10 | 20 | 009:36 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091300008 | New_Event | Bad Weather | Include | Include | Weather | 576 | 2021-09-13 | 11520 | keep | 0 | Sep | 2021 | 0.0078462 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-09-13 06:40 | 2021-09-13 11:46 | 20 | 005:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21091300005 | New_Event |  |  | Include | Wildlife | 306 | 2021-09-13 | 6120 | keep | 0 | Sep | 2021 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-09-13 06:46 | 2021-09-13 11:08 | 6 | 004:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR PORTAFUSIBLE QUEMADO | R21091300006 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2021-09-13 | 1572 | keep | 0 | Sep | 2021 | 0.0010707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-09-13 06:53 | 2021-09-13 12:28 | 1541 | 005:35 | T | NO SE REPORTO CAUSA | SE REMPLAZO 1 FUSIBLE DE 125 STANDARD SPEED EN LA ALTA DEL TRANSFORMADOR NO SE REPORTO CAUSA | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-09-13 | 516235 | keep | 0 | Sep | 2021 | 0.35161 | 0.0010496 | Sustained | FALSE | FALSE | Not_TMED_Event | 1541
ARECIBO | 2021-09-13 06:53 | 2021-09-13 12:28 | 307 | 005:35 | T | NO SE REPORTO CAUSA | SE REMPLAZO 1 FUSIBLE DE 125 STANDARD SPEED EN LA ALTA DEL TRANSFORMADOR NO SE REPORTO CAUSA | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-09-13 | 102845 | keep | 0 | Sep | 2021 | 0.070047 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
ARECIBO | 2021-09-13 06:53 | 2021-09-13 12:28 | 1277 | 005:35 | T | NO SE REPORTO CAUSA | SE REMPLAZO 1 FUSIBLE DE 125 STANDARD SPEED EN LA ALTA DEL TRANSFORMADOR NO SE REPORTO CAUSA | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-09-13 | 427795 | keep | 0 | Sep | 2021 | 0.29137 | 0.00086976 | Sustained | FALSE | FALSE | Not_TMED_Event | 1277
ARECIBO | 2021-09-13 06:53 | 2021-09-13 12:28 | 1644 | 005:35 | T | NO SE REPORTO CAUSA | SE REMPLAZO 1 FUSIBLE DE 125 STANDARD SPEED EN LA ALTA DEL TRANSFORMADOR NO SE REPORTO CAUSA | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-09-13 | 550740 | keep | 0 | Sep | 2021 | 0.37511 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
ARECIBO | 2021-09-13 06:53 | 2021-09-13 12:28 | 1831 | 005:35 | T | NO SE REPORTO CAUSA | SE REMPLAZO 1 FUSIBLE DE 125 STANDARD SPEED EN LA ALTA DEL TRANSFORMADOR NO SE REPORTO CAUSA | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-09-13 | 613385 | keep | 0 | Sep | 2021 | 0.41777 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
UTUADO | 2021-09-13 06:55 | 2021-09-14 13:43 | 200 | 030:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REPARO PUENTES PRIMARIOS | A21091300022 | New_Event | Wire Down | Include | Include | Equipment | 1848 | 2021-09-13 | 369600 | keep | 0 | Sep | 2021 | 0.25173 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-09-13 07:04 | 2021-09-13 10:28 | 1 | 003:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21091300007 | New_Event | Bad Weather | Include | Include | Weather | 204 | 2021-09-13 | 204 | keep | 0 | Sep | 2021 | 0.00013894 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-13 07:20 | 2021-09-13 12:38 | 1 | 005:18 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | M21091300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2021-09-13 | 318 | keep | 0 | Sep | 2021 | 0.00021659 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-09-13 07:21 | 2021-09-13 21:24 | 13 | 014:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR UNO DE IGUAL CAPACIDAD CAJAS Y PARARRAYO | B21091300023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 843 | 2021-09-13 | 10959 | keep | 0 | Sep | 2021 | 0.0074641 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-09-13 07:28 | 2021-09-13 17:24 | 300 | 009:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO TRASPATIO Y SE CERRO MACHETES | B21091300024 | New_Event | Wire Down | Include | Include | Equipment | 596 | 2021-09-13 | 178800 | keep | 0 | Sep | 2021 | 0.12178 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-09-13 07:32 | 2021-09-15 12:56 | 40 | 053:24 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091300020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3204 | 2021-09-13 | 128160 | keep | 0 | Sep | 2021 | 0.087289 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-13 07:33 | 2021-09-14 22:51 | 20 | 039:18 | P | DESGANCHE | SE CERRO PUENTE ABIERTO DESGANCHE | B21091300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2358 | 2021-09-13 | 47160 | keep | 0 | Sep | 2021 | 0.03212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-13 07:34 | 2021-09-13 15:57 | 30 | 008:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEA | B21091300027 | New_Event |  |  | Include | Wildlife | 503 | 2021-09-13 | 15090 | keep | 0 | Sep | 2021 | 0.010278 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-13 07:38 | 2021-09-13 11:52 | 10 | 004:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE POR REPTIL | R21091300008 | New_Event |  |  | Include | Wildlife | 254 | 2021-09-13 | 2540 | keep | 0 | Sep | 2021 | 0.00173 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-13 07:49 | 2021-09-13 17:27 | 100 | 009:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | C21091300023 | New_Event | Bad Weather | Include | Include | Weather | 578 | 2021-09-13 | 57800 | keep | 0 | Sep | 2021 | 0.039367 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-13 08:12 | 2021-09-13 17:00 | 20 | 008:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 25 EN CORTE DE LINEA SE REEMPLAZO AISLDORES ROTOS | A21091300099 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 528 | 2021-09-13 | 10560 | keep | 0 | Sep | 2021 | 0.0071924 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-13 08:25 | 2021-09-13 18:24 | 5 | 009:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZARON DISCOS | B21091300039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 599 | 2021-09-13 | 2995 | keep | 0 | Sep | 2021 | 0.0020399 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-09-13 08:25 | 2021-09-13 15:14 | 3 | 006:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21091300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 409 | 2021-09-13 | 1227 | keep | 0 | Sep | 2021 | 0.0008357 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-09-13 08:26 | 2021-09-13 16:36 | 1 | 008:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA | P21091300011 | New_Event | Cutout Failure | Include | Include | Equipment | 490 | 2021-09-13 | 490 | keep | 0 | Sep | 2021 | 0.00033374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-13 08:29 | 2021-09-13 12:43 | 50 | 004:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEAS CAMION CRUZO LINEAS PRIMARIAS | A21091300106 | New_Event | Wire Down | Include | Include | Equipment | 254 | 2021-09-13 | 12700 | keep | 0 | Sep | 2021 | 0.0086499 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-13 08:41 | 2021-09-13 09:30 | 23 | 000:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21091300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2021-09-13 | 1127 | keep | 0 | Sep | 2021 | 0.00076759 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
BAYAMON | 2021-09-13 08:44 | 2021-09-13 18:52 | 30 | 010:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091300045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 608 | 2021-09-13 | 18240 | keep | 0 | Sep | 2021 | 0.012423 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-13 08:45 | 2021-09-13 16:51 | 1 | 008:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21091300032 | New_Event | Cutout Failure | Include | Include | Equipment | 486 | 2021-09-13 | 486 | keep | 0 | Sep | 2021 | 0.00033101 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-09-13 08:47 | 2021-09-13 11:12 | 50 | 002:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091300033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2021-09-13 | 7250 | keep | 0 | Sep | 2021 | 0.0049379 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-13 08:47 | 2021-09-13 08:48 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21091300034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 2457 | keep | 0 | Sep | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
CAGUAS | 2021-09-13 08:48 | 2021-09-13 12:29 | 150 | 003:41 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21091300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-09-13 | 33150 | keep | 0 | Sep | 2021 | 0.022578 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-09-13 08:55 | 2021-09-14 17:49 | 30 | 032:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091300125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1974 | 2021-09-13 | 59220 | keep | 0 | Sep | 2021 | 0.040334 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-13 09:06 | 2021-09-13 12:55 | 1 | 003:49 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA REMPLAZO PARARRAYO | R21091300012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 229 | 2021-09-13 | 229 | keep | 0 | Sep | 2021 | 0.00015597 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-09-13 09:12 | 2021-09-13 14:20 | 12 | 005:08 | P | SECUNDARIA/ESTRUCTURA AVERIADA | REEMPLAZO BARRA EN PEDESTAL Y AJUSTO BUSHING EN TRANSFORMADOR | R21091300013 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 308 | 2021-09-13 | 3696 | keep | 0 | Sep | 2021 | 0.0025173 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-09-13 09:16 | 2021-09-13 14:13 | 50 | 004:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40, 1 X 30 EN CORTES DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091300042 | New_Event | Bad Weather | Include | Include | Weather | 297 | 2021-09-13 | 14850 | keep | 0 | Sep | 2021 | 0.010114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-13 09:31 | 2021-09-13 12:02 | 45 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | P21091300017 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-09-13 | 6795 | keep | 0 | Sep | 2021 | 0.004628 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-13 09:39 | 2021-09-14 09:53 | 50 | 024:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091300055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1454 | 2021-09-13 | 72700 | keep | 0 | Sep | 2021 | 0.049516 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-13 09:48 | 2021-09-13 16:17 | 40 | 006:29 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA REMPLAZO 3 PARARRAYOS Y 3 CAJAS | C21091300048 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 389 | 2021-09-13 | 15560 | keep | 0 | Sep | 2021 | 0.010598 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-13 09:49 | 2021-09-13 16:25 | 5 | 006:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091300049 | New_Event | Bad Weather | Include | Include | Weather | 396 | 2021-09-13 | 1980 | keep | 0 | Sep | 2021 | 0.0013486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-09-13 09:50 | 2021-09-13 09:54 | 1952 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL ALIMENTADOR NO RECERRO | P21091300023 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-09-13 | 7808 | keep | 0 | Sep | 2021 | 0.005318 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
MAYAGÃœEZ | 2021-09-13 10:00 | 2021-09-13 17:49 | 150 | 007:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21091300090 | New_Event | Wire Down | Include | Include | Equipment | 469 | 2021-09-13 | 70350 | keep | 0 | Sep | 2021 | 0.047915 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-09-13 10:07 | 2021-09-13 10:08 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-03 | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-09-13 10:07 | 2021-09-13 10:08 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1204-05 | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-09-13 10:08 | 2021-09-13 10:46 | 102 | 000:38 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA | S21091300001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 38 | 2021-09-13 | 3876 | keep | 0 | Sep | 2021 | 0.0026399 | 6.9472e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 102
BAYAMON | 2021-09-13 10:15 | 2021-09-13 17:52 | 1 | 007:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS | B21091300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2021-09-13 | 457 | keep | 0 | Sep | 2021 | 0.00031126 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-09-13 10:17 | 2021-09-13 19:49 | 1 | 009:32 | P | NO SE REPORTO CAUSA | 2 X 25 EN SU HACIA BOMBAS | B21091300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 572 | 2021-09-13 | 572 | keep | 0 | Sep | 2021 | 0.00038959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-13 10:23 | 2021-09-13 18:56 | 40 | 008:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091300053 | New_Event | Bad Weather | Include | Include | Weather | 513 | 2021-09-13 | 20520 | keep | 0 | Sep | 2021 | 0.013976 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-13 10:24 | 2021-09-13 15:45 | 5 | 005:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21091300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2021-09-13 | 1605 | keep | 0 | Sep | 2021 | 0.0010932 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
PONCE | 2021-09-13 10:25 | 2021-09-13 14:24 | 1952 | 003:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO | P21091300035 | New_Event | Wire Down | Include | Include | Equipment | 239 | 2021-09-13 | 466528 | keep | 0 | Sep | 2021 | 0.31775 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
GUAYAMA | 2021-09-13 10:28 | 2021-09-13 16:10 | 15 | 005:42 | P | ESTRUCTURA AVERIADA | SE REMMPLAZO POSTE PRIMARIO PARTIDO | P21091300032 | New_Event | Defective Pole | Include | Include | Equipment | 342 | 2021-09-13 | 5130 | keep | 0 | Sep | 2021 | 0.003494 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-13 10:30 | 2021-09-13 13:44 | 1 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21091300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2021-09-13 | 194 | keep | 0 | Sep | 2021 | 0.00013213 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-13 10:41 | 2021-09-13 13:30 | 40 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091300071 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-09-13 | 6760 | keep | 0 | Sep | 2021 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-13 10:42 | 2021-09-13 10:43 | 3070 | 000:01 | T | DESGANCHE | RECERRO | B21091300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-13 | 3070 | keep | 0 | Sep | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-09-13 10:43 | 2021-09-13 11:35 | 35 | 000:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100133 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-09-13 | 1820 | keep | 0 | Sep | 2021 | 0.0012396 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-09-13 11:05 | 2021-09-13 13:05 | 10 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091300084 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-09-13 | 1200 | keep | 0 | Sep | 2021 | 0.00081731 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-13 11:08 | 2021-09-13 19:30 | 40 | 008:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO Y SE ENCONTRO PUENTE ABIERTO | B21091300080 | New_Event | Wire Down | Include | Include | Equipment | 502 | 2021-09-13 | 20080 | keep | 0 | Sep | 2021 | 0.013676 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-09-13 11:09 | 2021-09-13 17:03 | 60 | 005:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 354 | 2021-09-13 | 21240 | keep | 0 | Sep | 2021 | 0.014466 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-13 11:09 | 2021-09-13 16:21 | 60 | 005:12 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA | B21091300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-09-13 | 18720 | keep | 0 | Sep | 2021 | 0.01275 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-13 11:14 | 2021-09-13 14:49 | 8 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21091100192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2021-09-13 | 1720 | keep | 0 | Sep | 2021 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-13 11:22 | 2021-09-13 14:26 | 7 | 003:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA QUEMADA | C21091300060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 184 | 2021-09-13 | 1288 | keep | 0 | Sep | 2021 | 0.00087725 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-13 11:27 | 2021-09-13 14:05 | 20 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | R21091300029 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2021-09-13 | 3160 | keep | 0 | Sep | 2021 | 0.0021523 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-13 11:29 | 2021-09-13 17:58 | 12 | 006:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21091300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 389 | 2021-09-13 | 4668 | keep | 0 | Sep | 2021 | 0.0031794 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 3070 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 537250 | keep | 0 | Sep | 2021 | 0.36592 | 0.002091 | Sustained | FALSE | TRUE | Not_TMED_Event | 3070
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 2735 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 478625 | keep | 0 | Sep | 2021 | 0.32599 | 0.0018628 | Sustained | FALSE | TRUE | Not_TMED_Event | 2735
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 1070 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 187250 | keep | 0 | Sep | 2021 | 0.12754 | 0.00072877 | Sustained | FALSE | TRUE | Not_TMED_Event | 1070
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 1647 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 288225 | keep | 0 | Sep | 2021 | 0.19631 | 0.0011218 | Sustained | FALSE | TRUE | Not_TMED_Event | 1647
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 3295 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 576625 | keep | 0 | Sep | 2021 | 0.39274 | 0.0022442 | Sustained | FALSE | TRUE | Not_TMED_Event | 3295
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 1180 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 206500 | keep | 0 | Sep | 2021 | 0.14065 | 0.00080369 | Sustained | FALSE | TRUE | Not_TMED_Event | 1180
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 320 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 56000 | keep | 0 | Sep | 2021 | 0.038141 | 0.00021795 | Sustained | FALSE | TRUE | Not_TMED_Event | 320
BAYAMON | 2021-09-13 11:35 | 2021-09-13 14:30 | 2234 | 002:55 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-09-13 | 390950 | keep | 0 | Sep | 2021 | 0.26627 | 0.0015216 | Sustained | FALSE | TRUE | Not_TMED_Event | 2234
ARECIBO | 2021-09-13 11:36 | 2021-09-13 11:37 | 2791 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2791 | keep | 0 | Sep | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | TRUE | Not_TMED_Event | 2791
ARECIBO | 2021-09-13 11:36 | 2021-09-13 11:37 | 1464 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1464 | keep | 0 | Sep | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
ARECIBO | 2021-09-13 11:36 | 2021-09-13 11:37 | 759 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 759 | keep | 0 | Sep | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | TRUE | Not_TMED_Event | 759
ARECIBO | 2021-09-13 11:36 | 2021-09-13 11:37 | 1500 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 1500
ARECIBO | 2021-09-13 11:36 | 2021-09-13 12:20 | 2132 | 000:44 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 44 | 2021-09-13 | 93808 | keep | 0 | Sep | 2021 | 0.063892 | 0.0014521 | Sustained | FALSE | TRUE | Not_TMED_Event | 2132
ARECIBO | 2021-09-13 11:36 | 2021-09-13 12:20 | 2366 | 000:44 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 44 | 2021-09-13 | 104104 | keep | 0 | Sep | 2021 | 0.070905 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
ARECIBO | 2021-09-13 11:36 | 2021-09-13 12:20 | 1976 | 000:44 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 44 | 2021-09-13 | 86944 | keep | 0 | Sep | 2021 | 0.059217 | 0.0013458 | Sustained | FALSE | TRUE | Not_TMED_Event | 1976
ARECIBO | 2021-09-13 11:36 | 2021-09-13 12:20 | 3688 | 000:44 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 44 | 2021-09-13 | 162272 | keep | 0 | Sep | 2021 | 0.11052 | 0.0025119 | Sustained | FALSE | TRUE | Not_TMED_Event | 3688
UTUADO | 2021-09-13 11:37 | 2021-09-13 17:37 | 40 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | A21091300186 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-09-13 | 14400 | keep | 0 | Sep | 2021 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-13 11:38 | 2021-09-13 13:56 | 7 | 002:18 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEANDO 37.5 KVA X 37.5 KVA | C21091300062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 138 | 2021-09-13 | 966 | keep | 0 | Sep | 2021 | 0.00065794 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-09-13 11:43 | 2021-09-13 16:20 | 30 | 004:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | B21091100089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 277 | 2021-09-13 | 8310 | keep | 0 | Sep | 2021 | 0.0056599 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-13 12:04 | 2021-09-13 20:00 | 50 | 007:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21091300070 | New_Event |  |  | Include | Wildlife | 476 | 2021-09-13 | 23800 | keep | 0 | Sep | 2021 | 0.01621 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-13 12:09 | 2021-09-13 16:10 | 60 | 004:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21091300204 | New_Event | Bad Weather | Include | Include | Weather | 241 | 2021-09-13 | 14460 | keep | 0 | Sep | 2021 | 0.0098486 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-09-13 12:16 | 2021-09-13 15:27 | 40 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CAJA DE CORTE DE LINEA | P21091300049 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2021-09-13 | 7640 | keep | 0 | Sep | 2021 | 0.0052036 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-13 12:20 | 2021-09-15 15:44 | 25 | 051:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES PRIMARIOS | A21091100070 | New_Event | Wire Down | Include | Include | Equipment | 3084 | 2021-09-13 | 77100 | keep | 0 | Sep | 2021 | 0.052512 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-09-13 12:22 | 2021-09-13 14:45 | 3 | 002:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21091300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-09-13 | 429 | keep | 0 | Sep | 2021 | 0.00029219 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
HUMACAO | 2021-09-13 12:28 | 2021-09-13 20:17 | 50 | 007:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21091300074 | New_Event |  |  | Include | Wildlife | 469 | 2021-09-13 | 23450 | keep | 0 | Sep | 2021 | 0.015972 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-13 12:28 | 2021-09-13 13:30 | 1644 | 001:02 | T | NO SE REPORTO CAUSA | SE CERRO EL INTERRUPTOR NO SE ENCONTRO CAUSA | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-09-13 | 101928 | keep | 0 | Sep | 2021 | 0.069423 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
ARECIBO | 2021-09-13 12:28 | 2021-09-13 13:30 | 1831 | 001:02 | T | NO SE REPORTO CAUSA | SE CERRO EL INTERUPTOR NO SE ENCONTRO CAUSA PARA EL DISPARO | A21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-09-13 | 113522 | keep | 0 | Sep | 2021 | 0.077319 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
ARECIBO | 2021-09-13 12:32 | 2021-09-13 15:40 | 50 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21091300227 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2021-09-13 | 9400 | keep | 0 | Sep | 2021 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-13 12:40 | 2021-09-13 20:21 | 10 | 007:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21091300236 | New_Event | Bad Weather | Include | Include | Weather | 461 | 2021-09-13 | 4610 | keep | 0 | Sep | 2021 | 0.0031399 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-13 12:49 | 2021-09-13 23:04 | 1 | 010:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA | M21091300116 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 615 | 2021-09-13 | 615 | keep | 0 | Sep | 2021 | 0.00041887 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-09-13 12:52 | 2021-09-13 15:23 | 8 | 002:31 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR Y 1 X 30 EN CORTE DE LINEA | R21091300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-09-13 | 1208 | keep | 0 | Sep | 2021 | 0.00082276 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BARRANQUITAS | 2021-09-13 12:52 | 2021-09-13 14:03 | 40 | 001:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO AISLADORES | C21091300096 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 71 | 2021-09-13 | 2840 | keep | 0 | Sep | 2021 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-13 13:03 | 2021-09-13 16:57 | 46 | 003:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR CULEBRA | R21091300032 | New_Event |  |  | Include | Wildlife | 234 | 2021-09-13 | 10764 | keep | 0 | Sep | 2021 | 0.0073313 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
CAGUAS | 2021-09-13 13:07 | 2021-09-14 09:53 | 10 | 020:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMDOR MAL TIEMPO | CV2109130008 | New_Event | Bad Weather | Include | Include | Weather | 1246 | 2021-09-13 | 12460 | keep | 0 | Sep | 2021 | 0.0084864 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-13 13:11 | 2021-09-13 13:12 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 2302 | keep | 0 | Sep | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
ARECIBO | 2021-09-13 13:24 | 2021-09-13 19:04 | 4 | 005:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21091100003 | New_Event | Wire Down | Include | Include | Equipment | 340 | 2021-09-13 | 1360 | keep | 0 | Sep | 2021 | 0.00092629 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-09-13 13:25 | 2021-09-13 21:39 | 30 | 008:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA POR DISCOS ROTOS | A21091300273 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 494 | 2021-09-13 | 14820 | keep | 0 | Sep | 2021 | 0.010094 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-13 13:27 | 2021-09-15 13:28 | 50 | 048:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21091300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2881 | 2021-09-13 | 144050 | keep | 0 | Sep | 2021 | 0.098112 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-13 13:35 | 2021-09-13 15:49 | 6285 | 002:14 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36700 | M21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-09-13 | 842190 | keep | 0 | Sep | 2021 | 0.57361 | 0.0042807 | Sustained | FALSE | TRUE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-09-13 13:35 | 2021-09-13 15:49 | 2225 | 002:14 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36700 | M21091300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-09-13 | 298150 | keep | 0 | Sep | 2021 | 0.20307 | 0.0015154 | Sustained | FALSE | TRUE | Not_TMED_Event | 2225
BARRANQUITAS | 2021-09-13 13:35 | 2021-09-13 13:36 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2635 | keep | 0 | Sep | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-13 13:35 | 2021-09-13 13:36 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2280 | keep | 0 | Sep | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-09-13 13:35 | 2021-09-13 13:36 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
BARRANQUITAS | 2021-09-13 13:39 | 2021-09-13 14:25 | 2635 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C21091300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2021-09-13 | 121210 | keep | 0 | Sep | 2021 | 0.082556 | 0.0017947 | Sustained | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-13 13:39 | 2021-09-13 14:25 | 2280 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C21091300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2021-09-13 | 104880 | keep | 0 | Sep | 2021 | 0.071433 | 0.0015529 | Sustained | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-09-13 13:39 | 2021-09-13 14:25 | 1617 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C21091300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2021-09-13 | 74382 | keep | 0 | Sep | 2021 | 0.050661 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
ARECIBO | 2021-09-13 13:40 | 2021-09-14 12:11 | 15 | 022:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21091300284 | New_Event | Wire Down | Include | Include | Equipment | 1351 | 2021-09-13 | 20265 | keep | 0 | Sep | 2021 | 0.013802 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1924 | keep | 0 | Sep | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 968 | keep | 0 | Sep | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 680 | keep | 0 | Sep | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2246 | keep | 0 | Sep | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2470 | keep | 0 | Sep | 2021 | 0.0016823 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1182 | keep | 0 | Sep | 2021 | 0.00080505 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2340 | keep | 0 | Sep | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1637 | keep | 0 | Sep | 2021 | 0.001115 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 1475 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 661 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 661 | keep | 0 | Sep | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1569 | keep | 0 | Sep | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2309 | keep | 0 | Sep | 2021 | 0.0015726 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2440 | keep | 0 | Sep | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 3973 | keep | 0 | Sep | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-09-13 13:41 | 2021-09-13 13:42 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P210913000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-13 | 2484 | keep | 0 | Sep | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
YAUCO | 2021-09-13 13:42 | 2021-09-13 14:16 | 1 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR POR SECUNDARIA CRUZADA | P21091300008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-09-13 | 34 | keep | 0 | Sep | 2021 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-13 13:46 | 2021-09-13 13:48 | 199 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-13 | 398 | keep | 0 | Sep | 2021 | 0.00027108 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
AGUADILLA | 2021-09-13 13:47 | 2021-09-13 21:15 | 1497 | 007:28 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR SE PATRULLO NO SE ENCONTRO AVERIA NI CAUSA | M21091300158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 448 | 2021-09-13 | 670656 | keep | 0 | Sep | 2021 | 0.45678 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
CAGUAS | 2021-09-13 13:48 | 2021-09-13 20:30 | 500 | 006:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA RETEZO LINEAS Y CERRO PUENTE | C21091300094 | New_Event | Wire Down | Include | Include | Equipment | 402 | 2021-09-13 | 201000 | keep | 0 | Sep | 2021 | 0.1369 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-09-13 13:51 | 2021-09-13 19:30 | 75 | 005:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE DESGANCHO | A21091300278 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2021-09-13 | 25425 | keep | 0 | Sep | 2021 | 0.017317 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-09-13 13:57 | 2021-09-13 16:15 | 50 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR CRUCE DE FASES POR AVE | P21091300057 | New_Event |  |  | Include | Wildlife | 138 | 2021-09-13 | 6900 | keep | 0 | Sep | 2021 | 0.0046996 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-13 14:01 | 2021-09-13 21:39 | 50 | 007:38 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARRARAYO AVERIADO | A21091300395 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 458 | 2021-09-13 | 22900 | keep | 0 | Sep | 2021 | 0.015597 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-13 14:03 | 2021-09-13 14:20 | 2410 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18400 | C21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-09-13 | 40970 | keep | 0 | Sep | 2021 | 0.027904 | 0.0016414 | Sustained | FALSE | TRUE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-09-13 14:03 | 2021-09-13 14:20 | 2826 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18400 | C21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-09-13 | 48042 | keep | 0 | Sep | 2021 | 0.032721 | 0.0019248 | Sustained | FALSE | TRUE | Not_TMED_Event | 2826
BAYAMON | 2021-09-13 14:06 | 2021-09-13 14:07 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 2147 | keep | 0 | Sep | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
AGUADILLA | 2021-09-13 14:18 | 2021-09-16 12:10 | 25 | 069:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON LIQUEO DE ACEITE DE PROLEC 50 KVA 7620/13200 #M20I10261 FID-31496550 X 50 KVA | M21091300063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4192 | 2021-09-13 | 104800 | keep | 0 | Sep | 2021 | 0.071379 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-09-13 14:20 | 2021-09-14 12:00 | 20 | 021:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091300301 | New_Event | Bad Weather | Include | Include | Weather | 1300 | 2021-09-13 | 26000 | keep | 0 | Sep | 2021 | 0.017708 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-13 14:20 | 2021-09-13 16:00 | 40 | 001:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO AISLADORES | C21091300096 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 100 | 2021-09-13 | 4000 | keep | 0 | Sep | 2021 | 0.0027244 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-13 14:30 | 2021-09-13 16:38 | 15 | 002:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO | A21091300312 | New_Event | Service Transformer Failure | Include | Include | Equipment | 128 | 2021-09-13 | 1920 | keep | 0 | Sep | 2021 | 0.0013077 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-13 14:30 | 2021-09-13 14:49 | 35 | 000:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091100133 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 19 | 2021-09-13 | 665 | keep | 0 | Sep | 2021 | 0.00045293 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-13 14:31 | 2021-09-13 19:08 | 120 | 004:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y 2 X 65 EN CORTE DE LINEA | S21091300064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-09-13 | 33240 | keep | 0 | Sep | 2021 | 0.02264 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-13 14:33 | 2021-09-13 20:02 | 55 | 005:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE SAFADO A AISLADOR | S21091100076 | New_Event | Wire Down | Include | Include | Equipment | 329 | 2021-09-13 | 18095 | keep | 0 | Sep | 2021 | 0.012324 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2021-09-13 14:36 | 2021-09-13 17:11 | 11 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21091300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2021-09-13 | 1705 | keep | 0 | Sep | 2021 | 0.0011613 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-09-13 14:47 | 2021-09-13 17:43 | 30 | 002:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA | M2109130060 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2021-09-13 | 5280 | keep | 0 | Sep | 2021 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-13 14:47 | 2021-09-13 18:40 | 50 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21091200060 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-09-13 | 11650 | keep | 0 | Sep | 2021 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-13 14:51 | 2021-09-13 16:00 | 40 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21091300201 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2021-09-13 | 2760 | keep | 0 | Sep | 2021 | 0.0018798 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-13 15:01 | 2021-09-13 21:46 | 150 | 006:45 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21091300130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2021-09-13 | 60750 | keep | 0 | Sep | 2021 | 0.041377 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-09-13 15:09 | 2021-09-13 15:10 | 2039 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | P21091300066 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-13 | 2039 | keep | 0 | Sep | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2021-09-13 15:10 | 2021-09-14 02:29 | 100 | 011:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1X65 EN CORTE DE LINEA POR MAL TIEMPO | P21091300098 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 679 | 2021-09-13 | 67900 | keep | 0 | Sep | 2021 | 0.046246 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-13 15:19 | 2021-09-13 18:23 | 7 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21091300320 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2021-09-13 | 1288 | keep | 0 | Sep | 2021 | 0.00087725 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-09-13 15:23 | 2021-09-13 22:06 | 13 | 006:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21091300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2021-09-13 | 5239 | keep | 0 | Sep | 2021 | 0.0035683 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
HUMACAO | 2021-09-13 15:26 | 2021-09-13 21:09 | 5 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091300140 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2021-09-13 | 1715 | keep | 0 | Sep | 2021 | 0.0011681 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-13 15:35 | 2021-09-14 09:53 | 40 | 018:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21091300142 | New_Event | Cutout Failure | Include | Include | Equipment | 1098 | 2021-09-13 | 43920 | keep | 0 | Sep | 2021 | 0.029914 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-13 15:37 | 2021-09-13 17:27 | 30 | 001:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21091300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-09-13 | 3300 | keep | 0 | Sep | 2021 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-13 15:37 | 2021-09-14 09:53 | 1 | 018:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091300143 | New_Event | Bad Weather | Include | Include | Weather | 1096 | 2021-09-13 | 1096 | keep | 0 | Sep | 2021 | 0.00074648 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-13 15:38 | 2021-09-13 15:41 | 3458 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR CON RE CLOSE RELAY EN OFF | M21091300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-09-13 | 10374 | keep | 0 | Sep | 2021 | 0.0070657 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2021-09-13 15:40 | 2021-09-13 18:06 | 100 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | M21091300281 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-09-13 | 14600 | keep | 0 | Sep | 2021 | 0.009944 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-13 15:41 | 2021-09-13 20:20 | 50 | 004:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21091300341 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 279 | 2021-09-13 | 13950 | keep | 0 | Sep | 2021 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-13 15:41 | 2021-09-14 13:20 | 60 | 021:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091300334 | New_Event | Bad Weather | Include | Include | Weather | 1299 | 2021-09-13 | 77940 | keep | 0 | Sep | 2021 | 0.053085 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-09-13 15:43 | 2021-09-13 15:44 | 3744 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21091300078 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-13 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-13 15:43 | 2021-09-13 15:44 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091300078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-09-13 15:44 | 2021-09-13 19:31 | 520 | 003:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | P21091300071 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2021-09-13 | 118040 | keep | 0 | Sep | 2021 | 0.080397 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
PONCE | 2021-09-13 15:44 | 2021-09-13 17:41 | 15 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X15 EN TRANSFORMADOR POR CRUCE DE FASES POR AVE | P21091300086 | 1st_after_momentary |  |  | Include | Wildlife | 117 | 2021-09-13 | 1755 | keep | 0 | Sep | 2021 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-13 15:47 | 2021-09-13 17:15 | 100 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 200 EN CORTE DE LINEA MAL TIEMPO | M21091300287 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-09-13 | 8800 | keep | 0 | Sep | 2021 | 0.0059936 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-09-13 15:49 | 2021-09-13 17:46 | 5 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R21091300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2021-09-13 | 585 | keep | 0 | Sep | 2021 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BARRANQUITAS | 2021-09-13 15:54 | 2021-09-13 18:06 | 50 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091200135 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2021-09-13 | 6600 | keep | 0 | Sep | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-13 15:57 | 2021-09-13 18:00 | 30 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091300307 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2021-09-13 | 3690 | keep | 0 | Sep | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-13 16:01 | 2021-09-15 14:16 | 50 | 046:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SAFADO A CAJA PRIMARIA NO FUNDIO FUSIBLE | R21091300045 | New_Event | Wire Down | Include | Include | Equipment | 2775 | 2021-09-13 | 138750 | keep | 0 | Sep | 2021 | 0.094502 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-13 16:08 | 2021-09-13 19:19 | 80 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21091300221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-09-13 | 15280 | keep | 0 | Sep | 2021 | 0.010407 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-13 16:29 | 2021-09-13 22:40 | 6 | 006:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR | A21091300356 | New_Event | Bad Weather | Include | Include | Weather | 371 | 2021-09-13 | 2226 | keep | 0 | Sep | 2021 | 0.0015161 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-13 16:30 | 2021-09-14 18:30 | 120 | 025:60 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M21091300356 | New_Event | Wire Down | Include | Include | Equipment | 1560 | 2021-09-13 | 187200 | keep | 0 | Sep | 2021 | 0.1275 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2021-09-13 16:40 | 2021-09-13 16:41 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-09-13 16:40 | 2021-09-13 16:41 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1204-05 | S21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-09-13 16:41 | 2021-09-14 01:27 | 160 | 008:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091300118 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 526 | 2021-09-13 | 84160 | keep | 0 | Sep | 2021 | 0.057321 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
ARECIBO | 2021-09-13 16:41 | 2021-09-14 10:51 | 10 | 018:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091300361 | New_Event | Bad Weather | Include | Include | Weather | 1090 | 2021-09-13 | 10900 | keep | 0 | Sep | 2021 | 0.0074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-13 16:42 | 2021-09-13 19:24 | 50 | 002:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X40 Y 1X50 EN DIFERENTES CORTES DE LINEA. SE LEVANTO ALAMBRE PRIMARIO | P21091300084 | New_Event | Wire Down | Include | Include | Equipment | 162 | 2021-09-13 | 8100 | keep | 0 | Sep | 2021 | 0.0055169 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-13 16:47 | 2021-09-14 10:05 | 50 | 017:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B21091300226 | New_Event | Wire Down | Include | Include | Equipment | 1038 | 2021-09-13 | 51900 | keep | 0 | Sep | 2021 | 0.035349 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-13 16:47 | 2021-09-14 16:40 | 15 | 023:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21091300364 | New_Event | Cutout Failure | Include | Include | Equipment | 1433 | 2021-09-13 | 21495 | keep | 0 | Sep | 2021 | 0.01464 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-09-13 16:47 | 2021-09-14 11:15 | 50 | 018:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091300362 | New_Event | Bad Weather | Include | Include | Weather | 1108 | 2021-09-13 | 55400 | keep | 0 | Sep | 2021 | 0.037733 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-13 16:48 | 2021-09-16 16:15 | 20 | 071:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21091300116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4287 | 2021-09-13 | 85740 | keep | 0 | Sep | 2021 | 0.058397 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-09-13 16:52 | 2021-09-14 12:10 | 150 | 019:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21091300359 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1158 | 2021-09-13 | 173700 | keep | 0 | Sep | 2021 | 0.11831 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-09-13 16:54 | 2021-09-13 18:14 | 6 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21091300227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-09-13 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-13 16:58 | 2021-09-13 18:13 | 1725 | 001:15 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR | C21091300080 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2021-09-13 | 129375 | keep | 0 | Sep | 2021 | 0.088117 | 0.0011749 | Sustained | FALSE | FALSE | Not_TMED_Event | 1725
MAYAGÃœEZ | 2021-09-13 17:00 | 2021-09-13 18:58 | 30 | 001:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091300365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-09-13 | 3540 | keep | 0 | Sep | 2021 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-13 17:03 | 2021-09-14 15:37 | 60 | 022:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091300367 | New_Event | Bad Weather | Include | Include | Weather | 1354 | 2021-09-13 | 81240 | keep | 0 | Sep | 2021 | 0.055332 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-13 17:08 | 2021-09-14 12:47 | 75 | 019:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21009130037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1179 | 2021-09-13 | 88425 | keep | 0 | Sep | 2021 | 0.060226 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-13 17:09 | 2021-09-16 16:30 | 7 | 071:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091300368 | New_Event | Bad Weather | Include | Include | Weather | 4281 | 2021-09-13 | 29967 | keep | 0 | Sep | 2021 | 0.02041 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-09-13 17:12 | 2021-09-15 11:27 | 100 | 042:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091300378 | New_Event | Bad Weather | Include | Include | Weather | 2535 | 2021-09-13 | 253500 | keep | 0 | Sep | 2021 | 0.17266 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-13 17:15 | 2021-09-13 17:17 | 2450 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO | C21091300173 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-13 | 4900 | keep | 0 | Sep | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
UTUADO | 2021-09-13 17:16 | 2021-09-14 15:37 | 3 | 022:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091300404 | New_Event | Bad Weather | Include | Include | Weather | 1341 | 2021-09-13 | 4023 | keep | 0 | Sep | 2021 | 0.00274 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
HUMACAO | 2021-09-13 17:17 | 2021-09-13 21:31 | 100 | 004:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21091300178 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 254 | 2021-09-13 | 25400 | keep | 0 | Sep | 2021 | 0.0173 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-13 17:17 | 2021-09-13 21:40 | 543 | 004:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR SE REPARO PUENTES PRIMARIOS EN TRONCAL DEL ALIMENTADOR | M21091300392 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2021-09-13 | 142809 | keep | 0 | Sep | 2021 | 0.097267 | 0.00036983 | Sustained | FALSE | FALSE | Not_TMED_Event | 543
SAN JUAN | 2021-09-13 17:23 | 2021-09-13 20:40 | 40 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-09-13 | 7880 | keep | 0 | Sep | 2021 | 0.005367 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-13 17:30 | 2021-09-14 12:02 | 12 | 018:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091300374 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1112 | 2021-09-13 | 13344 | keep | 0 | Sep | 2021 | 0.0090885 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BARRANQUITAS | 2021-09-13 17:32 | 2021-09-14 14:51 | 20 | 021:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21091300175 | New_Event | Wire Down | Include | Include | Equipment | 1279 | 2021-09-13 | 25580 | keep | 0 | Sep | 2021 | 0.017422 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-13 17:32 | 2021-09-14 14:31 | 30 | 020:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C21091300175 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1259 | 2021-09-13 | 37770 | keep | 0 | Sep | 2021 | 0.025725 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-09-13 17:40 | 2021-09-14 11:27 | 60 | 017:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21091300393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1067 | 2021-09-13 | 64020 | keep | 0 | Sep | 2021 | 0.043604 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-13 17:41 | 2021-09-14 15:45 | 15 | 022:04 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M21009130395 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1324 | 2021-09-13 | 19860 | keep | 0 | Sep | 2021 | 0.013527 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-09-13 17:46 | 2021-09-14 09:53 | 100 | 016:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21091300399 | New_Event | Bad Weather | Include | Include | Weather | 967 | 2021-09-13 | 96700 | keep | 0 | Sep | 2021 | 0.065862 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-13 17:47 | 2021-09-13 17:48 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 1310 | keep | 0 | Sep | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
MAYAGÃœEZ | 2021-09-13 17:49 | 2021-09-13 18:50 | 1617 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-09-13 | 98637 | keep | 0 | Sep | 2021 | 0.067181 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-13 17:49 | 2021-09-13 18:50 | 1017 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-09-13 | 62037 | keep | 0 | Sep | 2021 | 0.042253 | 0.00069267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-13 17:49 | 2021-09-13 18:50 | 828 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-09-13 | 50508 | keep | 0 | Sep | 2021 | 0.034401 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-13 17:49 | 2021-09-13 18:50 | 863 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-09-13 | 52643 | keep | 0 | Sep | 2021 | 0.035855 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-13 17:49 | 2021-09-13 18:50 | 309 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-09-13 | 18849 | keep | 0 | Sep | 2021 | 0.012838 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-13 17:49 | 2021-09-13 18:50 | 176 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-09-13 | 10736 | keep | 0 | Sep | 2021 | 0.0073122 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
CAGUAS | 2021-09-13 17:50 | 2021-09-14 15:27 | 5 | 021:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091300181 | New_Event | Bad Weather | Include | Include | Weather | 1297 | 2021-09-13 | 6485 | keep | 0 | Sep | 2021 | 0.0044169 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-09-13 17:56 | 2021-09-14 11:20 | 100 | 017:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21091300403 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1044 | 2021-09-13 | 104400 | keep | 0 | Sep | 2021 | 0.071106 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-13 18:00 | 2021-09-13 20:15 | 200 | 002:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA PRIMARIA | M21091200140 | New_Event | Wire Down | Include | Include | Equipment | 135 | 2021-09-13 | 27000 | keep | 0 | Sep | 2021 | 0.01839 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-09-13 18:01 | 2021-09-13 18:55 | 15 | 000:54 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21091300090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-09-13 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-09-13 18:05 | 2021-09-13 22:50 | 50 | 004:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21091300409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-09-13 | 14250 | keep | 0 | Sep | 2021 | 0.0097056 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-13 18:08 | 2021-09-14 09:53 | 10 | 015:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE Y LINEA SECUNDARIA | C21091300051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 945 | 2021-09-13 | 9450 | keep | 0 | Sep | 2021 | 0.0064364 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-09-13 18:13 | 2021-09-13 18:46 | 1 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21091300051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-09-13 | 33 | keep | 0 | Sep | 2021 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-13 18:13 | 2021-09-13 19:25 | 425 | 001:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR | C21091300080 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 72 | 2021-09-13 | 30600 | keep | 0 | Sep | 2021 | 0.020842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-09-13 18:15 | 2021-09-13 19:14 | 50 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R21091300052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-09-13 | 2950 | keep | 0 | Sep | 2021 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-13 18:17 | 2021-09-13 19:08 | 15 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN TRANSFORMADOR | S21091300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-09-13 | 765 | keep | 0 | Sep | 2021 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-13 18:32 | 2021-09-13 19:40 | 25 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21091300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2021-09-13 | 1700 | keep | 0 | Sep | 2021 | 0.0011579 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-09-13 18:36 | 2021-09-14 13:27 | 25 | 018:51 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | P21091300092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1131 | 2021-09-13 | 28275 | keep | 0 | Sep | 2021 | 0.019258 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-09-13 18:37 | 2021-09-13 18:38 | 457 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-13 | 457 | keep | 0 | Sep | 2021 | 0.00031126 | 0.00031126 | Momentary | FALSE | FALSE | Not_TMED_Event | 457
MAYAGÃœEZ | 2021-09-13 18:50 | 2021-09-13 20:45 | 40 | 001:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21091200228 | Partial_restoration | Wire Down | Include | Include | Equipment | 115 | 2021-09-13 | 4600 | keep | 0 | Sep | 2021 | 0.003133 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-13 18:50 | 2021-09-14 15:40 | 150 | 020:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21091300090 | Partial_restoration | Wire Down | Include | Include | Equipment | 1250 | 2021-09-13 | 187500 | keep | 0 | Sep | 2021 | 0.12771 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-13 19:00 | 2021-09-14 15:23 | 100 | 020:23 | P | DESGANCHE | 1 X 100 1 X 30 EN CORTES DE LINEA 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21091300240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1223 | 2021-09-13 | 122300 | keep | 0 | Sep | 2021 | 0.083298 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-13 19:09 | 2021-09-14 09:53 | 80 | 014:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21091300196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 884 | 2021-09-13 | 70720 | keep | 0 | Sep | 2021 | 0.048167 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-09-13 19:18 | 2021-09-13 20:04 | 30 | 000:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21091300437 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-09-13 | 1380 | keep | 0 | Sep | 2021 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-09-13 19:19 | 2021-09-13 20:26 | 180 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 140 EN CORTES DE LINEAS CRUCE POR AVE | R21091300057 | New_Event |  |  | Include | Wildlife | 67 | 2021-09-13 | 12060 | keep | 0 | Sep | 2021 | 0.008214 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
CAGUAS | 2021-09-13 19:25 | 2021-09-13 19:33 | 1725 | 000:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | C21091300080 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2021-09-13 | 13800 | keep | 0 | Sep | 2021 | 0.0093991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-13 19:30 | 2021-09-13 22:13 | 80 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y SE CERRO PUENTE ABIERTO | B21091300080 | Additional_clients | Wire Down | Include | Include | Equipment | 163 | 2021-09-13 | 13040 | keep | 0 | Sep | 2021 | 0.0088815 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-13 19:30 | 2021-09-14 10:05 | 100 | 014:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091300390 | New_Event | Bad Weather | Include | Include | Weather | 875 | 2021-09-13 | 87500 | keep | 0 | Sep | 2021 | 0.059596 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-13 19:33 | 2021-09-14 11:20 | 300 | 015:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO AISLADOR | C21091300223 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 947 | 2021-09-13 | 284100 | keep | 0 | Sep | 2021 | 0.1935 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-09-13 19:34 | 2021-09-14 06:51 | 50 | 011:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21091300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 677 | 2021-09-13 | 33850 | keep | 0 | Sep | 2021 | 0.023055 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-13 19:34 | 2021-09-14 11:37 | 40 | 016:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091300437 | New_Event | Bad Weather | Include | Include | Weather | 963 | 2021-09-13 | 38520 | keep | 0 | Sep | 2021 | 0.026236 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-13 19:55 | 2021-09-13 20:57 | 457 | 001:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO AVERIA POR CONDUCTOR EN EL SUELO Y SE CERRO INTERRUPTOR | S21091300143 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 62 | 2021-09-13 | 28334 | keep | 0 | Sep | 2021 | 0.019298 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
CANOVANAS | 2021-09-13 20:17 | 2021-09-13 21:06 | 80 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CORTES DE LINEAS MAL TIEMPO | R21091300062 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-09-13 | 3920 | keep | 0 | Sep | 2021 | 0.0026699 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-13 20:23 | 2021-09-14 16:30 | 35 | 020:07 | P | CABLE SOTERRADO AVERIADO | SE LEVANTO PROVISIONAL AEREO Y SE ENERGIZO TRANSFORMADORES T-73 AL T-6 | S21091300146 | New_Event | UG Cable Fault | Include | Include | Equipment | 1207 | 2021-09-13 | 42245 | keep | 0 | Sep | 2021 | 0.028773 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-09-13 20:38 | 2021-09-14 20:02 | 100 | 023:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21091300451 | New_Event | Wire Down | Include | Include | Equipment | 1404 | 2021-09-13 | 140400 | keep | 0 | Sep | 2021 | 0.095626 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-13 20:45 | 2021-09-14 01:17 | 50 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO TODO NORMAL EN EL SISTEMA SOTERRADO | P21091300102 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2021-09-13 | 13600 | keep | 0 | Sep | 2021 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-09-13 20:50 | 2021-09-14 16:40 | 40 | 019:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091300455 | New_Event | Bad Weather | Include | Include | Weather | 1190 | 2021-09-13 | 47600 | keep | 0 | Sep | 2021 | 0.03242 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-13 20:57 | 2021-09-13 23:29 | 120 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES | S21091300143 | Partial_restoration | Wire Down | Include | Include | Equipment | 152 | 2021-09-13 | 18240 | keep | 0 | Sep | 2021 | 0.012423 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-13 21:12 | 2021-09-13 21:13 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21091300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-13 | 4431 | keep | 0 | Sep | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
MAYAGÃœEZ | 2021-09-13 21:12 | 2021-09-14 09:53 | 40 | 012:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091300463 | New_Event | Vegetation Contact | Include | Include | Vegetation | 761 | 2021-09-13 | 30440 | keep | 0 | Sep | 2021 | 0.020733 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-13 21:17 | 2021-09-13 21:30 | 75 | 000:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 ENCORTE DE LINEA MAL TIEMPO | M21091300466 | New_Event | Bad Weather | Include | Include | Weather | 13 | 2021-09-13 | 975 | keep | 0 | Sep | 2021 | 0.00066407 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-13 21:27 | 2021-09-14 17:17 | 20 | 019:50 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU | B21091300249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1190 | 2021-09-13 | 23800 | keep | 0 | Sep | 2021 | 0.01621 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-13 21:33 | 2021-09-13 22:46 | 990 | 001:13 | T | DESCONECTIVO DEFECTUOSO | MACHETE QUEMANDOSE SE ABRIO Y LUEGO SE CERRO | M21091300473 | New_Event | Switch Failure | Include | Include | Equipment | 73 | 2021-09-13 | 72270 | keep | 0 | Sep | 2021 | 0.049223 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2021-09-13 22:46 | 2021-09-14 16:20 | 50 | 017:34 | P | DESCONECTIVO DEFECTUOSO | MACHETES QUEMADOS SE ENERGIZO A TRAVES DE NORMALLY-OPEN | M21091400012 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1054 | 2021-09-13 | 52700 | keep | 0 | Sep | 2021 | 0.035894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-13 22:46 | 2021-09-14 17:45 | 150 | 018:59 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400316 | New_Event | Bad Weather | Include | Include | Weather | 1139 | 2021-09-13 | 170850 | keep | 0 | Sep | 2021 | 0.11637 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-09-13 22:49 | 2021-09-14 09:53 | 12 | 011:04 | P | TRANSFORMADOR AVERIADO | REMPLAZO 2 TRANSFORMADORES QUEMADOS 50 KVA X 50 KVA | C21091300220 | New_Event | Service Transformer Failure | Include | Include | Equipment | 664 | 2021-09-13 | 7968 | keep | 0 | Sep | 2021 | 0.005427 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-09-13 23:07 | 2021-09-14 12:17 | 8 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091300221 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-09-13 | 6320 | keep | 0 | Sep | 2021 | 0.0043045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-14 00:30 | 2021-09-14 13:36 | 5 | 013:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091400002 | New_Event | Bad Weather | Include | Include | Weather | 786 | 2021-09-14 | 3930 | keep | 0 | Sep | 2021 | 0.0026767 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
PONCE | 2021-09-14 01:17 | 2021-09-14 01:31 | 520 | 000:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION DE FOREMAN JESUS JAIME PARA CERRAR PUENTE PRIMARIO EN TRONCAL. | P21091400002 | Additional_clients | Wire Down | Include | Include | Equipment | 14 | 2021-09-14 | 7280 | keep | 0 | Sep | 2021 | 0.0049584 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
FAJARDO | 2021-09-14 01:27 | 2021-09-14 09:53 | 40 | 008:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21091400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2021-09-14 | 20240 | keep | 0 | Sep | 2021 | 0.013785 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CAGUAS | 2021-09-14 03:28 | 2021-09-14 11:36 | 80 | 008:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21091400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2021-09-14 | 39040 | keep | 0 | Sep | 2021 | 0.02659 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BAYAMON | 2021-09-14 04:00 | 2021-09-15 21:25 | 20 | 041:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | B21091400007 | New_Event | Cutout Failure | Include | Include | Equipment | 2485 | 2021-09-14 | 49700 | keep | 0 | Sep | 2021 | 0.03385 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
CAGUAS | 2021-09-14 05:06 | 2021-09-14 05:07 | 2302 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21091400005 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-14 | 2302 | keep | 0 | Sep | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | TMED_Event | 2302
CAGUAS | 2021-09-14 05:07 | 2021-09-14 10:39 | 1 | 005:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN TRANSFORMADORES CRUCE POR AVE | C21091400007 | 1st_after_momentary |  |  | Include | Wildlife | 332 | 2021-09-14 | 332 | keep | 0 | Sep | 2021 | 0.00022612 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2021-09-14 05:10 | 2021-09-14 07:53 | 6481 | 002:43 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO Y SE CERRO POR SCADA | S21091400000 | New_Event | Switch Failure | Include | Include | Equipment | 163 | 2021-09-14 | 1056403 | keep | 0 | Sep | 2021 | 0.71951 | 0.0044142 | Sustained | FALSE | FALSE | TMED_Event | 6481
VEGA BAJA | 2021-09-14 06:18 | 2021-09-14 12:52 | 60 | 006:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21091400003 | New_Event | Wire Down | Include | Include | Equipment | 394 | 2021-09-14 | 23640 | keep | 0 | Sep | 2021 | 0.016101 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
PONCE | 2021-09-14 06:57 | 2021-09-14 06:58 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | TMED_Event | 3718
ARECIBO | 2021-09-14 06:59 | 2021-09-14 09:29 | 100 | 002:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-09-14 | 15000 | keep | 0 | Sep | 2021 | 0.010216 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-09-14 07:02 | 2021-09-14 07:03 | 74 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1529-11 | S21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 74 | keep | 0 | Sep | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2021-09-14 07:02 | 2021-09-14 07:03 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1521-02 | S21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1370 | keep | 0 | Sep | 2021 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | TMED_Event | 1370
BAYAMON | 2021-09-14 07:03 | 2021-09-16 00:35 | 12 | 041:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE, SECUNDARIA Y DOS TOMAS POR ARBOL QUE CAYO ENCIMA DE LA SECUNDARIA | S21091400098 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2492 | 2021-09-14 | 29904 | keep | 0 | Sep | 2021 | 0.020367 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
FAJARDO | 2021-09-14 07:27 | 2021-09-14 09:17 | 50 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21091400043 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-09-14 | 5500 | keep | 0 | Sep | 2021 | 0.003746 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-09-14 07:36 | 2021-09-14 09:53 | 40 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091400011 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-09-14 | 5480 | keep | 0 | Sep | 2021 | 0.0037324 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-09-14 07:46 | 2021-09-14 19:27 | 199 | 011:41 | T | DESGANCHE | SE REPARO INTERRUPTOR QUE NO CERRABA POR SCADA Y SE REALIZO DESGANCHE EN VARIOS PUNTOS | S21091400176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 701 | 2021-09-14 | 139499 | keep | 0 | Sep | 2021 | 0.095012 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
CAGUAS | 2021-09-14 07:49 | 2021-09-14 09:53 | 40 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA REPARO NEUTRAL PRIMARIO ROTO | C21091400013 | New_Event | Wire Down | Include | Include | Equipment | 124 | 2021-09-14 | 4960 | keep | 0 | Sep | 2021 | 0.0033782 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-09-14 07:50 | 2021-09-14 13:25 | 50 | 005:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21091400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-09-14 | 16750 | keep | 0 | Sep | 2021 | 0.011408 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-09-14 07:58 | 2021-09-14 13:45 | 15 | 005:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21091400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 347 | 2021-09-14 | 5205 | keep | 0 | Sep | 2021 | 0.0035451 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
MAYAGÃœEZ | 2021-09-14 08:09 | 2021-09-14 09:43 | 100 | 001:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21091400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-09-14 | 9400 | keep | 0 | Sep | 2021 | 0.0064023 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-09-14 08:21 | 2021-09-14 09:53 | 1 | 001:32 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 20 EN SU | S21091200033 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 92 | 2021-09-14 | 92 | keep | 0 | Sep | 2021 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2021-09-14 08:28 | 2021-09-14 10:49 | 6481 | 002:21 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE CERRO POR SCADA | S21091400000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 141 | 2021-09-14 | 913821 | keep | 0 | Sep | 2021 | 0.6224 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-09-14 08:29 | 2021-09-14 08:30 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1307 | keep | 0 | Sep | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | TMED_Event | 1307
BAYAMON | 2021-09-14 08:30 | 2021-09-14 14:26 | 1 | 005:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZARON 2 CAJAS PRIMARIAS | B21091400014 | New_Event | Cutout Failure | Include | Include | Equipment | 356 | 2021-09-14 | 356 | keep | 0 | Sep | 2021 | 0.00024247 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
CAGUAS | 2021-09-14 08:43 | 2021-09-14 13:47 | 6 | 005:04 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEANDO DE 37.5 KVA X 50 KVA HC @ GIS UPDATES | C21091400015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 304 | 2021-09-14 | 1824 | keep | 0 | Sep | 2021 | 0.0012423 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
ARECIBO | 2021-09-14 08:46 | 2021-09-15 18:16 | 1 | 033:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091400024 | New_Event | Bad Weather | Include | Include | Weather | 2010 | 2021-09-14 | 2010 | keep | 0 | Sep | 2021 | 0.001369 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2021-09-14 08:49 | 2021-09-14 14:38 | 12 | 005:49 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21091400002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 349 | 2021-09-14 | 4188 | keep | 0 | Sep | 2021 | 0.0028524 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
SAN JUAN | 2021-09-14 09:04 | 2021-09-14 14:00 | 1 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21091400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2021-09-14 | 296 | keep | 0 | Sep | 2021 | 0.0002016 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
BAYAMON | 2021-09-14 09:18 | 2021-09-14 19:42 | 20 | 010:24 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE WR-5933782 | S21091400000 | New_Event | Defective Pole | Include | Include | Equipment | 624 | 2021-09-14 | 12480 | keep | 0 | Sep | 2021 | 0.0085001 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
FAJARDO | 2021-09-14 09:21 | 2021-09-14 12:48 | 7 | 003:27 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR LIQUEANDO | R21091400079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 207 | 2021-09-14 | 1449 | keep | 0 | Sep | 2021 | 0.00098691 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
SAN JUAN | 2021-09-14 09:28 | 2021-09-14 09:53 | 10 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFORMADOR | S21091400037 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-09-14 | 250 | keep | 0 | Sep | 2021 | 0.00017027 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
CANOVANAS | 2021-09-14 09:32 | 2021-09-14 09:53 | 9 | 000:21 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21091400082 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 21 | 2021-09-14 | 189 | keep | 0 | Sep | 2021 | 0.00012873 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
YAUCO | 2021-09-14 09:40 | 2021-09-14 09:41 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091400033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 2484 | keep | 0 | Sep | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | TMED_Event | 2484
SAN JUAN | 2021-09-14 09:42 | 2021-09-14 09:43 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 5290 | keep | 0 | Sep | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | TMED_Event | 5290
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:17 | 2402 | 000:24 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 24 | 2021-09-14 | 57648 | keep | 0 | Sep | 2021 | 0.039264 | 0.001636 | Sustained | TRUE | TRUE | TMED_Event | 2402
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:16 | 4028 | 000:23 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 23 | 2021-09-14 | 92644 | keep | 0 | Sep | 2021 | 0.063099 | 0.0027435 | Sustained | TRUE | TRUE | TMED_Event | 4028
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:16 | 2617 | 000:23 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 23 | 2021-09-14 | 60191 | keep | 0 | Sep | 2021 | 0.040996 | 0.0017824 | Sustained | TRUE | TRUE | TMED_Event | 2617
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:17 | 6136 | 000:24 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 24 | 2021-09-14 | 147264 | keep | 0 | Sep | 2021 | 0.1003 | 0.0041792 | Sustained | TRUE | TRUE | TMED_Event | 6136
BAYAMON | 2021-09-14 09:53 | 2021-09-14 11:34 | 966 | 001:41 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 101 | 2021-09-14 | 97566 | keep | 0 | Sep | 2021 | 0.066452 | 0.00065794 | Sustained | TRUE | TRUE | TMED_Event | 966
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:18 | 186 | 000:25 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 25 | 2021-09-14 | 4650 | keep | 0 | Sep | 2021 | 0.0031671 | 0.00012668 | Sustained | TRUE | TRUE | TMED_Event | 186
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:19 | 1746 | 000:26 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 26 | 2021-09-14 | 45396 | keep | 0 | Sep | 2021 | 0.030919 | 0.0011892 | Sustained | TRUE | TRUE | TMED_Event | 1746
BAYAMON | 2021-09-14 09:53 | 2021-09-14 10:19 | 112 | 000:26 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 26 | 2021-09-14 | 2912 | keep | 0 | Sep | 2021 | 0.0019833 | 7.6283e-05 | Sustained | TRUE | TRUE | TMED_Event | 112
VEGA BAJA | 2021-09-14 09:53 | 2021-09-14 10:03 | 1310 | 000:10 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 10 | 2021-09-14 | 13100 | keep | 0 | Sep | 2021 | 0.0089224 | 0.00089224 | Sustained | TRUE | TRUE | TMED_Event | 1310
VEGA BAJA | 2021-09-14 09:53 | 2021-09-14 10:03 | 215 | 000:10 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 10 | 2021-09-14 | 2150 | keep | 0 | Sep | 2021 | 0.0014644 | 0.00014644 | Sustained | TRUE | TRUE | TMED_Event | 215
VEGA BAJA | 2021-09-14 09:53 | 2021-09-14 10:03 | 1 | 000:10 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 10 | 2021-09-14 | 10 | keep | 0 | Sep | 2021 | 6.811e-06 | 6.811e-07 | Sustained | TRUE | TRUE | TMED_Event | 1
VEGA BAJA | 2021-09-14 09:53 | 2021-09-14 10:15 | 603 | 000:22 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 22 | 2021-09-14 | 13266 | keep | 0 | Sep | 2021 | 0.0090354 | 0.0004107 | Sustained | TRUE | TRUE | TMED_Event | 603
VEGA BAJA | 2021-09-14 09:53 | 2021-09-14 10:15 | 6 | 000:22 | T | RELEVO DE CARGA AUTOMATICO | DISPARO LINEA 51100 SACA DE SERVICIO A ECOELECTRICA | B21091400000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 22 | 2021-09-14 | 132 | keep | 0 | Sep | 2021 | 8.9905e-05 | 4.0866e-06 | Sustained | TRUE | TRUE | TMED_Event | 6
CAGUAS | 2021-09-14 09:59 | 2021-09-14 20:08 | 40 | 010:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA REPARO NEUTRAL PRIMARIO ROTO | C21091400013 | Partial_restoration | Wire Down | Include | Include | Equipment | 609 | 2021-09-14 | 24360 | keep | 0 | Sep | 2021 | 0.016591 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CAGUAS | 2021-09-14 09:59 | 2021-09-14 12:39 | 10 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMDOR MAL TIEMPO | C21091300008 | Partial_restoration | Bad Weather | Include | Include | Weather | 160 | 2021-09-14 | 1600 | keep | 0 | Sep | 2021 | 0.0010898 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-09-14 09:59 | 2021-09-14 14:04 | 40 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091400011 | Partial_restoration | Bad Weather | Include | Include | Weather | 245 | 2021-09-14 | 9800 | keep | 0 | Sep | 2021 | 0.0066747 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CAGUAS | 2021-09-14 10:00 | 2021-09-14 18:10 | 12 | 008:10 | P | TRANSFORMADOR AVERIADO | REMPLAZO 2 TRANSFORMADORES QUEMADOS 50 KVA X 50 KVA | C21091300220 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 490 | 2021-09-14 | 5880 | keep | 0 | Sep | 2021 | 0.0040048 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BARRANQUITAS | 2021-09-14 10:00 | 2021-09-14 14:30 | 80 | 004:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21091300196 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 270 | 2021-09-14 | 21600 | keep | 0 | Sep | 2021 | 0.014712 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
BAYAMON | 2021-09-14 10:02 | 2021-09-14 14:37 | 6 | 004:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO PEDESTAL | B21091400000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 275 | 2021-09-14 | 1650 | keep | 0 | Sep | 2021 | 0.0011238 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
SAN JUAN | 2021-09-14 10:03 | 2021-09-15 11:01 | 10 | 024:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFORMADOR | S21091400037 | New_Event | Wire Down | Include | Include | Equipment | 1498 | 2021-09-14 | 14980 | keep | 0 | Sep | 2021 | 0.010203 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
UTUADO | 2021-09-14 10:03 | 2021-09-14 12:35 | 1527 | 002:32 | T | OTRAS CAUSAS | SE SECCIONALIZO ALIMENTADOR SE CERRO INTERRUPTOR | A21091400068 | New_Event | Other Causes | Include | Include | Other | 152 | 2021-09-14 | 232104 | keep | 0 | Sep | 2021 | 0.15808 | 0.00104 | Sustained | FALSE | FALSE | TMED_Event | 1527
AGUADILLA | 2021-09-14 10:04 | 2021-09-14 14:29 | 6 | 004:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091400042 | New_Event | Bad Weather | Include | Include | Weather | 265 | 2021-09-14 | 1590 | keep | 0 | Sep | 2021 | 0.0010829 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BAYAMON | 2021-09-14 10:16 | 2021-09-14 18:18 | 50 | 008:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091300055 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 482 | 2021-09-14 | 24100 | keep | 0 | Sep | 2021 | 0.016414 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
BAYAMON | 2021-09-14 10:16 | 2021-09-14 17:48 | 1 | 007:32 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 20 EN SU | S21091200033 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 452 | 2021-09-14 | 452 | keep | 0 | Sep | 2021 | 0.00030786 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-09-14 10:16 | 2021-09-15 16:36 | 60 | 030:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091400224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1820 | 2021-09-14 | 109200 | keep | 0 | Sep | 2021 | 0.074376 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-09-14 10:16 | 2021-09-14 12:24 | 10 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | S21091300031 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-09-14 | 1280 | keep | 0 | Sep | 2021 | 0.0008718 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
AGUADILLA | 2021-09-14 10:28 | 2021-09-14 12:40 | 100 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21091300399 | Partial_restoration | Bad Weather | Include | Include | Weather | 132 | 2021-09-14 | 13200 | keep | 0 | Sep | 2021 | 0.0089905 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 10:28 | 2021-09-14 14:00 | 50 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA | M21091400045 | New_Event |  |  | Include | Wildlife | 212 | 2021-09-14 | 10600 | keep | 0 | Sep | 2021 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-09-14 10:28 | 2021-09-14 14:00 | 100 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400037 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-09-14 | 21200 | keep | 0 | Sep | 2021 | 0.014439 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-09-14 10:28 | 2021-09-14 12:00 | 40 | 001:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091300463 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-09-14 | 3680 | keep | 0 | Sep | 2021 | 0.0025064 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CAGUAS | 2021-09-14 10:29 | 2021-09-14 12:32 | 1 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091300143 | Partial_restoration | Bad Weather | Include | Include | Weather | 123 | 2021-09-14 | 123 | keep | 0 | Sep | 2021 | 8.3775e-05 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-09-14 10:33 | 2021-09-14 11:48 | 200 | 001:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA REEMPLAZARON AISLADORES ROTOS | R21091400212 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2021-09-14 | 15000 | keep | 0 | Sep | 2021 | 0.010216 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
FAJARDO | 2021-09-14 10:37 | 2021-09-14 18:48 | 50 | 008:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO HACIA RISER | R21091400295 | New_Event | Wire Down | Include | Include | Equipment | 491 | 2021-09-14 | 24550 | keep | 0 | Sep | 2021 | 0.016721 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
FAJARDO | 2021-09-14 10:38 | 2021-09-14 10:52 | 40 | 000:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21091400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2021-09-14 | 560 | keep | 0 | Sep | 2021 | 0.00038141 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CAGUAS | 2021-09-14 10:39 | 2021-09-14 13:51 | 2302 | 003:12 | S | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION EN LOCK OUT SE ENCONTRO BUS SUPPORT AVERIADO EL 20-SEPT-21 SE ENTIENDE FUE LA MISMA CAUSA | C21091400011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 192 | 2021-09-14 | 441984 | keep | 0 | Sep | 2021 | 0.30103 | 0.0015679 | Sustained | FALSE | FALSE | TMED_Event | 2302
CAGUAS | 2021-09-14 10:39 | 2021-09-14 13:51 | 1342 | 003:12 | S | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION EN LOCK OUT SE ENCONTRO BUS SUPPORT AVERIADO EL 20-SEPT-21 SE ENTIENDE FUE LA MISMA CAUSA | C21091400011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 192 | 2021-09-14 | 257664 | keep | 0 | Sep | 2021 | 0.17549 | 0.00091403 | Sustained | FALSE | FALSE | TMED_Event | 1342
CAGUAS | 2021-09-14 10:39 | 2021-09-14 13:51 | 34 | 003:12 | S | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION EN LOCK OUT SE ENCONTRO BUS SUPPORT AVERIADO EL 20-SEPT-21 SE ENTIENDE FUE LA MISMA CAUSA | C21091400011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 192 | 2021-09-14 | 6528 | keep | 0 | Sep | 2021 | 0.0044462 | 2.3157e-05 | Sustained | FALSE | FALSE | TMED_Event | 34
CAGUAS | 2021-09-14 10:39 | 2021-09-14 13:51 | 1742 | 003:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION 3015-00 LOCK OUT SE ENCONTRO BUS SUPPORT AVERIADO EL 20-SEPT-21 SE ENTIENDE FUE LA MISMA CAUSA 80% DE LA CARGA POR EL 3015-07 | C21091400011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 192 | 2021-09-14 | 334464 | keep | 0 | Sep | 2021 | 0.2278 | 0.0011865 | Sustained | FALSE | FALSE | TMED_Event | 1742
MAYAGÃœEZ | 2021-09-14 10:39 | 2021-09-14 13:50 | 3 | 003:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 10 KVA X 15 KVA | M21091200069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 191 | 2021-09-14 | 573 | keep | 0 | Sep | 2021 | 0.00039027 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
CAGUAS | 2021-09-14 10:40 | 2021-09-14 11:28 | 10 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE Y LINEA SECUNDARIA | C21091300051 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-09-14 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CAGUAS | 2021-09-14 10:46 | 2021-09-14 15:49 | 10 | 005:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21091300054 | New_Event | Bad Weather | Include | Include | Weather | 303 | 2021-09-14 | 3030 | keep | 0 | Sep | 2021 | 0.0020637 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2021-09-14 10:48 | 2021-09-14 16:55 | 40 | 006:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400046 | New_Event | Bad Weather | Include | Include | Weather | 367 | 2021-09-14 | 14680 | keep | 0 | Sep | 2021 | 0.0099985 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CANOVANAS | 2021-09-14 10:51 | 2021-09-14 17:38 | 9 | 006:47 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21091400082 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 407 | 2021-09-14 | 3663 | keep | 0 | Sep | 2021 | 0.0024949 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
ARECIBO | 2021-09-14 11:03 | 2021-09-14 12:15 | 30 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400052 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2021-09-14 | 2160 | keep | 0 | Sep | 2021 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
FAJARDO | 2021-09-14 11:13 | 2021-09-14 13:24 | 5 | 002:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 8 EN TRANSFORMADOR REPARO BUSHING | R21091400166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2021-09-14 | 655 | keep | 0 | Sep | 2021 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CAGUAS | 2021-09-14 11:20 | 2021-09-14 11:23 | 1725 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO PERSONAL REALIZANDO OPERACIONES | C21091300223 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-09-14 | 5175 | keep | 0 | Sep | 2021 | 0.0035247 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2021-09-14 11:22 | 2021-09-14 11:31 | 6481 | 000:09 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-09-14 | 58329 | keep | 0 | Sep | 2021 | 0.039728 | 0.0044142 | Sustained | FALSE | FALSE | TMED_Event | 6481
CAGUAS | 2021-09-14 11:23 | 2021-09-14 14:10 | 300 | 002:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO AISLADOR | C21091300223 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 167 | 2021-09-14 | 50100 | keep | 0 | Sep | 2021 | 0.034123 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
MAYAGÃœEZ | 2021-09-14 11:31 | 2021-09-14 20:50 | 8 | 009:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400067 | New_Event | Bad Weather | Include | Include | Weather | 559 | 2021-09-14 | 4472 | keep | 0 | Sep | 2021 | 0.0030459 | 5.4488e-06 | Sustained | FALSE | TRUE | TMED_Event | 8
BAYAMON | 2021-09-14 11:33 | 2021-09-14 16:29 | 6 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B21091400042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2021-09-14 | 1776 | keep | 0 | Sep | 2021 | 0.0012096 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
CANOVANAS | 2021-09-14 11:48 | 2021-09-14 11:49 | 1648 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21091400000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-14 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2021-09-14 11:49 | 2021-09-14 19:19 | 200 | 007:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA REEMPLAZARON AISLADORES ROTOS | R21091400212 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 450 | 2021-09-14 | 90000 | keep | 0 | Sep | 2021 | 0.061299 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
BAYAMON | 2021-09-14 11:50 | 2021-09-14 11:52 | 1812 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO Y SE CERRO POR SCADA | B21091400064 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-09-14 | 3624 | keep | 0 | Sep | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | TMED_Event | 1812
BAYAMON | 2021-09-14 11:52 | 2021-09-14 14:24 | 605 | 002:32 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR POR SCADA PARA REMPLAZAR MACHETE Y CERRAR PUENTE A LA SALIDA DE ALIMENTADOR | B21091400064 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 152 | 2021-09-14 | 91960 | keep | 0 | Sep | 2021 | 0.062634 | 0.00041206 | Sustained | FALSE | FALSE | TMED_Event | 605
ARECIBO | 2021-09-14 11:54 | 2021-09-15 13:00 | 40 | 025:06 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21091400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1506 | 2021-09-14 | 60240 | keep | 0 | Sep | 2021 | 0.041029 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
AGUADILLA | 2021-09-14 11:58 | 2021-09-14 15:20 | 80 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400073 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2021-09-14 | 16160 | keep | 0 | Sep | 2021 | 0.011007 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
HUMACAO | 2021-09-14 12:08 | 2021-09-14 13:14 | 1 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091400218 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2021-09-14 | 66 | keep | 0 | Sep | 2021 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
FAJARDO | 2021-09-14 12:09 | 2021-09-14 14:37 | 11 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21091400190 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2021-09-14 | 1628 | keep | 0 | Sep | 2021 | 0.0011088 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
SAN JUAN | 2021-09-14 12:20 | 2021-09-14 12:40 | 6481 | 000:20 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21091400000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-09-14 | 129620 | keep | 0 | Sep | 2021 | 0.088284 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
ARECIBO | 2021-09-14 12:29 | 2021-09-14 12:30 | 2201 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400081 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-14 | 2201 | keep | 0 | Sep | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | TMED_Event | 2201
HUMACAO | 2021-09-14 12:37 | 2021-09-14 12:38 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 12600 | C21091400269 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 2450 | keep | 0 | Sep | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | TRUE | TMED_Event | 2450
HUMACAO | 2021-09-14 12:37 | 2021-09-14 12:38 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 12600 | C21091400269 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 640 | keep | 0 | Sep | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | TRUE | TMED_Event | 640
HUMACAO | 2021-09-14 12:40 | 2021-09-14 12:42 | 2450 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO | C21091400245 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-14 | 4900 | keep | 0 | Sep | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | TMED_Event | 2450
ARECIBO | 2021-09-14 12:42 | 2021-09-14 12:59 | 5 | 000:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PROTAFUSIBLE AVERIADO | A21091400081 | New_Event | Cutout Failure | Include | Include | Equipment | 17 | 2021-09-14 | 85 | keep | 0 | Sep | 2021 | 5.7893e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CAGUAS | 2021-09-14 13:03 | 2021-09-14 15:04 | 40 | 002:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21091400259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-09-14 | 4840 | keep | 0 | Sep | 2021 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
HUMACAO | 2021-09-14 13:05 | 2021-09-14 17:45 | 4 | 004:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21091400262 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 280 | 2021-09-14 | 1120 | keep | 0 | Sep | 2021 | 0.00076283 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
ARECIBO | 2021-09-14 13:05 | 2021-09-14 13:06 | 2201 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400087 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-09-14 | 2201 | keep | 0 | Sep | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | TMED_Event | 2201
SAN JUAN | 2021-09-14 13:07 | 2021-09-14 13:11 | 6481 | 000:04 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21091400000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-14 | 25924 | keep | 0 | Sep | 2021 | 0.017657 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
ARECIBO | 2021-09-14 13:12 | 2021-09-14 13:13 | 2201 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400087 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-09-14 | 2201 | keep | 0 | Sep | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | TMED_Event | 2201
HUMACAO | 2021-09-14 13:13 | 2021-09-14 13:16 | 2450 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO | C21091400270 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 3 | 2021-09-14 | 7350 | keep | 0 | Sep | 2021 | 0.0050061 | 0.0016687 | Momentary | FALSE | FALSE | TMED_Event | 2450
ARECIBO | 2021-09-14 13:15 | 2021-09-14 13:16 | 2201 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400093 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-09-14 | 2201 | keep | 0 | Sep | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | TMED_Event | 2201
ARECIBO | 2021-09-14 13:15 | 2021-09-14 17:13 | 250 | 003:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400095 | New_Event | Bad Weather | Include | Include | Weather | 238 | 2021-09-14 | 59500 | keep | 0 | Sep | 2021 | 0.040525 | 0.00017027 | Sustained | FALSE | TRUE | TMED_Event | 250
HUMACAO | 2021-09-14 13:16 | 2021-09-14 18:45 | 80 | 005:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21091400333 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 329 | 2021-09-14 | 26320 | keep | 0 | Sep | 2021 | 0.017926 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-09-14 13:17 | 2021-09-14 14:56 | 2201 | 001:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA ZAFADA DE AISLADOR SE CERRO INTERRUPTOR | A21091400099 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 99 | 2021-09-14 | 217899 | keep | 0 | Sep | 2021 | 0.14841 | 0.0014991 | Sustained | FALSE | TRUE | TMED_Event | 2201
HUMACAO | 2021-09-14 13:46 | 2021-09-14 18:04 | 30 | 004:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21091400292 | New_Event | Bad Weather | Include | Include | Weather | 258 | 2021-09-14 | 7740 | keep | 0 | Sep | 2021 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-09-14 13:51 | 2021-09-14 18:00 | 1 | 004:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN TRANSFORMADORES CRUCE POR AVE | C21091400007 | New_Event |  |  | Include | Wildlife | 249 | 2021-09-14 | 249 | keep | 0 | Sep | 2021 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2021-09-14 13:51 | 2021-09-14 13:52 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21091400119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 4381 | keep | 0 | Sep | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | TRUE | TMED_Event | 4381
FAJARDO | 2021-09-14 13:52 | 2021-09-14 15:29 | 3003 | 001:37 | T | MAL TIEMPO/RAYOS/WET ASH | CERRADO INTERRUPTOR EN SUBESTACION NO TENIA RTU SUBESTACION | R21091400225 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-09-14 | 291291 | keep | 0 | Sep | 2021 | 0.1984 | 0.0020453 | Sustained | FALSE | FALSE | TMED_Event | 3003
BAYAMON | 2021-09-14 13:54 | 2021-09-14 13:55 | 842 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 842 | keep | 0 | Sep | 2021 | 0.00057348 | 0.00057348 | Momentary | FALSE | FALSE | TMED_Event | 842
CANOVANAS | 2021-09-14 13:56 | 2021-09-14 16:00 | 11 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21091400227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-09-14 | 1364 | keep | 0 | Sep | 2021 | 0.00092901 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
MAYAGÃœEZ | 2021-09-14 14:00 | 2021-09-14 14:01 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21091400122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 6285 | keep | 0 | Sep | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | TMED_Event | 6285
MAYAGÃœEZ | 2021-09-14 14:01 | 2021-09-14 19:35 | 50 | 005:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA IGUANA CRUSANDO LINEAS | M21091400045 | Partial_restoration |  |  | Include | Wildlife | 334 | 2021-09-14 | 16700 | keep | 0 | Sep | 2021 | 0.011374 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 14:01 | 2021-09-14 16:00 | 100 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400037 | Partial_restoration | Bad Weather | Include | Include | Weather | 119 | 2021-09-14 | 11900 | keep | 0 | Sep | 2021 | 0.008105 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
PONCE | 2021-09-14 14:05 | 2021-09-14 14:06 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1606 | keep | 0 | Sep | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | TMED_Event | 1606
PONCE | 2021-09-14 14:05 | 2021-09-14 14:19 | 3718 | 000:14 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR. SE VERIFICO CON EL PERSONAL EN EL AREA DE TRABAJO. Y SE LE DIO PRUEBA AL INTERRUPTOR. QUEDO EN SERVICIO | P21091400078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2021-09-14 | 52052 | keep | 0 | Sep | 2021 | 0.035452 | 0.0025323 | Sustained | FALSE | FALSE | TMED_Event | 3718
UTUADO | 2021-09-14 14:15 | 2021-09-14 14:50 | 200 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REPARO PUENTES PRIMARIOS | A21091300022 | Partial_restoration | Wire Down | Include | Include | Equipment | 35 | 2021-09-14 | 7000 | keep | 0 | Sep | 2021 | 0.0047677 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
ARECIBO | 2021-09-14 14:18 | 2021-09-14 16:59 | 100 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400126 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2021-09-14 | 16100 | keep | 0 | Sep | 2021 | 0.010966 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-09-14 14:24 | 2021-09-14 15:53 | 1812 | 001:29 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR POR SCADA PARA REMPLAZAR MACHETE Y CERRAR PUENTE A LA SALIDA DE ALIMENTADOR | B21091400064 | Additional_clients | Switch Failure | Include | Include | Equipment | 89 | 2021-09-14 | 161268 | keep | 0 | Sep | 2021 | 0.10984 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
PONCE | 2021-09-14 14:27 | 2021-09-14 14:28 | 2308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE HIZO 2 OPERACIONES | P21091400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 2308 | keep | 0 | Sep | 2021 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | TMED_Event | 2308
ARECIBO | 2021-09-14 14:30 | 2021-09-14 16:27 | 15 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400131 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-09-14 | 1755 | keep | 0 | Sep | 2021 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
BAYAMON | 2021-09-14 14:34 | 2021-09-14 16:07 | 2861 | 001:33 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA | B21091400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2021-09-14 | 266073 | keep | 0 | Sep | 2021 | 0.18122 | 0.0019486 | Sustained | FALSE | FALSE | TMED_Event | 2861
ARECIBO | 2021-09-14 14:39 | 2021-09-14 14:40 | 67 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400136 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-14 | 67 | keep | 0 | Sep | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | TMED_Event | 67
ARECIBO | 2021-09-14 14:40 | 2021-09-14 18:30 | 60 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400225 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 230 | 2021-09-14 | 13800 | keep | 0 | Sep | 2021 | 0.0093991 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
AGUADILLA | 2021-09-14 14:41 | 2021-09-14 14:42 | 1497 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1497 | keep | 0 | Sep | 2021 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | TMED_Event | 1497
AGUADILLA | 2021-09-14 14:43 | 2021-09-14 14:45 | 1497 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400139 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-14 | 2994 | keep | 0 | Sep | 2021 | 0.0020392 | 0.0010196 | Momentary | FALSE | FALSE | TMED_Event | 1497
UTUADO | 2021-09-14 14:50 | 2021-09-14 14:51 | 934 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21091400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 934 | keep | 0 | Sep | 2021 | 0.00063614 | 0.00063614 | Momentary | FALSE | TRUE | TMED_Event | 934
UTUADO | 2021-09-14 14:50 | 2021-09-14 14:51 | 4 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21091400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 4 | keep | 0 | Sep | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | TRUE | TMED_Event | 4
UTUADO | 2021-09-14 14:50 | 2021-09-14 14:51 | 1479 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21091400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1479 | keep | 0 | Sep | 2021 | 0.0010073 | 0.0010073 | Momentary | FALSE | TRUE | TMED_Event | 1479
UTUADO | 2021-09-14 14:50 | 2021-09-14 14:51 | 1841 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21091400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1841 | keep | 0 | Sep | 2021 | 0.0012539 | 0.0012539 | Momentary | FALSE | TRUE | TMED_Event | 1841
UTUADO | 2021-09-14 14:50 | 2021-09-14 14:51 | 1950 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21091400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1950 | keep | 0 | Sep | 2021 | 0.0013281 | 0.0013281 | Momentary | FALSE | TRUE | TMED_Event | 1950
UTUADO | 2021-09-14 14:51 | 2021-09-14 21:25 | 200 | 006:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REPARO PUENTES PRIMARIOS | A21091300022 | Partial_restoration | Wire Down | Include | Include | Equipment | 394 | 2021-09-14 | 78800 | keep | 0 | Sep | 2021 | 0.05367 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
BARRANQUITAS | 2021-09-14 14:51 | 2021-09-14 16:45 | 229 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2900 NO RTU | C21091400323 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-09-14 | 26106 | keep | 0 | Sep | 2021 | 0.017781 | 0.00015597 | Sustained | FALSE | TRUE | TMED_Event | 229
BARRANQUITAS | 2021-09-14 14:51 | 2021-09-14 16:45 | 1246 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2900 NO RTU | C21091400323 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-09-14 | 142044 | keep | 0 | Sep | 2021 | 0.096746 | 0.00084864 | Sustained | FALSE | TRUE | TMED_Event | 1246
BAYAMON | 2021-09-14 14:53 | 2021-09-14 15:59 | 6 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21091400057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-09-14 | 396 | keep | 0 | Sep | 2021 | 0.00026971 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
VEGA BAJA | 2021-09-14 14:53 | 2021-09-14 18:53 | 59 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21091400089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-09-14 | 14160 | keep | 0 | Sep | 2021 | 0.0096443 | 4.0185e-05 | Sustained | FALSE | TRUE | TMED_Event | 59
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 1405 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 50580 | keep | 0 | Sep | 2021 | 0.03445 | 0.00095694 | Sustained | FALSE | TRUE | TMED_Event | 1405
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 669 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 24084 | keep | 0 | Sep | 2021 | 0.016404 | 0.00045565 | Sustained | FALSE | TRUE | TMED_Event | 669
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 1527 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 54972 | keep | 0 | Sep | 2021 | 0.037441 | 0.00104 | Sustained | FALSE | TRUE | TMED_Event | 1527
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 1054 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 37944 | keep | 0 | Sep | 2021 | 0.025843 | 0.00071787 | Sustained | FALSE | TRUE | TMED_Event | 1054
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 932 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 33552 | keep | 0 | Sep | 2021 | 0.022852 | 0.00063478 | Sustained | FALSE | TRUE | TMED_Event | 932
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 705 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 25380 | keep | 0 | Sep | 2021 | 0.017286 | 0.00048017 | Sustained | FALSE | TRUE | TMED_Event | 705
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 1521 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 54756 | keep | 0 | Sep | 2021 | 0.037294 | 0.0010359 | Sustained | FALSE | TRUE | TMED_Event | 1521
UTUADO | 2021-09-14 14:54 | 2021-09-14 15:30 | 882 | 000:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-09-14 | 31752 | keep | 0 | Sep | 2021 | 0.021626 | 0.00060073 | Sustained | FALSE | TRUE | TMED_Event | 882
HUMACAO | 2021-09-14 14:56 | 2021-09-14 18:33 | 80 | 003:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 40 EN CORTES DE LINEA MAL TIEMPO | C21091400322 | New_Event | Bad Weather | Include | Include | Weather | 217 | 2021-09-14 | 17360 | keep | 0 | Sep | 2021 | 0.011824 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-09-14 14:56 | 2021-09-14 15:47 | 2201 | 000:51 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-09-14 | 112251 | keep | 0 | Sep | 2021 | 0.076454 | 0.0014991 | Sustained | FALSE | TRUE | TMED_Event | 2201
ARECIBO | 2021-09-14 14:56 | 2021-09-14 15:47 | 1986 | 000:51 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-09-14 | 101286 | keep | 0 | Sep | 2021 | 0.068985 | 0.0013527 | Sustained | FALSE | TRUE | TMED_Event | 1986
ARECIBO | 2021-09-14 14:56 | 2021-09-14 15:47 | 199 | 000:51 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-09-14 | 10149 | keep | 0 | Sep | 2021 | 0.0069124 | 0.00013554 | Sustained | FALSE | TRUE | TMED_Event | 199
ARECIBO | 2021-09-14 14:56 | 2021-09-14 15:47 | 24 | 000:51 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-09-14 | 1224 | keep | 0 | Sep | 2021 | 0.00083366 | 1.6346e-05 | Sustained | FALSE | TRUE | TMED_Event | 24
PONCE | 2021-09-14 15:00 | 2021-09-14 19:14 | 100 | 004:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X100 EN CONVERTIDOR. SE LEVANTO LINEA PRIMARIA | P21091400087 | New_Event | Wire Down | Include | Include | Equipment | 254 | 2021-09-14 | 25400 | keep | 0 | Sep | 2021 | 0.0173 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-09-14 15:02 | 2021-09-15 00:13 | 3522 | 009:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 1940622 | keep | 0 | Sep | 2021 | 1.3217 | 0.0023988 | Sustained | FALSE | TRUE | TMED_Event | 3522
MAYAGÃœEZ | 2021-09-14 15:02 | 2021-09-15 00:13 | 1337 | 009:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 736687 | keep | 0 | Sep | 2021 | 0.50175 | 0.00091062 | Sustained | FALSE | TRUE | TMED_Event | 1337
MAYAGÃœEZ | 2021-09-14 15:02 | 2021-09-15 00:13 | 2825 | 009:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 1556575 | keep | 0 | Sep | 2021 | 1.0602 | 0.0019241 | Sustained | FALSE | TRUE | TMED_Event | 2825
MAYAGÃœEZ | 2021-09-14 15:02 | 2021-09-15 00:13 | 1287 | 009:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 709137 | keep | 0 | Sep | 2021 | 0.48299 | 0.00087657 | Sustained | FALSE | TRUE | TMED_Event | 1287
MAYAGÃœEZ | 2021-09-14 15:02 | 2021-09-15 00:13 | 1417 | 009:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 780767 | keep | 0 | Sep | 2021 | 0.53178 | 0.00096511 | Sustained | FALSE | TRUE | TMED_Event | 1417
MAYAGÃœEZ | 2021-09-14 15:02 | 2021-09-15 00:13 | 80 | 009:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 44080 | keep | 0 | Sep | 2021 | 0.030023 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
UTUADO | 2021-09-14 15:02 | 2021-09-15 00:13 | 1633 | 009:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 899783 | keep | 0 | Sep | 2021 | 0.61284 | 0.0011122 | Sustained | FALSE | TRUE | TMED_Event | 1633
UTUADO | 2021-09-14 15:02 | 2021-09-15 00:13 | 1624 | 009:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 551 | 2021-09-14 | 894824 | keep | 0 | Sep | 2021 | 0.60946 | 0.0011061 | Sustained | FALSE | TRUE | TMED_Event | 1624
HUMACAO | 2021-09-14 15:11 | 2021-09-14 19:22 | 50 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091400332 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2021-09-14 | 12550 | keep | 0 | Sep | 2021 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
FAJARDO | 2021-09-14 15:13 | 2021-09-14 17:00 | 1 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE SECUNDARIO EN BANCO DE TRANSFORMADOR | R21091400258 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-09-14 | 107 | keep | 0 | Sep | 2021 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2021-09-14 15:19 | 2021-09-14 15:20 | 1883 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-14 | 1883 | keep | 0 | Sep | 2021 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | TMED_Event | 1883
ARECIBO | 2021-09-14 15:20 | 2021-09-15 10:38 | 100 | 019:18 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21091400217 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1158 | 2021-09-14 | 115800 | keep | 0 | Sep | 2021 | 0.078871 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-09-14 15:20 | 2021-09-14 15:21 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 3431 | keep | 0 | Sep | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | TMED_Event | 3431
FAJARDO | 2021-09-14 15:29 | 2021-09-14 16:02 | 140 | 000:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | R21091400223 | Partial_restoration | Bad Weather | Include | Include | Weather | 33 | 2021-09-14 | 4620 | keep | 0 | Sep | 2021 | 0.0031467 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:30 | 2021-09-14 15:45 | 50 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800122 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2021-09-14 | 750 | keep | 0 | Sep | 2021 | 0.00051082 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-09-14 15:34 | 2021-09-15 10:50 | 50 | 019:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21091400172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1156 | 2021-09-14 | 57800 | keep | 0 | Sep | 2021 | 0.039367 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-09-14 15:37 | 2021-09-14 18:18 | 281 | 002:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 45241 | keep | 0 | Sep | 2021 | 0.030813 | 0.00019139 | Sustained | FALSE | TRUE | TMED_Event | 281
MAYAGÃœEZ | 2021-09-14 15:37 | 2021-09-14 18:18 | 1252 | 002:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 201572 | keep | 0 | Sep | 2021 | 0.13729 | 0.00085273 | Sustained | FALSE | TRUE | TMED_Event | 1252
MAYAGÃœEZ | 2021-09-14 15:37 | 2021-09-14 18:18 | 595 | 002:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 95795 | keep | 0 | Sep | 2021 | 0.065246 | 0.00040525 | Sustained | FALSE | TRUE | TMED_Event | 595
MAYAGÃœEZ | 2021-09-14 15:37 | 2021-09-14 18:18 | 51 | 002:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 8211 | keep | 0 | Sep | 2021 | 0.0055925 | 3.4736e-05 | Sustained | FALSE | TRUE | TMED_Event | 51
MAYAGÃœEZ | 2021-09-14 15:37 | 2021-09-14 18:18 | 721 | 002:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 116081 | keep | 0 | Sep | 2021 | 0.079062 | 0.00049107 | Sustained | FALSE | TRUE | TMED_Event | 721
UTUADO | 2021-09-14 15:37 | 2021-09-14 18:18 | 1382 | 002:41 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 222502 | keep | 0 | Sep | 2021 | 0.15155 | 0.00094127 | Sustained | FALSE | TRUE | TMED_Event | 1382
UTUADO | 2021-09-14 15:37 | 2021-09-14 18:18 | 654 | 002:41 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-09-14 | 105294 | keep | 0 | Sep | 2021 | 0.071715 | 0.00044544 | Sustained | FALSE | TRUE | TMED_Event | 654
PONCE | 2021-09-14 15:40 | 2021-09-14 17:02 | 50 | 001:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1X65 EN CORTE DE LINEA POR MAL TIEMPO | P21091400093 | New_Event | Bad Weather | Include | Include | Weather | 82 | 2021-09-14 | 4100 | keep | 0 | Sep | 2021 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-09-14 15:40 | 2021-09-14 16:09 | 1617 | 000:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-09-14 | 46893 | keep | 0 | Sep | 2021 | 0.031939 | 0.0011013 | Sustained | FALSE | TRUE | TMED_Event | 1617
MAYAGÃœEZ | 2021-09-14 15:40 | 2021-09-14 16:09 | 1017 | 000:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-09-14 | 29493 | keep | 0 | Sep | 2021 | 0.020088 | 0.00069267 | Sustained | FALSE | TRUE | TMED_Event | 1017
MAYAGÃœEZ | 2021-09-14 15:40 | 2021-09-14 16:09 | 828 | 000:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-09-14 | 24012 | keep | 0 | Sep | 2021 | 0.016354 | 0.00056395 | Sustained | FALSE | TRUE | TMED_Event | 828
MAYAGÃœEZ | 2021-09-14 15:40 | 2021-09-14 16:09 | 863 | 000:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-09-14 | 25027 | keep | 0 | Sep | 2021 | 0.017046 | 0.00058779 | Sustained | FALSE | TRUE | TMED_Event | 863
MAYAGÃœEZ | 2021-09-14 15:40 | 2021-09-14 16:09 | 309 | 000:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-09-14 | 8961 | keep | 0 | Sep | 2021 | 0.0061033 | 0.00021046 | Sustained | FALSE | TRUE | TMED_Event | 309
MAYAGÃœEZ | 2021-09-14 15:40 | 2021-09-14 16:09 | 176 | 000:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-09-14 | 5104 | keep | 0 | Sep | 2021 | 0.0034763 | 0.00011987 | Sustained | FALSE | TRUE | TMED_Event | 176
AGUADILLA | 2021-09-14 15:43 | 2021-09-15 10:26 | 78 | 018:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091400179 | New_Event | Bad Weather | Include | Include | Weather | 1123 | 2021-09-14 | 87594 | keep | 0 | Sep | 2021 | 0.05966 | 5.3125e-05 | Sustained | FALSE | FALSE | TMED_Event | 78
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 1405 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 29505 | keep | 0 | Sep | 2021 | 0.020096 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 669 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 14049 | keep | 0 | Sep | 2021 | 0.0095687 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 1527 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 32067 | keep | 0 | Sep | 2021 | 0.021841 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 1054 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 22134 | keep | 0 | Sep | 2021 | 0.015075 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 932 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 19572 | keep | 0 | Sep | 2021 | 0.01333 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 705 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 14805 | keep | 0 | Sep | 2021 | 0.010084 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 1521 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 31941 | keep | 0 | Sep | 2021 | 0.021755 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 15:45 | 2021-09-14 16:06 | 882 | 000:21 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21091400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-09-14 | 18522 | keep | 0 | Sep | 2021 | 0.012615 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
ARECIBO | 2021-09-14 15:47 | 2021-09-14 15:55 | 2201 | 000:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA ZAFADA DE AISLADOR SE CERRO INTERRUPTOR | A21091400099 | Partial_restoration | Wire Down | Include | Include | Equipment | 8 | 2021-09-14 | 17608 | keep | 0 | Sep | 2021 | 0.011993 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
ARECIBO | 2021-09-14 15:52 | 2021-09-14 18:54 | 50 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400189 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2021-09-14 | 9100 | keep | 0 | Sep | 2021 | 0.006198 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-09-14 15:53 | 2021-09-14 17:43 | 55 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091400343 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-09-14 | 6050 | keep | 0 | Sep | 2021 | 0.0041206 | 3.746e-05 | Sustained | FALSE | TRUE | TMED_Event | 55
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 16:33 | 6481 | 000:37 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO COORDINADO POR PERSONAL DE CAMPO | S21091400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 37 | 2021-09-14 | 239797 | keep | 0 | Sep | 2021 | 0.16332 | 0.0044142 | Sustained | FALSE | FALSE | TMED_Event | 6481
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 9 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 9 | keep | 0 | Sep | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | TRUE | TMED_Event | 9
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 6 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 6 | keep | 0 | Sep | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | TRUE | TMED_Event | 6
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | TMED_Event | 1
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | TMED_Event | 1
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 12 | keep | 0 | Sep | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | TRUE | TMED_Event | 12
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 331 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 331 | keep | 0 | Sep | 2021 | 0.00022544 | 0.00022544 | Momentary | FALSE | TRUE | TMED_Event | 331
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 1132 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1132 | keep | 0 | Sep | 2021 | 0.000771 | 0.000771 | Momentary | FALSE | TRUE | TMED_Event | 1132
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 234 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 234 | keep | 0 | Sep | 2021 | 0.00015938 | 0.00015938 | Momentary | FALSE | TRUE | TMED_Event | 234
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | TMED_Event | 2179
SAN JUAN | 2021-09-14 15:56 | 2021-09-14 15:57 | 5062 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | TRUE | TMED_Event | 5062
AGUADILLA | 2021-09-14 15:58 | 2021-09-14 19:19 | 150 | 003:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400189 | New_Event | Bad Weather | Include | Include | Weather | 201 | 2021-09-14 | 30150 | keep | 0 | Sep | 2021 | 0.020535 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
AGUADILLA | 2021-09-14 15:58 | 2021-09-15 14:35 | 40 | 022:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091400189 | New_Event | Bad Weather | Include | Include | Weather | 1357 | 2021-09-14 | 54280 | keep | 0 | Sep | 2021 | 0.03697 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-09-14 16:01 | 2021-09-14 16:02 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-14 | 108 | keep | 0 | Sep | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
MAYAGÃœEZ | 2021-09-14 16:03 | 2021-09-14 16:04 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-09-14 | 108 | keep | 0 | Sep | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
MAYAGÃœEZ | 2021-09-14 16:04 | 2021-09-14 16:05 | 146 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA | M21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 146 | keep | 0 | Sep | 2021 | 9.944e-05 | 9.944e-05 | Momentary | FALSE | FALSE | TMED_Event | 146
MAYAGÃœEZ | 2021-09-14 16:05 | 2021-09-14 16:06 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-09-14 | 108 | keep | 0 | Sep | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
BAYAMON | 2021-09-14 16:06 | 2021-09-14 20:38 | 200 | 004:32 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21091400185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2021-09-14 | 54400 | keep | 0 | Sep | 2021 | 0.037052 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-09-14 16:06 | 2021-09-15 12:18 | 50 | 020:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500176 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1212 | 2021-09-14 | 60600 | keep | 0 | Sep | 2021 | 0.041274 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
AGUADILLA | 2021-09-14 16:06 | 2021-09-14 19:19 | 200 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | M21091400198 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-09-14 | 38600 | keep | 0 | Sep | 2021 | 0.02629 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
AGUADILLA | 2021-09-14 16:06 | 2021-09-14 23:06 | 100 | 007:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21091400198 | New_Event | Bad Weather | Include | Include | Weather | 420 | 2021-09-14 | 42000 | keep | 0 | Sep | 2021 | 0.028606 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
UTUADO | 2021-09-14 16:06 | 2021-09-15 14:55 | 50 | 022:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090800122 | Partial_restoration | Bad Weather | Include | Include | Weather | 1369 | 2021-09-14 | 68450 | keep | 0 | Sep | 2021 | 0.046621 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-09-14 16:06 | 2021-09-14 19:40 | 705 | 003:34 | T | DESGANCHE | SE RETIRO BAMBUS SOBRE LINEAS PRIMARIAS Y SE CERRO INTERRUPTOR PORTATIL | A21091400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-09-14 | 150870 | keep | 0 | Sep | 2021 | 0.10276 | 0.00048017 | Sustained | FALSE | TRUE | TMED_Event | 705
UTUADO | 2021-09-14 16:06 | 2021-09-14 19:40 | 1521 | 003:34 | T | DESGANCHE | SE RETIRO BAMBUS SOBRE LINEAS PRIMARIAS Y SE CERRO INTERRUPTOR PORTATIL | A21091400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-09-14 | 325494 | keep | 0 | Sep | 2021 | 0.22169 | 0.0010359 | Sustained | FALSE | TRUE | TMED_Event | 1521
UTUADO | 2021-09-14 16:06 | 2021-09-14 19:40 | 882 | 003:34 | T | DESGANCHE | SE RETIRO BAMBUS SOBRE LINEAS PRIMARIAS Y SE CERRO INTERRUPTOR PORTATIL | A21091400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-09-14 | 188748 | keep | 0 | Sep | 2021 | 0.12856 | 0.00060073 | Sustained | FALSE | TRUE | TMED_Event | 882
MAYAGÃœEZ | 2021-09-14 16:09 | 2021-09-14 17:45 | 150 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21091300090 | Partial_restoration | Wire Down | Include | Include | Equipment | 96 | 2021-09-14 | 14400 | keep | 0 | Sep | 2021 | 0.0098078 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 16:09 | 2021-09-14 19:00 | 50 | 002:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091400203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-09-14 | 8550 | keep | 0 | Sep | 2021 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
AGUADILLA | 2021-09-14 16:10 | 2021-09-14 16:11 | 1497 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1497 | keep | 0 | Sep | 2021 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | TMED_Event | 1497
ARECIBO | 2021-09-14 16:12 | 2021-09-14 18:30 | 60 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400210 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-09-14 | 8280 | keep | 0 | Sep | 2021 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-09-14 16:13 | 2021-09-15 12:50 | 40 | 020:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21091400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1237 | 2021-09-14 | 49480 | keep | 0 | Sep | 2021 | 0.033701 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
AGUADILLA | 2021-09-14 16:13 | 2021-09-14 16:14 | 1497 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1497 | keep | 0 | Sep | 2021 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | TMED_Event | 1497
PONCE | 2021-09-14 16:15 | 2021-09-14 18:00 | 100 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 2X80 EN CORTE DE LINEA POR MAL TIEMPO | P21091400102 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2021-09-14 | 10500 | keep | 0 | Sep | 2021 | 0.0071515 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
YAUCO | 2021-09-14 16:17 | 2021-09-14 19:08 | 100 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA Y 1X10 EN TRANSFORMADOR POR MAL TIEMPO | P21091400104 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2021-09-14 | 17100 | keep | 0 | Sep | 2021 | 0.011647 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-09-14 16:17 | 2021-09-15 13:00 | 50 | 020:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091400213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1243 | 2021-09-14 | 62150 | keep | 0 | Sep | 2021 | 0.04233 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-09-14 16:18 | 2021-09-14 20:10 | 5 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21091400215 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2021-09-14 | 1160 | keep | 0 | Sep | 2021 | 0.00079007 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
ARECIBO | 2021-09-14 16:21 | 2021-09-16 10:07 | 30 | 041:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400221 | New_Event | Bad Weather | Include | Include | Weather | 2506 | 2021-09-14 | 75180 | keep | 0 | Sep | 2021 | 0.051205 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
ARECIBO | 2021-09-14 16:21 | 2021-09-16 12:50 | 10 | 044:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50 KVA | A21091400221 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2669 | 2021-09-14 | 26690 | keep | 0 | Sep | 2021 | 0.018178 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2021-09-14 16:21 | 2021-09-14 22:37 | 50 | 006:16 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | A21091400220 | New_Event | Bad Weather | Include | Include | Weather | 376 | 2021-09-14 | 18800 | keep | 0 | Sep | 2021 | 0.012805 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-09-14 16:22 | 2021-09-15 21:05 | 25 | 028:43 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU-2 SE REPARO AVERIA DEL SU-2 AL T-343 | B21091400124 | New_Event | UG Cable Fault | Include | Include | Equipment | 1723 | 2021-09-14 | 43075 | keep | 0 | Sep | 2021 | 0.029338 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
MAYAGÃœEZ | 2021-09-14 16:28 | 2021-09-14 16:29 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | TMED_Event | 179
MAYAGÃœEZ | 2021-09-14 16:28 | 2021-09-14 16:29 | 179 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-14 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | TMED_Event | 179
ARECIBO | 2021-09-14 16:28 | 2021-09-15 10:47 | 5 | 018:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091400227 | New_Event | Bad Weather | Include | Include | Weather | 1099 | 2021-09-14 | 5495 | keep | 0 | Sep | 2021 | 0.0037426 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
MAYAGÃœEZ | 2021-09-14 16:29 | 2021-09-15 23:24 | 75 | 030:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21091400378 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1855 | 2021-09-14 | 139125 | keep | 0 | Sep | 2021 | 0.094757 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
ARECIBO | 2021-09-14 16:35 | 2021-09-15 13:20 | 40 | 020:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091400231 | New_Event | Bad Weather | Include | Include | Weather | 1245 | 2021-09-14 | 49800 | keep | 0 | Sep | 2021 | 0.033919 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-09-14 16:42 | 2021-09-14 17:45 | 1 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | M21091400241 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-09-14 | 63 | keep | 0 | Sep | 2021 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
BARRANQUITAS | 2021-09-14 16:45 | 2021-09-14 20:31 | 20 | 003:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21091300175 | Partial_restoration | Wire Down | Include | Include | Equipment | 226 | 2021-09-14 | 4520 | keep | 0 | Sep | 2021 | 0.0030786 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BARRANQUITAS | 2021-09-14 16:45 | 2021-09-15 13:24 | 30 | 020:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C21091300175 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1239 | 2021-09-14 | 37170 | keep | 0 | Sep | 2021 | 0.025316 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2021-09-14 16:47 | 2021-09-15 14:39 | 25 | 021:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | S21091400264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1312 | 2021-09-14 | 32800 | keep | 0 | Sep | 2021 | 0.02234 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
HUMACAO | 2021-09-14 16:49 | 2021-09-14 20:24 | 30 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21091400365 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-09-14 | 6450 | keep | 0 | Sep | 2021 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
AGUADILLA | 2021-09-14 16:51 | 2021-09-15 17:45 | 60 | 024:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA SE CERRO CORTE DE LINEA | M21091400248 | New_Event | Wire Down | Include | Include | Equipment | 1494 | 2021-09-14 | 89640 | keep | 0 | Sep | 2021 | 0.061053 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-09-14 16:53 | 2021-09-14 20:03 | 80 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400242 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-09-14 | 15200 | keep | 0 | Sep | 2021 | 0.010353 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-09-14 16:53 | 2021-09-15 15:43 | 100 | 022:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21091400243 | New_Event | Wire Down | Include | Include | Equipment | 1370 | 2021-09-14 | 137000 | keep | 0 | Sep | 2021 | 0.09331 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-09-14 16:53 | 2021-09-14 20:00 | 30 | 003:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091400243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-09-14 | 5610 | keep | 0 | Sep | 2021 | 0.0038209 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
ARECIBO | 2021-09-14 16:56 | 2021-09-15 10:03 | 40 | 017:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21091400248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1027 | 2021-09-14 | 41080 | keep | 0 | Sep | 2021 | 0.027979 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-09-14 17:00 | 2021-09-15 14:29 | 30 | 021:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE ELIMINO BAJANTE VACANTE QUE CRUZO LINEA | B21091400133 | New_Event | Wire Down | Include | Include | Equipment | 1289 | 2021-09-14 | 38670 | keep | 0 | Sep | 2021 | 0.026338 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-09-14 17:04 | 2021-09-14 18:46 | 10 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21091400196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-09-14 | 1020 | keep | 0 | Sep | 2021 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 22:55 | 684 | 005:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO N/O EN SU-4 HACIA SU-1 SE DEJO SECCIONALIZADO AISLADOR ROTO Y DEL SU-1 AL RISER | R21091400296 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 348 | 2021-09-14 | 238032 | keep | 0 | Sep | 2021 | 0.16212 | 0.00046587 | Sustained | FALSE | FALSE | TMED_Event | 684
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 9 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 9 | keep | 0 | Sep | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | TRUE | TMED_Event | 9
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 6 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 6 | keep | 0 | Sep | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | TRUE | TMED_Event | 6
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | TMED_Event | 1
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | TMED_Event | 1
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 12 | keep | 0 | Sep | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | TRUE | TMED_Event | 12
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 331 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 331 | keep | 0 | Sep | 2021 | 0.00022544 | 0.00022544 | Momentary | FALSE | TRUE | TMED_Event | 331
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 1132 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1132 | keep | 0 | Sep | 2021 | 0.000771 | 0.000771 | Momentary | FALSE | TRUE | TMED_Event | 1132
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 234 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 234 | keep | 0 | Sep | 2021 | 0.00015938 | 0.00015938 | Momentary | FALSE | TRUE | TMED_Event | 234
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | TMED_Event | 2179
SAN JUAN | 2021-09-14 17:07 | 2021-09-14 17:08 | 5062 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3600 | R21091400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | TRUE | TMED_Event | 5062
UTUADO | 2021-09-14 17:07 | 2021-09-15 12:40 | 80 | 019:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 Y 1 X 65 EN CORTES DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21091400257 | New_Event | Wire Down | Include | Include | Equipment | 1173 | 2021-09-14 | 93840 | keep | 0 | Sep | 2021 | 0.063914 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-09-14 17:10 | 2021-09-14 21:42 | 10 | 004:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400261 | New_Event | Bad Weather | Include | Include | Weather | 272 | 2021-09-14 | 2720 | keep | 0 | Sep | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
CAGUAS | 2021-09-14 17:15 | 2021-09-15 09:47 | 55 | 016:32 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN SU-10 CONSTRUYO PROVISONAL AEREO DE AEREO EXISTENTE @ T-27 | C21091400371 | New_Event | UG Cable Fault | Include | Include | Equipment | 992 | 2021-09-14 | 54560 | keep | 0 | Sep | 2021 | 0.037161 | 3.746e-05 | Sustained | FALSE | FALSE | TMED_Event | 55
ARECIBO | 2021-09-14 17:15 | 2021-09-15 13:00 | 5 | 019:45 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21091400264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1185 | 2021-09-14 | 5925 | keep | 0 | Sep | 2021 | 0.0040355 | 3.4055e-06 | Sustained | FALSE | TRUE | TMED_Event | 5
ARECIBO | 2021-09-14 17:20 | 2021-09-15 09:20 | 20 | 016:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091400271 | New_Event | Bad Weather | Include | Include | Weather | 960 | 2021-09-14 | 19200 | keep | 0 | Sep | 2021 | 0.013077 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
BAYAMON | 2021-09-14 17:22 | 2021-09-14 20:00 | 50 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 30 EN PROVISIONAL | B21091400140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-09-14 | 7900 | keep | 0 | Sep | 2021 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-09-14 17:23 | 2021-09-14 18:31 | 1935 | 001:08 | T | SOBRECARGA | DISPARO DE INTERRUPTOR POR SOBRE CARGA SE ABRIO Y SE SEPARO LA CARGA TRANSFERIDA A ESTE DEL 1707-04 Y SE VOLVIO A CERRAR | B21091400000 | New_Event | Trip Due To Overload | Include | Include | Other | 68 | 2021-09-14 | 131580 | keep | 0 | Sep | 2021 | 0.089619 | 0.0013179 | Sustained | FALSE | FALSE | TMED_Event | 1935
BAYAMON | 2021-09-14 17:23 | 2021-09-14 18:53 | 1501 | 001:30 | T | SOBRECARGA | DISPARO DE INTERRUPTOR POR SOBRE CARGA SE ABRIO Y SE SEPARO LA CARGA TRANSFERIDA DEL 1707-04 Y SE VOLVIO A CERRAR AL 1707-01 Y EL 1707-04 SE DEJO ATRAVES DEL TRANSFORMADOR 1707-00 | B21091400000 | New_Event | Trip Due To Overload | Include | Include | Other | 90 | 2021-09-14 | 135090 | keep | 0 | Sep | 2021 | 0.092009 | 0.0010223 | Sustained | FALSE | FALSE | TMED_Event | 1501
BAYAMON | 2021-09-14 17:23 | 2021-09-14 18:31 | 600 | 001:08 | P | SOBRECARGA | DISPARO DE INTERRUPTOR POR SOBRE CARGA SE ABRIO Y SE SEPARO LA CARGA TRANSFERIDA DEL 1707-04 Y SE VOLVIO A CERRAR AL 1707-01 QUE LLEVA 100AMP DEL 1708-02 | B21091400000 | New_Event | Trip Due To Overload | Include | Include | Other | 68 | 2021-09-14 | 40800 | keep | 0 | Sep | 2021 | 0.027789 | 0.00040866 | Sustained | FALSE | FALSE | TMED_Event | 600
SAN JUAN | 2021-09-14 17:24 | 2021-09-14 21:57 | 109 | 004:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R21091400310 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-09-14 | 29757 | keep | 0 | Sep | 2021 | 0.020267 | 7.4239e-05 | Sustained | FALSE | TRUE | TMED_Event | 109
HUMACAO | 2021-09-14 17:26 | 2021-09-14 20:27 | 8 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091400373 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-09-14 | 1448 | keep | 0 | Sep | 2021 | 0.00098623 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
AGUADILLA | 2021-09-14 17:26 | 2021-09-15 11:40 | 40 | 018:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400278 | New_Event | Bad Weather | Include | Include | Weather | 1094 | 2021-09-14 | 43760 | keep | 0 | Sep | 2021 | 0.029805 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-09-14 17:26 | 2021-09-15 10:02 | 50 | 016:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR ES ROTOS | A21091400290 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 996 | 2021-09-14 | 49800 | keep | 0 | Sep | 2021 | 0.033919 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-09-14 17:27 | 2021-09-14 19:25 | 600 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA MAL TIEMPO | M21091400279 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-09-14 | 70800 | keep | 0 | Sep | 2021 | 0.048222 | 0.00040866 | Sustained | FALSE | TRUE | TMED_Event | 600
MAYAGÃœEZ | 2021-09-14 17:30 | 2021-09-15 12:15 | 15 | 018:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500174 | New_Event | Bad Weather | Include | Include | Weather | 1125 | 2021-09-14 | 16875 | keep | 0 | Sep | 2021 | 0.011493 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
MAYAGÃœEZ | 2021-09-14 17:30 | 2021-09-14 17:31 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-09-14 17:33 | 2021-09-14 17:34 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-09-14 17:36 | 2021-09-14 17:37 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21091400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-09-14 17:39 | 2021-09-14 21:52 | 3147 | 004:13 | T | BREAKER DEFECTUOSO O NO OPERA | SE REMPLAZO FUSIBLE FUNDIDO EN MOTOR DE RECARGA DEL INTERRUPTOR | M21091400000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 253 | 2021-09-14 | 796191 | keep | 0 | Sep | 2021 | 0.54228 | 0.0021434 | Sustained | FALSE | FALSE | TMED_Event | 3147
HUMACAO | 2021-09-14 17:43 | 2021-09-14 17:57 | 1089 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-09-14 | 15246 | keep | 0 | Sep | 2021 | 0.010384 | 0.00074171 | Sustained | FALSE | TRUE | TMED_Event | 1089
HUMACAO | 2021-09-14 17:43 | 2021-09-14 17:57 | 3896 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-09-14 | 54544 | keep | 0 | Sep | 2021 | 0.03715 | 0.0026535 | Sustained | FALSE | TRUE | TMED_Event | 3896
HUMACAO | 2021-09-14 17:43 | 2021-09-14 17:57 | 1467 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-09-14 | 20538 | keep | 0 | Sep | 2021 | 0.013988 | 0.00099917 | Sustained | FALSE | TRUE | TMED_Event | 1467
AGUADILLA | 2021-09-14 17:43 | 2021-09-15 16:00 | 7 | 022:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | M21091400294 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1337 | 2021-09-14 | 9359 | keep | 0 | Sep | 2021 | 0.0063744 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
MAYAGÃœEZ | 2021-09-14 17:45 | 2021-09-14 18:01 | 1097 | 000:16 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 16 | 2021-09-14 | 17552 | keep | 0 | Sep | 2021 | 0.011955 | 0.00074716 | Sustained | FALSE | TRUE | TMED_Event | 1097
MAYAGÃœEZ | 2021-09-14 17:45 | 2021-09-14 18:01 | 3458 | 000:16 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 16 | 2021-09-14 | 55328 | keep | 0 | Sep | 2021 | 0.037684 | 0.0023552 | Sustained | FALSE | TRUE | TMED_Event | 3458
MAYAGÃœEZ | 2021-09-14 17:45 | 2021-09-14 18:01 | 4381 | 000:16 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 16 | 2021-09-14 | 70096 | keep | 0 | Sep | 2021 | 0.047742 | 0.0029839 | Sustained | FALSE | TRUE | TMED_Event | 4381
MAYAGÃœEZ | 2021-09-14 17:45 | 2021-09-14 18:01 | 990 | 000:16 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 16 | 2021-09-14 | 15840 | keep | 0 | Sep | 2021 | 0.010789 | 0.00067428 | Sustained | FALSE | TRUE | TMED_Event | 990
UTUADO | 2021-09-14 17:46 | 2021-09-16 12:25 | 150 | 042:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21091400291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2559 | 2021-09-14 | 383850 | keep | 0 | Sep | 2021 | 0.26144 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CAGUAS | 2021-09-14 17:47 | 2021-09-14 17:48 | 2343 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 2343 | keep | 0 | Sep | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | TMED_Event | 2343
SAN JUAN | 2021-09-14 17:54 | 2021-09-15 14:11 | 50 | 020:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21091300131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1217 | 2021-09-14 | 60850 | keep | 0 | Sep | 2021 | 0.041445 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-09-14 17:57 | 2021-09-14 19:26 | 55 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091400343 | Partial_restoration | Bad Weather | Include | Include | Weather | 89 | 2021-09-14 | 4895 | keep | 0 | Sep | 2021 | 0.003334 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
AGUADILLA | 2021-09-14 17:59 | 2021-09-15 00:09 | 125 | 006:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091400313 | New_Event | Bad Weather | Include | Include | Weather | 370 | 2021-09-14 | 46250 | keep | 0 | Sep | 2021 | 0.031501 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
MAYAGÃœEZ | 2021-09-14 18:01 | 2021-09-14 18:50 | 150 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400316 | Partial_restoration | Bad Weather | Include | Include | Weather | 49 | 2021-09-14 | 7350 | keep | 0 | Sep | 2021 | 0.0050061 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 18:02 | 2021-09-14 21:15 | 1 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | M21091400241 | Partial_restoration | Bad Weather | Include | Include | Weather | 193 | 2021-09-14 | 193 | keep | 0 | Sep | 2021 | 0.00013145 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CAGUAS | 2021-09-14 18:04 | 2021-09-15 16:25 | 89 | 022:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO REEMPLAZARON TRES CAJAS DE CORTE DE LINEA Y SE CERRO MACHETES | C21091400381 | New_Event | Wire Down | Include | Include | Equipment | 1341 | 2021-09-14 | 119349 | keep | 0 | Sep | 2021 | 0.081288 | 6.0617e-05 | Sustained | FALSE | TRUE | TMED_Event | 89
ARECIBO | 2021-09-14 18:06 | 2021-09-15 13:35 | 60 | 019:29 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A21091400303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1169 | 2021-09-14 | 70140 | keep | 0 | Sep | 2021 | 0.047772 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-09-14 18:07 | 2021-09-15 12:10 | 60 | 018:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS Y SE CERRO PUENTE PRIMARIO ABIERTO | A21091400304 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1083 | 2021-09-14 | 64980 | keep | 0 | Sep | 2021 | 0.044258 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CAGUAS | 2021-09-14 18:10 | 2021-09-15 12:51 | 110 | 018:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | C21091400383 | New_Event | Wire Down | Include | Include | Equipment | 1121 | 2021-09-14 | 123310 | keep | 0 | Sep | 2021 | 0.083986 | 7.492e-05 | Sustained | FALSE | TRUE | TMED_Event | 110
ARECIBO | 2021-09-14 18:10 | 2021-09-14 19:50 | 10 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400305 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-09-14 | 1000 | keep | 0 | Sep | 2021 | 0.0006811 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
MAYAGÃœEZ | 2021-09-14 18:16 | 2021-09-15 11:20 | 8 | 017:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091300323 | New_Event | Bad Weather | Include | Include | Weather | 1024 | 2021-09-14 | 8192 | keep | 0 | Sep | 2021 | 0.0055795 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
UTUADO | 2021-09-14 18:18 | 2021-09-15 16:20 | 3 | 022:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091300404 | Partial_restoration | Bad Weather | Include | Include | Weather | 1322 | 2021-09-14 | 3966 | keep | 0 | Sep | 2021 | 0.0027012 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 18:19 | 2021-09-15 13:10 | 60 | 018:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400325 | New_Event | Bad Weather | Include | Include | Weather | 1131 | 2021-09-14 | 67860 | keep | 0 | Sep | 2021 | 0.046219 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-09-14 18:22 | 2021-09-14 22:18 | 30 | 003:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA | A21091400312 | New_Event | Bad Weather | Include | Include | Weather | 236 | 2021-09-14 | 7080 | keep | 0 | Sep | 2021 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-09-14 18:26 | 2021-09-14 20:30 | 20 | 002:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | M21091400332 | New_Event | Service Transformer Failure | Include | Include | Equipment | 124 | 2021-09-14 | 2480 | keep | 0 | Sep | 2021 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2021-09-14 18:36 | 2021-09-15 19:17 | 30 | 024:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | B21091400161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1481 | 2021-09-14 | 44430 | keep | 0 | Sep | 2021 | 0.030261 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
UTUADO | 2021-09-14 18:41 | 2021-09-15 10:22 | 8 | 015:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA | A21091400326 | New_Event | Service Transformer Failure | Include | Include | Equipment | 941 | 2021-09-14 | 7528 | keep | 0 | Sep | 2021 | 0.0051273 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
AGUADILLA | 2021-09-14 18:42 | 2021-09-15 12:00 | 40 | 017:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400278 | New_Event | Bad Weather | Include | Include | Weather | 1038 | 2021-09-14 | 41520 | keep | 0 | Sep | 2021 | 0.028279 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
AGUADILLA | 2021-09-14 18:42 | 2021-09-15 17:20 | 7 | 022:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25 KVA | M21091400345 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1358 | 2021-09-14 | 9506 | keep | 0 | Sep | 2021 | 0.0064745 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
SAN JUAN | 2021-09-14 18:44 | 2021-09-15 18:27 | 180 | 023:43 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | R21091400323 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1423 | 2021-09-14 | 256140 | keep | 0 | Sep | 2021 | 0.17446 | 0.0001226 | Sustained | FALSE | TRUE | TMED_Event | 180
BAYAMON | 2021-09-14 18:46 | 2021-09-16 18:45 | 25 | 047:59 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21091300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2879 | 2021-09-14 | 71975 | keep | 0 | Sep | 2021 | 0.049022 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
BAYAMON | 2021-09-14 18:48 | 2021-09-15 09:54 | 40 | 015:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21091400166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 906 | 2021-09-14 | 36240 | keep | 0 | Sep | 2021 | 0.024683 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-09-14 18:55 | 2021-09-15 17:23 | 600 | 022:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21091400332 | New_Event | Wire Down | Include | Include | Equipment | 1348 | 2021-09-14 | 808800 | keep | 0 | Sep | 2021 | 0.55087 | 0.00040866 | Sustained | FALSE | TRUE | TMED_Event | 600
AGUADILLA | 2021-09-14 18:57 | 2021-09-15 10:00 | 60 | 015:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21091400189 | New_Event | Wire Down | Include | Include | Equipment | 903 | 2021-09-14 | 54180 | keep | 0 | Sep | 2021 | 0.036902 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
HUMACAO | 2021-09-14 18:58 | 2021-09-14 20:28 | 30 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21091400389 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-09-14 | 2700 | keep | 0 | Sep | 2021 | 0.001839 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
ARECIBO | 2021-09-14 19:02 | 2021-09-15 18:55 | 70 | 023:53 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091400333 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1433 | 2021-09-14 | 100310 | keep | 0 | Sep | 2021 | 0.068321 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
ARECIBO | 2021-09-14 19:03 | 2021-09-14 22:00 | 40 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO | A21091400334 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-14 | 7080 | keep | 0 | Sep | 2021 | 0.0048222 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-09-14 19:08 | 2021-09-15 16:55 | 12 | 021:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRES CRUZADOS | M21091400359 | New_Event | Wire Down | Include | Include | Equipment | 1307 | 2021-09-14 | 15684 | keep | 0 | Sep | 2021 | 0.010682 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
BAYAMON | 2021-09-14 19:10 | 2021-09-15 11:19 | 50 | 016:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21091400171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 969 | 2021-09-14 | 48450 | keep | 0 | Sep | 2021 | 0.032999 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-09-14 19:13 | 2021-09-18 16:50 | 5 | 093:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091400335 | New_Event | Bad Weather | Include | Include | Weather | 5617 | 2021-09-14 | 28085 | keep | 0 | Sep | 2021 | 0.019129 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BARRANQUITAS | 2021-09-14 19:14 | 2021-09-14 20:32 | 60 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091400396 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-09-14 | 4680 | keep | 0 | Sep | 2021 | 0.0031875 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BARRANQUITAS | 2021-09-14 19:14 | 2021-09-14 20:33 | 100 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C21091400039 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2021-09-14 | 7900 | keep | 0 | Sep | 2021 | 0.0053807 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-09-14 19:17 | 2021-09-15 09:37 | 30 | 014:20 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO | B21091400173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2021-09-14 | 25800 | keep | 0 | Sep | 2021 | 0.017572 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BAYAMON | 2021-09-14 19:19 | 2021-09-15 12:57 | 200 | 017:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21091400174 | New_Event | Wire Down | Include | Include | Equipment | 1058 | 2021-09-14 | 211600 | keep | 0 | Sep | 2021 | 0.14412 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
ARECIBO | 2021-09-14 19:22 | 2021-09-14 20:30 | 15 | 001:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 Y 2 X 10 EN TRANSFORMADORES DIFERENTES MAL TIEMPO DESCARGAS ELECTRICAS | A21091400337 | New_Event | Bad Weather | Include | Include | Weather | 68 | 2021-09-14 | 1020 | keep | 0 | Sep | 2021 | 0.00069472 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
MAYAGÃœEZ | 2021-09-14 19:23 | 2021-09-14 22:22 | 100 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21091400370 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-09-14 | 17900 | keep | 0 | Sep | 2021 | 0.012192 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BARRANQUITAS | 2021-09-14 19:24 | 2021-09-15 17:27 | 60 | 022:03 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C21091400399 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1323 | 2021-09-14 | 79380 | keep | 0 | Sep | 2021 | 0.054065 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
UTUADO | 2021-09-14 19:27 | 2021-09-15 12:28 | 30 | 017:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS 1 X 30 EN CORTE DE LINEA SE REALIZO0 DESGANCHE 2 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE 1 X 15 EN TRANSFORMADOR SE REPARO NEUTRAL EN SECUNDARIA | A21091400339 | New_Event | Wire Down | Include | Include | Equipment | 1021 | 2021-09-14 | 30630 | keep | 0 | Sep | 2021 | 0.020862 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
HUMACAO | 2021-09-14 19:29 | 2021-09-15 15:18 | 16 | 019:49 | P | TRANSFORMADOR AVERIADO | REEMPLAZARON DOS TRANSFORMADORES AVERIADOS DE 37.5KVA X 25KVA Y 37.5KVA X 50KVA HC @ GIS UPDATE | C21091400397 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1189 | 2021-09-14 | 19024 | keep | 0 | Sep | 2021 | 0.012957 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
AGUADILLA | 2021-09-14 19:34 | 2021-09-14 21:20 | 10 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21091400376 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-09-14 | 1060 | keep | 0 | Sep | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
UTUADO | 2021-09-14 19:35 | 2021-09-14 21:50 | 80 | 002:15 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REPARO POSTE PARTIDO Y SE LLEVO LINEAS ZAFADAS A SU LUGAR | A21091400339 | New_Event | Defective Pole | Include | Include | Equipment | 135 | 2021-09-14 | 10800 | keep | 0 | Sep | 2021 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
YAUCO | 2021-09-14 19:49 | 2021-09-15 10:23 | 100 | 014:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21091400155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 874 | 2021-09-14 | 87400 | keep | 0 | Sep | 2021 | 0.059528 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-09-14 19:52 | 2021-09-15 14:28 | 15 | 018:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21091300035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1116 | 2021-09-14 | 16740 | keep | 0 | Sep | 2021 | 0.011402 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
MAYAGÃœEZ | 2021-09-14 19:58 | 2021-09-15 18:00 | 40 | 022:02 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40 EN RISER DESCARGAS ELECTRICAS | M21091400381 | New_Event | Bad Weather | Include | Include | Weather | 1322 | 2021-09-14 | 52880 | keep | 0 | Sep | 2021 | 0.036016 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
HUMACAO | 2021-09-14 20:09 | 2021-09-15 12:59 | 170 | 016:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTES DE LINEA SE LEVANTARON CONDUCTORES DEL SUELO | C21091400413 | New_Event | Wire Down | Include | Include | Equipment | 1010 | 2021-09-14 | 171700 | keep | 0 | Sep | 2021 | 0.11694 | 0.00011579 | Sustained | FALSE | TRUE | TMED_Event | 170
AGUADILLA | 2021-09-14 20:10 | 2021-09-15 13:40 | 50 | 017:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400383 | New_Event | Bad Weather | Include | Include | Weather | 1050 | 2021-09-14 | 52500 | keep | 0 | Sep | 2021 | 0.035758 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-09-14 20:10 | 2021-09-14 21:35 | 15 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091400347 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-09-14 | 1275 | keep | 0 | Sep | 2021 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
CANOVANAS | 2021-09-14 20:13 | 2021-09-14 22:11 | 4 | 001:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y TOMA | R21091400334 | New_Event | Secondary Wire Down | Include | Include | Equipment | 118 | 2021-09-14 | 472 | keep | 0 | Sep | 2021 | 0.00032148 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
MAYAGÃœEZ | 2021-09-14 20:14 | 2021-09-15 16:18 | 40 | 020:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400216 | New_Event | Bad Weather | Include | Include | Weather | 1204 | 2021-09-14 | 48160 | keep | 0 | Sep | 2021 | 0.032802 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
AGUADILLA | 2021-09-14 20:14 | 2021-09-15 11:34 | 150 | 015:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400189 | New_Event | Bad Weather | Include | Include | Weather | 920 | 2021-09-14 | 138000 | keep | 0 | Sep | 2021 | 0.093991 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
AGUADILLA | 2021-09-14 20:14 | 2021-09-14 22:55 | 200 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | M21091400198 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2021-09-14 | 32200 | keep | 0 | Sep | 2021 | 0.021931 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-09-14 20:16 | 2021-09-14 20:51 | 8 | 000:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091400387 | New_Event | Bad Weather | Include | Include | Weather | 35 | 2021-09-14 | 280 | keep | 0 | Sep | 2021 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
UTUADO | 2021-09-14 20:23 | 2021-09-15 09:09 | 7 | 012:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091400348 | New_Event | Bad Weather | Include | Include | Weather | 766 | 2021-09-14 | 5362 | keep | 0 | Sep | 2021 | 0.003652 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
SAN JUAN | 2021-09-14 20:24 | 2021-09-15 13:24 | 100 | 017:00 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21091400240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1020 | 2021-09-14 | 102000 | keep | 0 | Sep | 2021 | 0.069472 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-09-14 20:24 | 2021-09-14 20:26 | 315 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21091400416 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-14 | 630 | keep | 0 | Sep | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | TMED_Event | 315
ARECIBO | 2021-09-14 20:45 | 2021-09-15 18:22 | 3 | 021:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091400349 | New_Event | Bad Weather | Include | Include | Weather | 1297 | 2021-09-14 | 3891 | keep | 0 | Sep | 2021 | 0.0026501 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
ARECIBO | 2021-09-14 20:45 | 2021-09-15 09:56 | 200 | 013:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091400349 | New_Event | Bad Weather | Include | Include | Weather | 791 | 2021-09-14 | 158200 | keep | 0 | Sep | 2021 | 0.10775 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CAGUAS | 2021-09-14 20:47 | 2021-09-15 17:34 | 40 | 020:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA REPARO NEUTRAL PRIMARIO ROTO | C21091400013 | New_Event | Wire Down | Include | Include | Equipment | 1247 | 2021-09-14 | 49880 | keep | 0 | Sep | 2021 | 0.033973 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
YAUCO | 2021-09-14 20:49 | 2021-09-14 22:08 | 1352 | 001:19 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400167 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 79 | 2021-09-14 | 106808 | keep | 0 | Sep | 2021 | 0.072746 | 0.00092084 | Sustained | FALSE | TRUE | TMED_Event | 1352
YAUCO | 2021-09-14 20:49 | 2021-09-14 22:08 | 3973 | 001:19 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400167 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 79 | 2021-09-14 | 313867 | keep | 0 | Sep | 2021 | 0.21377 | 0.002706 | Sustained | FALSE | TRUE | TMED_Event | 3973
YAUCO | 2021-09-14 20:49 | 2021-09-14 22:08 | 2484 | 001:19 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400167 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 79 | 2021-09-14 | 196236 | keep | 0 | Sep | 2021 | 0.13366 | 0.0016918 | Sustained | FALSE | TRUE | TMED_Event | 2484
AGUADILLA | 2021-09-14 20:50 | 2021-09-14 23:17 | 50 | 002:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21091400396 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2021-09-14 | 7350 | keep | 0 | Sep | 2021 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-09-14 20:51 | 2021-09-14 22:54 | 1097 | 002:03 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | Partial_restoration | Load Shed (Contingency) | Include | Include | Power Supply | 123 | 2021-09-14 | 134931 | keep | 0 | Sep | 2021 | 0.091901 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 20:51 | 2021-09-14 22:54 | 3458 | 002:03 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | Partial_restoration | Load Shed (Contingency) | Include | Include | Power Supply | 123 | 2021-09-14 | 425334 | keep | 0 | Sep | 2021 | 0.28969 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 20:51 | 2021-09-14 22:54 | 4381 | 002:03 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | Partial_restoration | Load Shed (Contingency) | Include | Include | Power Supply | 123 | 2021-09-14 | 538863 | keep | 0 | Sep | 2021 | 0.36702 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-09-14 20:51 | 2021-09-14 22:54 | 990 | 002:03 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | Partial_restoration | Load Shed (Contingency) | Include | Include | Power Supply | 123 | 2021-09-14 | 121770 | keep | 0 | Sep | 2021 | 0.082937 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
BARRANQUITAS | 2021-09-14 20:51 | 2021-09-15 15:06 | 60 | 018:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091400396 | New_Event | Bad Weather | Include | Include | Weather | 1095 | 2021-09-14 | 65700 | keep | 0 | Sep | 2021 | 0.044748 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BARRANQUITAS | 2021-09-14 20:51 | 2021-09-15 11:22 | 100 | 014:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C21091400039 | New_Event | Bad Weather | Include | Include | Weather | 871 | 2021-09-14 | 87100 | keep | 0 | Sep | 2021 | 0.059323 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-09-14 20:53 | 2021-09-14 22:19 | 528 | 001:26 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 86 | 2021-09-14 | 45408 | keep | 0 | Sep | 2021 | 0.030927 | 0.00035962 | Sustained | FALSE | TRUE | TMED_Event | 528
MAYAGÃœEZ | 2021-09-14 20:53 | 2021-09-14 22:19 | 4664 | 001:26 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 86 | 2021-09-14 | 401104 | keep | 0 | Sep | 2021 | 0.27319 | 0.0031766 | Sustained | FALSE | TRUE | TMED_Event | 4664
MAYAGÃœEZ | 2021-09-14 20:53 | 2021-09-14 22:19 | 1352 | 001:26 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR LINEA 50300 POR DISPARO LINEA 40300 | M21091400000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 86 | 2021-09-14 | 116272 | keep | 0 | Sep | 2021 | 0.079192 | 0.00092084 | Sustained | FALSE | TRUE | TMED_Event | 1352
CANOVANAS | 2021-09-14 20:55 | 2021-09-14 20:56 | 1648 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21091400343 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-14 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | TMED_Event | 1648
PONCE | 2021-09-14 20:55 | 2021-09-14 22:20 | 75 | 001:25 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINE 50300 POR DISPARO LINEA 40300 | P210914000XX | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 85 | 2021-09-14 | 6375 | keep | 0 | Sep | 2021 | 0.004342 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
CANOVANAS | 2021-09-14 20:56 | 2021-09-14 23:24 | 230 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100, 1 X 80, 1 X 65 Y 1 X 20 EN CORTES DE LINEA MAL TIEMPO | R21091400344 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 148 | 2021-09-14 | 34040 | keep | 0 | Sep | 2021 | 0.023184 | 0.00015665 | Sustained | FALSE | TRUE | TMED_Event | 230
PONCE | 2021-09-14 20:56 | 2021-09-14 23:19 | 120 | 002:23 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400172 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 143 | 2021-09-14 | 17160 | keep | 0 | Sep | 2021 | 0.011688 | 8.1731e-05 | Sustained | FALSE | TRUE | TMED_Event | 120
PONCE | 2021-09-14 20:56 | 2021-09-14 23:19 | 2446 | 002:23 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400172 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 143 | 2021-09-14 | 349778 | keep | 0 | Sep | 2021 | 0.23823 | 0.001666 | Sustained | FALSE | TRUE | TMED_Event | 2446
PONCE | 2021-09-14 20:56 | 2021-09-14 23:19 | 752 | 002:23 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400172 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 143 | 2021-09-14 | 107536 | keep | 0 | Sep | 2021 | 0.073242 | 0.00051218 | Sustained | FALSE | TRUE | TMED_Event | 752
PONCE | 2021-09-14 20:56 | 2021-09-14 23:19 | 2696 | 002:23 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 SU CARGA ATRAVES DEL 5011-04 | P21091400172 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 143 | 2021-09-14 | 385528 | keep | 0 | Sep | 2021 | 0.26258 | 0.0018362 | Sustained | FALSE | TRUE | TMED_Event | 2696
PONCE | 2021-09-14 20:58 | 2021-09-14 23:48 | 595 | 002:50 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400175 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 170 | 2021-09-14 | 101150 | keep | 0 | Sep | 2021 | 0.068893 | 0.00040525 | Sustained | FALSE | TRUE | TMED_Event | 595
PONCE | 2021-09-14 20:58 | 2021-09-14 23:48 | 1007 | 002:50 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400175 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 170 | 2021-09-14 | 171190 | keep | 0 | Sep | 2021 | 0.1166 | 0.00068586 | Sustained | FALSE | TRUE | TMED_Event | 1007
PONCE | 2021-09-14 20:58 | 2021-09-14 23:48 | 9 | 002:50 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400175 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 170 | 2021-09-14 | 1530 | keep | 0 | Sep | 2021 | 0.0010421 | 6.1299e-06 | Sustained | FALSE | TRUE | TMED_Event | 9
PONCE | 2021-09-14 21:00 | 2021-09-14 23:21 | 2379 | 002:21 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400178 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 141 | 2021-09-14 | 335439 | keep | 0 | Sep | 2021 | 0.22847 | 0.0016203 | Sustained | FALSE | TRUE | TMED_Event | 2379
PONCE | 2021-09-14 21:04 | 2021-09-14 23:22 | 3744 | 002:18 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA LINEA 50300 POR DISPARO LINEA 40300 | P21091400182 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 138 | 2021-09-14 | 516672 | keep | 0 | Sep | 2021 | 0.3519 | 0.00255 | Sustained | FALSE | TRUE | TMED_Event | 3744
ARECIBO | 2021-09-14 21:15 | 2021-09-14 21:16 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091400352 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1494 | keep | 0 | Sep | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | TMED_Event | 1494
SAN JUAN | 2021-09-14 21:22 | 2021-09-14 21:23 | 844 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 844 | keep | 0 | Sep | 2021 | 0.00057484 | 0.00057484 | Momentary | FALSE | FALSE | TMED_Event | 844
BAYAMON | 2021-09-14 21:27 | 2021-09-15 18:18 | 30 | 020:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091400198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1251 | 2021-09-14 | 37530 | keep | 0 | Sep | 2021 | 0.025562 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-09-14 21:30 | 2021-09-15 11:45 | 35 | 014:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091300138 | New_Event | Bad Weather | Include | Include | Weather | 855 | 2021-09-14 | 29925 | keep | 0 | Sep | 2021 | 0.020382 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
MAYAGÃœEZ | 2021-09-14 21:35 | 2021-09-15 17:00 | 25 | 019:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 15 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21091400416 | New_Event | Wire Down | Include | Include | Equipment | 1165 | 2021-09-14 | 29125 | keep | 0 | Sep | 2021 | 0.019837 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
BAYAMON | 2021-09-14 21:44 | 2021-09-15 20:02 | 50 | 022:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091400254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1338 | 2021-09-14 | 66900 | keep | 0 | Sep | 2021 | 0.045565 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-09-14 21:45 | 2021-09-14 21:46 | 1533 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE LLEVA EL 1709-05 | S21091400000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-14 | 1533 | keep | 0 | Sep | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | TMED_Event | 1533
BAYAMON | 2021-09-14 21:45 | 2021-09-14 21:46 | 2364 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE CARGA POR EL 1709-03 | S21091400000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-14 | 2364 | keep | 0 | Sep | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | TMED_Event | 2364
BAYAMON | 2021-09-14 21:46 | 2021-09-15 17:54 | 200 | 020:08 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO MACHETE AVERIADO EN SU-1 | S21091400258 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1208 | 2021-09-14 | 241600 | keep | 0 | Sep | 2021 | 0.16455 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
SAN JUAN | 2021-09-14 22:07 | 2021-09-15 14:06 | 8 | 015:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TOMA Y REEMPLAZARON SECUNDARIA AVERIADA | R21091400348 | New_Event | Secondary Wire Down | Include | Include | Equipment | 959 | 2021-09-14 | 7672 | keep | 0 | Sep | 2021 | 0.0052254 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2021-09-14 22:17 | 2021-09-16 14:30 | 8 | 040:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091400067 | Partial_restoration | Bad Weather | Include | Include | Weather | 2413 | 2021-09-14 | 19304 | keep | 0 | Sep | 2021 | 0.013148 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
YAUCO | 2021-09-14 22:39 | 2021-09-15 11:45 | 75 | 013:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 54 EN CORTE DE LINEA MAL TIEMPO | P21091400204 | New_Event | Bad Weather | Include | Include | Weather | 786 | 2021-09-14 | 58950 | keep | 0 | Sep | 2021 | 0.040151 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
MAYAGÃœEZ | 2021-09-14 22:54 | 2021-09-16 16:15 | 8 | 041:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091400387 | Partial_restoration | Bad Weather | Include | Include | Weather | 2481 | 2021-09-14 | 19848 | keep | 0 | Sep | 2021 | 0.013518 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
VEGA BAJA | 2021-09-14 22:55 | 2021-09-15 21:22 | 35 | 022:27 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21091400206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1347 | 2021-09-14 | 47145 | keep | 0 | Sep | 2021 | 0.03211 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
HUMACAO | 2021-09-14 23:51 | 2021-09-14 23:52 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21091400434 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | TMED_Event | 1827
FAJARDO | 2021-09-14 23:52 | 2021-09-14 23:53 | 1394 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 16500 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 1394 | keep | 0 | Sep | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | TRUE | TMED_Event | 1394
FAJARDO | 2021-09-14 23:52 | 2021-09-14 23:53 | 412 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 16500 | R21091400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-14 | 412 | keep | 0 | Sep | 2021 | 0.00028061 | 0.00028061 | Momentary | FALSE | TRUE | TMED_Event | 412
HUMACAO | 2021-09-14 23:56 | 2021-09-14 23:57 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21091400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-14 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | TMED_Event | 2354
CANOVANAS | 2021-09-15 00:12 | 2021-09-15 10:03 | 250 | 009:51 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40, 1 X 20, 1 X 50, 1 X 65 Y 1 X 100 EN CORTES DE LINEAS MAL TIEMPO | R21091500004 | New_Event | Bad Weather | Include | Include | Weather | 591 | 2021-09-15 | 147750 | keep | 0 | Sep | 2021 | 0.10063 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-09-15 00:14 | 2021-09-15 12:23 | 100 | 012:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE DESGANCHO | R21091500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 729 | 2021-09-15 | 72900 | keep | 0 | Sep | 2021 | 0.049652 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-15 00:37 | 2021-09-15 14:54 | 70 | 014:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21091500009 | New_Event | Bad Weather | Include | Include | Weather | 857 | 2021-09-15 | 59990 | keep | 0 | Sep | 2021 | 0.040859 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-09-15 00:42 | 2021-09-15 09:45 | 190 | 009:03 | P | DESGANCHE | 2 X 40 Y 2 X 50 EN CORTES DE LINEA SE REALIZO DESGANCHE CRITICO | R21091500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2021-09-15 | 103170 | keep | 0 | Sep | 2021 | 0.070269 | 0.00012941 | Sustained | FALSE | TRUE | Not_TMED_Event | 190
MAYAGÃœEZ | 2021-09-15 01:01 | 2021-09-15 12:15 | 60 | 011:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500005 | New_Event | Bad Weather | Include | Include | Weather | 674 | 2021-09-15 | 40440 | keep | 0 | Sep | 2021 | 0.027543 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-15 02:41 | 2021-09-15 15:18 | 20 | 012:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | C21091500003 | New_Event | Bad Weather | Include | Include | Weather | 757 | 2021-09-15 | 15140 | keep | 0 | Sep | 2021 | 0.010312 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-09-15 02:55 | 2021-09-16 12:49 | 6 | 033:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO | C21091500001 | New_Event | Cutout Failure | Include | Include | Equipment | 2034 | 2021-09-15 | 12204 | keep | 0 | Sep | 2021 | 0.0083121 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-09-15 03:25 | 2021-09-15 03:26 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21091500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 2126 | keep | 0 | Sep | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2021-09-15 03:46 | 2021-09-15 11:40 | 120 | 007:54 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500012 | New_Event | Bad Weather | Include | Include | Weather | 474 | 2021-09-15 | 56880 | keep | 0 | Sep | 2021 | 0.038741 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-15 04:00 | 2021-09-15 13:35 | 60 | 009:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21091500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 575 | 2021-09-15 | 34500 | keep | 0 | Sep | 2021 | 0.023498 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-09-15 04:11 | 2021-09-15 04:12 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210915000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
GUAYAMA | 2021-09-15 04:22 | 2021-09-15 09:48 | 50 | 005:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P21091500002 | New_Event | Bad Weather | Include | Include | Weather | 326 | 2021-09-15 | 16300 | keep | 0 | Sep | 2021 | 0.011102 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-15 04:26 | 2021-09-15 14:41 | 120 | 010:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE LEVANTO PRIMARIA | B21091500008 | New_Event | Wire Down | Include | Include | Equipment | 615 | 2021-09-15 | 73800 | keep | 0 | Sep | 2021 | 0.050265 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-15 04:29 | 2021-09-15 16:42 | 100 | 012:13 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | S21091500005 | New_Event | Switch Failure | Include | Include | Equipment | 733 | 2021-09-15 | 73300 | keep | 0 | Sep | 2021 | 0.049924 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-09-15 05:07 | 2021-09-15 12:00 | 100 | 006:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEAS MAL TIEMPO | P21091500004 | New_Event | Bad Weather | Include | Include | Weather | 413 | 2021-09-15 | 41300 | keep | 0 | Sep | 2021 | 0.028129 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-09-15 05:16 | 2021-09-15 14:55 | 100 | 009:39 | P | PARARRAYOS DEFECTUOSO | 2X65 EN CORTE DE LINEA POR PARARRAYO QUEMADO. SE ELIMINO YA QUE MONTURA ESTABA FUERA DE SERVICIO | P21091500005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 579 | 2021-09-15 | 57900 | keep | 0 | Sep | 2021 | 0.039435 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-15 05:33 | 2021-09-15 11:49 | 35 | 006:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21091500017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 376 | 2021-09-15 | 13160 | keep | 0 | Sep | 2021 | 0.0089632 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-09-15 05:42 | 2021-09-15 10:30 | 100 | 004:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500020 | New_Event | Bad Weather | Include | Include | Weather | 288 | 2021-09-15 | 28800 | keep | 0 | Sep | 2021 | 0.019616 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-15 05:58 | 2021-09-15 11:19 | 50 | 005:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091400207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-09-15 | 16050 | keep | 0 | Sep | 2021 | 0.010932 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-15 05:58 | 2021-09-15 12:15 | 50 | 006:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE RETEZO PRIMARIA | B21091500014 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2021-09-15 | 18850 | keep | 0 | Sep | 2021 | 0.012839 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-15 06:05 | 2021-09-15 18:50 | 90 | 012:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE HACIA CAJA PRIMARIA | R21091500026 | New_Event | Wire Down | Include | Include | Equipment | 765 | 2021-09-15 | 68850 | keep | 0 | Sep | 2021 | 0.046893 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
GUAYAMA | 2021-09-15 06:11 | 2021-09-15 12:05 | 50 | 005:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21091500009 | New_Event | Bad Weather | Include | Include | Weather | 354 | 2021-09-15 | 17700 | keep | 0 | Sep | 2021 | 0.012055 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-15 06:58 | 2021-09-15 17:25 | 70 | 010:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CORTES DE LINEAS MAL TIEMPO | C21091500017 | New_Event | Bad Weather | Include | Include | Weather | 627 | 2021-09-15 | 43890 | keep | 0 | Sep | 2021 | 0.029893 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-09-15 07:07 | 2021-09-15 16:05 | 80 | 008:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR | C21091500021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 538 | 2021-09-15 | 43040 | keep | 0 | Sep | 2021 | 0.029314 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-15 07:17 | 2021-09-15 10:22 | 9 | 003:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO UNA CAJA AVERIADA MARCA CHIM DE 100AMP EN EL TRANSFORMADOR CON FID33702762 | A21091500015 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2021-09-15 | 1665 | keep | 0 | Sep | 2021 | 0.001134 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-09-15 07:36 | 2021-09-15 16:29 | 4 | 008:53 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE ROTO Y CERRO PUENTE PRIMARIO | C21091500024 | New_Event | Defective Pole | Include | Include | Equipment | 533 | 2021-09-15 | 2132 | keep | 0 | Sep | 2021 | 0.0014521 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-09-15 07:46 | 2021-09-15 20:00 | 30 | 012:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN RISER DESCARGAS ELECTRICAS | M21091500313 | New_Event | Bad Weather | Include | Include | Weather | 734 | 2021-09-15 | 22020 | keep | 0 | Sep | 2021 | 0.014998 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-09-15 07:50 | 2021-09-15 13:08 | 79 | 005:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21091500027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 318 | 2021-09-15 | 25122 | keep | 0 | Sep | 2021 | 0.01711 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
MAYAGÃœEZ | 2021-09-15 08:00 | 2021-09-15 13:40 | 5 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21091500196 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2021-09-15 | 1700 | keep | 0 | Sep | 2021 | 0.0011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-15 08:12 | 2021-09-15 10:33 | 3 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | C21091500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-09-15 | 423 | keep | 0 | Sep | 2021 | 0.0002881 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2021-09-15 08:13 | 2021-09-15 14:57 | 100 | 006:44 | P | MAL TIEMPO/RAYOS/WET ASH | 2X50 EN CORTE DE LINEA POR MAL TIEMPO | P21091500023 | New_Event | Bad Weather | Include | Include | Weather | 404 | 2021-09-15 | 40400 | keep | 0 | Sep | 2021 | 0.027516 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-09-15 08:25 | 2021-09-16 16:46 | 1 | 032:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y CERRO CORTE DE LINEA | R21091500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1941 | 2021-09-15 | 1941 | keep | 0 | Sep | 2021 | 0.001322 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-15 08:46 | 2021-09-15 15:15 | 60 | 006:29 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500039 | New_Event | Bad Weather | Include | Include | Weather | 389 | 2021-09-15 | 23340 | keep | 0 | Sep | 2021 | 0.015897 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-09-15 08:58 | 2021-09-15 16:50 | 10 | 007:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1X20 EN TRANSFORMADOR POR MAL TIEMPO | P21091500031 | New_Event | Bad Weather | Include | Include | Weather | 472 | 2021-09-15 | 4720 | keep | 0 | Sep | 2021 | 0.0032148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-15 09:02 | 2021-09-15 09:07 | 1394 | 000:05 | S | LINEA DE TRANSMISION 38KV | OPERACIONES LINEA 16500 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-15 | 6970 | keep | 0 | Sep | 2021 | 0.0047472 | 0.00094945 | Momentary | FALSE | TRUE | Not_TMED_Event | 1394
FAJARDO | 2021-09-15 09:02 | 2021-09-15 09:07 | 412 | 000:05 | S | LINEA DE TRANSMISION 38KV | OPERACIONES LINEA 16500 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-15 | 2060 | keep | 0 | Sep | 2021 | 0.0014031 | 0.00028061 | Momentary | FALSE | TRUE | Not_TMED_Event | 412
UTUADO | 2021-09-15 09:05 | 2021-09-16 15:23 | 10 | 030:18 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | A21091500208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1818 | 2021-09-15 | 18180 | keep | 0 | Sep | 2021 | 0.012382 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-09-15 09:06 | 2021-09-15 09:08 | 2286 | 000:02 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 4572 | keep | 0 | Sep | 2021 | 0.003114 | 0.001557 | Momentary | FALSE | TRUE | Not_TMED_Event | 2286
FAJARDO | 2021-09-15 09:06 | 2021-09-15 09:08 | 693 | 000:02 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 1386 | keep | 0 | Sep | 2021 | 0.000944 | 0.000472 | Momentary | FALSE | TRUE | Not_TMED_Event | 693
BAYAMON | 2021-09-15 09:11 | 2021-09-16 22:41 | 8 | 037:30 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR TIPO NX | B21091500145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2250 | 2021-09-15 | 18000 | keep | 0 | Sep | 2021 | 0.01226 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-09-15 09:11 | 2021-09-15 11:24 | 15 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21091500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-09-15 | 1995 | keep | 0 | Sep | 2021 | 0.0013588 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-15 09:12 | 2021-09-15 10:44 | 3 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIAS | R21091500046 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2021-09-15 | 276 | keep | 0 | Sep | 2021 | 0.00018798 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
HUMACAO | 2021-09-15 09:12 | 2021-09-15 19:30 | 5 | 010:18 | P | DESGANCHE | 2 X 80 Y 2 X 65 EN CORTES DE LINEAS | C21091500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2021-09-15 | 3090 | keep | 0 | Sep | 2021 | 0.0021046 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-09-15 09:12 | 2021-09-15 15:22 | 70 | 006:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA | C21091500045 | New_Event | Wire Down | Include | Include | Equipment | 370 | 2021-09-15 | 25900 | keep | 0 | Sep | 2021 | 0.01764 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2021-09-15 09:12 | 2021-09-15 17:50 | 120 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE SUBIO PRIMARIA Y SE REALIZO DESGANCHE CARGA POR EL 9103-02 | B21091500050 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-09-15 | 62160 | keep | 0 | Sep | 2021 | 0.042337 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-15 09:20 | 2021-09-15 20:36 | 65 | 011:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S21091400033 | New_Event | Wire Down | Include | Include | Equipment | 676 | 2021-09-15 | 43940 | keep | 0 | Sep | 2021 | 0.029927 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-09-15 09:22 | 2021-09-15 18:50 | 30 | 009:28 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 KVA POR IGUAL CAPACIDAD | S21091400035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 568 | 2021-09-15 | 17040 | keep | 0 | Sep | 2021 | 0.011606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-09-15 09:28 | 2021-09-15 10:21 | 10 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | R21091500061 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-09-15 | 530 | keep | 0 | Sep | 2021 | 0.00036098 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-15 09:28 | 2021-09-15 16:00 | 1 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500102 | New_Event | Bad Weather | Include | Include | Weather | 392 | 2021-09-15 | 392 | keep | 0 | Sep | 2021 | 0.00026699 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-09-15 09:29 | 2021-09-15 18:12 | 80 | 008:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21091500058 | New_Event |  |  | Include | Wildlife | 523 | 2021-09-15 | 41840 | keep | 0 | Sep | 2021 | 0.028497 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
FAJARDO | 2021-09-15 09:36 | 2021-09-15 09:37 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-15 | 1839 | keep | 0 | Sep | 2021 | 0.0012525 | 0.0012525 | Momentary | FALSE | TRUE | Not_TMED_Event | 1839
FAJARDO | 2021-09-15 09:36 | 2021-09-15 09:37 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-15 | 1778 | keep | 0 | Sep | 2021 | 0.001211 | 0.001211 | Momentary | FALSE | TRUE | Not_TMED_Event | 1778
FAJARDO | 2021-09-15 09:36 | 2021-09-15 09:37 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-15 | 1376 | keep | 0 | Sep | 2021 | 0.00093719 | 0.00093719 | Momentary | FALSE | TRUE | Not_TMED_Event | 1376
FAJARDO | 2021-09-15 09:36 | 2021-09-15 09:37 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-15 | 293 | keep | 0 | Sep | 2021 | 0.00019956 | 0.00019956 | Momentary | FALSE | TRUE | Not_TMED_Event | 293
FAJARDO | 2021-09-15 09:36 | 2021-09-15 09:37 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-15 | 1215 | keep | 0 | Sep | 2021 | 0.00082753 | 0.00082753 | Momentary | FALSE | TRUE | Not_TMED_Event | 1215
BARRANQUITAS | 2021-09-15 09:50 | 2021-09-16 21:32 | 10 | 035:42 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | C21091500062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2142 | 2021-09-15 | 21420 | keep | 0 | Sep | 2021 | 0.014589 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-15 09:54 | 2021-09-15 19:16 | 40 | 009:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500108 | New_Event | Bad Weather | Include | Include | Weather | 562 | 2021-09-15 | 22480 | keep | 0 | Sep | 2021 | 0.015311 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-15 09:55 | 2021-09-16 10:35 | 30 | 024:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | M21091500112 | New_Event | Bad Weather | Include | Include | Weather | 1480 | 2021-09-15 | 44400 | keep | 0 | Sep | 2021 | 0.030241 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-15 09:57 | 2021-09-15 22:01 | 10 | 012:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR RAYO | S21091500034 | New_Event | Bad Weather | Include | Include | Weather | 724 | 2021-09-15 | 7240 | keep | 0 | Sep | 2021 | 0.0049311 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-15 09:59 | 2021-09-15 10:00 | 693 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21091500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-15 | 693 | keep | 0 | Sep | 2021 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
ARECIBO | 2021-09-15 09:59 | 2021-09-15 12:34 | 3 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091500078 | Partial_restoration | Bad Weather | Include | Include | Weather | 155 | 2021-09-15 | 465 | keep | 0 | Sep | 2021 | 0.00031671 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-09-15 10:00 | 2021-09-15 15:23 | 70 | 005:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R21091500089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 323 | 2021-09-15 | 22610 | keep | 0 | Sep | 2021 | 0.0154 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-09-15 10:00 | 2021-09-16 13:45 | 30 | 027:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600047 | New_Event | Bad Weather | Include | Include | Weather | 1665 | 2021-09-15 | 49950 | keep | 0 | Sep | 2021 | 0.034021 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-15 10:03 | 2021-09-15 10:09 | 2106 | 000:06 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE VERIFICO PERSONAL FUERA | R21091500000 | Additional_clients | Bad Weather | Include | Include | Weather | 6 | 2021-09-15 | 12636 | keep | 0 | Sep | 2021 | 0.0086063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-15 10:04 | 2021-09-15 10:35 | 25 | 000:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500011 | New_Event | Bad Weather | Include | Include | Weather | 31 | 2021-09-15 | 775 | keep | 0 | Sep | 2021 | 0.00052785 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-09-15 10:06 | 2021-09-15 11:00 | 1 | 000:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R21091500068 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2021-09-15 | 54 | keep | 0 | Sep | 2021 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-15 10:08 | 2021-09-15 11:45 | 30 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500117 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-09-15 | 2910 | keep | 0 | Sep | 2021 | 0.001982 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-15 10:09 | 2021-09-15 12:31 | 250 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40, 1 X 20, 1 X 50, 1 X 65 Y 1 X 100 EN CORTES DE LINEAS MAL TIEMPO | R21091500004 | Partial_restoration | Bad Weather | Include | Include | Weather | 142 | 2021-09-15 | 35500 | keep | 0 | Sep | 2021 | 0.024179 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-15 10:14 | 2021-09-16 19:00 | 50 | 032:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500086 | New_Event | Bad Weather | Include | Include | Weather | 1966 | 2021-09-15 | 98300 | keep | 0 | Sep | 2021 | 0.066952 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-15 10:16 | 2021-09-15 10:17 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 58 | keep | 0 | Sep | 2021 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
MAYAGÃœEZ | 2021-09-15 10:17 | 2021-09-15 14:05 | 1 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091500120 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2021-09-15 | 228 | keep | 0 | Sep | 2021 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-15 10:18 | 2021-09-15 15:11 | 60 | 004:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091500068 | New_Event | Bad Weather | Include | Include | Weather | 293 | 2021-09-15 | 17580 | keep | 0 | Sep | 2021 | 0.011974 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-09-15 10:19 | 2021-09-15 10:21 | 1394 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 2788 | keep | 0 | Sep | 2021 | 0.0018989 | 0.00094945 | Momentary | FALSE | TRUE | Not_TMED_Event | 1394
FAJARDO | 2021-09-15 10:19 | 2021-09-15 10:21 | 412 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 824 | keep | 0 | Sep | 2021 | 0.00056122 | 0.00028061 | Momentary | FALSE | TRUE | Not_TMED_Event | 412
HUMACAO | 2021-09-15 10:20 | 2021-09-15 16:21 | 70 | 006:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091500069 | New_Event | Bad Weather | Include | Include | Weather | 361 | 2021-09-15 | 25270 | keep | 0 | Sep | 2021 | 0.017211 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-15 10:20 | 2021-09-15 15:20 | 5 | 005:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21091500122 | New_Event | Bad Weather | Include | Include | Weather | 300 | 2021-09-15 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-09-15 10:20 | 2021-09-15 14:00 | 25 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500123 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2021-09-15 | 5500 | keep | 0 | Sep | 2021 | 0.003746 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-15 10:20 | 2021-09-15 15:45 | 36 | 005:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2021-09-15 | 11700 | keep | 0 | Sep | 2021 | 0.0079688 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
FAJARDO | 2021-09-15 10:21 | 2021-09-15 10:22 | 1234 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21091500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-15 | 1234 | keep | 0 | Sep | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-09-15 10:21 | 2021-09-15 10:23 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 4686 | keep | 0 | Sep | 2021 | 0.0031916 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
FAJARDO | 2021-09-15 10:21 | 2021-09-15 10:23 | 1830 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 3660 | keep | 0 | Sep | 2021 | 0.0024928 | 0.0012464 | Momentary | FALSE | TRUE | Not_TMED_Event | 1830
FAJARDO | 2021-09-15 10:21 | 2021-09-15 10:23 | 710 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00048358 | Momentary | FALSE | TRUE | Not_TMED_Event | 710
FAJARDO | 2021-09-15 10:21 | 2021-09-15 10:23 | 969 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 1938 | keep | 0 | Sep | 2021 | 0.00132 | 0.00065998 | Momentary | FALSE | TRUE | Not_TMED_Event | 969
FAJARDO | 2021-09-15 10:22 | 2021-09-15 19:35 | 10 | 009:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | R21091500061 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 553 | 2021-09-15 | 5530 | keep | 0 | Sep | 2021 | 0.0037665 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-09-15 10:24 | 2021-09-15 15:41 | 1 | 005:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | R21091500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 317 | 2021-09-15 | 317 | keep | 0 | Sep | 2021 | 0.00021591 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-15 10:24 | 2021-09-15 16:20 | 15 | 005:56 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA TRANSFORMADOR QUEMADO EN LA LINEA | A21091500089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 356 | 2021-09-15 | 5340 | keep | 0 | Sep | 2021 | 0.003637 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-09-15 10:31 | 2021-09-15 15:40 | 60 | 005:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091500071 | New_Event | Bad Weather | Include | Include | Weather | 309 | 2021-09-15 | 18540 | keep | 0 | Sep | 2021 | 0.012628 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-15 10:36 | 2021-09-15 12:44 | 870 | 002:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | C21091500072 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-09-15 | 111360 | keep | 0 | Sep | 2021 | 0.075847 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-09-15 10:38 | 2021-09-15 16:20 | 30 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500135 | New_Event | Bad Weather | Include | Include | Weather | 342 | 2021-09-15 | 10260 | keep | 0 | Sep | 2021 | 0.006988 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-15 10:39 | 2021-09-15 12:35 | 100 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | R21091500079 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-09-15 | 11600 | keep | 0 | Sep | 2021 | 0.0079007 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-15 10:40 | 2021-09-15 21:04 | 5 | 010:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA DEFECTUOSA NO FUNDIO FUSIBLE | C21091500043 | New_Event | Cutout Failure | Include | Include | Equipment | 624 | 2021-09-15 | 3120 | keep | 0 | Sep | 2021 | 0.002125 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-09-15 10:41 | 2021-09-16 14:57 | 5 | 028:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | B21091500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1696 | 2021-09-15 | 8480 | keep | 0 | Sep | 2021 | 0.0057757 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-09-15 10:44 | 2021-09-15 16:48 | 100 | 006:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091500076 | New_Event | Bad Weather | Include | Include | Weather | 364 | 2021-09-15 | 36400 | keep | 0 | Sep | 2021 | 0.024792 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-15 10:45 | 2021-09-16 11:20 | 40 | 024:35 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL CERCA DE LINEAS PRIMARIAS | M21091500190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1475 | 2021-09-15 | 59000 | keep | 0 | Sep | 2021 | 0.040185 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-15 10:46 | 2021-09-15 14:29 | 45 | 003:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21091500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-09-15 | 10035 | keep | 0 | Sep | 2021 | 0.0068348 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-09-15 10:47 | 2021-09-15 15:30 | 75 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2021-09-15 | 21225 | keep | 0 | Sep | 2021 | 0.014456 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
FAJARDO | 2021-09-15 10:50 | 2021-09-15 16:55 | 40 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO ROTO | R21091500080 | New_Event | Wire Down | Include | Include | Equipment | 365 | 2021-09-15 | 14600 | keep | 0 | Sep | 2021 | 0.009944 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-15 10:50 | 2021-09-15 18:32 | 12 | 007:42 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | R21091500080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 462 | 2021-09-15 | 5544 | keep | 0 | Sep | 2021 | 0.003776 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-15 10:50 | 2021-09-15 12:15 | 8 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21091300407 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2021-09-15 | 680 | keep | 0 | Sep | 2021 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BARRANQUITAS | 2021-09-15 10:55 | 2021-09-15 19:52 | 10 | 008:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21091500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 537 | 2021-09-15 | 5370 | keep | 0 | Sep | 2021 | 0.0036575 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-15 10:57 | 2021-09-15 10:59 | 1879 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C21091500080 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-09-15 | 3758 | keep | 0 | Sep | 2021 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2021-09-15 11:04 | 2021-09-15 19:30 | 40 | 008:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21091500069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 506 | 2021-09-15 | 20240 | keep | 0 | Sep | 2021 | 0.013785 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-15 11:07 | 2021-09-15 11:08 | 650 | 000:01 | T | DESGANCHE | SE ABRIO EL INTERRUPTOR AUTORIZADO POR CARLOS MUÃ‘IZ PARA ABRIR MACHETES EN LA SALIDA DEL ALIMENTADOR | A21091500098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-15 | 650 | keep | 0 | Sep | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2021-09-15 11:08 | 2021-09-15 18:40 | 250 | 007:32 | P | DESGANCHE | SE DESGANCHO Y SE CERRO MACHETES | A21091500099 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 452 | 2021-09-15 | 113000 | keep | 0 | Sep | 2021 | 0.076964 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-09-15 11:11 | 2021-09-15 11:13 | 3458 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21091500153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-15 | 6916 | keep | 0 | Sep | 2021 | 0.0047105 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2021-09-15 11:12 | 2021-09-15 22:14 | 10 | 011:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RAISER POR DESCARGAS ELECTRICAS | M21091500152 | New_Event | Bad Weather | Include | Include | Weather | 662 | 2021-09-15 | 6620 | keep | 0 | Sep | 2021 | 0.0045089 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-09-15 11:17 | 2021-09-15 16:47 | 40 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1X40 EN CORTE DE LINEA POR MAL TIEMPO | P21091500055 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2021-09-15 | 13200 | keep | 0 | Sep | 2021 | 0.0089905 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-15 11:21 | 2021-09-16 20:02 | 40 | 032:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21091500085 | New_Event | Bad Weather | Include | Include | Weather | 1961 | 2021-09-15 | 78440 | keep | 0 | Sep | 2021 | 0.053425 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-15 11:23 | 2021-09-15 20:04 | 6 | 008:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50 KVA | M21091500156 | New_Event | Service Transformer Failure | Include | Include | Equipment | 521 | 2021-09-15 | 3126 | keep | 0 | Sep | 2021 | 0.0021291 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-15 11:24 | 2021-09-15 13:57 | 100 | 002:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2X100 EN CORTE DE LINEA POR CRUCE DE LINEAS POR ANIMAL | P21091500056 | New_Event |  |  | Include | Wildlife | 153 | 2021-09-15 | 15300 | keep | 0 | Sep | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-15 11:25 | 2021-09-18 12:18 | 6 | 072:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA SOTERRADA AVERIADA | B21091500101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 4373 | 2021-09-15 | 26238 | keep | 0 | Sep | 2021 | 0.017871 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-15 11:28 | 2021-09-15 14:40 | 80 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091500159 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-09-15 | 15360 | keep | 0 | Sep | 2021 | 0.010462 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-09-15 11:32 | 2021-09-15 17:28 | 30 | 005:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA RAYOS | C21091500088 | New_Event | Bad Weather | Include | Include | Weather | 356 | 2021-09-15 | 10680 | keep | 0 | Sep | 2021 | 0.0072741 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-15 11:34 | 2021-09-15 15:40 | 50 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1X40 EN CORTE DE LINEA POR MAL TIEMPO | P21091500058 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2021-09-15 | 12300 | keep | 0 | Sep | 2021 | 0.0083775 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-15 11:35 | 2021-09-15 20:22 | 9 | 008:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091500089 | New_Event | Bad Weather | Include | Include | Weather | 527 | 2021-09-15 | 4743 | keep | 0 | Sep | 2021 | 0.0032304 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2021-09-15 11:39 | 2021-09-15 15:12 | 50 | 003:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN CORTE DE LINEA POR CONTACTO DE AVE | P21091500060 | New_Event |  |  | Include | Wildlife | 213 | 2021-09-15 | 10650 | keep | 0 | Sep | 2021 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-15 11:43 | 2021-09-15 19:36 | 25 | 007:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21091500164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2021-09-15 | 11825 | keep | 0 | Sep | 2021 | 0.008054 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-15 11:46 | 2021-09-15 13:55 | 100 | 002:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21091500166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-09-15 | 12900 | keep | 0 | Sep | 2021 | 0.0087861 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-15 11:55 | 2021-09-15 16:30 | 60 | 004:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091500096 | New_Event | Bad Weather | Include | Include | Weather | 275 | 2021-09-15 | 16500 | keep | 0 | Sep | 2021 | 0.011238 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-15 11:57 | 2021-09-15 17:26 | 90 | 005:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091500097 | New_Event | Bad Weather | Include | Include | Weather | 329 | 2021-09-15 | 29610 | keep | 0 | Sep | 2021 | 0.020167 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-09-15 11:57 | 2021-09-15 14:10 | 1 | 002:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO 1 CAJA PRIMARIA AVERIADA EN RISER FID3375013 MARCA SHINT DE 100AMP | A21091500110 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2021-09-15 | 133 | keep | 0 | Sep | 2021 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-09-15 12:04 | 2021-09-15 17:33 | 11 | 005:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21091500100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 329 | 2021-09-15 | 3619 | keep | 0 | Sep | 2021 | 0.0024649 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-09-15 12:11 | 2021-09-15 19:37 | 45 | 007:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21091500103 | New_Event | Bad Weather | Include | Include | Weather | 446 | 2021-09-15 | 20070 | keep | 0 | Sep | 2021 | 0.01367 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-09-15 12:11 | 2021-09-15 13:47 | 1879 | 001:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2021-09-15 | 180384 | keep | 0 | Sep | 2021 | 0.12286 | 0.0012798 | Sustained | FALSE | TRUE | Not_TMED_Event | 1879
ARECIBO | 2021-09-15 12:11 | 2021-09-15 13:47 | 2777 | 001:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2021-09-15 | 266592 | keep | 0 | Sep | 2021 | 0.18157 | 0.0018914 | Sustained | FALSE | TRUE | Not_TMED_Event | 2777
ARECIBO | 2021-09-15 12:11 | 2021-09-15 13:47 | 2 | 001:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2021-09-15 | 192 | keep | 0 | Sep | 2021 | 0.00013077 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
ARECIBO | 2021-09-15 12:11 | 2021-09-15 13:47 | 2839 | 001:36 | T | LINEA DE TRANSMISION 38KV | DOSPARO DE LINEA 2200 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2021-09-15 | 272544 | keep | 0 | Sep | 2021 | 0.18563 | 0.0019336 | Sustained | FALSE | TRUE | Not_TMED_Event | 2839
ARECIBO | 2021-09-15 12:11 | 2021-09-15 13:47 | 1160 | 001:36 | T | LINEA DE TRANSMISION 38KV | DOSPARO DE LINEA 2200 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2021-09-15 | 111360 | keep | 0 | Sep | 2021 | 0.075847 | 0.00079007 | Sustained | FALSE | TRUE | Not_TMED_Event | 1160
ARECIBO | 2021-09-15 12:11 | 2021-09-15 13:47 | 1860 | 001:36 | T | LINEA DE TRANSMISION 38KV | DOSPARO DE LINEA 2200 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2021-09-15 | 178560 | keep | 0 | Sep | 2021 | 0.12162 | 0.0012668 | Sustained | FALSE | TRUE | Not_TMED_Event | 1860
PONCE | 2021-09-15 12:18 | 2021-09-15 15:04 | 2446 | 002:46 | T | DESGANCHE | SE SACO ARBOL SOBRE LINEAS Y SE PROBO EL ALIMENTADOR QUEDANDO EN SERVICIO | P21091500067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-09-15 | 406036 | keep | 0 | Sep | 2021 | 0.27655 | 0.001666 | Sustained | FALSE | TRUE | Not_TMED_Event | 2446
HUMACAO | 2021-09-15 12:27 | 2021-09-15 19:30 | 110 | 007:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21091500108 | New_Event | Bad Weather | Include | Include | Weather | 423 | 2021-09-15 | 46530 | keep | 0 | Sep | 2021 | 0.031691 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
ARECIBO | 2021-09-15 12:27 | 2021-09-15 12:28 | 1227 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A21091500129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-15 | 1227 | keep | 0 | Sep | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
UTUADO | 2021-09-15 12:30 | 2021-09-15 13:45 | 12 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN DOS TRANSFORMADORES DISTINTOS LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091500164 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2021-09-15 | 900 | keep | 0 | Sep | 2021 | 0.00061299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-15 12:44 | 2021-09-15 17:46 | 35 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO SPACER Y CERRARON MACHETES | C21091500072 | Partial_restoration | Wire Down | Include | Include | Equipment | 302 | 2021-09-15 | 10570 | keep | 0 | Sep | 2021 | 0.0071992 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-15 12:50 | 2021-09-15 14:00 | 50 | 001:10 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091500186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-09-15 | 3500 | keep | 0 | Sep | 2021 | 0.0023838 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-15 12:57 | 2021-09-15 16:30 | 30 | 003:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500156 | New_Event | Bad Weather | Include | Include | Weather | 213 | 2021-09-15 | 6390 | keep | 0 | Sep | 2021 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-15 12:59 | 2021-09-15 15:07 | 45 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21091500118 | New_Event |  |  | Include | Wildlife | 128 | 2021-09-15 | 5760 | keep | 0 | Sep | 2021 | 0.0039231 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-09-15 13:19 | 2021-09-15 15:34 | 12 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21091500201 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-09-15 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-15 13:25 | 2021-09-16 15:06 | 8 | 025:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21091500123 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1541 | 2021-09-15 | 12328 | keep | 0 | Sep | 2021 | 0.0083965 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-15 13:26 | 2021-09-15 21:16 | 120 | 007:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21091500124 | New_Event | Bad Weather | Include | Include | Weather | 470 | 2021-09-15 | 56400 | keep | 0 | Sep | 2021 | 0.038414 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-09-15 13:26 | 2021-09-15 14:30 | 125 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091500203 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-09-15 | 8000 | keep | 0 | Sep | 2021 | 0.0054488 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CANOVANAS | 2021-09-15 13:40 | 2021-09-15 16:19 | 45 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR MAL TIEMPO | R21091500095 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2021-09-15 | 7155 | keep | 0 | Sep | 2021 | 0.0048732 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-15 13:43 | 2021-09-15 19:56 | 25 | 006:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REPORTA AVERIA POR DESGANCHE | S21091500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2021-09-15 | 9325 | keep | 0 | Sep | 2021 | 0.0063512 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-15 13:44 | 2021-09-15 22:35 | 16 | 008:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | M21091500205 | New_Event | Bad Weather | Include | Include | Weather | 531 | 2021-09-15 | 8496 | keep | 0 | Sep | 2021 | 0.0057866 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-09-15 13:54 | 2021-09-15 14:41 | 15 | 000:47 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU-5 | S21091500084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2021-09-15 | 705 | keep | 0 | Sep | 2021 | 0.00048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-09-15 13:56 | 2021-09-15 19:27 | 15 | 005:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR REEMPLAZO POSTE ROTO POR CAMION | R21091500097 | New_Event |  |  | Include | Wildlife | 331 | 2021-09-15 | 4965 | keep | 0 | Sep | 2021 | 0.0033816 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-15 14:00 | 2021-09-15 18:00 | 40 | 004:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500221 | New_Event | Bad Weather | Include | Include | Weather | 240 | 2021-09-15 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-15 14:04 | 2021-09-15 17:56 | 10 | 003:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21091200101 | New_Event | Wire Down | Include | Include | Equipment | 232 | 2021-09-15 | 2320 | keep | 0 | Sep | 2021 | 0.0015801 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-15 14:11 | 2021-09-15 18:03 | 2 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091500195 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2021-09-15 | 464 | keep | 0 | Sep | 2021 | 0.00031603 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2021-09-15 14:12 | 2021-09-15 14:50 | 14 | 000:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21091500203 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-09-15 | 532 | keep | 0 | Sep | 2021 | 0.00036234 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-09-15 14:14 | 2021-09-15 17:10 | 30 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500212 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-09-15 | 5280 | keep | 0 | Sep | 2021 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-15 14:14 | 2021-09-15 14:29 | 2825 | 000:15 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR A PETICION DE A LUGO ERRONEAMENTE | M21091500213 | New_Event | Human Error | Include | Include | Other | 15 | 2021-09-15 | 42375 | keep | 0 | Sep | 2021 | 0.028861 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
BAYAMON | 2021-09-15 14:19 | 2021-09-15 14:21 | 1935 | 000:02 | T | ERROR HUMANO | DISPARO PERSONAL DE CDS HACIENDO PRUEBAS EN LA PORTATIL #10 E INTERRUPTORES PROVISIONALES CERRADO EN EL CAMPO LLEVA 100 AMP DEL 1708-02 | B21091500000 | New_Event | Human Error | Include | Include | Other | 2 | 2021-09-15 | 3870 | keep | 0 | Sep | 2021 | 0.0026358 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-09-15 14:19 | 2021-09-15 14:21 | 600 | 000:02 | P | ERROR HUMANO | DISPARO 1707-01 PERSONAL DE CDS HACIENDO PRUEBAS EN LA PORTATIL #10 E INTERRUPTORES PROVISIONALES CERRADO EN EL CAMPO LLEVA 100 AMP DEL 1708-02 | B21091500000 | New_Event | Human Error | Include | Include | Other | 2 | 2021-09-15 | 1200 | keep | 0 | Sep | 2021 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
MAYAGÃœEZ | 2021-09-15 14:30 | 2021-09-15 19:22 | 721 | 004:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR ALAMBRE PARTIDO EN TRONCAL | M21091500218 | New_Event | Wire Down | Include | Include | Equipment | 292 | 2021-09-15 | 210532 | keep | 0 | Sep | 2021 | 0.14339 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
AGUADILLA | 2021-09-15 14:32 | 2021-09-15 15:10 | 80 | 000:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21091500157 | New_Event | Wire Down | Include | Include | Equipment | 38 | 2021-09-15 | 3040 | keep | 0 | Sep | 2021 | 0.0020705 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-15 14:32 | 2021-09-15 18:00 | 60 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500221 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2021-09-15 | 12480 | keep | 0 | Sep | 2021 | 0.0085001 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-15 14:35 | 2021-09-16 14:52 | 7 | 024:17 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 25 KVA | C21091500139 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1457 | 2021-09-15 | 10199 | keep | 0 | Sep | 2021 | 0.0069465 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-09-15 14:41 | 2021-09-16 12:35 | 40 | 021:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500206 | New_Event | Bad Weather | Include | Include | Weather | 1314 | 2021-09-15 | 52560 | keep | 0 | Sep | 2021 | 0.035798 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-15 14:43 | 2021-09-15 16:29 | 95 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21091500142 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-09-15 | 10070 | keep | 0 | Sep | 2021 | 0.0068586 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
FAJARDO | 2021-09-15 14:45 | 2021-09-15 21:43 | 9 | 006:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | R21091500100 | New_Event | Bad Weather | Include | Include | Weather | 418 | 2021-09-15 | 3762 | keep | 0 | Sep | 2021 | 0.0025623 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-09-15 14:57 | 2021-09-15 17:30 | 45 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500230 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-09-15 | 6885 | keep | 0 | Sep | 2021 | 0.0046893 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
GUAYAMA | 2021-09-15 14:59 | 2021-09-15 15:07 | 464 | 000:08 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO ALIMENTADOR. SE VERIFICO CON EL PERSONAL TRABAJANDO EN EL AREA Y EL SUPERVISOR OSVALDO GALIO CERTIFICO PERSONAL FUERA DE LINEA. SE LE DIO PRUEBA Y QUEDO EN SERVICIO. CERTIFICARON QUE FUE POR CONTACTO DE AVE | P210915000XX | New_Event |  |  | Include | Wildlife | 8 | 2021-09-15 | 3712 | keep | 0 | Sep | 2021 | 0.0025282 | 0.00031603 | Sustained | FALSE | TRUE | Not_TMED_Event | 464
ARECIBO | 2021-09-15 15:07 | 2021-09-15 17:25 | 6 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091500210 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-09-15 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-09-15 15:10 | 2021-09-15 17:18 | 30 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21091500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-09-15 | 3840 | keep | 0 | Sep | 2021 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-15 15:17 | 2021-09-15 18:35 | 70 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500242 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-09-15 | 13860 | keep | 0 | Sep | 2021 | 0.00944 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-09-15 15:26 | 2021-09-15 18:23 | 50 | 002:57 | P | DESGANCHE | 1X40 EN CORTE DE LINEA POR DESGANCHE | P21091500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-09-15 | 8850 | keep | 0 | Sep | 2021 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-15 15:27 | 2021-09-15 21:15 | 20 | 005:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500285 | New_Event | Bad Weather | Include | Include | Weather | 348 | 2021-09-15 | 6960 | keep | 0 | Sep | 2021 | 0.0047404 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-09-15 15:28 | 2021-09-16 15:23 | 30 | 023:55 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21091500214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1435 | 2021-09-15 | 43050 | keep | 0 | Sep | 2021 | 0.029321 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-15 15:38 | 2021-09-15 19:14 | 12 | 003:36 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | R21091500108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-09-15 | 2592 | keep | 0 | Sep | 2021 | 0.0017654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-09-15 15:44 | 2021-09-16 10:23 | 9 | 018:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21091500151 | New_Event | Bad Weather | Include | Include | Weather | 1119 | 2021-09-15 | 10071 | keep | 0 | Sep | 2021 | 0.0068593 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-09-15 15:44 | 2021-09-15 15:56 | 4 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | A21091500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2021-09-15 | 48 | keep | 0 | Sep | 2021 | 3.2693e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-09-15 15:47 | 2021-09-15 20:53 | 20 | 005:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21091500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2021-09-15 | 6120 | keep | 0 | Sep | 2021 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-15 15:52 | 2021-09-15 20:56 | 10 | 005:04 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21091500218 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 304 | 2021-09-15 | 3040 | keep | 0 | Sep | 2021 | 0.0020705 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-09-15 16:04 | 2021-09-16 09:48 | 20 | 017:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINAEA DESGANCHE | M21091500259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1064 | 2021-09-15 | 21280 | keep | 0 | Sep | 2021 | 0.014494 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-15 16:05 | 2021-09-19 18:55 | 50 | 098:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANDHE | A21091500221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5930 | 2021-09-15 | 296500 | keep | 0 | Sep | 2021 | 0.20194 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-15 16:06 | 2021-09-15 18:40 | 50 | 002:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1X50 EN CORTE DE LINEA POR MAL TIEMPO | P21091500099 | New_Event | Bad Weather | Include | Include | Weather | 154 | 2021-09-15 | 7700 | keep | 0 | Sep | 2021 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-15 16:08 | 2021-09-15 16:10 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21091500155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-15 | 1740 | keep | 0 | Sep | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2021-09-15 16:09 | 2021-09-15 18:40 | 25 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500223 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-09-15 | 3775 | keep | 0 | Sep | 2021 | 0.0025711 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-09-15 16:18 | 2021-09-15 17:49 | 30 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091500264 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2021-09-15 | 2730 | keep | 0 | Sep | 2021 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-15 16:20 | 2021-09-15 17:14 | 7 | 000:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | A21091500228 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 54 | 2021-09-15 | 378 | keep | 0 | Sep | 2021 | 0.00025745 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-15 16:39 | 2021-09-15 21:22 | 40 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091500117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2021-09-15 | 11320 | keep | 0 | Sep | 2021 | 0.00771 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-15 16:46 | 2021-09-15 17:51 | 10 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | C21091300134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-09-15 | 650 | keep | 0 | Sep | 2021 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-15 16:51 | 2021-09-15 20:37 | 6 | 003:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5KVA | A21091500231 | New_Event | Service Transformer Failure | Include | Include | Equipment | 226 | 2021-09-15 | 1356 | keep | 0 | Sep | 2021 | 0.00092357 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-15 16:54 | 2021-09-16 12:30 | 2 | 019:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091500279 | New_Event | Bad Weather | Include | Include | Weather | 1176 | 2021-09-15 | 2352 | keep | 0 | Sep | 2021 | 0.0016019 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-09-15 17:00 | 2021-09-15 21:38 | 90 | 004:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR Y REPARAR CONDUCTOR ROTO VIVO EN EL SUELO | C21091500170 | New_Event | Wire Down | Include | Include | Equipment | 278 | 2021-09-15 | 25020 | keep | 0 | Sep | 2021 | 0.017041 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 1222 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 2444 | keep | 0 | Sep | 2021 | 0.0016646 | 0.0008323 | Momentary | FALSE | TRUE | Not_TMED_Event | 1222
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 2756 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 5512 | keep | 0 | Sep | 2021 | 0.0037542 | 0.0018771 | Momentary | FALSE | TRUE | Not_TMED_Event | 2756
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 2833 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 5666 | keep | 0 | Sep | 2021 | 0.0038591 | 0.0019295 | Momentary | FALSE | TRUE | Not_TMED_Event | 2833
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 1218 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 2436 | keep | 0 | Sep | 2021 | 0.0016591 | 0.00082957 | Momentary | FALSE | TRUE | Not_TMED_Event | 1218
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 1345 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 2690 | keep | 0 | Sep | 2021 | 0.0018321 | 0.00091607 | Momentary | FALSE | TRUE | Not_TMED_Event | 1345
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 1265 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 2530 | keep | 0 | Sep | 2021 | 0.0017232 | 0.00086159 | Momentary | FALSE | TRUE | Not_TMED_Event | 1265
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 2071 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 4142 | keep | 0 | Sep | 2021 | 0.0028211 | 0.0014105 | Momentary | FALSE | TRUE | Not_TMED_Event | 2071
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 760 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 1520 | keep | 0 | Sep | 2021 | 0.0010353 | 0.00051763 | Momentary | FALSE | TRUE | Not_TMED_Event | 760
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 509 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 1018 | keep | 0 | Sep | 2021 | 0.00069336 | 0.00034668 | Momentary | FALSE | TRUE | Not_TMED_Event | 509
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 2620 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 5240 | keep | 0 | Sep | 2021 | 0.0035689 | 0.0017845 | Momentary | FALSE | TRUE | Not_TMED_Event | 2620
ARECIBO | 2021-09-15 17:10 | 2021-09-15 17:12 | 1916 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21091500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-15 | 3832 | keep | 0 | Sep | 2021 | 0.00261 | 0.001305 | Momentary | FALSE | TRUE | Not_TMED_Event | 1916
ARECIBO | 2021-09-15 17:11 | 2021-09-15 17:12 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21091500234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 3431 | keep | 0 | Sep | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-09-15 17:14 | 2021-09-15 17:19 | 1883 | 000:05 | T | TRANSFORMADOR AVERIADO | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | A21091500235 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 5 | 2021-09-15 | 9415 | keep | 0 | Sep | 2021 | 0.0064125 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-15 17:15 | 2021-09-15 17:16 | 1916 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | A21091500237 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 1916 | keep | 0 | Sep | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2021-09-15 17:19 | 2021-09-15 17:38 | 7 | 000:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA | A21091500228 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 19 | 2021-09-15 | 133 | keep | 0 | Sep | 2021 | 9.0586e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-15 17:21 | 2021-09-16 15:00 | 15 | 021:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500239 | New_Event | Bad Weather | Include | Include | Weather | 1299 | 2021-09-15 | 19485 | keep | 0 | Sep | 2021 | 0.013271 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
PONCE | 2021-09-15 17:29 | 2021-09-15 19:51 | 50 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1X65 EN RAISER POR MAL TIEMPO | P21091500106 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-09-15 | 7100 | keep | 0 | Sep | 2021 | 0.0048358 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-09-15 17:33 | 2021-09-16 11:11 | 1 | 017:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 EN RISER SE REMPLAZARON 2 CAJAS PRIMARIAS QUEMADAS EN RISER | S21091500125 | New_Event | Cutout Failure | Include | Include | Equipment | 1058 | 2021-09-15 | 1058 | keep | 0 | Sep | 2021 | 0.0007206 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-09-15 17:35 | 2021-09-16 11:10 | 50 | 017:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500243 | New_Event | Bad Weather | Include | Include | Weather | 1055 | 2021-09-15 | 52750 | keep | 0 | Sep | 2021 | 0.035928 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-15 17:36 | 2021-09-16 12:09 | 20 | 018:33 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER SE SECCIONALIZO AVERIA DE SU 1 A T 22 | B21091500149 | New_Event | UG Cable Fault | Include | Include | Equipment | 1113 | 2021-09-15 | 22260 | keep | 0 | Sep | 2021 | 0.015161 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-15 17:36 | 2021-09-16 15:51 | 50 | 022:15 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21091500107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1335 | 2021-09-15 | 66750 | keep | 0 | Sep | 2021 | 0.045463 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-15 17:38 | 2021-09-15 19:50 | 1883 | 002:12 | T | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS SE CERRO INTERRUPTOR | A21091500245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-09-15 | 248556 | keep | 0 | Sep | 2021 | 0.16929 | 0.0012825 | Sustained | FALSE | TRUE | Not_TMED_Event | 1883
ARECIBO | 2021-09-15 17:39 | 2021-09-15 21:00 | 15 | 003:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA DEL TRANSFORMADOR AVERIADA | A21091500245 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2021-09-15 | 3015 | keep | 0 | Sep | 2021 | 0.0020535 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-15 17:41 | 2021-09-16 11:21 | 700 | 017:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 1 X 200 EN ENTRADA Y SALIDA DEL CONVERTIDOR | C21091500186 | New_Event | Cutout Failure | Include | Include | Equipment | 1060 | 2021-09-15 | 742000 | keep | 0 | Sep | 2021 | 0.50537 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
ARECIBO | 2021-09-15 17:48 | 2021-09-15 17:49 | 1227 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21091500249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-15 | 1227 | keep | 0 | Sep | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-09-15 17:51 | 2021-09-15 17:52 | 2201 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21091500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-15 | 2201 | keep | 0 | Sep | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-09-15 17:52 | 2021-09-15 18:50 | 60 | 000:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500279 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 58 | 2021-09-15 | 3480 | keep | 0 | Sep | 2021 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-15 17:54 | 2021-09-16 01:09 | 200 | 007:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA Y 1 X 30 EN TRANSFORMADOR SE ANCLO AISLADOR ZAFADO | B21091500152 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 435 | 2021-09-15 | 87000 | keep | 0 | Sep | 2021 | 0.059255 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-15 17:54 | 2021-09-15 17:55 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21091500251 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 3431 | keep | 0 | Sep | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BARRANQUITAS | 2021-09-15 17:54 | 2021-09-16 19:57 | 100 | 026:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21091500190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1563 | 2021-09-15 | 156300 | keep | 0 | Sep | 2021 | 0.10646 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-15 17:55 | 2021-09-15 21:03 | 1227 | 003:08 | T | DESGANCHE | SE RETIRO RAMAS SOBRE LINEAS PRIMARIAS SE CERRO INTERRUPTOR | A21091500252 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-09-15 | 230676 | keep | 0 | Sep | 2021 | 0.15711 | 0.0008357 | Sustained | FALSE | TRUE | Not_TMED_Event | 1227
CAGUAS | 2021-09-15 17:59 | 2021-09-16 10:47 | 99 | 016:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 40 EN CORTES DE LINEA LLUVIAS | C21091500191 | New_Event | Bad Weather | Include | Include | Weather | 1008 | 2021-09-15 | 99792 | keep | 0 | Sep | 2021 | 0.067968 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BAYAMON | 2021-09-15 18:02 | 2021-09-16 16:53 | 50 | 022:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091500153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1371 | 2021-09-15 | 68550 | keep | 0 | Sep | 2021 | 0.046689 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-15 18:12 | 2021-09-16 19:10 | 20 | 024:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500259 | New_Event | Bad Weather | Include | Include | Weather | 1498 | 2021-09-15 | 29960 | keep | 0 | Sep | 2021 | 0.020406 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-15 18:14 | 2021-09-16 16:35 | 13 | 022:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50 KVA | A21091500260 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1341 | 2021-09-15 | 17433 | keep | 0 | Sep | 2021 | 0.011874 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2021-09-15 18:33 | 2021-09-16 11:47 | 3 | 017:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | C21091500193 | New_Event | Bad Weather | Include | Include | Weather | 1034 | 2021-09-15 | 3102 | keep | 0 | Sep | 2021 | 0.0021128 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-09-15 18:34 | 2021-09-16 12:00 | 40 | 017:26 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500298 | New_Event | Bad Weather | Include | Include | Weather | 1046 | 2021-09-15 | 41840 | keep | 0 | Sep | 2021 | 0.028497 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-15 18:34 | 2021-09-16 18:25 | 30 | 023:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500273 | New_Event | Bad Weather | Include | Include | Weather | 1431 | 2021-09-15 | 42930 | keep | 0 | Sep | 2021 | 0.029239 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-15 18:35 | 2021-09-16 11:45 | 7 | 017:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21091500275 | New_Event | Cutout Failure | Include | Include | Equipment | 1030 | 2021-09-15 | 7210 | keep | 0 | Sep | 2021 | 0.0049107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-09-15 18:36 | 2021-09-16 11:41 | 3 | 017:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES QUEMADOS | C21091500194 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1025 | 2021-09-15 | 3075 | keep | 0 | Sep | 2021 | 0.0020944 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-09-15 18:40 | 2021-09-15 19:20 | 50 | 000:40 | P | ESTRUCTURA AVERIADA | POSTE PARTIDO EN LA PERILLA. SE INSTALO AISLADOR Y SE LEVANTO LINEA | P21091500110 | New_Event | Defective Pole | Include | Include | Equipment | 40 | 2021-09-15 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-15 18:41 | 2021-09-16 14:10 | 30 | 019:29 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21091500281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1169 | 2021-09-15 | 35070 | keep | 0 | Sep | 2021 | 0.023886 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-15 18:47 | 2021-09-16 11:05 | 35 | 016:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500283 | New_Event | Bad Weather | Include | Include | Weather | 978 | 2021-09-15 | 34230 | keep | 0 | Sep | 2021 | 0.023314 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
UTUADO | 2021-09-15 18:51 | 2021-09-15 20:20 | 8 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500285 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-09-15 | 712 | keep | 0 | Sep | 2021 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
ARECIBO | 2021-09-15 18:58 | 2021-09-15 19:18 | 5 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA PARA REPARACION SECUNDARIA | A21091500253 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-09-15 | 100 | keep | 0 | Sep | 2021 | 6.811e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-09-15 19:01 | 2021-09-16 11:15 | 5 | 016:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500289 | New_Event | Bad Weather | Include | Include | Weather | 974 | 2021-09-15 | 4870 | keep | 0 | Sep | 2021 | 0.0033169 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
FAJARDO | 2021-09-15 19:12 | 2021-09-15 20:40 | 55 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21091500121 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-09-15 | 4840 | keep | 0 | Sep | 2021 | 0.0032965 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
ARECIBO | 2021-09-15 19:12 | 2021-09-16 11:30 | 25 | 016:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500290 | New_Event | Bad Weather | Include | Include | Weather | 978 | 2021-09-15 | 24450 | keep | 0 | Sep | 2021 | 0.016653 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-15 19:17 | 2021-09-15 19:18 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 726 | keep | 0 | Sep | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-09-15 19:17 | 2021-09-15 19:18 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 3932 | keep | 0 | Sep | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-09-15 19:17 | 2021-09-15 19:18 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2021-09-15 19:18 | 2021-09-15 22:53 | 30 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 5 EN T-5 (FUSIBLE INTERNO EN EL PM DE 5 AMPS) | S21091500153 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-09-15 | 6450 | keep | 0 | Sep | 2021 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-09-15 19:20 | 2021-09-16 15:23 | 40 | 020:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21091500297 | New_Event | Wire Down | Include | Include | Equipment | 1203 | 2021-09-15 | 48120 | keep | 0 | Sep | 2021 | 0.032774 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-15 19:22 | 2021-09-16 11:45 | 125 | 016:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091500203 | New_Event | Bad Weather | Include | Include | Weather | 983 | 2021-09-15 | 122875 | keep | 0 | Sep | 2021 | 0.08369 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
AGUADILLA | 2021-09-15 19:33 | 2021-09-15 21:18 | 80 | 001:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21091500314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-09-15 | 8400 | keep | 0 | Sep | 2021 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-15 19:39 | 2021-09-16 15:32 | 50 | 019:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21091500167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1193 | 2021-09-15 | 59650 | keep | 0 | Sep | 2021 | 0.040627 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-09-15 19:49 | 2021-09-15 23:55 | 80 | 004:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B21091500169 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2021-09-15 | 19680 | keep | 0 | Sep | 2021 | 0.013404 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-15 19:49 | 2021-09-15 19:50 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 9207-09 | B21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 1859 | keep | 0 | Sep | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-09-15 19:49 | 2021-09-15 19:50 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA TRANFERIDA AL 9207-08 | B21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 7 | keep | 0 | Sep | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-15 19:56 | 2021-09-16 12:29 | 40 | 016:33 | P | ESTRUCTURA AVERIADA | 1 X 100 EN CORTE DE LINEA SE RETIRO PELIGRO DE POSTE PARTIDO | S21091500145 | New_Event | Defective Pole | Include | Include | Equipment | 993 | 2021-09-15 | 39720 | keep | 0 | Sep | 2021 | 0.027053 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-15 19:59 | 2021-09-15 21:30 | 50 | 001:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091500307 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2021-09-15 | 4550 | keep | 0 | Sep | 2021 | 0.003099 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-15 20:11 | 2021-09-15 20:28 | 50 | 000:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21091500201 | New_Event |  |  | Include | Wildlife | 17 | 2021-09-15 | 850 | keep | 0 | Sep | 2021 | 0.00057893 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-15 20:17 | 2021-09-16 21:20 | 40 | 025:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500311 | New_Event | Bad Weather | Include | Include | Weather | 1503 | 2021-09-15 | 60120 | keep | 0 | Sep | 2021 | 0.040947 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-15 20:20 | 2021-09-16 11:30 | 20 | 015:10 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | M21091600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 910 | 2021-09-15 | 18200 | keep | 0 | Sep | 2021 | 0.012396 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-09-15 20:29 | 2021-09-15 23:49 | 90 | 003:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100, 3 X 50 Y 3 X 40 EN CORTES DE LINEAS REEMPLAZO AISLADOR | R21091500123 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 200 | 2021-09-15 | 18000 | keep | 0 | Sep | 2021 | 0.01226 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
PONCE | 2021-09-15 20:31 | 2021-09-16 17:33 | 16 | 021:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE TRANSFORMADOR | P21096150011 | New_Event | Cutout Failure | Include | Include | Equipment | 1262 | 2021-09-15 | 20192 | keep | 0 | Sep | 2021 | 0.013753 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2021-09-15 20:47 | 2021-09-15 20:48 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
ARECIBO | 2021-09-15 21:01 | 2021-09-17 14:45 | 50 | 041:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21091500323 | New_Event | Bad Weather | Include | Include | Weather | 2504 | 2021-09-15 | 125200 | keep | 0 | Sep | 2021 | 0.085273 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-15 21:01 | 2021-09-16 17:30 | 2 | 020:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25 KVA | A21091500324 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1229 | 2021-09-15 | 2458 | keep | 0 | Sep | 2021 | 0.0016741 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-09-15 21:02 | 2021-09-16 11:10 | 50 | 014:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091500290 | New_Event | Bad Weather | Include | Include | Weather | 848 | 2021-09-15 | 42400 | keep | 0 | Sep | 2021 | 0.028878 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-15 21:10 | 2021-09-15 21:20 | 2777 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR AUTORIZADO POR ING BILLY CUCURELLA | A21091500336 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2021-09-15 | 27770 | keep | 0 | Sep | 2021 | 0.018914 | 0.0018914 | Sustained | FALSE | FALSE | Not_TMED_Event | 2777
SAN JUAN | 2021-09-15 21:16 | 2021-09-17 09:54 | 80 | 036:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21091500148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2198 | 2021-09-15 | 175840 | keep | 0 | Sep | 2021 | 0.11976 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-15 21:29 | 2021-09-16 12:22 | 50 | 014:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091500337 | New_Event | Bad Weather | Include | Include | Weather | 893 | 2021-09-15 | 44650 | keep | 0 | Sep | 2021 | 0.030411 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-15 21:58 | 2021-09-16 13:31 | 40 | 015:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR | B21091500174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 933 | 2021-09-15 | 37320 | keep | 0 | Sep | 2021 | 0.025418 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-15 22:02 | 2021-09-16 15:25 | 15 | 017:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091500329 | New_Event | Bad Weather | Include | Include | Weather | 1043 | 2021-09-15 | 15645 | keep | 0 | Sep | 2021 | 0.010656 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-15 23:05 | 2021-09-16 15:08 | 10 | 016:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARAR SECUNDARIA | A21091500344 | New_Event | Secondary Wire Down | Include | Include | Equipment | 963 | 2021-09-15 | 9630 | keep | 0 | Sep | 2021 | 0.0065589 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-15 23:18 | 2021-09-15 23:19 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 2704 | keep | 0 | Sep | 2021 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2021-09-15 23:20 | 2021-09-16 12:33 | 7 | 013:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21091500179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 793 | 2021-09-15 | 5551 | keep | 0 | Sep | 2021 | 0.0037808 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2021-09-15 23:27 | 2021-09-16 09:10 | 50 | 009:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P21091500117 | New_Event | Bad Weather | Include | Include | Weather | 583 | 2021-09-15 | 29150 | keep | 0 | Sep | 2021 | 0.019854 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-15 23:33 | 2021-09-16 16:35 | 50 | 017:02 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO TRAMO SOTERRADO | S21091500154 | New_Event | UG Cable Fault | Include | Include | Equipment | 1022 | 2021-09-15 | 51100 | keep | 0 | Sep | 2021 | 0.034804 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-15 23:46 | 2021-09-15 23:47 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-15 | 1526 | keep | 0 | Sep | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-09-16 00:10 | 2021-09-16 20:26 | 60 | 020:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21091600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1216 | 2021-09-16 | 72960 | keep | 0 | Sep | 2021 | 0.049693 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-16 03:02 | 2021-09-16 12:08 | 40 | 009:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 546 | 2021-09-16 | 21840 | keep | 0 | Sep | 2021 | 0.014875 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-16 03:24 | 2021-09-16 10:25 | 40 | 007:01 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21091500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 421 | 2021-09-16 | 16840 | keep | 0 | Sep | 2021 | 0.01147 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-16 03:27 | 2021-09-16 15:17 | 50 | 011:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091600004 | New_Event | Bad Weather | Include | Include | Weather | 710 | 2021-09-16 | 35500 | keep | 0 | Sep | 2021 | 0.024179 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-16 04:47 | 2021-09-16 04:48 | 2178 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO RR/OFF | C21091600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-16 | 2178 | keep | 0 | Sep | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2021-09-16 05:02 | 2021-09-16 05:03 | 2178 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO RR/OFF | C21091600000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-09-16 | 2178 | keep | 0 | Sep | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2021-09-16 05:03 | 2021-09-17 09:20 | 1 | 028:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN BANCO DE TRANSFORMADORES CRUCE CON AVE | C21091600169 | 1st_after_momentary |  |  | Include | Wildlife | 1697 | 2021-09-16 | 1697 | keep | 0 | Sep | 2021 | 0.0011558 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-16 05:31 | 2021-09-16 05:32 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 1606 | keep | 0 | Sep | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
HUMACAO | 2021-09-16 05:37 | 2021-09-16 05:38 | 2354 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21091600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-16 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2021-09-16 06:05 | 2021-09-16 06:06 | 1588 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1711-03 | B21091600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 1588 | keep | 0 | Sep | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-09-16 06:05 | 2021-09-16 06:06 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 1711-01 | B21091600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 13 | keep | 0 | Sep | 2021 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-09-16 06:05 | 2021-09-16 10:20 | 50 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600007 | New_Event | Bad Weather | Include | Include | Weather | 255 | 2021-09-16 | 12750 | keep | 0 | Sep | 2021 | 0.008684 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-16 06:12 | 2021-09-16 16:42 | 20 | 010:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REMPLAZO DISCO | C21091600007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 630 | 2021-09-16 | 12600 | keep | 0 | Sep | 2021 | 0.0085818 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-16 06:17 | 2021-09-16 12:34 | 125 | 006:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091600016 | New_Event | Bad Weather | Include | Include | Weather | 377 | 2021-09-16 | 47125 | keep | 0 | Sep | 2021 | 0.032097 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-09-16 06:18 | 2021-09-16 13:38 | 500 | 007:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIAS | C21091600008 | New_Event | Bad Weather | Include | Include | Weather | 440 | 2021-09-16 | 220000 | keep | 0 | Sep | 2021 | 0.14984 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
PONCE | 2021-09-16 06:43 | 2021-09-16 12:50 | 50 | 006:07 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21091600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2021-09-16 | 18350 | keep | 0 | Sep | 2021 | 0.012498 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-16 06:45 | 2021-09-16 09:40 | 50 | 002:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | P21091600002 | New_Event |  |  | Include | Wildlife | 175 | 2021-09-16 | 8750 | keep | 0 | Sep | 2021 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-09-16 07:08 | 2021-09-16 10:34 | 50 | 003:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEAS DESGANCHE | P21091600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-09-16 | 10300 | keep | 0 | Sep | 2021 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-16 07:09 | 2021-09-16 14:10 | 60 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZARON LINEAS | S21091600011 | New_Event | Wire Down | Include | Include | Equipment | 421 | 2021-09-16 | 25260 | keep | 0 | Sep | 2021 | 0.017204 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-09-16 07:22 | 2021-09-16 16:13 | 5 | 008:51 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO SE TRANSFIRIO LA CARGA A OTRO TRANSFORMADOR | C21091600022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 531 | 2021-09-16 | 2655 | keep | 0 | Sep | 2021 | 0.0018083 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-16 07:24 | 2021-09-16 10:50 | 50 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600016 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2021-09-16 | 10300 | keep | 0 | Sep | 2021 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-16 07:41 | 2021-09-16 19:15 | 50 | 011:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE ABRIO PUENTES PARA SECCIONALIZAR | M21091600022 | New_Event | Wire Down | Include | Include | Equipment | 694 | 2021-09-16 | 34700 | keep | 0 | Sep | 2021 | 0.023634 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-16 07:49 | 2021-09-16 10:10 | 100 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | P21091600018 | New_Event |  |  | Include | Wildlife | 141 | 2021-09-16 | 14100 | keep | 0 | Sep | 2021 | 0.0096034 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-16 07:53 | 2021-09-16 15:20 | 40 | 007:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600022 | New_Event | Bad Weather | Include | Include | Weather | 447 | 2021-09-16 | 17880 | keep | 0 | Sep | 2021 | 0.012178 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-16 07:54 | 2021-09-16 18:19 | 95 | 010:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21091600016 | New_Event | Bad Weather | Include | Include | Weather | 625 | 2021-09-16 | 59375 | keep | 0 | Sep | 2021 | 0.04044 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
ARECIBO | 2021-09-16 08:11 | 2021-09-16 08:12 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21091600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 2697 | keep | 0 | Sep | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
SAN JUAN | 2021-09-16 08:21 | 2021-09-16 15:45 | 1 | 007:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-5 A TRANSCLOSURE | R21091600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 444 | 2021-09-16 | 444 | keep | 0 | Sep | 2021 | 0.00030241 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-09-16 08:22 | 2021-09-16 11:46 | 10 | 003:24 | P | DESGANCHE | 1X15 EN TRANSFORMADOR POR DESGANCHE | P21091600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-09-16 | 2040 | keep | 0 | Sep | 2021 | 0.0013894 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-16 08:23 | 2021-09-16 11:32 | 50 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA | S21091600014 | New_Event |  |  | Include | Wildlife | 189 | 2021-09-16 | 9450 | keep | 0 | Sep | 2021 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-16 08:33 | 2021-09-16 14:10 | 100 | 005:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600030 | New_Event | Bad Weather | Include | Include | Weather | 337 | 2021-09-16 | 33700 | keep | 0 | Sep | 2021 | 0.022953 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-16 08:39 | 2021-09-16 11:13 | 100 | 002:34 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTES DE LINEA | R21091600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-09-16 | 15400 | keep | 0 | Sep | 2021 | 0.010489 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-16 08:40 | 2021-09-16 10:14 | 4 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR LLUVIAS | R21091600010 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2021-09-16 | 376 | keep | 0 | Sep | 2021 | 0.00025609 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-09-16 08:44 | 2021-09-16 12:33 | 40 | 003:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600033 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2021-09-16 | 9160 | keep | 0 | Sep | 2021 | 0.0062388 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-16 08:55 | 2021-09-16 14:19 | 150 | 005:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30, 1 X 50 Y 2 X 100 EN CORTES DE LINEAS MAL TIEMPO | R21091600012 | New_Event | Bad Weather | Include | Include | Weather | 324 | 2021-09-16 | 48600 | keep | 0 | Sep | 2021 | 0.033101 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-16 08:59 | 2021-09-16 11:14 | 75 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600035 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-09-16 | 10125 | keep | 0 | Sep | 2021 | 0.0068961 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-16 09:10 | 2021-09-16 18:20 | 40 | 009:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600036 | New_Event | Bad Weather | Include | Include | Weather | 550 | 2021-09-16 | 22000 | keep | 0 | Sep | 2021 | 0.014984 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-16 09:11 | 2021-09-16 13:12 | 941 | 004:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | B21091500047 | New_Event | Wire Down | Include | Include | Equipment | 241 | 2021-09-16 | 226781 | keep | 0 | Sep | 2021 | 0.15446 | 0.00064091 | Sustained | FALSE | TRUE | Not_TMED_Event | 941
BAYAMON | 2021-09-16 09:21 | 2021-09-16 15:47 | 30 | 006:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN SU | B21091600029 | New_Event | Wire Down | Include | Include | Equipment | 386 | 2021-09-16 | 11580 | keep | 0 | Sep | 2021 | 0.0078871 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-09-16 09:28 | 2021-09-16 11:57 | 5 | 002:29 | P | DESGANCHE | 2 X 8 EN TRANSFORMADOR | R21091600019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-09-16 | 745 | keep | 0 | Sep | 2021 | 0.00050742 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-16 09:31 | 2021-09-16 16:33 | 1 | 007:02 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21091600033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2021-09-16 | 422 | keep | 0 | Sep | 2021 | 0.00028742 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-09-16 09:35 | 2021-09-16 10:56 | 1 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21091600021 | New_Event |  |  | Include | Wildlife | 81 | 2021-09-16 | 81 | keep | 0 | Sep | 2021 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-16 09:37 | 2021-09-16 17:05 | 30 | 007:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21091600035 | New_Event | Cutout Failure | Include | Include | Equipment | 448 | 2021-09-16 | 13440 | keep | 0 | Sep | 2021 | 0.0091539 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-16 09:46 | 2021-09-16 15:40 | 1 | 005:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091600045 | New_Event | Bad Weather | Include | Include | Weather | 354 | 2021-09-16 | 354 | keep | 0 | Sep | 2021 | 0.00024111 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-09-16 09:48 | 2021-09-16 13:28 | 50 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600108 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2021-09-16 | 11000 | keep | 0 | Sep | 2021 | 0.007492 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-16 09:49 | 2021-09-16 11:19 | 80 | 001:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PIN POLE TOP | R21091600023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 90 | 2021-09-16 | 7200 | keep | 0 | Sep | 2021 | 0.0049039 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-16 10:08 | 2021-09-16 16:07 | 15 | 005:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21091600041 | New_Event | Bad Weather | Include | Include | Weather | 359 | 2021-09-16 | 5385 | keep | 0 | Sep | 2021 | 0.0036677 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-09-16 10:13 | 2021-09-16 16:35 | 100 | 006:22 | P | ESTRUCTURA AVERIADA | REMPLAZO POSTE PARTIDO Y TRANSFORMADOR DE 50 KVA X 50 KVA | C21091000088 | New_Event | Defective Pole | Include | Include | Equipment | 382 | 2021-09-16 | 38200 | keep | 0 | Sep | 2021 | 0.026018 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-09-16 10:15 | 2021-09-16 10:16 | 928 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1422-05 | S21091600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 928 | keep | 0 | Sep | 2021 | 0.00063206 | 0.00063206 | Momentary | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-09-16 10:15 | 2021-09-16 10:16 | 637 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1338-02 | S21091600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 637 | keep | 0 | Sep | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
VEGA BAJA | 2021-09-16 10:19 | 2021-09-16 11:36 | 10 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO Y SE LEVANTO SECUNDARIA SE REALIZO DESGANCHE | B21091500097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-09-16 | 770 | keep | 0 | Sep | 2021 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-16 10:21 | 2021-09-17 12:05 | 40 | 025:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21091600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1544 | 2021-09-16 | 61760 | keep | 0 | Sep | 2021 | 0.042064 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-16 10:24 | 2021-09-16 14:18 | 3 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21091600043 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2021-09-16 | 702 | keep | 0 | Sep | 2021 | 0.00047813 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-09-16 10:26 | 2021-09-16 12:12 | 1 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER AVE CRUZO LINEAS | A21091600055 | New_Event |  |  | Include | Wildlife | 106 | 2021-09-16 | 106 | keep | 0 | Sep | 2021 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-16 10:34 | 2021-09-17 15:41 | 12 | 029:07 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO BARRA EN PEDESTAL | C21091600044 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1747 | 2021-09-16 | 20964 | keep | 0 | Sep | 2021 | 0.014278 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-09-16 10:36 | 2021-09-16 14:59 | 45 | 004:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21091600024 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2021-09-16 | 11835 | keep | 0 | Sep | 2021 | 0.0080608 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-09-16 10:36 | 2021-09-16 17:23 | 1 | 006:47 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 12 NX EN GABINETE POR CONTAMINACION | P21091600028 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 407 | 2021-09-16 | 407 | keep | 0 | Sep | 2021 | 0.00027721 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-16 10:38 | 2021-09-16 16:32 | 50 | 005:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-09-16 | 17700 | keep | 0 | Sep | 2021 | 0.012055 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-16 10:39 | 2021-09-17 16:28 | 2 | 029:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA X 15 KVA | M21091600043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1789 | 2021-09-16 | 3578 | keep | 0 | Sep | 2021 | 0.002437 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2021-09-16 10:43 | 2021-09-16 12:20 | 30 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600060 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-09-16 | 2910 | keep | 0 | Sep | 2021 | 0.001982 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-16 10:47 | 2021-09-16 20:20 | 20 | 009:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600061 | New_Event | Bad Weather | Include | Include | Weather | 573 | 2021-09-16 | 11460 | keep | 0 | Sep | 2021 | 0.0078054 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-16 10:51 | 2021-09-17 13:43 | 34 | 026:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CORTE DE LINEA ZAFADO | C21091600049 | New_Event | Wire Down | Include | Include | Equipment | 1612 | 2021-09-16 | 54808 | keep | 0 | Sep | 2021 | 0.037329 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
YAUCO | 2021-09-16 10:53 | 2021-09-16 16:41 | 50 | 005:48 | P | NO SE REPORTO CAUSA | 1X50 EN CORTE DE LINEA. NO SE REPORTA CAUSA | P21091600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2021-09-16 | 17400 | keep | 0 | Sep | 2021 | 0.011851 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-16 11:00 | 2021-09-16 17:41 | 10 | 006:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21091600041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 401 | 2021-09-16 | 4010 | keep | 0 | Sep | 2021 | 0.0027312 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-16 11:04 | 2021-09-16 11:45 | 10 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS EN BAJANTE TRANSFORMADOR | B21091500095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-09-16 | 410 | keep | 0 | Sep | 2021 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-16 11:11 | 2021-09-16 15:10 | 8 | 003:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091600066 | New_Event | Bad Weather | Include | Include | Weather | 239 | 2021-09-16 | 1912 | keep | 0 | Sep | 2021 | 0.0013023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-16 11:19 | 2021-09-16 16:35 | 30 | 005:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600067 | New_Event | Bad Weather | Include | Include | Weather | 316 | 2021-09-16 | 9480 | keep | 0 | Sep | 2021 | 0.0064568 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-16 11:30 | 2021-09-16 15:23 | 8 | 003:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR HOWARD 37.5 KVA 4160 SERIAL-1701881118 FID-33688944 X 37.5 KVA | A21091600071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 233 | 2021-09-16 | 1864 | keep | 0 | Sep | 2021 | 0.0012696 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-16 11:34 | 2021-09-16 15:08 | 50 | 003:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21091600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-09-16 | 10700 | keep | 0 | Sep | 2021 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-16 11:41 | 2021-09-16 11:42 | 928 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1422-05 | S21091600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 928 | keep | 0 | Sep | 2021 | 0.00063206 | 0.00063206 | Momentary | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-09-16 11:41 | 2021-09-16 11:42 | 637 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1338-02 | S21091600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 637 | keep | 0 | Sep | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
BARRANQUITAS | 2021-09-16 11:46 | 2021-09-16 19:28 | 3 | 007:42 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR NO CAUSA | C21091600060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 462 | 2021-09-16 | 1386 | keep | 0 | Sep | 2021 | 0.000944 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2021-09-16 11:47 | 2021-09-16 16:02 | 12 | 004:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZARON BARRAS DE PEDESTAL AVERIADAS | R21091600044 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 255 | 2021-09-16 | 3060 | keep | 0 | Sep | 2021 | 0.0020842 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-09-16 11:51 | 2021-09-16 19:04 | 1 | 007:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C21091600061 | New_Event |  |  | Include | Wildlife | 433 | 2021-09-16 | 433 | keep | 0 | Sep | 2021 | 0.00029491 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-16 11:52 | 2021-09-16 16:29 | 80 | 004:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR REMPLAZO PORTAFUSIBLE QUEMADO | C21091600062 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2021-09-16 | 22160 | keep | 0 | Sep | 2021 | 0.015093 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-16 11:54 | 2021-09-17 12:53 | 17 | 024:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR ERMCO 50KVA 2400/4160 # B20-12095891 FID-33637963 X 50 KVA | A21091600077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1499 | 2021-09-16 | 25483 | keep | 0 | Sep | 2021 | 0.017356 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-09-16 12:01 | 2021-09-16 13:35 | 100 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTES PRIMARIOS ROTOS SE ABRIO INTERRUPTOR PARA REPARAR | M21091600053 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-09-16 | 9400 | keep | 0 | Sep | 2021 | 0.0064023 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-16 12:05 | 2021-09-16 15:00 | 60 | 002:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21091600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-09-16 | 10500 | keep | 0 | Sep | 2021 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-16 12:12 | 2021-09-16 14:45 | 7 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091600057 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-09-16 | 1071 | keep | 0 | Sep | 2021 | 0.00072945 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-09-16 12:22 | 2021-09-16 12:23 | 1883 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR | A21091600088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-16 | 1883 | keep | 0 | Sep | 2021 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
CAGUAS | 2021-09-16 12:23 | 2021-09-16 12:24 | 2907 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21091600067 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-16 | 2907 | keep | 0 | Sep | 2021 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
AGUADILLA | 2021-09-16 12:23 | 2021-09-16 15:20 | 2 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO | M21091600061 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-16 | 354 | keep | 0 | Sep | 2021 | 0.00024111 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-09-16 12:24 | 2021-09-16 16:22 | 2907 | 003:58 | T | ANIMAL U OBJETO EXTRAÃ‘O | PERSONAL CONTRATISTA DEL MUNICIPIO TUMBO CONDUCTOR | C21091600070 | 1st_after_momentary |  |  | Include | Wildlife | 238 | 2021-09-16 | 691866 | keep | 0 | Sep | 2021 | 0.47123 | 0.0019799 | Sustained | FALSE | FALSE | Not_TMED_Event | 2907
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 2791 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 5582 | keep | 0 | Sep | 2021 | 0.0038019 | 0.0019009 | Momentary | FALSE | TRUE | Not_TMED_Event | 2791
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 1464 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 2928 | keep | 0 | Sep | 2021 | 0.0019942 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 759 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 1518 | keep | 0 | Sep | 2021 | 0.0010339 | 0.00051695 | Momentary | FALSE | TRUE | Not_TMED_Event | 759
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 1500 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 3000 | keep | 0 | Sep | 2021 | 0.0020433 | 0.0010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 1500
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 2132 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 4264 | keep | 0 | Sep | 2021 | 0.0029042 | 0.0014521 | Momentary | FALSE | TRUE | Not_TMED_Event | 2132
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 2366 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 4732 | keep | 0 | Sep | 2021 | 0.0032229 | 0.0016115 | Momentary | FALSE | TRUE | Not_TMED_Event | 2366
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 1976 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 3952 | keep | 0 | Sep | 2021 | 0.0026917 | 0.0013458 | Momentary | FALSE | TRUE | Not_TMED_Event | 1976
ARECIBO | 2021-09-16 12:33 | 2021-09-16 12:35 | 3688 | 000:02 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 7376 | keep | 0 | Sep | 2021 | 0.0050238 | 0.0025119 | Momentary | FALSE | TRUE | Not_TMED_Event | 3688
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 3070 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 6140 | keep | 0 | Sep | 2021 | 0.0041819 | 0.002091 | Momentary | FALSE | TRUE | Not_TMED_Event | 3070
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 2735 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 5470 | keep | 0 | Sep | 2021 | 0.0037256 | 0.0018628 | Momentary | FALSE | TRUE | Not_TMED_Event | 2735
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 1070 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 2140 | keep | 0 | Sep | 2021 | 0.0014575 | 0.00072877 | Momentary | FALSE | TRUE | Not_TMED_Event | 1070
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 1647 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 3294 | keep | 0 | Sep | 2021 | 0.0022435 | 0.0011218 | Momentary | FALSE | TRUE | Not_TMED_Event | 1647
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 3295 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 6590 | keep | 0 | Sep | 2021 | 0.0044884 | 0.0022442 | Momentary | FALSE | TRUE | Not_TMED_Event | 3295
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 1180 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 2360 | keep | 0 | Sep | 2021 | 0.0016074 | 0.00080369 | Momentary | FALSE | TRUE | Not_TMED_Event | 1180
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 320 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 640 | keep | 0 | Sep | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | TRUE | Not_TMED_Event | 320
BAYAMON | 2021-09-16 12:33 | 2021-09-16 12:35 | 2234 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21091600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 4468 | keep | 0 | Sep | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | TRUE | Not_TMED_Event | 2234
ARECIBO | 2021-09-16 12:35 | 2021-09-16 16:40 | 40 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600033 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-09-16 | 9800 | keep | 0 | Sep | 2021 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-16 12:35 | 2021-09-16 14:20 | 7 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21091500179 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 105 | 2021-09-16 | 735 | keep | 0 | Sep | 2021 | 0.00050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-16 12:43 | 2021-09-16 16:42 | 15 | 003:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO CAUSA | C21091600110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2021-09-16 | 3585 | keep | 0 | Sep | 2021 | 0.0024417 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BARRANQUITAS | 2021-09-16 12:53 | 2021-09-16 18:12 | 10 | 005:19 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | C21091500113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 319 | 2021-09-16 | 3190 | keep | 0 | Sep | 2021 | 0.0021727 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-16 12:57 | 2021-09-16 15:10 | 1 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN RISER MAL TIEMPO | R21091600033 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-09-16 | 133 | keep | 0 | Sep | 2021 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-16 12:58 | 2021-09-16 16:00 | 10 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600104 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2021-09-16 | 1820 | keep | 0 | Sep | 2021 | 0.0012396 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
PONCE | 2021-09-16 13:02 | 2021-09-16 14:40 | 200 | 001:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN RISER POR CAJA PRIMARIA QUEMADA. SE CAMBIO LA CAJA POR UNA DE 200A | P21091600052 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2021-09-16 | 19600 | keep | 0 | Sep | 2021 | 0.013349 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-09-16 13:05 | 2021-09-17 12:23 | 1 | 023:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25 KVA | A21091600108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1398 | 2021-09-16 | 1398 | keep | 0 | Sep | 2021 | 0.00095217 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-09-16 13:06 | 2021-09-16 15:31 | 426 | 002:25 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SACO TENSOR CRUZANDO LINEAS. SE LE DIO PRUEBA AL INTERRUPTOR Y QUEDO EN SERVICIO | P21091600053 | New_Event |  |  | Include | Wildlife | 145 | 2021-09-16 | 61770 | keep | 0 | Sep | 2021 | 0.042071 | 0.00029015 | Sustained | FALSE | TRUE | Not_TMED_Event | 426
UTUADO | 2021-09-16 13:15 | 2021-09-16 15:23 | 30 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600112 | Partial_restoration | Bad Weather | Include | Include | Weather | 128 | 2021-09-16 | 3840 | keep | 0 | Sep | 2021 | 0.0026154 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-16 13:20 | 2021-09-17 15:05 | 1 | 025:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091600071 | New_Event | Bad Weather | Include | Include | Weather | 1545 | 2021-09-16 | 1545 | keep | 0 | Sep | 2021 | 0.0010523 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-16 13:21 | 2021-09-16 19:58 | 55 | 006:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21091600055 | New_Event | Wire Down | Include | Include | Equipment | 397 | 2021-09-16 | 21835 | keep | 0 | Sep | 2021 | 0.014872 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CANOVANAS | 2021-09-16 13:25 | 2021-09-16 15:50 | 30 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA RETEZO LINEA PRIMARIA | R21091600036 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2021-09-16 | 4350 | keep | 0 | Sep | 2021 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-16 13:25 | 2021-09-16 16:36 | 53 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21091600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-09-16 | 10123 | keep | 0 | Sep | 2021 | 0.0068947 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 1138 | keep | 0 | Sep | 2021 | 0.00077509 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 1245 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 2490 | keep | 0 | Sep | 2021 | 0.0016959 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 1155 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 2310 | keep | 0 | Sep | 2021 | 0.0015733 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 867 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 1734 | keep | 0 | Sep | 2021 | 0.001181 | 0.00059051 | Momentary | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 257 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 514 | keep | 0 | Sep | 2021 | 0.00035008 | 0.00017504 | Momentary | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 1336 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 2672 | keep | 0 | Sep | 2021 | 0.0018199 | 0.00090994 | Momentary | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 3315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 6630 | keep | 0 | Sep | 2021 | 0.0045157 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-09-16 13:28 | 2021-09-16 13:30 | 1718 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-16 | 3436 | keep | 0 | Sep | 2021 | 0.0023402 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
AGUADILLA | 2021-09-16 13:30 | 2021-09-17 15:00 | 50 | 025:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600108 | New_Event | Bad Weather | Include | Include | Weather | 1530 | 2021-09-16 | 76500 | keep | 0 | Sep | 2021 | 0.052104 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-16 13:35 | 2021-09-16 16:00 | 45 | 002:25 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZARON 2 PARARRAYOS | B21091600061 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 145 | 2021-09-16 | 6525 | keep | 0 | Sep | 2021 | 0.0044441 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-09-16 13:35 | 2021-09-16 17:05 | 281 | 003:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTES ABIERTOS EN TRONCAL DEL ALIMENTADOR AUTORIZADO POR EL ING CHRISTIAN FELICIANO | M21091600084 | Additional_clients | Wire Down | Include | Include | Equipment | 210 | 2021-09-16 | 59010 | keep | 0 | Sep | 2021 | 0.040191 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-16 13:36 | 2021-09-16 19:10 | 15 | 005:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER DESCARGAS ELECTRICAS | A21091600120 | New_Event | Bad Weather | Include | Include | Weather | 334 | 2021-09-16 | 5010 | keep | 0 | Sep | 2021 | 0.0034123 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-09-16 13:37 | 2021-09-16 17:48 | 4 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | M21091600077 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2021-09-16 | 1004 | keep | 0 | Sep | 2021 | 0.00068382 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-09-16 13:37 | 2021-09-16 17:05 | 300 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091600078 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2021-09-16 | 62400 | keep | 0 | Sep | 2021 | 0.0425 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-09-16 13:44 | 2021-09-16 22:25 | 100 | 008:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21091600079 | New_Event | Wire Down | Include | Include | Equipment | 521 | 2021-09-16 | 52100 | keep | 0 | Sep | 2021 | 0.035485 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-09-16 13:46 | 2021-09-16 19:30 | 60 | 005:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21091600127 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-09-16 | 20640 | keep | 0 | Sep | 2021 | 0.014058 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-16 13:47 | 2021-09-17 10:45 | 40 | 020:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600128 | New_Event | Bad Weather | Include | Include | Weather | 1258 | 2021-09-16 | 50320 | keep | 0 | Sep | 2021 | 0.034273 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-16 13:53 | 2021-09-16 19:03 | 6 | 005:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO PM PARA REPARAR SECUNDARIA | B21091600064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 310 | 2021-09-16 | 1860 | keep | 0 | Sep | 2021 | 0.0012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-16 13:53 | 2021-09-16 18:18 | 20 | 004:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091600087 | New_Event | Bad Weather | Include | Include | Weather | 265 | 2021-09-16 | 5300 | keep | 0 | Sep | 2021 | 0.0036098 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-16 13:57 | 2021-09-16 20:55 | 100 | 006:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091600088 | New_Event | Bad Weather | Include | Include | Weather | 418 | 2021-09-16 | 41800 | keep | 0 | Sep | 2021 | 0.02847 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-16 14:05 | 2021-09-16 15:40 | 50 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600134 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-09-16 | 4750 | keep | 0 | Sep | 2021 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-16 14:12 | 2021-09-16 14:21 | 9 | 000:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | R21091500098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 9 | 2021-09-16 | 81 | keep | 0 | Sep | 2021 | 5.5169e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2021-09-16 14:12 | 2021-09-16 14:13 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 2286 | keep | 0 | Sep | 2021 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
ARECIBO | 2021-09-16 14:20 | 2021-09-17 11:45 | 1 | 021:25 | P | DESGANCHE | 3 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21091600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1285 | 2021-09-16 | 1285 | keep | 0 | Sep | 2021 | 0.00087521 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-16 14:31 | 2021-09-16 15:05 | 30 | 000:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600101 | New_Event | Bad Weather | Include | Include | Weather | 34 | 2021-09-16 | 1020 | keep | 0 | Sep | 2021 | 0.00069472 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-16 14:31 | 2021-09-16 15:45 | 40 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600127 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2021-09-16 | 2960 | keep | 0 | Sep | 2021 | 0.002016 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-16 14:34 | 2021-09-16 16:45 | 15 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21091600145 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-09-16 | 1965 | keep | 0 | Sep | 2021 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-16 14:36 | 2021-09-16 14:37 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210916000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2021-09-16 14:50 | 2021-09-17 23:07 | 100 | 032:17 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA PODER REEMPLAZAR TRANSFORMADOR QUEMADO DE 50KVA 2400/4160V MARCA-ENRICO #668382 X 50 KVA | M21091600108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1937 | 2021-09-16 | 193700 | keep | 0 | Sep | 2021 | 0.13193 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-16 14:55 | 2021-09-17 09:05 | 100 | 018:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | A21091600157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1090 | 2021-09-16 | 109000 | keep | 0 | Sep | 2021 | 0.074239 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-16 14:56 | 2021-09-16 18:30 | 8 | 003:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5 KVA | A21091600158 | New_Event | Service Transformer Failure | Include | Include | Equipment | 214 | 2021-09-16 | 1712 | keep | 0 | Sep | 2021 | 0.001166 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-16 15:00 | 2021-09-16 19:00 | 60 | 004:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091600114 | New_Event | Bad Weather | Include | Include | Weather | 240 | 2021-09-16 | 14400 | keep | 0 | Sep | 2021 | 0.0098078 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-16 15:08 | 2021-09-17 15:57 | 12 | 024:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO 3 DISCO Y SE REEMPLAZO CT DE MEDICION | R21091600062 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1489 | 2021-09-16 | 17868 | keep | 0 | Sep | 2021 | 0.01217 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
PONCE | 2021-09-16 15:08 | 2021-09-16 16:46 | 50 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1X65 EN CORTE DE LINEA POR MAL TIEMPO | P21091600062 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2021-09-16 | 4900 | keep | 0 | Sep | 2021 | 0.0033374 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-16 15:12 | 2021-09-16 19:05 | 7 | 003:53 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21091600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2021-09-16 | 1631 | keep | 0 | Sep | 2021 | 0.0011109 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-16 15:18 | 2021-09-16 15:19 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091600067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-16 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-16 15:21 | 2021-09-16 18:59 | 55 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21091600068 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2021-09-16 | 11990 | keep | 0 | Sep | 2021 | 0.0081663 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-09-16 15:23 | 2021-09-17 12:34 | 80 | 021:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21091600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1271 | 2021-09-16 | 101680 | keep | 0 | Sep | 2021 | 0.069254 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 1405 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 21075 | keep | 0 | Sep | 2021 | 0.014354 | 0.00095694 | Sustained | FALSE | TRUE | Not_TMED_Event | 1405
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 669 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 10035 | keep | 0 | Sep | 2021 | 0.0068348 | 0.00045565 | Sustained | FALSE | TRUE | Not_TMED_Event | 669
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 1527 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 22905 | keep | 0 | Sep | 2021 | 0.0156 | 0.00104 | Sustained | FALSE | TRUE | Not_TMED_Event | 1527
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 1054 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 15810 | keep | 0 | Sep | 2021 | 0.010768 | 0.00071787 | Sustained | FALSE | TRUE | Not_TMED_Event | 1054
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 932 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 13980 | keep | 0 | Sep | 2021 | 0.0095217 | 0.00063478 | Sustained | FALSE | TRUE | Not_TMED_Event | 932
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 1633 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 24495 | keep | 0 | Sep | 2021 | 0.016683 | 0.0011122 | Sustained | FALSE | TRUE | Not_TMED_Event | 1633
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 1624 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 24360 | keep | 0 | Sep | 2021 | 0.016591 | 0.0011061 | Sustained | FALSE | TRUE | Not_TMED_Event | 1624
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 705 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 10575 | keep | 0 | Sep | 2021 | 0.0072026 | 0.00048017 | Sustained | FALSE | TRUE | Not_TMED_Event | 705
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 1521 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 22815 | keep | 0 | Sep | 2021 | 0.015539 | 0.0010359 | Sustained | FALSE | TRUE | Not_TMED_Event | 1521
UTUADO | 2021-09-16 15:23 | 2021-09-16 15:38 | 882 | 000:15 | T | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 2400 | A21091600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-09-16 | 13230 | keep | 0 | Sep | 2021 | 0.0090109 | 0.00060073 | Sustained | FALSE | TRUE | Not_TMED_Event | 882
ARECIBO | 2021-09-16 15:25 | 2021-09-17 15:50 | 75 | 024:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21091600167 | New_Event | Bad Weather | Include | Include | Weather | 1465 | 2021-09-16 | 109875 | keep | 0 | Sep | 2021 | 0.074835 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-09-16 15:28 | 2021-09-16 15:29 | 1 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21091600049 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-16 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-16 15:30 | 2021-09-16 21:58 | 60 | 006:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091600125 | New_Event | Bad Weather | Include | Include | Weather | 388 | 2021-09-16 | 23280 | keep | 0 | Sep | 2021 | 0.015856 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-09-16 15:31 | 2021-09-16 19:11 | 10 | 003:40 | P | DESGANCHE | 1X10 EN TRANSFORMADOR POR DESGANCHE | P21091600063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-09-16 | 2200 | keep | 0 | Sep | 2021 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-16 15:38 | 2021-09-16 20:10 | 40 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21091500297 | Partial_restoration | Wire Down | Include | Include | Equipment | 272 | 2021-09-16 | 10880 | keep | 0 | Sep | 2021 | 0.0074103 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-16 15:38 | 2021-09-17 10:30 | 30 | 018:52 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21091500214 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1132 | 2021-09-16 | 33960 | keep | 0 | Sep | 2021 | 0.02313 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-16 15:38 | 2021-09-17 14:25 | 15 | 022:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA 2400/4160 EATON # DB2A22024Y4JPOG FID-31545649 X 37.5 KVA | A21091600101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1367 | 2021-09-16 | 20505 | keep | 0 | Sep | 2021 | 0.013966 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-09-16 15:38 | 2021-09-17 10:00 | 10 | 018:22 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | A21091500208 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1102 | 2021-09-16 | 11020 | keep | 0 | Sep | 2021 | 0.0075057 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-16 15:38 | 2021-09-16 16:25 | 30 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091600112 | Partial_restoration | Bad Weather | Include | Include | Weather | 47 | 2021-09-16 | 1410 | keep | 0 | Sep | 2021 | 0.00096034 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-16 15:38 | 2021-09-17 17:55 | 8 | 026:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR HOWARD 37.5 KVA 4160 SERIAL-1701881118 FID-33688944 X 37.5 KVA | A21091600071 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1577 | 2021-09-16 | 12616 | keep | 0 | Sep | 2021 | 0.0085927 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-16 15:39 | 2021-09-16 18:35 | 120 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21091600130 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-09-16 | 21120 | keep | 0 | Sep | 2021 | 0.014385 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
HUMACAO | 2021-09-16 15:40 | 2021-09-16 19:04 | 8 | 003:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21091600103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 204 | 2021-09-16 | 1632 | keep | 0 | Sep | 2021 | 0.0011115 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-16 15:41 | 2021-09-16 17:45 | 30 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21091600131 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2021-09-16 | 3720 | keep | 0 | Sep | 2021 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-09-16 15:43 | 2021-09-16 18:12 | 40 | 002:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21091600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-09-16 | 5960 | keep | 0 | Sep | 2021 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-16 15:51 | 2021-09-16 19:22 | 45 | 003:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600132 | New_Event | Bad Weather | Include | Include | Weather | 211 | 2021-09-16 | 9495 | keep | 0 | Sep | 2021 | 0.006467 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-09-16 16:04 | 2021-09-16 19:22 | 50 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21091600110 | New_Event |  |  | Include | Wildlife | 198 | 2021-09-16 | 9900 | keep | 0 | Sep | 2021 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-16 16:06 | 2021-09-17 16:13 | 3 | 024:07 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C21091600112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1447 | 2021-09-16 | 4341 | keep | 0 | Sep | 2021 | 0.0029566 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2021-09-16 16:08 | 2021-09-16 19:10 | 4 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091600184 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2021-09-16 | 728 | keep | 0 | Sep | 2021 | 0.00049584 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-09-16 16:12 | 2021-09-16 20:18 | 1 | 004:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA | C21091600114 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2021-09-16 | 246 | keep | 0 | Sep | 2021 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-09-16 16:14 | 2021-09-16 16:15 | 2379 | 000:01 | T | DESGANCHE | RECIERRE | P21091600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-16 | 2379 | keep | 0 | Sep | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-09-16 16:15 | 2021-09-16 18:22 | 100 | 002:07 | P | DESGANCHE | 1X100 EN CORTE DE LINEA POR DESGANCHE | P21091600073 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-09-16 | 12700 | keep | 0 | Sep | 2021 | 0.0086499 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-16 16:19 | 2021-09-16 18:07 | 10 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR Y SE RETIRO IGUANA | B21091600085 | New_Event |  |  | Include | Wildlife | 108 | 2021-09-16 | 1080 | keep | 0 | Sep | 2021 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-16 16:34 | 2021-09-17 11:30 | 10 | 018:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAARON CAJAS PRIMARIAS EN TRANSFORMADOR | P21091600071 | New_Event | Cutout Failure | Include | Include | Equipment | 1136 | 2021-09-16 | 11360 | keep | 0 | Sep | 2021 | 0.0077372 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-16 16:38 | 2021-09-16 17:33 | 55 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 25 EN CORTES DE LINEAS MAL TIEMPO | R21091600056 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2021-09-16 | 3025 | keep | 0 | Sep | 2021 | 0.0020603 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
UTUADO | 2021-09-16 17:00 | 2021-09-17 14:20 | 15 | 021:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | A21091600071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1280 | 2021-09-16 | 19200 | keep | 0 | Sep | 2021 | 0.013077 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-09-16 17:05 | 2021-09-16 20:10 | 1 | 003:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR IATO 25 KVA 13200 / 120-240 # 2055099347 FID-1000270945 X 25 KVA | M21091600152 | New_Event | Service Transformer Failure | Include | Include | Equipment | 185 | 2021-09-16 | 185 | keep | 0 | Sep | 2021 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-16 17:10 | 2021-09-16 19:46 | 5 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21091600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2021-09-16 | 780 | keep | 0 | Sep | 2021 | 0.00053125 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-09-16 17:53 | 2021-09-17 13:41 | 14 | 019:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REEMPLAZO 2 CAJAS PRIMARIAS | R21091600064 | New_Event | Cutout Failure | Include | Include | Equipment | 1188 | 2021-09-16 | 16632 | keep | 0 | Sep | 2021 | 0.011328 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-09-16 17:57 | 2021-09-17 09:57 | 30 | 016:00 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X 20 EN PROVISIONAL AEREO SE REMPLAZO TERMINACION SOTERRADA | B21091600098 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 960 | 2021-09-16 | 28800 | keep | 0 | Sep | 2021 | 0.019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-09-16 17:59 | 2021-09-17 13:38 | 2 | 019:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIA TOMAS ZULFATADAS | C21091600133 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1179 | 2021-09-16 | 2358 | keep | 0 | Sep | 2021 | 0.001606 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-09-16 18:01 | 2021-09-16 20:50 | 40 | 002:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | A21091600208 | New_Event |  |  | Include | Wildlife | 169 | 2021-09-16 | 6760 | keep | 0 | Sep | 2021 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-16 18:08 | 2021-09-17 09:29 | 1090 | 015:21 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR SE PATRULLO | C21091600136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 921 | 2021-09-16 | 1003890 | keep | 0 | Sep | 2021 | 0.68374 | 0.00074239 | Sustained | FALSE | FALSE | Not_TMED_Event | 1090
UTUADO | 2021-09-16 18:09 | 2021-09-16 19:15 | 1 | 001:06 | P | PARARRAYOS DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REMPLAZO PARARRAYO CRUZADO | A21091600210 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 66 | 2021-09-16 | 66 | keep | 0 | Sep | 2021 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-16 18:21 | 2021-09-17 16:33 | 40 | 022:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21091600139 | New_Event | Bad Weather | Include | Include | Weather | 1332 | 2021-09-16 | 53280 | keep | 0 | Sep | 2021 | 0.036289 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-16 18:29 | 2021-09-16 23:11 | 200 | 004:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 1 X 80 Y 1 X 50 REEMPLAZO AISLADORES QUEMADOS | R21091600066 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 282 | 2021-09-16 | 56400 | keep | 0 | Sep | 2021 | 0.038414 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-16 18:50 | 2021-09-16 19:40 | 6 | 000:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091600166 | New_Event | Bad Weather | Include | Include | Weather | 50 | 2021-09-16 | 300 | keep | 0 | Sep | 2021 | 0.00020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-09-16 18:50 | 2021-09-16 21:12 | 2 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091600226 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-09-16 | 284 | keep | 0 | Sep | 2021 | 0.00019343 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-09-16 18:55 | 2021-09-17 10:05 | 50 | 015:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091600230 | New_Event | Bad Weather | Include | Include | Weather | 910 | 2021-09-16 | 45500 | keep | 0 | Sep | 2021 | 0.03099 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-16 19:07 | 2021-09-17 15:30 | 350 | 020:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600169 | New_Event | Bad Weather | Include | Include | Weather | 1223 | 2021-09-16 | 428050 | keep | 0 | Sep | 2021 | 0.29154 | 0.00023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 350
MAYAGÃœEZ | 2021-09-16 19:15 | 2021-09-17 16:30 | 15 | 021:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES | M21091700022 | New_Event | Wire Down | Include | Include | Equipment | 1275 | 2021-09-16 | 19125 | keep | 0 | Sep | 2021 | 0.013026 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-16 19:17 | 2021-09-17 16:55 | 90 | 021:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21091600180 | New_Event | Wire Down | Include | Include | Equipment | 1298 | 2021-09-16 | 116820 | keep | 0 | Sep | 2021 | 0.079566 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
GUAYAMA | 2021-09-16 19:21 | 2021-09-16 20:23 | 10 | 001:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN TRANSFORMADOR POR PORTAFUSIBLES QUEMADO | P21091600087 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2021-09-16 | 620 | keep | 0 | Sep | 2021 | 0.00042228 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-16 19:37 | 2021-09-17 03:44 | 8 | 008:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091700179 | New_Event | Bad Weather | Include | Include | Weather | 487 | 2021-09-16 | 3896 | keep | 0 | Sep | 2021 | 0.0026535 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-16 19:47 | 2021-09-17 16:36 | 50 | 020:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600181 | New_Event | Bad Weather | Include | Include | Weather | 1249 | 2021-09-16 | 62450 | keep | 0 | Sep | 2021 | 0.042534 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-09-16 20:03 | 2021-09-17 10:16 | 111 | 014:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR MAL TIEMPO. | P21091600094 | New_Event | Bad Weather | Include | Include | Weather | 853 | 2021-09-16 | 94683 | keep | 0 | Sep | 2021 | 0.064488 | 7.5602e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 111
GUAYAMA | 2021-09-16 20:13 | 2021-09-16 23:11 | 250 | 002:58 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21091600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-09-16 | 44500 | keep | 0 | Sep | 2021 | 0.030309 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-09-16 20:20 | 2021-09-17 17:15 | 300 | 020:55 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091600187 | New_Event | Bad Weather | Include | Include | Weather | 1255 | 2021-09-16 | 376500 | keep | 0 | Sep | 2021 | 0.25643 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-09-16 20:54 | 2021-09-17 19:25 | 13 | 022:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR ITON 37.5KVA 2400 SERIE 2055094408 FID-33638369 X 50 KVA | A21091600257 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1351 | 2021-09-16 | 17563 | keep | 0 | Sep | 2021 | 0.011962 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2021-09-16 21:01 | 2021-09-17 10:59 | 90 | 013:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21091600131 | New_Event | Bad Weather | Include | Include | Weather | 838 | 2021-09-16 | 75420 | keep | 0 | Sep | 2021 | 0.051368 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-09-16 21:15 | 2021-09-17 10:18 | 120 | 013:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C21091600173 | New_Event |  |  | Include | Wildlife | 783 | 2021-09-16 | 93960 | keep | 0 | Sep | 2021 | 0.063996 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-09-16 21:33 | 2021-09-17 11:55 | 1 | 014:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091600213 | New_Event | Bad Weather | Include | Include | Weather | 862 | 2021-09-16 | 862 | keep | 0 | Sep | 2021 | 0.0005871 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-16 22:02 | 2021-09-17 10:40 | 300 | 012:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A21091600268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 758 | 2021-09-16 | 227400 | keep | 0 | Sep | 2021 | 0.15488 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-09-16 22:07 | 2021-09-16 22:48 | 200 | 000:41 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A21091600222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-09-16 | 8200 | keep | 0 | Sep | 2021 | 0.005585 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-16 22:26 | 2021-09-17 12:36 | 10 | 014:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN CORTE DE LINEA SE REPARO BAJANTE | C21091600187 | New_Event | Secondary Wire Down | Include | Include | Equipment | 850 | 2021-09-16 | 8500 | keep | 0 | Sep | 2021 | 0.0057893 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-09-16 23:15 | 2021-09-17 10:44 | 55 | 011:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21091600082 | New_Event | Bad Weather | Include | Include | Weather | 689 | 2021-09-16 | 37895 | keep | 0 | Sep | 2021 | 0.02581 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CANOVANAS | 2021-09-17 02:07 | 2021-09-17 02:08 | 4188 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21091700003 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-17 | 4188 | keep | 0 | Sep | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-09-17 02:08 | 2021-09-17 12:39 | 21 | 010:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21091700018 | 1st_after_momentary |  |  | Include | Wildlife | 631 | 2021-09-17 | 13251 | keep | 0 | Sep | 2021 | 0.0090252 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
HUMACAO | 2021-09-17 03:04 | 2021-09-17 11:05 | 40 | 008:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | C21091700002 | New_Event | Bad Weather | Include | Include | Weather | 481 | 2021-09-17 | 19240 | keep | 0 | Sep | 2021 | 0.013104 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-17 03:11 | 2021-09-17 03:12 | 2468 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 2468 | keep | 0 | Sep | 2021 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
ARECIBO | 2021-09-17 03:38 | 2021-09-17 03:39 | 2132 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21091700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-17 | 2132 | keep | 0 | Sep | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-09-17 03:39 | 2021-09-17 19:40 | 50 | 016:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21091700118 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 961 | 2021-09-17 | 48050 | keep | 0 | Sep | 2021 | 0.032727 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-17 03:44 | 2021-09-17 03:45 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR MAL TIEMPO | M21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 6285 | keep | 0 | Sep | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-09-17 03:45 | 2021-09-17 16:45 | 8 | 013:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091700179 | New_Event | Bad Weather | Include | Include | Weather | 780 | 2021-09-17 | 6240 | keep | 0 | Sep | 2021 | 0.00425 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-17 04:08 | 2021-09-17 04:09 | 327 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 327 | keep | 0 | Sep | 2021 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
VEGA BAJA | 2021-09-17 04:57 | 2021-09-17 10:36 | 45 | 005:39 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21091700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2021-09-17 | 15255 | keep | 0 | Sep | 2021 | 0.01039 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-09-17 05:01 | 2021-09-17 13:18 | 2704 | 008:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE REPARO CONDUCTOR PRIMARIO | B21091700004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 497 | 2021-09-17 | 1343888 | keep | 0 | Sep | 2021 | 0.91532 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2021-09-17 05:15 | 2021-09-17 05:16 | 3957 | 000:01 | T | DESGANCHE | RECERRO EL 1908-03 COMPANIA PRIVADA DESGANCHO EL 1908-03. SE CONCLUYE QUE EL RECIERRE SE DEBIO A DESGANCHE | S21091700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-17 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-17 05:16 | 2021-09-17 15:10 | 80 | 009:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21091700054 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 594 | 2021-09-17 | 47520 | keep | 0 | Sep | 2021 | 0.032366 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-17 05:26 | 2021-09-17 14:50 | 12 | 009:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZARON CAJA DE TRANSFORMADOR DEFECTUOSA | C21091700005 | New_Event | Cutout Failure | Include | Include | Equipment | 564 | 2021-09-17 | 6768 | keep | 0 | Sep | 2021 | 0.0046097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-09-17 06:07 | 2021-09-17 14:29 | 1 | 008:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2X15 EN TRANSFORMADOR POR MAL TIEMPO | P21091700002 | New_Event | Bad Weather | Include | Include | Weather | 502 | 2021-09-17 | 502 | keep | 0 | Sep | 2021 | 0.00034191 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-17 06:33 | 2021-09-17 06:34 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 2106 | keep | 0 | Sep | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
ARECIBO | 2021-09-17 06:33 | 2021-09-17 09:24 | 2 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21091700004 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2021-09-17 | 342 | keep | 0 | Sep | 2021 | 0.00023293 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-09-17 06:47 | 2021-09-17 09:13 | 40 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21091700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-09-17 | 5840 | keep | 0 | Sep | 2021 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-09-17 06:49 | 2021-09-17 11:39 | 40 | 004:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE. | P21091700005 | New_Event |  |  | Include | Wildlife | 290 | 2021-09-17 | 11600 | keep | 0 | Sep | 2021 | 0.0079007 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-09-17 06:50 | 2021-09-17 10:36 | 20 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21091700024 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-09-17 | 4520 | keep | 0 | Sep | 2021 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-17 06:59 | 2021-09-17 12:00 | 100 | 005:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-09-17 | 30100 | keep | 0 | Sep | 2021 | 0.020501 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-17 07:07 | 2021-09-17 13:21 | 836 | 006:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO HACIA CORTE DE LINEA | C21091700009 | New_Event | Wire Down | Include | Include | Equipment | 374 | 2021-09-17 | 312664 | keep | 0 | Sep | 2021 | 0.21295 | 0.0005694 | Sustained | FALSE | TRUE | Not_TMED_Event | 836
MAYAGÃœEZ | 2021-09-17 07:10 | 2021-09-17 12:32 | 150 | 005:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21091700029 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2021-09-17 | 48300 | keep | 0 | Sep | 2021 | 0.032897 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-17 07:11 | 2021-09-17 12:48 | 10 | 005:37 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21091700014 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 337 | 2021-09-17 | 3370 | keep | 0 | Sep | 2021 | 0.0022953 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-17 07:11 | 2021-09-17 16:00 | 25 | 008:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN TRANSFORMADOR | S21091700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 529 | 2021-09-17 | 13225 | keep | 0 | Sep | 2021 | 0.0090075 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-09-17 07:21 | 2021-09-17 15:54 | 35 | 008:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21091700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2021-09-17 | 17955 | keep | 0 | Sep | 2021 | 0.012229 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-17 07:21 | 2021-09-17 15:05 | 3 | 007:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21091700009 | New_Event | Bad Weather | Include | Include | Weather | 464 | 2021-09-17 | 1392 | keep | 0 | Sep | 2021 | 0.00094808 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-09-17 07:28 | 2021-09-17 15:54 | 100 | 008:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR AVE | C21091700010 | New_Event |  |  | Include | Wildlife | 506 | 2021-09-17 | 50600 | keep | 0 | Sep | 2021 | 0.034463 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-17 07:29 | 2021-09-17 10:54 | 170 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21091700011 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2021-09-17 | 34850 | keep | 0 | Sep | 2021 | 0.023736 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
HUMACAO | 2021-09-17 07:38 | 2021-09-17 18:19 | 70 | 010:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21091700013 | New_Event | Bad Weather | Include | Include | Weather | 641 | 2021-09-17 | 44870 | keep | 0 | Sep | 2021 | 0.030561 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-09-17 07:39 | 2021-09-17 15:39 | 10 | 008:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE HIZO DESGANCHE | P21091700008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 480 | 2021-09-17 | 4800 | keep | 0 | Sep | 2021 | 0.0032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-17 07:44 | 2021-09-17 13:08 | 35 | 005:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | B21091700024 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2021-09-17 | 11340 | keep | 0 | Sep | 2021 | 0.0077236 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-17 07:49 | 2021-09-17 11:15 | 12 | 003:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CAMION CRUZO SECUNDARIA | A21091700012 | New_Event |  |  | Include | Wildlife | 206 | 2021-09-17 | 2472 | keep | 0 | Sep | 2021 | 0.0016837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-17 07:50 | 2021-09-17 19:36 | 15 | 011:46 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA | C21091700014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 706 | 2021-09-17 | 10590 | keep | 0 | Sep | 2021 | 0.0072128 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-09-17 07:58 | 2021-09-17 10:55 | 6 | 002:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5 KVA | A21091700015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 177 | 2021-09-17 | 1062 | keep | 0 | Sep | 2021 | 0.00072332 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-17 08:10 | 2021-09-17 08:13 | 455 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1715-05 | B21091700000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-09-17 | 1365 | keep | 0 | Sep | 2021 | 0.0009297 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
BAYAMON | 2021-09-17 08:10 | 2021-09-17 08:13 | 776 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1714-03 | B21091700000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-09-17 | 2328 | keep | 0 | Sep | 2021 | 0.0015856 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
BAYAMON | 2021-09-17 08:13 | 2021-09-17 14:48 | 300 | 006:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PARA CERRAR PUENTE ABIERTO | B21091700041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 395 | 2021-09-17 | 118500 | keep | 0 | Sep | 2021 | 0.08071 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-09-17 08:14 | 2021-09-17 08:15 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210917000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-09-17 08:14 | 2021-09-17 08:15 | 948 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210917000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 948 | keep | 0 | Sep | 2021 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
PONCE | 2021-09-17 08:14 | 2021-09-17 08:15 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210917000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 113 | keep | 0 | Sep | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
MAYAGÃœEZ | 2021-09-17 08:15 | 2021-09-17 13:57 | 5 | 005:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21091700039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 342 | 2021-09-17 | 1710 | keep | 0 | Sep | 2021 | 0.0011647 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-09-17 08:16 | 2021-09-17 08:17 | 533 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1330-05 | S21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 533 | keep | 0 | Sep | 2021 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
PONCE | 2021-09-17 08:17 | 2021-09-17 12:00 | 16 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P21091700009 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2021-09-17 | 3568 | keep | 0 | Sep | 2021 | 0.0024301 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-09-17 08:18 | 2021-09-17 14:33 | 25 | 006:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO PRIMARIA | B21091700033 | New_Event | Wire Down | Include | Include | Equipment | 375 | 2021-09-17 | 9375 | keep | 0 | Sep | 2021 | 0.0063853 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-09-17 08:21 | 2021-09-17 08:22 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210917000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 778 | keep | 0 | Sep | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-09-17 08:24 | 2021-09-17 14:24 | 50 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1X65 EN CORTE DE LINEA POR MAL TIEMPO | P21091700048 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-09-17 | 18000 | keep | 0 | Sep | 2021 | 0.01226 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-17 08:26 | 2021-09-17 18:46 | 14 | 010:20 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | C21091600024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 620 | 2021-09-17 | 8680 | keep | 0 | Sep | 2021 | 0.0059119 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2021-09-17 08:31 | 2021-09-17 18:19 | 50 | 009:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21091700022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2021-09-17 | 29400 | keep | 0 | Sep | 2021 | 0.020024 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-17 08:32 | 2021-09-17 11:25 | 60 | 002:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A21091700029 | New_Event | Cutout Failure | Include | Include | Equipment | 173 | 2021-09-17 | 10380 | keep | 0 | Sep | 2021 | 0.0070698 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-17 08:33 | 2021-09-17 19:35 | 4 | 011:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091700212 | New_Event | Bad Weather | Include | Include | Weather | 662 | 2021-09-17 | 2648 | keep | 0 | Sep | 2021 | 0.0018035 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-09-17 09:05 | 2021-09-17 09:06 | 2366 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A21091700000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-17 | 2366 | keep | 0 | Sep | 2021 | 0.0016115 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-17 09:06 | 2021-09-17 12:15 | 300 | 003:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REPARO AISLADOR ZAFADO | A21091700037 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2021-09-17 | 56700 | keep | 0 | Sep | 2021 | 0.038618 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-09-17 09:06 | 2021-09-17 17:30 | 100 | 008:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | A21091600157 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 504 | 2021-09-17 | 50400 | keep | 0 | Sep | 2021 | 0.034327 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-09-17 09:08 | 2021-09-17 11:37 | 13 | 002:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO AISLADOR | R21091700013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 149 | 2021-09-17 | 1937 | keep | 0 | Sep | 2021 | 0.0013193 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
SAN JUAN | 2021-09-17 09:29 | 2021-09-17 10:35 | 1 | 001:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 25 AMP CRUCE POR RATA | R21091700014 | New_Event |  |  | Include | Wildlife | 66 | 2021-09-17 | 66 | keep | 0 | Sep | 2021 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-17 09:29 | 2021-09-17 09:30 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21091700000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 2900 | keep | 0 | Sep | 2021 | 0.0019752 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-17 09:30 | 2021-09-17 10:34 | 1090 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR SE PATRULLO | C21091600136 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 64 | 2021-09-17 | 69760 | keep | 0 | Sep | 2021 | 0.047513 | 0.00074239 | Sustained | FALSE | FALSE | Not_TMED_Event | 1090
BAYAMON | 2021-09-17 09:34 | 2021-09-17 22:28 | 45 | 012:54 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | B21091700054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 774 | 2021-09-17 | 34830 | keep | 0 | Sep | 2021 | 0.023723 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-09-17 09:34 | 2021-09-17 16:30 | 12 | 006:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21091700043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2021-09-17 | 4992 | keep | 0 | Sep | 2021 | 0.0034 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
HUMACAO | 2021-09-17 09:39 | 2021-09-17 20:48 | 11 | 011:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091700031 | New_Event | Bad Weather | Include | Include | Weather | 669 | 2021-09-17 | 7359 | keep | 0 | Sep | 2021 | 0.0050122 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-09-17 09:43 | 2021-09-17 14:55 | 2 | 005:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1X 10 EN TRANSFORMADOR MAL TIEMPO | A21091700047 | New_Event | Bad Weather | Include | Include | Weather | 312 | 2021-09-17 | 624 | keep | 0 | Sep | 2021 | 0.000425 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-09-17 09:49 | 2021-09-17 16:00 | 1 | 006:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091700077 | New_Event | Bad Weather | Include | Include | Weather | 371 | 2021-09-17 | 371 | keep | 0 | Sep | 2021 | 0.00025269 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-17 09:49 | 2021-09-17 13:45 | 400 | 003:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21091700048 | New_Event | Wire Down | Include | Include | Equipment | 236 | 2021-09-17 | 94400 | keep | 0 | Sep | 2021 | 0.064295 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2021-09-17 10:00 | 2021-09-17 10:40 | 15 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21091600075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-09-17 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-17 10:00 | 2021-09-17 11:55 | 70 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LLINEA LLUVIAS | C21091700036 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-09-17 | 8050 | keep | 0 | Sep | 2021 | 0.0054828 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-09-17 10:10 | 2021-09-17 13:00 | 1 | 002:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | M21091700082 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2021-09-17 | 170 | keep | 0 | Sep | 2021 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-17 10:13 | 2021-09-17 13:52 | 19 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C21091700041 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-09-17 | 4161 | keep | 0 | Sep | 2021 | 0.002834 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
MAYAGÃœEZ | 2021-09-17 10:31 | 2021-09-17 15:38 | 70 | 005:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091700086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-09-17 | 21490 | keep | 0 | Sep | 2021 | 0.014637 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-17 10:33 | 2021-09-17 15:17 | 4 | 004:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091700087 | New_Event | Bad Weather | Include | Include | Weather | 284 | 2021-09-17 | 1136 | keep | 0 | Sep | 2021 | 0.00077372 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-09-17 10:42 | 2021-09-17 11:11 | 80 | 000:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21091500148 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-09-17 | 2320 | keep | 0 | Sep | 2021 | 0.0015801 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-09-17 11:00 | 2021-09-18 16:17 | 43 | 029:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21091700047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1757 | 2021-09-17 | 75551 | keep | 0 | Sep | 2021 | 0.051457 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
MAYAGÃœEZ | 2021-09-17 11:05 | 2021-09-17 15:10 | 2 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091700095 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-09-17 | 490 | keep | 0 | Sep | 2021 | 0.00033374 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-09-17 11:07 | 2021-09-17 15:12 | 1 | 004:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M21091700097 | New_Event | Wire Down | Include | Include | Equipment | 245 | 2021-09-17 | 245 | keep | 0 | Sep | 2021 | 0.00016687 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-17 11:09 | 2021-09-17 16:50 | 60 | 005:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21091700061 | New_Event | Bad Weather | Include | Include | Weather | 341 | 2021-09-17 | 20460 | keep | 0 | Sep | 2021 | 0.013935 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-17 11:09 | 2021-09-17 16:10 | 4 | 005:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21091600108 | New_Event | Bad Weather | Include | Include | Weather | 301 | 2021-09-17 | 1204 | keep | 0 | Sep | 2021 | 0.00082004 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-09-17 11:11 | 2021-09-17 11:12 | 1742 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 1742 | keep | 0 | Sep | 2021 | 0.0011865 | 0.0011865 | Momentary | FALSE | FALSE | Not_TMED_Event | 1742
ARECIBO | 2021-09-17 11:16 | 2021-09-17 17:00 | 25 | 005:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21091700065 | New_Event | Bad Weather | Include | Include | Weather | 344 | 2021-09-17 | 8600 | keep | 0 | Sep | 2021 | 0.0058574 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-09-17 11:17 | 2021-09-17 17:43 | 1 | 006:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN BANCO DE TRANSFORMADOR MAL TIEMPO | C21091700053 | New_Event | Bad Weather | Include | Include | Weather | 386 | 2021-09-17 | 386 | keep | 0 | Sep | 2021 | 0.0002629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-17 11:20 | 2021-09-17 12:24 | 4 | 001:04 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21091700026 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 64 | 2021-09-17 | 256 | keep | 0 | Sep | 2021 | 0.00017436 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-09-17 11:20 | 2021-09-17 16:55 | 60 | 005:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091700103 | New_Event | Bad Weather | Include | Include | Weather | 335 | 2021-09-17 | 20100 | keep | 0 | Sep | 2021 | 0.01369 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-17 11:23 | 2021-09-17 11:54 | 4 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA LEVANTAR SECUNDARIA | R21091700016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-09-17 | 124 | keep | 0 | Sep | 2021 | 8.4456e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-09-17 11:35 | 2021-09-17 18:09 | 40 | 006:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | A21091700069 | New_Event | Wire Down | Include | Include | Equipment | 394 | 2021-09-17 | 15760 | keep | 0 | Sep | 2021 | 0.010734 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-17 11:44 | 2021-09-17 17:27 | 11 | 005:43 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR | C21091700058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 343 | 2021-09-17 | 3773 | keep | 0 | Sep | 2021 | 0.0025698 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2021-09-17 11:51 | 2021-09-17 15:54 | 50 | 004:03 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21091700027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-09-17 | 12150 | keep | 0 | Sep | 2021 | 0.0082753 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-17 11:55 | 2021-09-20 20:27 | 2 | 080:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091700073 | New_Event | Bad Weather | Include | Include | Weather | 4832 | 2021-09-17 | 9664 | keep | 0 | Sep | 2021 | 0.0065821 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
UTUADO | 2021-09-17 11:58 | 2021-09-18 18:37 | 15 | 030:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21091700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1839 | 2021-09-17 | 27585 | keep | 0 | Sep | 2021 | 0.018788 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-17 11:59 | 2021-09-17 15:00 | 120 | 003:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091700110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-09-17 | 21720 | keep | 0 | Sep | 2021 | 0.014793 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
VEGA BAJA | 2021-09-17 12:06 | 2021-09-17 13:47 | 10 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE SECUNDARIO | B21091400154 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-09-17 | 1010 | keep | 0 | Sep | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-17 12:20 | 2021-09-18 13:07 | 11 | 024:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091700064 | New_Event | Bad Weather | Include | Include | Weather | 1487 | 2021-09-17 | 16357 | keep | 0 | Sep | 2021 | 0.011141 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-09-17 12:25 | 2021-09-17 15:31 | 24 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN AEREO PROVISIONAL MAL TIEMPO | R21091700031 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-09-17 | 4464 | keep | 0 | Sep | 2021 | 0.0030404 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2021-09-17 12:36 | 2021-09-17 15:31 | 55 | 002:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C21091700066 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2021-09-17 | 9625 | keep | 0 | Sep | 2021 | 0.0065555 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CAGUAS | 2021-09-17 12:36 | 2021-09-17 14:27 | 2 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES EN BAJANTE SECUNDARIO DE TRANSFORMADOR | C21091700000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2021-09-17 | 222 | keep | 0 | Sep | 2021 | 0.0001512 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2021-09-17 12:43 | 2021-09-17 15:40 | 30 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21091700079 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-17 | 5310 | keep | 0 | Sep | 2021 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-17 12:48 | 2021-09-18 12:00 | 80 | 023:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P21091700029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1392 | 2021-09-17 | 111360 | keep | 0 | Sep | 2021 | 0.075847 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-17 12:51 | 2021-09-17 17:12 | 70 | 004:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE. | P21091700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-09-17 | 18270 | keep | 0 | Sep | 2021 | 0.012444 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-09-17 12:58 | 2021-09-17 12:59 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-17 12:58 | 2021-09-17 12:59 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
SAN JUAN | 2021-09-17 12:59 | 2021-09-17 18:00 | 113 | 005:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE AEREO PROVISIONAL | R21091700032 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2021-09-17 | 34013 | keep | 0 | Sep | 2021 | 0.023166 | 7.6964e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 113
BARRANQUITAS | 2021-09-17 13:07 | 2021-09-17 17:48 | 180 | 004:41 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | C21091700077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 281 | 2021-09-17 | 50580 | keep | 0 | Sep | 2021 | 0.03445 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-09-17 13:12 | 2021-09-17 14:00 | 8 | 000:48 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN CORTE DE LINEA TRANSFORMADOR QUEMADO NO HAY INFORMACION DE ESE DIA QUE SE REMPLAZO | M21091700121 | New_Event | Service Transformer Failure | Include | Include | Equipment | 48 | 2021-09-17 | 384 | keep | 0 | Sep | 2021 | 0.00026154 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-17 13:13 | 2021-09-17 19:05 | 10 | 005:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | M21091700122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 352 | 2021-09-17 | 3520 | keep | 0 | Sep | 2021 | 0.0023975 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-17 13:28 | 2021-09-17 18:40 | 50 | 005:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REPORTA AVERIA POR DESGANCHE | S21091700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2021-09-17 | 15600 | keep | 0 | Sep | 2021 | 0.010625 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 591 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 7683 | keep | 0 | Sep | 2021 | 0.0052329 | 0.00040253 | Sustained | FALSE | TRUE | Not_TMED_Event | 591
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:05 | 1924 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-09-17 | 51948 | keep | 0 | Sep | 2021 | 0.035382 | 0.0013104 | Sustained | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:05 | 968 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-09-17 | 26136 | keep | 0 | Sep | 2021 | 0.017801 | 0.0006593 | Sustained | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:05 | 680 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-09-17 | 18360 | keep | 0 | Sep | 2021 | 0.012505 | 0.00046314 | Sustained | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:05 | 2246 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-09-17 | 60642 | keep | 0 | Sep | 2021 | 0.041303 | 0.0015297 | Sustained | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 2011 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 26143 | keep | 0 | Sep | 2021 | 0.017806 | 0.0013697 | Sustained | FALSE | TRUE | Not_TMED_Event | 2011
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 339 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 4407 | keep | 0 | Sep | 2021 | 0.0030016 | 0.00023089 | Sustained | FALSE | TRUE | Not_TMED_Event | 339
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 2470 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 32110 | keep | 0 | Sep | 2021 | 0.02187 | 0.0016823 | Sustained | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 1182 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 15366 | keep | 0 | Sep | 2021 | 0.010466 | 0.00080505 | Sustained | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 2340 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 30420 | keep | 0 | Sep | 2021 | 0.020719 | 0.0015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-09-17 13:38 | 2021-09-17 13:51 | 1637 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-09-17 | 21281 | keep | 0 | Sep | 2021 | 0.014494 | 0.001115 | Sustained | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 1475 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 33925 | keep | 0 | Sep | 2021 | 0.023106 | 0.0010046 | Sustained | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 661 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 15203 | keep | 0 | Sep | 2021 | 0.010355 | 0.0004502 | Sustained | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 1569 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 36087 | keep | 0 | Sep | 2021 | 0.024579 | 0.0010686 | Sustained | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 2309 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 53107 | keep | 0 | Sep | 2021 | 0.036171 | 0.0015726 | Sustained | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 2179 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 50117 | keep | 0 | Sep | 2021 | 0.034134 | 0.0014841 | Sustained | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 2440 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 56120 | keep | 0 | Sep | 2021 | 0.038223 | 0.0016619 | Sustained | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 1352 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 31096 | keep | 0 | Sep | 2021 | 0.021179 | 0.00092084 | Sustained | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 3973 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 91379 | keep | 0 | Sep | 2021 | 0.062238 | 0.002706 | Sustained | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-09-17 13:38 | 2021-09-17 14:01 | 2484 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P210917000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-09-17 | 57132 | keep | 0 | Sep | 2021 | 0.038912 | 0.0016918 | Sustained | FALSE | TRUE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-09-17 13:38 | 2021-09-17 13:51 | 281 | 000:13 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO I | M21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 3653 | keep | 0 | Sep | 2021 | 0.002488 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-17 13:38 | 2021-09-17 13:51 | 1252 | 000:13 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO I | M21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 16276 | keep | 0 | Sep | 2021 | 0.011086 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-09-17 13:38 | 2021-09-17 13:51 | 595 | 000:13 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO I | M21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 7735 | keep | 0 | Sep | 2021 | 0.0052683 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-09-17 13:38 | 2021-09-17 13:51 | 51 | 000:13 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO I | M21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 663 | keep | 0 | Sep | 2021 | 0.00045157 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-09-17 13:38 | 2021-09-17 13:51 | 721 | 000:13 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO I | M21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 9373 | keep | 0 | Sep | 2021 | 0.0063839 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2021-09-17 13:38 | 2021-09-17 13:51 | 1382 | 000:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO-1 | A21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 17966 | keep | 0 | Sep | 2021 | 0.012237 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2021-09-17 13:38 | 2021-09-17 13:51 | 654 | 000:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO-1 | A21091700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2021-09-17 | 8502 | keep | 0 | Sep | 2021 | 0.0057907 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
SAN JUAN | 2021-09-17 13:50 | 2021-09-17 17:58 | 8 | 004:08 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR EN PEDESTAL SE DEJO CLIENTE FUERA PARA QUE REPARE | R21091700034 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 248 | 2021-09-17 | 1984 | keep | 0 | Sep | 2021 | 0.0013513 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-09-17 13:56 | 2021-09-17 18:58 | 11 | 005:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091700086 | New_Event | Bad Weather | Include | Include | Weather | 302 | 2021-09-17 | 3322 | keep | 0 | Sep | 2021 | 0.0022626 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 1339 | keep | 0 | Sep | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 470 | keep | 0 | Sep | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | TRUE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 2483 | keep | 0 | Sep | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | TRUE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 2190 | keep | 0 | Sep | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | TRUE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 3006 | keep | 0 | Sep | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | TRUE | Not_TMED_Event | 179
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 107 | keep | 0 | Sep | 2021 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 1666 | keep | 0 | Sep | 2021 | 0.0011347 | 0.0011347 | Momentary | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 4387 | keep | 0 | Sep | 2021 | 0.002988 | 0.002988 | Momentary | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-09-17 13:57 | 2021-09-17 13:58 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 13400 | M21091700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-17 | 4304 | keep | 0 | Sep | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2021-09-17 13:58 | 2021-09-17 16:50 | 5 | 002:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21091700039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 172 | 2021-09-17 | 860 | keep | 0 | Sep | 2021 | 0.00058574 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-09-17 14:00 | 2021-09-19 18:10 | 10 | 052:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21091700087 | New_Event | Wire Down | Include | Include | Equipment | 3130 | 2021-09-17 | 31300 | keep | 0 | Sep | 2021 | 0.021318 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-09-17 14:06 | 2021-09-17 14:44 | 110 | 000:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21091700088 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-09-17 | 4180 | keep | 0 | Sep | 2021 | 0.002847 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
MAYAGÃœEZ | 2021-09-17 14:08 | 2021-09-17 18:54 | 7 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091700138 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2021-09-17 | 2002 | keep | 0 | Sep | 2021 | 0.0013636 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-09-17 14:20 | 2021-09-17 17:45 | 3000 | 003:25 | P | NO SE REPORTO CAUSA | 9405-05 DISPARO PERO NO OPERO POR SCADA SE CERRO EN EL CAMPO LLEVA PARTE DEL 1710-05 | B21091700119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-09-17 | 615000 | keep | 0 | Sep | 2021 | 0.41887 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2021-09-17 14:20 | 2021-09-17 17:45 | 3511 | 003:25 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO PERO NO OPERO POR SCADA SE CERRO EN EL CAMPO LLEVA PARTE DEL 1710-05 | B21091700119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-09-17 | 719755 | keep | 0 | Sep | 2021 | 0.49022 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
CANOVANAS | 2021-09-17 14:25 | 2021-09-17 15:03 | 11 | 000:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21091700039 | New_Event |  |  | Include | Wildlife | 38 | 2021-09-17 | 418 | keep | 0 | Sep | 2021 | 0.0002847 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2021-09-17 14:27 | 2021-09-17 14:28 | 2635 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21091700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-17 | 2635 | keep | 0 | Sep | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-17 14:28 | 2021-09-18 11:56 | 120 | 021:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21091700172 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1288 | 2021-09-17 | 154560 | keep | 0 | Sep | 2021 | 0.10527 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-17 14:48 | 2021-09-17 16:56 | 150 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1715-05 PARA HACER OPERACIONES LLEVA 1714-03 | B21091700041 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-09-17 | 19200 | keep | 0 | Sep | 2021 | 0.013077 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-09-17 15:01 | 2021-09-17 16:17 | 8 | 001:16 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE DESGANCHO Y SE REPARO SECUNDARIA | B21091600017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 76 | 2021-09-17 | 608 | keep | 0 | Sep | 2021 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-09-17 15:14 | 2021-09-17 15:15 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210917000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-17 15:14 | 2021-09-17 15:15 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210917000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
SAN JUAN | 2021-09-17 15:22 | 2021-09-17 15:23 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 1615 | keep | 0 | Sep | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2021-09-17 15:29 | 2021-09-17 16:10 | 10 | 000:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21091500107 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 41 | 2021-09-17 | 410 | keep | 0 | Sep | 2021 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-17 15:29 | 2021-09-17 17:50 | 150 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21091700159 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2021-09-17 | 21150 | keep | 0 | Sep | 2021 | 0.014405 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-09-17 15:35 | 2021-09-17 15:36 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 LLEVANDO LA CARGA DEL 1346-04 | S21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 726 | keep | 0 | Sep | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-09-17 15:35 | 2021-09-17 15:36 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 LLEVANDO LA CARGA DEL 1346-04 | S21091700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3932 | keep | 0 | Sep | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
PONCE | 2021-09-17 15:39 | 2021-09-17 15:40 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091700067 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-17 15:39 | 2021-09-17 15:40 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE. SU CARGA ESTA POR EL 5004-06 | P21091700067 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2021-09-17 15:41 | 2021-09-17 18:39 | 80 | 002:58 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21091700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-09-17 | 14240 | keep | 0 | Sep | 2021 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-09-17 16:04 | 2021-09-17 17:06 | 30 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO | R21091700043 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2021-09-17 | 1860 | keep | 0 | Sep | 2021 | 0.0012668 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-09-17 16:06 | 2021-09-17 21:10 | 837 | 005:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO LINEAS PRIMARIAS | R21091700044 | New_Event | Wire Down | Include | Include | Equipment | 304 | 2021-09-17 | 254448 | keep | 0 | Sep | 2021 | 0.1733 | 0.00057008 | Sustained | FALSE | TRUE | Not_TMED_Event | 837
UTUADO | 2021-09-17 16:06 | 2021-09-17 19:35 | 30 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21091700110 | Partial_restoration | Bad Weather | Include | Include | Weather | 209 | 2021-09-17 | 6270 | keep | 0 | Sep | 2021 | 0.0042705 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-17 16:07 | 2021-09-18 19:25 | 15 | 027:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | S21091700089 | New_Event | Cutout Failure | Include | Include | Equipment | 1638 | 2021-09-17 | 24570 | keep | 0 | Sep | 2021 | 0.016735 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-17 16:29 | 2021-09-18 09:49 | 40 | 017:20 | P | NO SE REPORTO CAUSA | 2 X 100 Y 1 X 50 EN CORTES DE LINEAS | B21091700208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1040 | 2021-09-17 | 41600 | keep | 0 | Sep | 2021 | 0.028334 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-17 16:34 | 2021-09-17 17:38 | 25 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21091700116 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-09-17 | 1600 | keep | 0 | Sep | 2021 | 0.0010898 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-17 16:36 | 2021-09-17 16:37 | 3006 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR UN SOLO RECIERRE NO SE REPORTO CAUSA | M21091700170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-17 | 3006 | keep | 0 | Sep | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2021-09-17 16:50 | 2021-09-18 00:20 | 358 | 007:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | P21091700074 | New_Event | Cutout Failure | Include | Include | Equipment | 450 | 2021-09-17 | 161100 | keep | 0 | Sep | 2021 | 0.10972 | 0.00024383 | Sustained | FALSE | TRUE | Not_TMED_Event | 358
BAYAMON | 2021-09-17 16:56 | 2021-09-17 16:57 | 878 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1715-05 PARA HACER OPERACIONES LLEVA 1714-03 Y 1714-02 EN DONDE CERRARON PUENTE ABIERTO Y SE NORMALIZO LA CARGA | B21091700041 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-17 | 878 | keep | 0 | Sep | 2021 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2021-09-17 16:56 | 2021-09-17 16:57 | 455 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1714-05 PARA HACER OPERACIONES LLEVA 1714-03 | B21091700041 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-09-17 | 455 | keep | 0 | Sep | 2021 | 0.0003099 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-17 16:56 | 2021-09-17 16:57 | 878 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1714-05 PARA HACER OPERACIONES LLEVA 1714-03 EN DONDE CERRARON PUENTE ABIERTO | B21091700041 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-17 | 878 | keep | 0 | Sep | 2021 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2021-09-17 17:11 | 2021-09-17 21:05 | 3000 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRO POR SCADA 1806-02 QUE LLEVA PARTE DEL 1717-01 | B21091700232 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-09-17 | 702000 | keep | 0 | Sep | 2021 | 0.47813 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2021-09-17 17:11 | 2021-09-17 21:05 | 4622 | 003:54 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRO POR SCADA LLEVA PARTE DEL 1717-01 | B21091700232 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-09-17 | 1081548 | keep | 0 | Sep | 2021 | 0.73664 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
PONCE | 2021-09-17 17:24 | 2021-09-17 17:25 | 2446 | 000:01 | T | DESGANCHE | RECIERRE | P21091700078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-17 | 2446 | keep | 0 | Sep | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
UTUADO | 2021-09-17 17:24 | 2021-09-17 18:30 | 70 | 001:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPARO BAJANTE PRIMARIO | A21091700123 | New_Event | Wire Down | Include | Include | Equipment | 66 | 2021-09-17 | 4620 | keep | 0 | Sep | 2021 | 0.0031467 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2021-09-17 17:25 | 2021-09-18 13:00 | 1 | 019:35 | P | DESGANCHE | 3 X 200 EN CORTE DE LINEA | P21091700080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1175 | 2021-09-17 | 1175 | keep | 0 | Sep | 2021 | 0.00080029 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-09-17 17:57 | 2021-09-17 20:48 | 12 | 002:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | C21091700119 | New_Event | Wire Down | Include | Include | Equipment | 171 | 2021-09-17 | 2052 | keep | 0 | Sep | 2021 | 0.0013976 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-17 17:58 | 2021-09-17 21:52 | 15 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21091700186 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2021-09-17 | 3510 | keep | 0 | Sep | 2021 | 0.0023906 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-17 18:09 | 2021-09-17 21:10 | 50 | 003:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21091700190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-09-17 | 9050 | keep | 0 | Sep | 2021 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-17 18:10 | 2021-09-17 18:11 | 1712 | 000:01 | T | DESGANCHE | RECIERRE | P21091700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-17 | 1712 | keep | 0 | Sep | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-09-17 18:11 | 2021-09-17 19:20 | 1712 | 001:09 | T | DESGANCHE | SE SACO ARBOL SOBRE LINEA | P210917000XX | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-09-17 | 118128 | keep | 0 | Sep | 2021 | 0.080456 | 0.001166 | Sustained | FALSE | TRUE | Not_TMED_Event | 1712
MAYAGÃœEZ | 2021-09-17 18:11 | 2021-09-17 19:30 | 100 | 001:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21091700191 | New_Event | Wire Down | Include | Include | Equipment | 79 | 2021-09-17 | 7900 | keep | 0 | Sep | 2021 | 0.0053807 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-17 18:17 | 2021-09-18 11:01 | 25 | 016:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21091700192 | New_Event | Bad Weather | Include | Include | Weather | 1004 | 2021-09-17 | 25100 | keep | 0 | Sep | 2021 | 0.017095 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-17 18:20 | 2021-09-18 11:01 | 70 | 016:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091700193 | New_Event | Bad Weather | Include | Include | Weather | 1001 | 2021-09-17 | 70070 | keep | 0 | Sep | 2021 | 0.047724 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-17 18:24 | 2021-09-18 13:27 | 60 | 019:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091700194 | New_Event | Bad Weather | Include | Include | Weather | 1143 | 2021-09-17 | 68580 | keep | 0 | Sep | 2021 | 0.04671 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-17 18:28 | 2021-09-21 11:32 | 18 | 089:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIAS | A21091700135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 5344 | 2021-09-17 | 96192 | keep | 0 | Sep | 2021 | 0.065516 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2021-09-17 18:29 | 2021-09-18 10:14 | 30 | 015:45 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO AVE MUERTA | R21091700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 945 | 2021-09-17 | 28350 | keep | 0 | Sep | 2021 | 0.019309 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-09-17 18:29 | 2021-09-18 10:45 | 10 | 016:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21091700136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 976 | 2021-09-17 | 9760 | keep | 0 | Sep | 2021 | 0.0066475 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-17 18:32 | 2021-09-18 12:09 | 84 | 017:37 | P | DESGANCHE | 1 X 40 Y 1 X 25 EN CORTES DE LINEA | R21091700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1057 | 2021-09-17 | 88788 | keep | 0 | Sep | 2021 | 0.060473 | 5.7212e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 84
PONCE | 2021-09-17 19:20 | 2021-09-17 19:40 | 50 | 000:20 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P210917000XX | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-09-17 | 1000 | keep | 0 | Sep | 2021 | 0.0006811 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-09-17 19:20 | 2021-09-18 13:10 | 300 | 017:50 | P | DESGANCHE | 1 X 140, 3 X 80 Y 3 X 30 EN DISTINTOS CORTES DE LINEA POR DESGANCHE. SE REEMPLAZO CAJA PRIMARIA QUEMADA. | P21091700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1070 | 2021-09-17 | 321000 | keep | 0 | Sep | 2021 | 0.21863 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-09-17 19:22 | 2021-09-17 20:45 | 200 | 001:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | A21091700142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-09-17 | 16600 | keep | 0 | Sep | 2021 | 0.011306 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-17 19:26 | 2021-09-18 16:45 | 1 | 021:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PROLEC 50 KVA 2400 V SERIE-M00F12168 FID-18418543 X 50KVA | M21091700218 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1279 | 2021-09-17 | 1279 | keep | 0 | Sep | 2021 | 0.00087112 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-09-17 19:29 | 2021-09-18 08:34 | 4 | 013:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | R21091700056 | New_Event | Bad Weather | Include | Include | Weather | 785 | 2021-09-17 | 3140 | keep | 0 | Sep | 2021 | 0.0021386 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-09-17 19:30 | 2021-09-18 16:15 | 23 | 020:45 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21091700109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1245 | 2021-09-17 | 28635 | keep | 0 | Sep | 2021 | 0.019503 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
YAUCO | 2021-09-17 19:32 | 2021-09-18 17:50 | 60 | 022:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA. SE REALIZO DESGANCHE Y SE LEVANTO LINEA PRIMARIA DEL PISO | P21091700106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1338 | 2021-09-17 | 80280 | keep | 0 | Sep | 2021 | 0.054678 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-17 20:07 | 2021-09-18 00:24 | 30 | 004:17 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA Y SE ANCLO PRIMARIA DESDE POSTE PARTIDO A POSTE DE ALUMBRADO PROVISIONALMENTE PARA REEMPLAZO DE POSTE MAÃ‘ANA | B21091700311 | New_Event | Defective Pole | Include | Include | Equipment | 257 | 2021-09-17 | 7710 | keep | 0 | Sep | 2021 | 0.0052512 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-17 20:12 | 2021-09-18 16:27 | 15 | 020:15 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21091700314 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1215 | 2021-09-17 | 18225 | keep | 0 | Sep | 2021 | 0.012413 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-17 20:40 | 2021-09-18 10:46 | 102 | 014:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 80 EN CORTE DE LINEA | S21091700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 846 | 2021-09-17 | 86292 | keep | 0 | Sep | 2021 | 0.058773 | 6.9472e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 102
HUMACAO | 2021-09-17 22:31 | 2021-09-18 09:58 | 175 | 011:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN AEREO PROVISIONAL MAL TIEMPO | C21091700133 | New_Event | Bad Weather | Include | Include | Weather | 687 | 2021-09-17 | 120225 | keep | 0 | Sep | 2021 | 0.081885 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2021-09-17 22:39 | 2021-09-18 11:31 | 10 | 012:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21091700239 | New_Event | Bad Weather | Include | Include | Weather | 772 | 2021-09-17 | 7720 | keep | 0 | Sep | 2021 | 0.0052581 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-17 22:54 | 2021-09-18 10:46 | 10 | 011:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21091700136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 712 | 2021-09-17 | 7120 | keep | 0 | Sep | 2021 | 0.0048494 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-17 23:06 | 2021-09-18 10:10 | 100 | 011:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA POR LINEA SAFADA DEL AISLADOR | A21091700156 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 664 | 2021-09-17 | 66400 | keep | 0 | Sep | 2021 | 0.045225 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-17 23:34 | 2021-09-18 17:40 | 61 | 018:06 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21091700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1086 | 2021-09-17 | 66246 | keep | 0 | Sep | 2021 | 0.04512 | 4.1547e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 61
ARECIBO | 2021-09-18 00:17 | 2021-09-18 10:38 | 6 | 010:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR POR MAL TIEMPO | A21091800001 | New_Event | Bad Weather | Include | Include | Weather | 621 | 2021-09-18 | 3726 | keep | 0 | Sep | 2021 | 0.0025378 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-18 00:24 | 2021-09-18 12:38 | 40 | 012:14 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE AVERIADO Y SE RELOCALIZARON AEREOS PROVISIONALES | B21091700311 | Additional_clients | Defective Pole | Include | Include | Equipment | 734 | 2021-09-18 | 29360 | keep | 0 | Sep | 2021 | 0.019997 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-18 01:42 | 2021-09-18 10:46 | 12 | 009:04 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA DESGANCHE | C21091800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 544 | 2021-09-18 | 6528 | keep | 0 | Sep | 2021 | 0.0044462 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-09-18 01:49 | 2021-09-18 12:31 | 5 | 010:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21091800004 | New_Event | Bad Weather | Include | Include | Weather | 642 | 2021-09-18 | 3210 | keep | 0 | Sep | 2021 | 0.0021863 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-09-18 02:06 | 2021-09-18 10:25 | 4 | 008:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | R21091800002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 499 | 2021-09-18 | 1996 | keep | 0 | Sep | 2021 | 0.0013595 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-09-18 02:42 | 2021-09-18 16:15 | 15 | 013:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21091800004 | New_Event | Bad Weather | Include | Include | Weather | 813 | 2021-09-18 | 12195 | keep | 0 | Sep | 2021 | 0.008306 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-18 04:23 | 2021-09-18 04:25 | 2620 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-18 | 5240 | keep | 0 | Sep | 2021 | 0.0035689 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
CAGUAS | 2021-09-18 04:48 | 2021-09-18 04:49 | 2448 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21091800005 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-18 | 2448 | keep | 0 | Sep | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2021-09-18 04:49 | 2021-09-18 17:34 | 682 | 012:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REEMPLAZARON 2 CAJA PRIMARIAS | C21091800006 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 765 | 2021-09-18 | 521730 | keep | 0 | Sep | 2021 | 0.35535 | 0.00046451 | Sustained | FALSE | TRUE | Not_TMED_Event | 682
HUMACAO | 2021-09-18 06:03 | 2021-09-18 06:04 | 2299 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21091800014 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-18 | 2299 | keep | 0 | Sep | 2021 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2021-09-18 06:04 | 2021-09-18 13:30 | 234 | 007:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A LINEA | C21091800017 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 446 | 2021-09-18 | 104364 | keep | 0 | Sep | 2021 | 0.071082 | 0.00015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 234
HUMACAO | 2021-09-18 06:04 | 2021-09-18 10:52 | 59 | 004:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21091800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-09-18 | 16992 | keep | 0 | Sep | 2021 | 0.011573 | 4.0185e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 59
FAJARDO | 2021-09-18 06:09 | 2021-09-18 06:10 | 1234 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21091800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-18 | 1234 | keep | 0 | Sep | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-09-18 06:10 | 2021-09-18 16:09 | 40 | 009:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21091800033 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 599 | 2021-09-18 | 23960 | keep | 0 | Sep | 2021 | 0.016319 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-18 06:25 | 2021-09-18 06:27 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1303-04 | S21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-18 | 3362 | keep | 0 | Sep | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-09-18 06:25 | 2021-09-18 06:27 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA EL 1303-01 Y EL 1346-06 | S21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-18 | 450 | keep | 0 | Sep | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-18 06:25 | 2021-09-18 06:27 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1303-04 | S21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-18 | 3196 | keep | 0 | Sep | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
UTUADO | 2021-09-18 06:31 | 2021-09-18 10:48 | 10 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | A21091800007 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-09-18 | 2570 | keep | 0 | Sep | 2021 | 0.0017504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-18 06:35 | 2021-09-18 17:07 | 7 | 010:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21091800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 632 | 2021-09-18 | 4424 | keep | 0 | Sep | 2021 | 0.0030132 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
ARECIBO | 2021-09-18 06:39 | 2021-09-18 09:20 | 45 | 002:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A21091800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-09-18 | 7245 | keep | 0 | Sep | 2021 | 0.0049345 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-09-18 07:13 | 2021-09-18 10:57 | 30 | 003:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21091800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-09-18 | 6720 | keep | 0 | Sep | 2021 | 0.004577 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-18 07:18 | 2021-09-18 16:40 | 40 | 009:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE SOLTO TESE A NEUTRAL | B21091800005 | New_Event | Wire Down | Include | Include | Equipment | 562 | 2021-09-18 | 22480 | keep | 0 | Sep | 2021 | 0.015311 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-18 07:25 | 2021-09-18 13:17 | 30 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO ABIERTO | B21091800006 | New_Event | Wire Down | Include | Include | Equipment | 352 | 2021-09-18 | 10560 | keep | 0 | Sep | 2021 | 0.0071924 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-18 07:27 | 2021-09-18 07:28 | 1702 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21091800026 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-18 | 1702 | keep | 0 | Sep | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-09-18 07:28 | 2021-09-19 19:34 | 40 | 036:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21091800033 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 2166 | 2021-09-18 | 86640 | keep | 0 | Sep | 2021 | 0.05901 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-09-18 07:31 | 2021-09-18 09:29 | 65 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21091800006 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-09-18 | 7670 | keep | 0 | Sep | 2021 | 0.005224 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-09-18 07:36 | 2021-09-18 07:37 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21091800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
MAYAGÃœEZ | 2021-09-18 07:41 | 2021-09-18 20:47 | 30 | 013:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | M21091800152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 786 | 2021-09-18 | 23580 | keep | 0 | Sep | 2021 | 0.01606 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-18 07:59 | 2021-09-18 12:30 | 5 | 004:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15 KVA X 25 KVA QUEMADO | C21091800032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 271 | 2021-09-18 | 1355 | keep | 0 | Sep | 2021 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-18 08:07 | 2021-09-18 10:26 | 25 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2021-09-18 | 3475 | keep | 0 | Sep | 2021 | 0.0023668 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-09-18 08:07 | 2021-09-18 14:30 | 70 | 006:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21091800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2021-09-18 | 26810 | keep | 0 | Sep | 2021 | 0.01826 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BARRANQUITAS | 2021-09-18 08:11 | 2021-09-18 18:56 | 45 | 010:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21091800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2021-09-18 | 29025 | keep | 0 | Sep | 2021 | 0.019769 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-09-18 08:26 | 2021-09-18 13:28 | 89 | 005:02 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE TRANSFORMADOR TRASPATIO | C21091700172 | New_Event | Service Transformer Failure | Include | Include | Equipment | 302 | 2021-09-18 | 26878 | keep | 0 | Sep | 2021 | 0.018306 | 6.0617e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 89
PONCE | 2021-09-18 09:00 | 2021-09-18 12:35 | 8 | 003:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P210918000XX | New_Event | Cutout Failure | Include | Include | Equipment | 215 | 2021-09-18 | 1720 | keep | 0 | Sep | 2021 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-18 09:01 | 2021-09-18 10:45 | 25 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-09-18 | 2600 | keep | 0 | Sep | 2021 | 0.0017708 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-18 09:08 | 2021-09-18 17:34 | 5 | 008:26 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER, SE DEJO FUERA SUBESTACION DE COW BOY POR PROBLEMA INTERIOR DEL CLIENTE A QUIEN SE LE ORIENTO EN EL LUGAR | B21091800022 | New_Event | UG Cable Fault | Include | Include | Equipment | 506 | 2021-09-18 | 2530 | keep | 0 | Sep | 2021 | 0.0017232 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-18 09:17 | 2021-09-19 17:17 | 2 | 031:60 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21091800021 | New_Event | Bad Weather | Include | Include | Weather | 1920 | 2021-09-18 | 3840 | keep | 0 | Sep | 2021 | 0.0026154 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
AGUADILLA | 2021-09-18 09:20 | 2021-09-18 11:46 | 9 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES EN VARIOS PUNTOS | M21091600038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-09-18 | 1314 | keep | 0 | Sep | 2021 | 0.00089496 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-09-18 09:27 | 2021-09-18 09:58 | 12 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES Y BAJANTE SECUNDARIO | B21091800026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-09-18 | 372 | keep | 0 | Sep | 2021 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-18 09:29 | 2021-09-18 10:46 | 50 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S21091800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-09-18 | 3850 | keep | 0 | Sep | 2021 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-18 09:30 | 2021-09-18 16:53 | 200 | 007:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M21091800063 | New_Event | Wire Down | Include | Include | Equipment | 443 | 2021-09-18 | 88600 | keep | 0 | Sep | 2021 | 0.060345 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-18 09:37 | 2021-09-19 17:53 | 3 | 032:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | B21091800028 | New_Event | Cutout Failure | Include | Include | Equipment | 1936 | 2021-09-18 | 5808 | keep | 0 | Sep | 2021 | 0.0039558 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
VEGA BAJA | 2021-09-18 10:17 | 2021-09-18 19:17 | 30 | 009:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR PRIMARIO | B21091800000 | New_Event | Wire Down | Include | Include | Equipment | 540 | 2021-09-18 | 16200 | keep | 0 | Sep | 2021 | 0.011034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-09-18 10:21 | 2021-09-18 20:05 | 115 | 009:44 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21091800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 584 | 2021-09-18 | 67160 | keep | 0 | Sep | 2021 | 0.045742 | 7.8326e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 115
CAGUAS | 2021-09-18 10:22 | 2021-09-18 12:56 | 15 | 002:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21091800068 | New_Event | Bad Weather | Include | Include | Weather | 154 | 2021-09-18 | 2310 | keep | 0 | Sep | 2021 | 0.0015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-18 10:26 | 2021-09-19 18:15 | 160 | 031:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21091800061 | New_Event | Wire Down | Include | Include | Equipment | 1909 | 2021-09-18 | 305440 | keep | 0 | Sep | 2021 | 0.20803 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2021-09-18 10:38 | 2021-09-18 15:02 | 5191 | 004:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO CARGA TRANSFERIDA AL 9405-05 | B21091800000 | New_Event | Wire Down | Include | Include | Equipment | 264 | 2021-09-18 | 1370424 | keep | 0 | Sep | 2021 | 0.93339 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
CAGUAS | 2021-09-18 10:38 | 2021-09-19 10:42 | 120 | 024:04 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA | C21091800070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1444 | 2021-09-18 | 173280 | keep | 0 | Sep | 2021 | 0.11802 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-09-18 10:38 | 2021-09-18 15:52 | 3511 | 005:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LLEVA LA CARGA DEL 1710-05 | B21091800000 | New_Event | Wire Down | Include | Include | Equipment | 314 | 2021-09-18 | 1102454 | keep | 0 | Sep | 2021 | 0.75088 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
VEGA BAJA | 2021-09-18 11:06 | 2021-09-18 11:27 | 12 | 000:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA RETIRAR PELIGRO DE POSTE SECUNDARIO PARTIDO POR IMPACTO DE VEHICULO | B21091600009 | New_Event |  |  | Include | Wildlife | 21 | 2021-09-18 | 252 | keep | 0 | Sep | 2021 | 0.00017164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-09-18 11:14 | 2021-09-18 15:42 | 22 | 004:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21091800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2021-09-18 | 5896 | keep | 0 | Sep | 2021 | 0.0040157 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
MAYAGÃœEZ | 2021-09-18 11:30 | 2021-09-18 15:00 | 90 | 003:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21091800072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-09-18 | 18900 | keep | 0 | Sep | 2021 | 0.012873 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-09-18 11:35 | 2021-09-19 14:00 | 80 | 026:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21091800029 | New_Event | Bad Weather | Include | Include | Weather | 1585 | 2021-09-18 | 126800 | keep | 0 | Sep | 2021 | 0.086363 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-18 11:43 | 2021-09-18 14:40 | 10 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21091800090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-09-18 | 1770 | keep | 0 | Sep | 2021 | 0.0012055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-18 11:55 | 2021-09-18 15:56 | 100 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 40 AMP EN EL SU - 1 Y 1 X 100 EN CORTE DE LINEA CRUCE POR RATON | R21091800018 | New_Event |  |  | Include | Wildlife | 241 | 2021-09-18 | 24100 | keep | 0 | Sep | 2021 | 0.016414 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-18 11:55 | 2021-09-18 18:15 | 5 | 006:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANFORMADOR DE 25 KVA X 25 KVA AVERIADO | C21091800087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 380 | 2021-09-18 | 1900 | keep | 0 | Sep | 2021 | 0.0012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-18 12:05 | 2021-09-18 19:40 | 100 | 007:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21091800036 | New_Event | Wire Down | Include | Include | Equipment | 455 | 2021-09-18 | 45500 | keep | 0 | Sep | 2021 | 0.03099 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-18 12:26 | 2021-09-18 21:03 | 6 | 008:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21091800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 517 | 2021-09-18 | 3102 | keep | 0 | Sep | 2021 | 0.0021128 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-18 12:34 | 2021-09-19 11:34 | 10 | 023:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN TRANSFORMADOR | B21091800110 | New_Event | Wire Down | Include | Include | Equipment | 1380 | 2021-09-18 | 13800 | keep | 0 | Sep | 2021 | 0.0093991 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-18 12:40 | 2021-09-18 21:08 | 42 | 008:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DIO LIGADURA A CONDUCTOR SAFADO EN AISLADOR | C21091800102 | New_Event | Wire Down | Include | Include | Equipment | 508 | 2021-09-18 | 21336 | keep | 0 | Sep | 2021 | 0.014532 | 2.8606e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 42
BAYAMON | 2021-09-18 12:42 | 2021-09-18 12:43 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTRRUPTOR | B21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 3941 | keep | 0 | Sep | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
SAN JUAN | 2021-09-18 13:15 | 2021-09-18 15:03 | 5 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE Y LINEA SECUNDARIA | R21091800022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2021-09-18 | 540 | keep | 0 | Sep | 2021 | 0.00036779 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-09-18 13:19 | 2021-09-18 17:30 | 70 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21091800094 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2021-09-18 | 17570 | keep | 0 | Sep | 2021 | 0.011967 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-09-18 13:23 | 2021-09-18 13:24 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210918000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 1712 | keep | 0 | Sep | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
CAGUAS | 2021-09-18 13:28 | 2021-09-19 14:36 | 30 | 025:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN CORTE DE LINEA REPARO SECUNDARIA | C21091800108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1508 | 2021-09-18 | 45240 | keep | 0 | Sep | 2021 | 0.030813 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-18 13:41 | 2021-09-18 13:42 | 2468 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 2468 | keep | 0 | Sep | 2021 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2021-09-18 13:42 | 2021-09-18 18:49 | 80 | 005:07 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21091800014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 307 | 2021-09-18 | 24560 | keep | 0 | Sep | 2021 | 0.016728 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-18 13:55 | 2021-09-18 15:14 | 1633 | 001:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A21091800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-18 | 129007 | keep | 0 | Sep | 2021 | 0.087866 | 0.0011122 | Sustained | FALSE | TRUE | Not_TMED_Event | 1633
UTUADO | 2021-09-18 13:55 | 2021-09-18 15:14 | 1624 | 001:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A21091800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-18 | 128296 | keep | 0 | Sep | 2021 | 0.087382 | 0.0011061 | Sustained | FALSE | TRUE | Not_TMED_Event | 1624
BAYAMON | 2021-09-18 13:57 | 2021-09-18 15:17 | 15 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21091700027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-09-18 | 1200 | keep | 0 | Sep | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-18 14:13 | 2021-09-18 14:14 | 473 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21091800119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 473 | keep | 0 | Sep | 2021 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
HUMACAO | 2021-09-18 14:30 | 2021-09-18 14:31 | 2450 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | C21091800122 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-18 | 2450 | keep | 0 | Sep | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-09-18 14:31 | 2021-09-18 16:45 | 158 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21091800124 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 134 | 2021-09-18 | 21172 | keep | 0 | Sep | 2021 | 0.01442 | 0.00010761 | Sustained | FALSE | TRUE | Not_TMED_Event | 158
PONCE | 2021-09-18 14:32 | 2021-09-18 14:33 | 23 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 900 | P210918000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-18 | 23 | keep | 0 | Sep | 2021 | 1.5665e-05 | 1.5665e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 23
PONCE | 2021-09-18 14:32 | 2021-09-18 14:33 | 969 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 900 | P210918000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-18 | 969 | keep | 0 | Sep | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | TRUE | Not_TMED_Event | 969
PONCE | 2021-09-18 14:32 | 2021-09-18 14:33 | 1712 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 900 | P210918000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-18 | 1712 | keep | 0 | Sep | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | TRUE | Not_TMED_Event | 1712
PONCE | 2021-09-18 14:32 | 2021-09-18 14:33 | 18 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 900 | P210918000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-18 | 18 | keep | 0 | Sep | 2021 | 1.226e-05 | 1.226e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 18
PONCE | 2021-09-18 14:32 | 2021-09-18 14:33 | 494 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 900 | P210918000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-18 | 494 | keep | 0 | Sep | 2021 | 0.00033646 | 0.00033646 | Momentary | FALSE | TRUE | Not_TMED_Event | 494
PONCE | 2021-09-18 14:33 | 2021-09-18 19:13 | 6 | 004:40 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | P21091800056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-09-18 | 1680 | keep | 0 | Sep | 2021 | 0.0011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-09-18 14:43 | 2021-09-18 17:17 | 64 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA, AVE CRUZO FASE | P21091800038 | New_Event |  |  | Include | Wildlife | 154 | 2021-09-18 | 9856 | keep | 0 | Sep | 2021 | 0.0067129 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
BAYAMON | 2021-09-18 15:02 | 2021-09-18 15:57 | 2500 | 000:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TRANSFIRIO CARGA AL 1718-03 POR PUENTE PRIMARIO AVERIADO | B21091800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 55 | 2021-09-18 | 137500 | keep | 0 | Sep | 2021 | 0.093651 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-18 15:28 | 2021-09-18 15:29 | 1131 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 1131 | keep | 0 | Sep | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
YAUCO | 2021-09-18 15:31 | 2021-09-19 09:25 | 45 | 017:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P21091800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1074 | 2021-09-18 | 48330 | keep | 0 | Sep | 2021 | 0.032917 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-18 16:11 | 2021-09-18 17:39 | 15 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21091700053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-09-18 | 1320 | keep | 0 | Sep | 2021 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-18 16:13 | 2021-09-18 17:27 | 1952 | 001:14 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. NO SE REPORTO LA CAUSA | P21091800048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2021-09-18 | 144448 | keep | 0 | Sep | 2021 | 0.098383 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
CANOVANAS | 2021-09-18 16:15 | 2021-09-18 18:31 | 80 | 002:16 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHO Y REEMPLAZO 2 CAJAS AVERIADAS | R21091800035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-09-18 | 10880 | keep | 0 | Sep | 2021 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-18 16:24 | 2021-09-19 14:38 | 98 | 022:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 Y 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE | S21091800046 | New_Event | Wire Down | Include | Include | Equipment | 1334 | 2021-09-18 | 130732 | keep | 0 | Sep | 2021 | 0.089041 | 6.6747e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 98
BAYAMON | 2021-09-18 16:26 | 2021-09-18 17:57 | 75 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 50 EN CORTE DE LINEA DIFERENTES | B21091800187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-09-18 | 6825 | keep | 0 | Sep | 2021 | 0.0046485 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
GUAYAMA | 2021-09-18 16:27 | 2021-09-18 21:45 | 250 | 005:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P21091800050 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2021-09-18 | 79500 | keep | 0 | Sep | 2021 | 0.054147 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-09-18 16:42 | 2021-09-18 16:44 | 870 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-18 | 1740 | keep | 0 | Sep | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2021-09-18 16:42 | 2021-09-19 09:21 | 200 | 016:39 | P | HERRAJE ROTO O PODRIDO | 1 X 80 EN CORTE DE LINEA REMPLAZO CRUCETA | A21091800065 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 999 | 2021-09-18 | 199800 | keep | 0 | Sep | 2021 | 0.13608 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-18 17:00 | 2021-09-18 20:45 | 85 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE | M21091800139 | New_Event |  |  | Include | Wildlife | 225 | 2021-09-18 | 19125 | keep | 0 | Sep | 2021 | 0.013026 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
SAN JUAN | 2021-09-18 17:09 | 2021-09-19 13:52 | 24 | 020:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21091800051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1243 | 2021-09-18 | 29832 | keep | 0 | Sep | 2021 | 0.020318 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
SAN JUAN | 2021-09-18 17:09 | 2021-09-20 22:34 | 4 | 053:25 | P | OTRAS CAUSAS | SE CERRARON MACHETES EN SU HACIA PISO 11 CLIENTE TRAJO SMU4 YA QUE ES PRIVADO | S21091800051 | New_Event | Other Causes | Include | Include | Other | 3205 | 2021-09-18 | 12820 | keep | 0 | Sep | 2021 | 0.0087316 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-09-18 17:10 | 2021-09-19 10:28 | 14 | 017:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE CON AVE | C21091800137 | New_Event |  |  | Include | Wildlife | 1038 | 2021-09-18 | 14532 | keep | 0 | Sep | 2021 | 0.0098977 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-09-18 17:17 | 2021-09-18 20:18 | 50 | 003:01 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN RISER, SE SECCIONALIZO EN T-15 AVERIADO | B21091800189 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2021-09-18 | 9050 | keep | 0 | Sep | 2021 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2021-09-18 17:30 | 2021-09-18 17:31 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
CAGUAS | 2021-09-18 17:34 | 2021-09-18 19:42 | 262 | 002:08 | P | DESCONECTIVO DEFECTUOSO | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO MACHETE QUEMADO EN RISER Y CAJA QUEMADA | C21091800134 | New_Event | Switch Failure | Include | Include | Equipment | 128 | 2021-09-18 | 33536 | keep | 0 | Sep | 2021 | 0.022841 | 0.00017845 | Sustained | FALSE | TRUE | Not_TMED_Event | 262
YAUCO | 2021-09-18 17:48 | 2021-09-19 10:19 | 159 | 016:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21091800071 | New_Event |  |  | Include | Wildlife | 991 | 2021-09-18 | 157569 | keep | 0 | Sep | 2021 | 0.10732 | 0.00010829 | Sustained | FALSE | TRUE | Not_TMED_Event | 159
YAUCO | 2021-09-18 17:48 | 2021-09-19 09:23 | 15 | 015:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA. | P21091800060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 935 | 2021-09-18 | 14025 | keep | 0 | Sep | 2021 | 0.0095524 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
PONCE | 2021-09-18 17:55 | 2021-09-19 10:33 | 456 | 016:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO PORTA FUSIBLE | P21091800062 | New_Event | Cutout Failure | Include | Include | Equipment | 998 | 2021-09-18 | 455088 | keep | 0 | Sep | 2021 | 0.30996 | 0.00031058 | Sustained | FALSE | TRUE | Not_TMED_Event | 456
PONCE | 2021-09-18 17:55 | 2021-09-19 10:33 | 456 | 016:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 CORTE DE LINEA | P21091800062 | New_Event | Cutout Failure | Include | Include | Equipment | 998 | 2021-09-18 | 455088 | keep | 0 | Sep | 2021 | 0.30996 | 0.00031058 | Sustained | FALSE | TRUE | Not_TMED_Event | 456
HUMACAO | 2021-09-18 18:04 | 2021-09-18 19:40 | 327 | 001:36 | S | NO SE REPORTO CAUSA | SUBESTACION SE FUE A LOCK OUT, SE INSPECCIONO Y NO SE ENCONTRO NADA. EL ING. LUIS MIRANDA AUTORIZO A ENERGIZAR | C21091800145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-09-18 | 31392 | keep | 0 | Sep | 2021 | 0.021381 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2021-09-18 18:04 | 2021-09-18 19:40 | 5630 | 001:36 | S | NO SE REPORTO CAUSA | SUBESTACION SE FUE A LOCK OUT, SE INSPECCIONO Y NO SE ENCONTRO NADA. EL ING. LUIS MIRANDA AUTORIZO A ENERGIZAR | C21091800145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-09-18 | 540480 | keep | 0 | Sep | 2021 | 0.36812 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-09-18 18:04 | 2021-09-18 19:40 | 2126 | 001:36 | S | NO SE REPORTO CAUSA | SUBESTACION SE FUE A LOCK OUT, SE INSPECCIONO Y NO SE ENCONTRO NADA. EL ING. LUIS MIRANDA AUTORIZO A ENERGIZAR | C21091800145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-09-18 | 204096 | keep | 0 | Sep | 2021 | 0.13901 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-09-18 18:04 | 2021-09-18 19:40 | 551 | 001:36 | S | NO SE REPORTO CAUSA | SUBESTACION SE FUE A LOCK OUT, SE INSPECCIONO Y NO SE ENCONTRO NADA. EL ING. LUIS MIRANDA AUTORIZO A ENERGIZAR | C21091800145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-09-18 | 52896 | keep | 0 | Sep | 2021 | 0.036027 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
CAGUAS | 2021-09-18 18:38 | 2021-09-18 22:03 | 260 | 003:25 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO CAUSA | C21091800172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-09-18 | 53300 | keep | 0 | Sep | 2021 | 0.036302 | 0.00017708 | Sustained | FALSE | TRUE | Not_TMED_Event | 260
FAJARDO | 2021-09-18 19:13 | 2021-09-18 19:14 | 1394 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21091800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-18 | 1394 | keep | 0 | Sep | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2021-09-18 19:14 | 2021-09-19 09:43 | 88 | 014:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | R21091800042 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 869 | 2021-09-18 | 76472 | keep | 0 | Sep | 2021 | 0.052085 | 5.9936e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 88
VEGA BAJA | 2021-09-18 19:17 | 2021-09-18 20:44 | 2216 | 001:27 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO | B21091800000 | Additional_clients | Wire Down | Include | Include | Equipment | 87 | 2021-09-18 | 192792 | keep | 0 | Sep | 2021 | 0.13131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-18 19:24 | 2021-09-19 01:05 | 60 | 005:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21091800155 | New_Event | Bad Weather | Include | Include | Weather | 341 | 2021-09-18 | 20460 | keep | 0 | Sep | 2021 | 0.013935 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-18 19:26 | 2021-09-20 22:35 | 45 | 051:09 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN CORTE DE LINEA SE CONSTRUYO PROVICIONAL AEREO | C21091800198 | New_Event | UG Cable Fault | Include | Include | Equipment | 3069 | 2021-09-18 | 138105 | keep | 0 | Sep | 2021 | 0.094063 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BARRANQUITAS | 2021-09-18 19:59 | 2021-09-19 14:01 | 40 | 018:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21091800206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1082 | 2021-09-18 | 43280 | keep | 0 | Sep | 2021 | 0.029478 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-18 20:04 | 2021-09-18 22:09 | 15 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21091800059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-09-18 | 1875 | keep | 0 | Sep | 2021 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-18 20:18 | 2021-09-19 19:46 | 30 | 023:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-15 AVERIADO DE 75KVA POR 75KVA A 13KV | B21091900010 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1408 | 2021-09-18 | 42240 | keep | 0 | Sep | 2021 | 0.028769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-18 22:22 | 2021-09-18 22:23 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-18 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-09-18 23:09 | 2021-09-19 12:30 | 30 | 013:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LIENEA SE RETIRO RAMA | M21091800175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 801 | 2021-09-18 | 24030 | keep | 0 | Sep | 2021 | 0.016367 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-09-18 23:26 | 2021-09-19 13:00 | 100 | 013:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21091800215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 814 | 2021-09-18 | 81400 | keep | 0 | Sep | 2021 | 0.055441 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-19 01:27 | 2021-09-19 01:42 | 3006 | 000:15 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21091900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-09-19 | 45090 | keep | 0 | Sep | 2021 | 0.030711 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
UTUADO | 2021-09-19 02:26 | 2021-09-19 15:23 | 20 | 012:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21091900001 | New_Event | Bad Weather | Include | Include | Weather | 777 | 2021-09-19 | 15540 | keep | 0 | Sep | 2021 | 0.010584 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-09-19 02:26 | 2021-09-19 13:24 | 1 | 010:58 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | A21091900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 658 | 2021-09-19 | 658 | keep | 0 | Sep | 2021 | 0.00044816 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-19 04:05 | 2021-09-19 04:06 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 1681 | keep | 0 | Sep | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-09-19 04:05 | 2021-09-19 04:06 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 1598 | keep | 0 | Sep | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-09-19 04:44 | 2021-09-19 14:15 | 158 | 009:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21091900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 571 | 2021-09-19 | 90218 | keep | 0 | Sep | 2021 | 0.061447 | 0.00010761 | Sustained | FALSE | TRUE | Not_TMED_Event | 158
MAYAGÃœEZ | 2021-09-19 05:00 | 2021-09-19 10:30 | 200 | 005:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M21091900035 | New_Event | Cutout Failure | Include | Include | Equipment | 330 | 2021-09-19 | 66000 | keep | 0 | Sep | 2021 | 0.044952 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-19 05:42 | 2021-09-19 10:56 | 1 | 005:14 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21091900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-09-19 | 314 | keep | 0 | Sep | 2021 | 0.00021386 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-19 06:17 | 2021-09-19 06:18 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 9101 02 SPARE | B21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 1494 | keep | 0 | Sep | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2021-09-19 06:24 | 2021-09-19 14:23 | 22 | 007:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO PUENTE DE LINEA A CAJA | R21091900002 | New_Event | Wire Down | Include | Include | Equipment | 479 | 2021-09-19 | 10538 | keep | 0 | Sep | 2021 | 0.0071774 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
SAN JUAN | 2021-09-19 06:40 | 2021-09-19 08:34 | 79 | 001:54 | T | CABLE SOTERRADO AVERIADO | SE TRANSFIRIO LA CARGA AL 1416-05 POR CABLE DE SALIDA AVERIADO | S21091900009 | New_Event | UG Cable Fault | Include | Include | Equipment | 114 | 2021-09-19 | 9006 | keep | 0 | Sep | 2021 | 0.0061339 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2021-09-19 07:30 | 2021-09-19 12:49 | 175 | 005:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21091900006 | New_Event |  |  | Include | Wildlife | 319 | 2021-09-19 | 55825 | keep | 0 | Sep | 2021 | 0.038022 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
MAYAGÃœEZ | 2021-09-19 07:34 | 2021-09-19 09:24 | 35 | 001:50 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21091900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-09-19 | 3850 | keep | 0 | Sep | 2021 | 0.0026222 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-19 07:41 | 2021-09-19 07:42 | 2379 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | P21091900007 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-19 | 2379 | keep | 0 | Sep | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-09-19 07:42 | 2021-09-19 15:46 | 176 | 008:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P21091900015 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 484 | 2021-09-19 | 85184 | keep | 0 | Sep | 2021 | 0.058018 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
SAN JUAN | 2021-09-19 07:49 | 2021-09-19 20:42 | 90 | 012:53 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN CORTE DE LINEA CONTAMINACION | R21091900011 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 773 | 2021-09-19 | 69570 | keep | 0 | Sep | 2021 | 0.047384 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CANOVANAS | 2021-09-19 08:14 | 2021-09-19 09:35 | 1 | 001:21 | P | OTRAS CAUSAS | 1 X 30 EN RISER Y 1 X 20 EN TRANSCLOSURE QUE NECESITA MANTENIMIENTO | R21091900012 | New_Event | Other Causes | Include | Include | Other | 81 | 2021-09-19 | 81 | keep | 0 | Sep | 2021 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-09-19 08:14 | 2021-09-19 08:15 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
ARECIBO | 2021-09-19 08:15 | 2021-09-19 11:37 | 30 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 40 EN CORTE DE LINEA PALOMA CRUZO LINEAS | A21091900007 | New_Event |  |  | Include | Wildlife | 202 | 2021-09-19 | 6060 | keep | 0 | Sep | 2021 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-19 08:24 | 2021-09-19 11:05 | 10 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21091900008 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2021-09-19 | 1610 | keep | 0 | Sep | 2021 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-19 08:28 | 2021-09-19 08:45 | 20 | 000:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21091800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2021-09-19 | 340 | keep | 0 | Sep | 2021 | 0.00023157 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-19 08:45 | 2021-09-19 09:00 | 8 | 000:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO PUENTE SAFADO EN TRANSFORMADOR | P21091900004 | New_Event | Wire Down | Include | Include | Equipment | 15 | 2021-09-19 | 120 | keep | 0 | Sep | 2021 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-19 08:46 | 2021-09-19 11:18 | 184 | 002:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | R21091900017 | New_Event |  |  | Include | Wildlife | 152 | 2021-09-19 | 27968 | keep | 0 | Sep | 2021 | 0.019049 | 0.00012532 | Sustained | FALSE | TRUE | Not_TMED_Event | 184
BAYAMON | 2021-09-19 08:55 | 2021-09-19 08:56 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 2617 | keep | 0 | Sep | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
ARECIBO | 2021-09-19 08:55 | 2021-09-20 10:50 | 50 | 025:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091900042 | New_Event | Bad Weather | Include | Include | Weather | 1555 | 2021-09-19 | 77750 | keep | 0 | Sep | 2021 | 0.052955 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-19 09:15 | 2021-09-19 15:49 | 7 | 006:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R21091900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2021-09-19 | 2758 | keep | 0 | Sep | 2021 | 0.0018785 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-09-19 09:18 | 2021-09-19 13:13 | 30 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2021-09-19 | 7050 | keep | 0 | Sep | 2021 | 0.0048017 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-19 09:26 | 2021-09-19 10:43 | 12 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE SECUNDARIO | B21091700531 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-09-19 | 924 | keep | 0 | Sep | 2021 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-19 09:34 | 2021-09-19 09:35 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
UTUADO | 2021-09-19 09:41 | 2021-09-19 11:39 | 20 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21091900016 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-09-19 | 2360 | keep | 0 | Sep | 2021 | 0.0016074 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-19 09:45 | 2021-09-19 16:55 | 2253 | 007:10 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PARTIDO | P21091900013 | New_Event | Defective Pole | Include | Include | Equipment | 430 | 2021-09-19 | 968790 | keep | 0 | Sep | 2021 | 0.65984 | 0.0015345 | Sustained | FALSE | FALSE | Not_TMED_Event | 2253
ARECIBO | 2021-09-19 09:45 | 2021-09-19 15:45 | 30 | 006:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21091900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2021-09-19 | 10800 | keep | 0 | Sep | 2021 | 0.0073558 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-19 09:55 | 2021-09-19 13:39 | 26 | 003:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21091900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-09-19 | 5824 | keep | 0 | Sep | 2021 | 0.0039667 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
CANOVANAS | 2021-09-19 09:56 | 2021-09-19 12:46 | 14 | 002:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REEMPLAZAR SECUNDARIA | R21091900021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 170 | 2021-09-19 | 2380 | keep | 0 | Sep | 2021 | 0.001621 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2021-09-19 09:59 | 2021-09-19 12:39 | 12 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIAS EN MAL ESTADO | A21091800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-09-19 | 1920 | keep | 0 | Sep | 2021 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-09-19 10:48 | 2021-09-19 10:49 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 2216 | keep | 0 | Sep | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
CAGUAS | 2021-09-19 10:57 | 2021-09-19 12:57 | 4 | 002:00 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR | C21091900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-09-19 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-09-19 11:08 | 2021-09-19 11:15 | 215 | 000:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | MANTA MOJADA OCASIONO ARCO DE CORRIENTE DISPARANDO EL ALIMENTADOR | P210919000XX | New_Event |  |  | Include | Wildlife | 7 | 2021-09-19 | 1505 | keep | 0 | Sep | 2021 | 0.001025 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-09-19 11:26 | 2021-09-19 11:38 | 10 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B21091900002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2021-09-19 | 120 | keep | 0 | Sep | 2021 | 8.1731e-05 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-19 11:54 | 2021-09-19 20:30 | 60 | 008:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21091900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2021-09-19 | 30960 | keep | 0 | Sep | 2021 | 0.021087 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-19 11:54 | 2021-09-19 12:45 | 1 | 000:51 | P | OTRAS CAUSAS | 2 X 20 EN BANCO DE TRANSFORMADOR PROBLEMA DEL CLIENTE | C21091900010 | New_Event | Other Causes | Include | Include | Other | 51 | 2021-09-19 | 51 | keep | 0 | Sep | 2021 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-19 11:58 | 2021-09-19 12:41 | 10 | 000:43 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA CONECTAR TOMA PARA SERVICIO NUEVO | B21091500132 | New_Event | Other Causes | Include | Include | Other | 43 | 2021-09-19 | 430 | keep | 0 | Sep | 2021 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-19 12:42 | 2021-09-19 18:41 | 50 | 005:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21091900013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2021-09-19 | 17950 | keep | 0 | Sep | 2021 | 0.012226 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-19 12:44 | 2021-09-19 17:15 | 1 | 004:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER DESCARGAS ELECTRICAS | M21091900074 | New_Event | Bad Weather | Include | Include | Weather | 271 | 2021-09-19 | 271 | keep | 0 | Sep | 2021 | 0.00018458 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-19 12:49 | 2021-09-19 15:30 | 12 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA CRUCE POR ALAMBRE | R21091900030 | New_Event | Wire Down | Include | Include | Equipment | 161 | 2021-09-19 | 1932 | keep | 0 | Sep | 2021 | 0.0013159 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-19 13:07 | 2021-09-19 18:40 | 6 | 005:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21091900078 | New_Event | Bad Weather | Include | Include | Weather | 333 | 2021-09-19 | 1998 | keep | 0 | Sep | 2021 | 0.0013608 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-19 13:14 | 2021-09-19 13:15 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 4634 | keep | 0 | Sep | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2021-09-19 13:20 | 2021-09-20 19:00 | 15 | 029:40 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE 35 PIES METAL | M21091900082 | New_Event | Defective Pole | Include | Include | Equipment | 1780 | 2021-09-19 | 26700 | keep | 0 | Sep | 2021 | 0.018185 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-19 13:36 | 2021-09-19 16:30 | 40 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A21091900030 | New_Event | Wire Down | Include | Include | Equipment | 174 | 2021-09-19 | 6960 | keep | 0 | Sep | 2021 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-09-19 13:51 | 2021-09-19 17:59 | 2 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21091900031 | New_Event | Bad Weather | Include | Include | Weather | 248 | 2021-09-19 | 496 | keep | 0 | Sep | 2021 | 0.00033782 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-09-19 13:57 | 2021-09-19 16:51 | 281 | 002:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 48894 | keep | 0 | Sep | 2021 | 0.033301 | 0.00019139 | Sustained | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-19 13:57 | 2021-09-19 16:51 | 1252 | 002:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 217848 | keep | 0 | Sep | 2021 | 0.14838 | 0.00085273 | Sustained | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-09-19 13:57 | 2021-09-19 16:51 | 595 | 002:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 103530 | keep | 0 | Sep | 2021 | 0.070514 | 0.00040525 | Sustained | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-09-19 13:57 | 2021-09-19 16:51 | 51 | 002:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 8874 | keep | 0 | Sep | 2021 | 0.006044 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-09-19 13:57 | 2021-09-19 16:51 | 721 | 002:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 125454 | keep | 0 | Sep | 2021 | 0.085446 | 0.00049107 | Sustained | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-09-19 13:57 | 2021-09-19 16:51 | 1382 | 002:54 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 240468 | keep | 0 | Sep | 2021 | 0.16378 | 0.00094127 | Sustained | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-19 13:57 | 2021-09-19 16:51 | 654 | 002:54 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21091900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2021-09-19 | 113796 | keep | 0 | Sep | 2021 | 0.077506 | 0.00044544 | Sustained | FALSE | TRUE | Not_TMED_Event | 654
BARRANQUITAS | 2021-09-19 14:10 | 2021-09-20 10:56 | 30 | 020:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21091900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1246 | 2021-09-19 | 37380 | keep | 0 | Sep | 2021 | 0.025459 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-19 14:21 | 2021-09-19 14:22 | 828 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
AGUADILLA | 2021-09-19 14:23 | 2021-09-19 18:15 | 50 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091900155 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2021-09-19 | 11600 | keep | 0 | Sep | 2021 | 0.0079007 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-19 14:31 | 2021-09-19 18:00 | 6 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21091900097 | New_Event | Bad Weather | Include | Include | Weather | 209 | 2021-09-19 | 1254 | keep | 0 | Sep | 2021 | 0.00085409 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-09-19 14:36 | 2021-09-19 17:37 | 18 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | A21091900039 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-09-19 | 3258 | keep | 0 | Sep | 2021 | 0.002219 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2021-09-19 14:37 | 2021-09-19 22:38 | 25 | 008:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO SAFADO | M21091900099 | New_Event | Wire Down | Include | Include | Equipment | 481 | 2021-09-19 | 12025 | keep | 0 | Sep | 2021 | 0.0081902 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-19 14:43 | 2021-09-19 17:14 | 80 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE DESCRUZO LINEA | B21091900035 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2021-09-19 | 12080 | keep | 0 | Sep | 2021 | 0.0082276 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-19 14:52 | 2021-09-20 12:16 | 75 | 021:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A21091900046 | New_Event | Wire Down | Include | Include | Equipment | 1284 | 2021-09-19 | 96300 | keep | 0 | Sep | 2021 | 0.065589 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-19 14:56 | 2021-09-20 11:15 | 50 | 020:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21091900049 | New_Event | Wire Down | Include | Include | Equipment | 1219 | 2021-09-19 | 60950 | keep | 0 | Sep | 2021 | 0.041513 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-19 15:21 | 2021-09-19 17:00 | 3147 | 001:39 | T | MAL TIEMPO/RAYOS/WET ASH | INFORMA JORGE TROCHE QUE HUBO MAL TIEMPO EN EL AREA | M21091900113 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-09-19 | 311553 | keep | 0 | Sep | 2021 | 0.2122 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-09-19 15:42 | 2021-09-19 15:43 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
UTUADO | 2021-09-19 15:47 | 2021-09-20 10:10 | 45 | 018:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21091900058 | New_Event | Bad Weather | Include | Include | Weather | 1103 | 2021-09-19 | 49635 | keep | 0 | Sep | 2021 | 0.033806 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-19 16:01 | 2021-09-19 16:09 | 50 | 000:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21091900040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-09-19 | 400 | keep | 0 | Sep | 2021 | 0.00027244 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-19 16:01 | 2021-09-19 16:02 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21091900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
PONCE | 2021-09-19 16:45 | 2021-09-19 17:50 | 8 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONEXIONES EN EL PEDESTAL | P21091900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-09-19 | 520 | keep | 0 | Sep | 2021 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-09-19 16:50 | 2021-09-19 19:20 | 78 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | P21091900026 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2021-09-19 | 11700 | keep | 0 | Sep | 2021 | 0.0079688 | 5.3125e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 78
UTUADO | 2021-09-19 17:08 | 2021-09-22 11:09 | 150 | 066:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA AVERIADA | A21092000119 | New_Event | Wire Down | Include | Include | Equipment | 3961 | 2021-09-19 | 594150 | keep | 0 | Sep | 2021 | 0.40467 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-09-19 17:16 | 2021-09-19 18:02 | 140 | 000:46 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | P21091900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-09-19 | 6440 | keep | 0 | Sep | 2021 | 0.0043863 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
MAYAGÃœEZ | 2021-09-19 17:46 | 2021-09-19 18:25 | 50 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21091900150 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-09-19 | 1950 | keep | 0 | Sep | 2021 | 0.0013281 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-19 17:53 | 2021-09-20 09:13 | 10 | 015:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21091900069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2021-09-19 | 9200 | keep | 0 | Sep | 2021 | 0.0062661 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-09-19 18:27 | 2021-09-20 11:45 | 114 | 017:18 | P | DESGANCHE | 1 X 100 EN RISER Y 2 X 50 EN SU-13 | C21091900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1038 | 2021-09-19 | 118332 | keep | 0 | Sep | 2021 | 0.080595 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
MAYAGÃœEZ | 2021-09-19 18:55 | 2021-09-20 12:27 | 50 | 017:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21091900163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1052 | 2021-09-19 | 52600 | keep | 0 | Sep | 2021 | 0.035826 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-19 18:59 | 2021-09-19 22:36 | 120 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21091900167 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2021-09-19 | 26040 | keep | 0 | Sep | 2021 | 0.017736 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
CAGUAS | 2021-09-19 19:23 | 2021-09-20 15:13 | 10 | 019:50 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO SE PASO LA CARGA A TRANSFORMADOR CERCANO DE 50 KVA | C21091900043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1190 | 2021-09-19 | 11900 | keep | 0 | Sep | 2021 | 0.008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-19 19:31 | 2021-09-19 19:32 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2021-09-19 19:38 | 2021-09-19 19:39 | 1854 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21091900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 1854 | keep | 0 | Sep | 2021 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
MAYAGÃœEZ | 2021-09-19 19:48 | 2021-09-20 09:49 | 200 | 014:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR PAJARO | M21091900184 | New_Event |  |  | Include | Wildlife | 841 | 2021-09-19 | 168200 | keep | 0 | Sep | 2021 | 0.11456 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-19 19:53 | 2021-09-19 19:54 | 2658 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M21091900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-19 | 2658 | keep | 0 | Sep | 2021 | 0.0018104 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
BARRANQUITAS | 2021-09-19 19:54 | 2021-09-20 15:52 | 1 | 019:58 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR ENREDADERA | C21091900047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1198 | 2021-09-19 | 1198 | keep | 0 | Sep | 2021 | 0.00081595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-09-19 19:56 | 2021-09-19 19:57 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 752 | keep | 0 | Sep | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-09-19 19:56 | 2021-09-19 19:57 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21091900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 2696 | keep | 0 | Sep | 2021 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
MAYAGÃœEZ | 2021-09-19 20:02 | 2021-09-19 20:03 | 2658 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M21091900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-19 | 2658 | keep | 0 | Sep | 2021 | 0.0018104 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
BAYAMON | 2021-09-19 20:10 | 2021-09-21 17:56 | 20 | 045:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM 1 AVERIADO 37.5KVA POR 37.5KVA A 13KV | B21091900049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2746 | 2021-09-19 | 54920 | keep | 0 | Sep | 2021 | 0.037406 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-19 20:15 | 2021-09-19 22:15 | 2658 | 002:00 | T | DESGANCHE | DISPARO DE INTERRUPTOR | M21091900196 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-09-19 | 318960 | keep | 0 | Sep | 2021 | 0.21724 | 0.0018104 | Sustained | FALSE | FALSE | Not_TMED_Event | 2658
MAYAGÃœEZ | 2021-09-19 21:05 | 2021-09-20 12:41 | 100 | 015:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO BAJANTE | M20919000208 | New_Event | Wire Down | Include | Include | Equipment | 936 | 2021-09-19 | 93600 | keep | 0 | Sep | 2021 | 0.063751 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-19 22:11 | 2021-09-20 15:55 | 10 | 017:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | M21091900218 | New_Event | Bad Weather | Include | Include | Weather | 1064 | 2021-09-19 | 10640 | keep | 0 | Sep | 2021 | 0.0072469 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-19 22:27 | 2021-09-20 11:16 | 80 | 012:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21091900056 | New_Event |  |  | Include | Wildlife | 769 | 2021-09-19 | 61520 | keep | 0 | Sep | 2021 | 0.041901 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-19 22:28 | 2021-09-19 23:05 | 2658 | 000:37 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR DESGANCHE SE SECCIONALIZO | M21091900221 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-09-19 | 98346 | keep | 0 | Sep | 2021 | 0.066983 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-19 22:40 | 2021-09-20 12:26 | 60 | 013:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21091900222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 826 | 2021-09-19 | 49560 | keep | 0 | Sep | 2021 | 0.033755 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-19 23:07 | 2021-09-20 11:05 | 80 | 011:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | M21092000224 | New_Event | Bad Weather | Include | Include | Weather | 718 | 2021-09-19 | 57440 | keep | 0 | Sep | 2021 | 0.039122 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-19 23:07 | 2021-09-19 23:08 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21091900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-19 | 1227 | keep | 0 | Sep | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2021-09-19 23:39 | 2021-09-20 11:00 | 20 | 011:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN CORTE DE LINEA | S21091900034 | New_Event | Wire Down | Include | Include | Equipment | 681 | 2021-09-19 | 13620 | keep | 0 | Sep | 2021 | 0.0092765 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-19 23:46 | 2021-09-19 23:48 | 2888 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21091900088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-19 | 5776 | keep | 0 | Sep | 2021 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
SAN JUAN | 2021-09-20 00:03 | 2021-09-20 10:33 | 40 | 010:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21092000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 630 | 2021-09-20 | 25200 | keep | 0 | Sep | 2021 | 0.017164 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-20 01:05 | 2021-09-20 05:08 | 3316 | 004:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE SIGUE PATRULLANDO | A21092000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2021-09-20 | 805788 | keep | 0 | Sep | 2021 | 0.54882 | 0.0022585 | Sustained | FALSE | FALSE | Not_TMED_Event | 3316
BAYAMON | 2021-09-20 01:31 | 2021-09-20 01:32 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 2617 | keep | 0 | Sep | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
ARECIBO | 2021-09-20 01:34 | 2021-09-20 10:23 | 20 | 008:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21092000003 | New_Event | Cutout Failure | Include | Include | Equipment | 529 | 2021-09-20 | 10580 | keep | 0 | Sep | 2021 | 0.007206 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-20 01:38 | 2021-09-20 01:39 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 3387 | keep | 0 | Sep | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-09-20 01:38 | 2021-09-20 20:13 | 20 | 018:35 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1115 | 2021-09-20 | 22300 | keep | 0 | Sep | 2021 | 0.015188 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-20 01:40 | 2021-09-20 01:41 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21092000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 3387 | keep | 0 | Sep | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
BAYAMON | 2021-09-20 02:17 | 2021-09-20 18:45 | 50 | 016:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 988 | 2021-09-20 | 49400 | keep | 0 | Sep | 2021 | 0.033646 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-20 02:48 | 2021-09-20 05:26 | 3957 | 002:38 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO ALIMENTADOR POR CONTROL | S21092000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-09-20 | 625206 | keep | 0 | Sep | 2021 | 0.42582 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
ARECIBO | 2021-09-20 03:11 | 2021-09-20 12:04 | 50 | 008:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100009 | New_Event | Bad Weather | Include | Include | Weather | 533 | 2021-09-20 | 26650 | keep | 0 | Sep | 2021 | 0.018151 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-20 03:38 | 2021-09-20 11:30 | 100 | 007:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000011 | New_Event | Bad Weather | Include | Include | Weather | 472 | 2021-09-20 | 47200 | keep | 0 | Sep | 2021 | 0.032148 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-20 03:41 | 2021-09-20 15:00 | 50 | 011:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21009200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 679 | 2021-09-20 | 33950 | keep | 0 | Sep | 2021 | 0.023123 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-20 04:39 | 2021-09-20 12:30 | 160 | 007:51 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | C21092000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2021-09-20 | 75360 | keep | 0 | Sep | 2021 | 0.051327 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
VEGA BAJA | 2021-09-20 04:44 | 2021-09-20 12:08 | 40 | 007:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA Y SE REALIZO DESGANCHE | B21092000011 | New_Event | Cutout Failure | Include | Include | Equipment | 444 | 2021-09-20 | 17760 | keep | 0 | Sep | 2021 | 0.012096 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-20 04:58 | 2021-09-20 10:10 | 25 | 005:12 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21092000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2021-09-20 | 7800 | keep | 0 | Sep | 2021 | 0.0053125 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-20 05:15 | 2021-09-20 14:41 | 12 | 009:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000014 | New_Event | Bad Weather | Include | Include | Weather | 566 | 2021-09-20 | 6792 | keep | 0 | Sep | 2021 | 0.004626 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-09-20 05:34 | 2021-09-20 09:57 | 20 | 004:23 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA EVENTO DE LLUVIA FUERTE Y RAYOS | B21092000014 | New_Event | Bad Weather | Include | Include | Weather | 263 | 2021-09-20 | 5260 | keep | 0 | Sep | 2021 | 0.0035826 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-20 05:44 | 2021-09-20 14:36 | 35 | 008:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2021-09-20 | 18620 | keep | 0 | Sep | 2021 | 0.012682 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-20 05:47 | 2021-09-20 11:18 | 10 | 005:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000017 | New_Event | Bad Weather | Include | Include | Weather | 331 | 2021-09-20 | 3310 | keep | 0 | Sep | 2021 | 0.0022544 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-20 06:14 | 2021-09-20 06:15 | 1382 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR LLEVA CARGA 1706 03 Y 1715 03 | B21092000000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-09-20 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-09-20 06:14 | 2021-09-20 06:15 | 663 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR CARGA POR 1706 02 | B21092000000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-09-20 | 663 | keep | 0 | Sep | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-09-20 06:14 | 2021-09-20 06:15 | 74 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR CARGA POR 1706 02 | B21092000000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-09-20 | 74 | keep | 0 | Sep | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2021-09-20 06:15 | 2021-09-20 21:25 | 100 | 015:10 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO | B21092000000 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 910 | 2021-09-20 | 91000 | keep | 0 | Sep | 2021 | 0.06198 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-09-20 06:18 | 2021-09-20 06:19 | 1702 | 000:01 | T | TRANSFORMADOR AVERIADO | RECERRO INTERRUPTOR | C21092000005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-20 | 1702 | keep | 0 | Sep | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-09-20 06:19 | 2021-09-20 17:24 | 22 | 011:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | C21092000033 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 665 | 2021-09-20 | 14630 | keep | 0 | Sep | 2021 | 0.0099644 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2021-09-20 06:36 | 2021-09-20 08:57 | 30 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092000006 | New_Event |  |  | Include | Wildlife | 141 | 2021-09-20 | 4230 | keep | 0 | Sep | 2021 | 0.002881 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-20 06:47 | 2021-09-20 08:54 | 60 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000021 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2021-09-20 | 7620 | keep | 0 | Sep | 2021 | 0.0051899 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-20 06:56 | 2021-09-20 19:14 | 60 | 012:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 738 | 2021-09-20 | 44280 | keep | 0 | Sep | 2021 | 0.030159 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-20 07:17 | 2021-09-20 11:30 | 12 | 004:13 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR | R21092000005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2021-09-20 | 3036 | keep | 0 | Sep | 2021 | 0.0020678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-09-20 07:21 | 2021-09-20 10:00 | 11 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21092000006 | New_Event |  |  | Include | Wildlife | 159 | 2021-09-20 | 1749 | keep | 0 | Sep | 2021 | 0.0011912 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-09-20 07:28 | 2021-09-20 07:29 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 2379 | keep | 0 | Sep | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-09-20 07:29 | 2021-09-20 16:00 | 100 | 008:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P21092000020 | New_Event | Bad Weather | Include | Include | Weather | 511 | 2021-09-20 | 51100 | keep | 0 | Sep | 2021 | 0.034804 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-20 07:44 | 2021-09-20 11:15 | 20 | 003:31 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21092000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-09-20 | 4220 | keep | 0 | Sep | 2021 | 0.0028742 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-20 07:45 | 2021-09-20 10:10 | 70 | 002:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092000015 | New_Event |  |  | Include | Wildlife | 145 | 2021-09-20 | 10150 | keep | 0 | Sep | 2021 | 0.0069131 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-09-20 07:46 | 2021-09-20 15:55 | 40 | 008:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | B21092000025 | New_Event | Bad Weather | Include | Include | Weather | 489 | 2021-09-20 | 19560 | keep | 0 | Sep | 2021 | 0.013322 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-20 07:49 | 2021-09-20 07:50 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21092000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 2107 | keep | 0 | Sep | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2021-09-20 07:51 | 2021-09-20 10:44 | 1 | 002:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | A21092000026 | New_Event | Cutout Failure | Include | Include | Equipment | 173 | 2021-09-20 | 173 | keep | 0 | Sep | 2021 | 0.00011783 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-20 07:55 | 2021-09-21 11:02 | 1 | 027:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21092000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1627 | 2021-09-20 | 1627 | keep | 0 | Sep | 2021 | 0.0011081 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-09-20 07:56 | 2021-09-20 07:59 | 2470 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21092000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-20 | 7410 | keep | 0 | Sep | 2021 | 0.0050469 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2021-09-20 08:00 | 2021-09-20 11:25 | 2470 | 003:25 | T | NO SE REPORTO CAUSA | SE PATRULLO ALIMENTADOR Y SE HICIERON MANIOBRAS Y EL ALIMENTADOR QUEDO EN SERVICIO. NO SE ENCONTRO CAUSA | P21092000012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-09-20 | 506350 | keep | 0 | Sep | 2021 | 0.34487 | 0.0016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2021-09-20 08:14 | 2021-09-20 08:15 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210920000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-09-20 08:20 | 2021-09-21 17:30 | 25 | 033:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA 2400 VOLT X LO MISMO | P21092000014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1990 | 2021-09-20 | 49750 | keep | 0 | Sep | 2021 | 0.033884 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-09-20 08:25 | 2021-09-20 22:37 | 40 | 014:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000033 | New_Event | Bad Weather | Include | Include | Weather | 852 | 2021-09-20 | 34080 | keep | 0 | Sep | 2021 | 0.023212 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-20 08:28 | 2021-09-20 11:35 | 80 | 003:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA LINEA ROTA | M21092000037 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2021-09-20 | 14960 | keep | 0 | Sep | 2021 | 0.010189 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-20 08:30 | 2021-09-20 11:38 | 3 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092000035 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-09-20 | 564 | keep | 0 | Sep | 2021 | 0.00038414 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-09-20 08:36 | 2021-09-20 20:46 | 4 | 012:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092000038 | New_Event | Bad Weather | Include | Include | Weather | 730 | 2021-09-20 | 2920 | keep | 0 | Sep | 2021 | 0.0019888 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-20 08:51 | 2021-09-20 13:00 | 1 | 004:09 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN SU-20 | S21092000036 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 249 | 2021-09-20 | 249 | keep | 0 | Sep | 2021 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-20 08:57 | 2021-09-20 11:17 | 2302 | 002:20 | S | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION SE FUE A LOCK OUT SE REEMPLAZO AISLACION Y DOS BUS SUPPORT | C21092000024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2021-09-20 | 322280 | keep | 0 | Sep | 2021 | 0.2195 | 0.0015679 | Sustained | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-09-20 08:57 | 2021-09-20 11:17 | 1342 | 002:20 | S | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION SE FUE A LOCK OUT SE REEMPLAZO AISLACION Y DOS BUS SUPPORT | C21092000024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2021-09-20 | 187880 | keep | 0 | Sep | 2021 | 0.12796 | 0.00091403 | Sustained | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-09-20 08:57 | 2021-09-20 11:17 | 34 | 002:20 | S | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION SE FUE A LOCK OUT SE REEMPLAZO AISLACION Y DOS BUS SUPPORT | C21092000024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2021-09-20 | 4760 | keep | 0 | Sep | 2021 | 0.003242 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2021-09-20 08:57 | 2021-09-20 10:35 | 1742 | 001:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | SUBESTACION SE FUE A LOCK OUT SE REEMPLAZO AISLACION Y DOS BUS SUPPORT | C21092000024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 98 | 2021-09-20 | 170716 | keep | 0 | Sep | 2021 | 0.11627 | 0.0011865 | Sustained | FALSE | FALSE | Not_TMED_Event | 1742
GUAYAMA | 2021-09-20 09:06 | 2021-09-20 12:05 | 50 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X50 EN CORTE DE LINEA POR AVE CRUZANDO LINEAS | P21092000021 | New_Event |  |  | Include | Wildlife | 179 | 2021-09-20 | 8950 | keep | 0 | Sep | 2021 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-20 09:09 | 2021-09-20 19:03 | 1 | 009:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN MONTURA DE TRANSFORMADORES | B21092000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 594 | 2021-09-20 | 594 | keep | 0 | Sep | 2021 | 0.00040457 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-20 09:14 | 2021-09-21 16:07 | 50 | 030:53 | P | SECUNDARIA/DESGANCHE | ABRIO CORTE DE LINEA PARA DESGANCHAR Y REPARAR SECUNDARIA TRAS PATIO | C21092000030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1853 | 2021-09-20 | 92650 | keep | 0 | Sep | 2021 | 0.063103 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-20 09:18 | 2021-09-20 12:15 | 40 | 002:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21092000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-09-20 | 7080 | keep | 0 | Sep | 2021 | 0.0048222 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-20 09:19 | 2021-09-20 17:55 | 3 | 008:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | C21092000032 | New_Event | Cutout Failure | Include | Include | Equipment | 516 | 2021-09-20 | 1548 | keep | 0 | Sep | 2021 | 0.0010543 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-09-20 09:26 | 2021-09-20 14:15 | 25 | 004:49 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | M21092000052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-09-20 | 7225 | keep | 0 | Sep | 2021 | 0.0049209 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-20 09:30 | 2021-09-20 14:00 | 10 | 004:30 | P | ESTRUCTURA AVERIADA | 1 X 25 EN CORTE DE LINEA SE ENDEREZO POSTE SE REALIZO DESGANCHE | A21091900013 | New_Event | Defective Pole | Include | Include | Equipment | 270 | 2021-09-20 | 2700 | keep | 0 | Sep | 2021 | 0.001839 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-20 09:32 | 2021-09-20 16:33 | 30 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000048 | New_Event | Bad Weather | Include | Include | Weather | 421 | 2021-09-20 | 12630 | keep | 0 | Sep | 2021 | 0.0086022 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-20 09:34 | 2021-09-21 19:51 | 100 | 034:17 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA QUEMADO X 15 KVA | A21092000049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2057 | 2021-09-20 | 205700 | keep | 0 | Sep | 2021 | 0.1401 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-20 09:39 | 2021-09-20 14:33 | 4 | 004:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | M21092000054 | New_Event | Bad Weather | Include | Include | Weather | 294 | 2021-09-20 | 1176 | keep | 0 | Sep | 2021 | 0.00080097 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-09-20 09:51 | 2021-09-20 15:00 | 3 | 005:09 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21009200051 | New_Event | Bad Weather | Include | Include | Weather | 309 | 2021-09-20 | 927 | keep | 0 | Sep | 2021 | 0.00063138 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-09-20 09:52 | 2021-09-20 10:34 | 10 | 000:42 | P | HERRAJE ROTO O PODRIDO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CRUCETA Y CAJA DE TRANSFORMADOR ROTA | R21092000008 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 42 | 2021-09-20 | 420 | keep | 0 | Sep | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-20 09:52 | 2021-09-20 17:40 | 60 | 007:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000052 | New_Event | Bad Weather | Include | Include | Weather | 468 | 2021-09-20 | 28080 | keep | 0 | Sep | 2021 | 0.019125 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-20 09:54 | 2021-09-20 09:55 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRRUPTOR | C21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-09-20 09:54 | 2021-09-21 14:35 | 4 | 028:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092000061 | New_Event | Bad Weather | Include | Include | Weather | 1721 | 2021-09-20 | 6884 | keep | 0 | Sep | 2021 | 0.0046887 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-09-20 09:55 | 2021-09-20 13:35 | 18 | 003:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | R21092000013 | New_Event | Wire Down | Include | Include | Equipment | 220 | 2021-09-20 | 3960 | keep | 0 | Sep | 2021 | 0.0026971 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
UTUADO | 2021-09-20 09:55 | 2021-09-20 12:25 | 2 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000053 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2021-09-20 | 300 | keep | 0 | Sep | 2021 | 0.00020433 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
ARECIBO | 2021-09-20 10:03 | 2021-09-20 20:09 | 30 | 010:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000057 | New_Event | Bad Weather | Include | Include | Weather | 606 | 2021-09-20 | 18180 | keep | 0 | Sep | 2021 | 0.012382 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-20 10:06 | 2021-09-20 17:00 | 50 | 006:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR MAL TIEMPO | P2109200032 | New_Event | Bad Weather | Include | Include | Weather | 414 | 2021-09-20 | 20700 | keep | 0 | Sep | 2021 | 0.014099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-09-20 10:11 | 2021-09-20 15:01 | 15 | 004:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21092000044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 290 | 2021-09-20 | 4350 | keep | 0 | Sep | 2021 | 0.0029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-20 10:13 | 2021-09-20 12:46 | 4 | 002:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15 KVA X 15 KVA | C21091900110 | New_Event | Service Transformer Failure | Include | Include | Equipment | 153 | 2021-09-20 | 612 | keep | 0 | Sep | 2021 | 0.00041683 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-20 10:26 | 2021-09-21 22:00 | 29 | 035:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO PUENTE DE LINEA A CAJA | S21092000049 | New_Event | Wire Down | Include | Include | Equipment | 2134 | 2021-09-20 | 61886 | keep | 0 | Sep | 2021 | 0.04215 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
CANOVANAS | 2021-09-20 10:40 | 2021-09-20 12:06 | 1 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 25 EN SU-7 CRUCE DE LINEAS | R21092000016 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2021-09-20 | 86 | keep | 0 | Sep | 2021 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-20 10:43 | 2021-09-20 18:07 | 150 | 007:24 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | R21092000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2021-09-20 | 66600 | keep | 0 | Sep | 2021 | 0.045361 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-09-20 10:52 | 2021-09-20 13:27 | 16 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21092000062 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-09-20 | 2480 | keep | 0 | Sep | 2021 | 0.0016891 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
CAGUAS | 2021-09-20 10:59 | 2021-09-20 15:53 | 8 | 004:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21092000063 | New_Event |  |  | Include | Wildlife | 294 | 2021-09-20 | 2352 | keep | 0 | Sep | 2021 | 0.0016019 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
CAGUAS | 2021-09-20 11:03 | 2021-09-21 11:13 | 10 | 024:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | C21092000064 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1450 | 2021-09-20 | 14500 | keep | 0 | Sep | 2021 | 0.0098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-20 11:05 | 2021-09-20 17:56 | 60 | 006:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21092000059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2021-09-20 | 24660 | keep | 0 | Sep | 2021 | 0.016796 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-20 11:12 | 2021-09-20 17:00 | 6 | 005:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A21092000064 | New_Event | Cutout Failure | Include | Include | Equipment | 348 | 2021-09-20 | 2088 | keep | 0 | Sep | 2021 | 0.0014221 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-20 11:17 | 2021-09-20 13:20 | 30 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092000006 | New_Event |  |  | Include | Wildlife | 123 | 2021-09-20 | 3690 | keep | 0 | Sep | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-20 11:21 | 2021-09-21 17:12 | 1 | 029:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO Y RELOCALIZO SECUNDARIA | C21092000066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1791 | 2021-09-20 | 1791 | keep | 0 | Sep | 2021 | 0.0012198 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-20 11:29 | 2021-09-20 15:20 | 1 | 003:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN RISER MAL TIEMPO | M21092000081 | New_Event | Bad Weather | Include | Include | Weather | 231 | 2021-09-20 | 231 | keep | 0 | Sep | 2021 | 0.00015733 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-20 11:30 | 2021-09-20 15:00 | 50 | 003:30 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21092000079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-09-20 | 10500 | keep | 0 | Sep | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-20 11:40 | 2021-09-20 17:15 | 6 | 005:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO Y SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21092000022 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2021-09-20 | 2010 | keep | 0 | Sep | 2021 | 0.001369 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-09-20 11:42 | 2021-09-20 12:37 | 4 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE NEUTRAL EN PEDESTAL | R21092000024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-09-20 | 220 | keep | 0 | Sep | 2021 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-09-20 11:43 | 2021-09-21 12:34 | 2 | 024:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15 KVA | A21092000066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1491 | 2021-09-20 | 2982 | keep | 0 | Sep | 2021 | 0.002031 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-09-20 11:45 | 2021-09-20 16:47 | 10 | 005:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C21092000074 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 302 | 2021-09-20 | 3020 | keep | 0 | Sep | 2021 | 0.0020569 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-20 12:02 | 2021-09-20 14:36 | 40 | 002:34 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE | R21092000028 | New_Event | Defective Pole | Include | Include | Equipment | 154 | 2021-09-20 | 6160 | keep | 0 | Sep | 2021 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-20 12:07 | 2021-09-20 14:29 | 10 | 002:22 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | R21092000025 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 142 | 2021-09-20 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-20 12:08 | 2021-09-21 15:00 | 30 | 026:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA | M21092000091 | New_Event | Wire Down | Include | Include | Equipment | 1612 | 2021-09-20 | 48360 | keep | 0 | Sep | 2021 | 0.032938 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-09-20 12:27 | 2021-09-20 15:38 | 12 | 003:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 75KVA X 75KVA POR DERRAME DE ACEITE | C21092000076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 191 | 2021-09-20 | 2292 | keep | 0 | Sep | 2021 | 0.0015611 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-09-20 12:37 | 2021-09-20 17:07 | 1 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | C21092000079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2021-09-20 | 270 | keep | 0 | Sep | 2021 | 0.0001839 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-20 12:42 | 2021-09-20 12:43 | 10211 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO CARGA POR EL 1206-03 | S21092000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-09-20 12:42 | 2021-09-20 12:43 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA 1204-05 | S21092000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-09-20 12:43 | 2021-09-20 13:00 | 251 | 000:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21092000085 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 17 | 2021-09-20 | 4267 | keep | 0 | Sep | 2021 | 0.0029062 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
SAN JUAN | 2021-09-20 13:00 | 2021-09-20 13:01 | 10211 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO CARGA POR EL 1206-03 | S21092000000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 10211 | keep | 0 | Sep | 2021 | 0.0069547 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-20 13:00 | 2021-09-20 13:01 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA 1204-05 | S21092000000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 4133 | keep | 0 | Sep | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-09-20 13:01 | 2021-09-20 16:32 | 251 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21092000085 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 211 | 2021-09-20 | 52961 | keep | 0 | Sep | 2021 | 0.036071 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
MAYAGÃœEZ | 2021-09-20 13:03 | 2021-09-20 21:30 | 500 | 008:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21092000099 | New_Event | Wire Down | Include | Include | Equipment | 507 | 2021-09-20 | 253500 | keep | 0 | Sep | 2021 | 0.17266 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
AGUADILLA | 2021-09-20 13:03 | 2021-09-20 17:25 | 12 | 004:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | M21092000098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 262 | 2021-09-20 | 3144 | keep | 0 | Sep | 2021 | 0.0021414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-09-20 13:10 | 2021-09-20 17:56 | 15 | 004:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21092000068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2021-09-20 | 4290 | keep | 0 | Sep | 2021 | 0.0029219 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-20 13:11 | 2021-09-20 20:10 | 2 | 006:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR ERMCO 15 KVA 2400/4160 X 15KVA SERIE- 82011973207 FID-23635394 | M21092000101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 419 | 2021-09-20 | 838 | keep | 0 | Sep | 2021 | 0.00057076 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-09-20 13:26 | 2021-09-20 14:51 | 15 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21092000033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2021-09-20 | 1275 | keep | 0 | Sep | 2021 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-20 13:27 | 2021-09-20 17:30 | 80 | 004:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C21092000088 | New_Event | Wire Down | Include | Include | Equipment | 243 | 2021-09-20 | 19440 | keep | 0 | Sep | 2021 | 0.01324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-20 13:30 | 2021-09-20 13:32 | 3458 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RE CLOSE RELAY EN OFF | M21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-20 | 6916 | keep | 0 | Sep | 2021 | 0.0047105 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
AGUADILLA | 2021-09-20 13:30 | 2021-09-20 16:00 | 15 | 002:30 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO CRUCETAS | M21092000103 | New_Event | Defective Pole | Include | Include | Equipment | 150 | 2021-09-20 | 2250 | keep | 0 | Sep | 2021 | 0.0015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-20 13:40 | 2021-09-21 10:31 | 25 | 020:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO PUENTE DE LINEA A CAJA | S21092000093 | New_Event | Cutout Failure | Include | Include | Equipment | 1251 | 2021-09-20 | 31275 | keep | 0 | Sep | 2021 | 0.021301 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-20 13:49 | 2021-09-20 16:36 | 1681 | 002:47 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA CARGA ESTA POR EL 1303-04 | S21092000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-09-20 | 280727 | keep | 0 | Sep | 2021 | 0.1912 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
AGUADILLA | 2021-09-20 13:50 | 2021-09-23 15:10 | 25 | 073:20 | P | ERROR HUMANO | SE CERRO CORTE DE LINEA QUE SE HABIA DEJADO ABIERTO DESDE 09/20/2021 PARA DESGANCHAR | M21092300024 | New_Event | Human Error | Include | Include | Other | 4400 | 2021-09-20 | 110000 | keep | 0 | Sep | 2021 | 0.07492 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-20 13:54 | 2021-09-20 21:45 | 20 | 007:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21092000114 | New_Event | Bad Weather | Include | Include | Weather | 471 | 2021-09-20 | 9420 | keep | 0 | Sep | 2021 | 0.0064159 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-20 14:10 | 2021-09-20 20:13 | 1 | 006:03 | P | OTRAS CAUSAS | 1 X 30 EN RISER EQUIPO DE MEDICION DEFECTUOSO | C21092000094 | New_Event | Other Causes | Include | Include | Other | 363 | 2021-09-20 | 363 | keep | 0 | Sep | 2021 | 0.00024724 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-20 14:12 | 2021-09-20 16:50 | 40 | 002:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | M21092000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-09-20 | 6320 | keep | 0 | Sep | 2021 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-20 14:13 | 2021-09-21 10:04 | 65 | 019:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21092000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1191 | 2021-09-20 | 77415 | keep | 0 | Sep | 2021 | 0.052727 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-09-20 14:14 | 2021-09-20 14:16 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-20 | 4468 | keep | 0 | Sep | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2021-09-20 14:15 | 2021-09-20 14:50 | 10 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR REPARAR PUENTE | M21092000056 | New_Event | Wire Down | Include | Include | Equipment | 35 | 2021-09-20 | 350 | keep | 0 | Sep | 2021 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-20 14:15 | 2021-09-20 17:47 | 15 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092000091 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-09-20 | 3180 | keep | 0 | Sep | 2021 | 0.0021659 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-20 14:16 | 2021-09-20 18:22 | 80 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092000079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-09-20 | 19680 | keep | 0 | Sep | 2021 | 0.013404 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-20 14:20 | 2021-09-20 17:30 | 40 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21092000120 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-09-20 | 7600 | keep | 0 | Sep | 2021 | 0.0051763 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-20 14:25 | 2021-09-20 15:10 | 6 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21092000067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-09-20 | 270 | keep | 0 | Sep | 2021 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-09-20 14:30 | 2021-09-20 16:10 | 15 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21092000049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2021-09-20 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-20 14:39 | 2021-09-20 15:21 | 6 | 000:42 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RETIRAR POSTE | S21092000000 | New_Event | Defective Pole | Include | Include | Equipment | 42 | 2021-09-20 | 252 | keep | 0 | Sep | 2021 | 0.00017164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-20 14:50 | 2021-09-20 15:58 | 1615 | 001:08 | T | MAL TIEMPO/RAYOS/WET ASH | DESGANCHE MAL TIEMPO | P210920000XX | New_Event | Bad Weather | Include | Include | Weather | 68 | 2021-09-20 | 109820 | keep | 0 | Sep | 2021 | 0.074798 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
ARECIBO | 2021-09-20 15:00 | 2021-09-20 16:00 | 2 | 001:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 25 KVA X 25KVA | A21092000099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2021-09-20 | 120 | keep | 0 | Sep | 2021 | 8.1731e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-09-20 15:02 | 2021-09-20 19:05 | 25 | 004:03 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | B21092000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-09-20 | 6075 | keep | 0 | Sep | 2021 | 0.0041377 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-20 15:07 | 2021-09-21 16:35 | 2 | 025:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21092000100 | New_Event | Bad Weather | Include | Include | Weather | 1528 | 2021-09-20 | 3056 | keep | 0 | Sep | 2021 | 0.0020814 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-09-20 15:08 | 2021-09-20 23:07 | 2422 | 007:59 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO MACHETE QUEMADO EN SU DE BURBUJAS Y SE CERRO N/O CONTRA 1346-02 | S21092000000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 479 | 2021-09-20 | 1160138 | keep | 0 | Sep | 2021 | 0.79016 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
MAYAGÃœEZ | 2021-09-20 15:22 | 2021-09-21 16:38 | 15 | 025:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD EN FID17258685 / MARCA EATON / #SERIE 2055105365 | M21092000145 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1516 | 2021-09-20 | 22740 | keep | 0 | Sep | 2021 | 0.015488 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-20 15:23 | 2021-09-20 19:30 | 60 | 004:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000102 | New_Event | Bad Weather | Include | Include | Weather | 247 | 2021-09-20 | 14820 | keep | 0 | Sep | 2021 | 0.010094 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-09-20 15:28 | 2021-09-21 17:08 | 100 | 025:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | P21092000114 | New_Event | Wire Down | Include | Include | Equipment | 1540 | 2021-09-20 | 154000 | keep | 0 | Sep | 2021 | 0.10489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-20 15:28 | 2021-09-20 15:29 | 176 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | M21092000148 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 176 | keep | 0 | Sep | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-09-20 15:29 | 2021-09-21 21:25 | 150 | 029:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21092000222 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1796 | 2021-09-20 | 269400 | keep | 0 | Sep | 2021 | 0.18349 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-20 15:35 | 2021-09-22 14:19 | 50 | 046:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092000149 | New_Event | Bad Weather | Include | Include | Weather | 2804 | 2021-09-20 | 140200 | keep | 0 | Sep | 2021 | 0.09549 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-20 15:36 | 2021-09-20 22:45 | 25 | 007:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN SWITCHING UNIT MAL TIEMPO DESCARGAS ELECTRICAS | M21092000150 | New_Event | Bad Weather | Include | Include | Weather | 429 | 2021-09-20 | 10725 | keep | 0 | Sep | 2021 | 0.0073047 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-09-20 15:41 | 2021-09-20 16:22 | 15 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21092000081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-09-20 | 615 | keep | 0 | Sep | 2021 | 0.00041887 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-20 15:42 | 2021-09-20 15:43 | 1712 | 000:01 | T | DESGANCHE | RECIERRE | P210920000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-20 | 1712 | keep | 0 | Sep | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-09-20 15:43 | 2021-09-21 13:12 | 50 | 021:29 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21092000208 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1289 | 2021-09-20 | 64450 | keep | 0 | Sep | 2021 | 0.043897 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-20 15:43 | 2021-09-20 22:08 | 700 | 006:25 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | P21092000202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2021-09-20 | 269500 | keep | 0 | Sep | 2021 | 0.18356 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
UTUADO | 2021-09-20 16:05 | 2021-09-20 19:10 | 100 | 003:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PEGADO A CRUCETA | A21092000106 | New_Event | Wire Down | Include | Include | Equipment | 185 | 2021-09-20 | 18500 | keep | 0 | Sep | 2021 | 0.0126 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-20 16:12 | 2021-09-20 18:13 | 5 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092000111 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-09-20 | 605 | keep | 0 | Sep | 2021 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-09-20 16:13 | 2021-09-20 21:00 | 20 | 004:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | M21092000165 | New_Event | Wire Down | Include | Include | Equipment | 287 | 2021-09-20 | 5740 | keep | 0 | Sep | 2021 | 0.0039095 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-20 16:27 | 2021-09-22 15:14 | 15 | 046:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD EN EL FID:19434943 / MARCA: HOWARD IND. / #SERIE: 2389362720 / VOLTAJE: 4.16KV / 120-240V | M21092000167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2807 | 2021-09-20 | 42105 | keep | 0 | Sep | 2021 | 0.028678 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-09-20 16:30 | 2021-09-20 18:24 | 60 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE DE LINEA A CAJA | R21092000035 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2021-09-20 | 6840 | keep | 0 | Sep | 2021 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-20 16:34 | 2021-09-20 18:35 | 1 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | M21092000169 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-09-20 | 121 | keep | 0 | Sep | 2021 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-09-20 16:50 | 2021-09-20 16:51 | 653 | 000:01 | T | NO SE REPORTO CAUSA | RECIERE | P210920000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 653 | keep | 0 | Sep | 2021 | 0.00044476 | 0.00044476 | Momentary | FALSE | FALSE | Not_TMED_Event | 653
FAJARDO | 2021-09-20 16:53 | 2021-09-20 18:45 | 50 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO PUENTE LINEA A CAJA | R21092000038 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2021-09-20 | 5600 | keep | 0 | Sep | 2021 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-20 16:56 | 2021-09-20 19:45 | 520 | 002:49 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO PARTIDO | P21092000154 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2021-09-20 | 87880 | keep | 0 | Sep | 2021 | 0.059855 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
UTUADO | 2021-09-20 17:08 | 2021-09-27 15:23 | 12 | 166:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092000119 | New_Event | Bad Weather | Include | Include | Weather | 9975 | 2021-09-20 | 119700 | keep | 0 | Sep | 2021 | 0.081527 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
UTUADO | 2021-09-20 17:08 | 2021-09-22 16:50 | 15 | 047:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | A21092000119 | New_Event | Wire Down | Include | Include | Equipment | 2862 | 2021-09-20 | 42930 | keep | 0 | Sep | 2021 | 0.029239 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-09-20 17:08 | 2021-09-21 16:47 | 200 | 023:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21092000119 | New_Event | Wire Down | Include | Include | Equipment | 1419 | 2021-09-20 | 283800 | keep | 0 | Sep | 2021 | 0.19329 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-20 17:18 | 2021-09-20 21:45 | 100 | 004:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | A21092000122 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2021-09-20 | 26700 | keep | 0 | Sep | 2021 | 0.018185 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-20 17:18 | 2021-09-20 17:49 | 50 | 000:31 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2021-09-20 | 1550 | keep | 0 | Sep | 2021 | 0.0010557 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-20 17:34 | 2021-09-21 12:40 | 40 | 019:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | S21092000262 | New_Event | Wire Down | Include | Include | Equipment | 1146 | 2021-09-20 | 45840 | keep | 0 | Sep | 2021 | 0.031221 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-20 18:00 | 2021-09-20 20:16 | 80 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092000103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2021-09-20 | 10880 | keep | 0 | Sep | 2021 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-20 18:21 | 2021-09-21 11:54 | 30 | 017:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B21092000142 | New_Event | Cutout Failure | Include | Include | Equipment | 1053 | 2021-09-20 | 31590 | keep | 0 | Sep | 2021 | 0.021516 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-20 18:29 | 2021-09-21 10:10 | 45 | 015:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | B21092000111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 941 | 2021-09-20 | 42345 | keep | 0 | Sep | 2021 | 0.028841 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-20 18:41 | 2021-09-20 19:40 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | S21091700067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-09-20 | 708 | keep | 0 | Sep | 2021 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-09-20 18:51 | 2021-09-21 12:33 | 10 | 017:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DE TRANSFORMADOR | P21092000176 | New_Event | Cutout Failure | Include | Include | Equipment | 1062 | 2021-09-20 | 10620 | keep | 0 | Sep | 2021 | 0.0072332 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-20 19:48 | 2021-09-21 00:50 | 10 | 005:02 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO DE EXISTENTE HACIA T-22 | B21092000136 | New_Event | UG Cable Fault | Include | Include | Equipment | 302 | 2021-09-20 | 3020 | keep | 0 | Sep | 2021 | 0.0020569 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-20 19:50 | 2021-09-20 21:06 | 150 | 001:16 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PARTIDO | M21092000210 | New_Event | Defective Pole | Include | Include | Equipment | 76 | 2021-09-20 | 11400 | keep | 0 | Sep | 2021 | 0.0077645 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-20 19:54 | 2021-09-22 11:00 | 15 | 039:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21092000129 | New_Event | Cutout Failure | Include | Include | Equipment | 2346 | 2021-09-20 | 35190 | keep | 0 | Sep | 2021 | 0.023968 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-20 20:23 | 2021-09-20 20:24 | 1860 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21092000308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 1860 | keep | 0 | Sep | 2021 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2021-09-20 20:24 | 2021-09-21 10:57 | 40 | 014:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21092000312 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 873 | 2021-09-20 | 34920 | keep | 0 | Sep | 2021 | 0.023784 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-20 20:39 | 2021-09-20 20:40 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1909-09 | S21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 222 | keep | 0 | Sep | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-09-20 20:39 | 2021-09-20 20:40 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1907-03 | S21092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 4456 | keep | 0 | Sep | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
GUAYAMA | 2021-09-20 20:40 | 2021-09-21 01:03 | 45 | 004:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21092000200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-09-20 | 11835 | keep | 0 | Sep | 2021 | 0.0080608 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-09-20 20:42 | 2021-09-20 20:43 | 520 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210920000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 520 | keep | 0 | Sep | 2021 | 0.00035417 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
PONCE | 2021-09-20 20:46 | 2021-09-20 20:47 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE | P210920000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-20 20:46 | 2021-09-20 20:47 | 3114 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE | P210920000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-09-20 20:46 | 2021-09-20 20:47 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL 10 | P210920000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-20 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
BAYAMON | 2021-09-20 20:50 | 2021-09-21 10:13 | 15 | 013:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN T-164 SE REEMPLAZO CAJA QUEMADA | B21092000142 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2021-09-20 | 12045 | keep | 0 | Sep | 2021 | 0.0082038 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-20 20:58 | 2021-09-21 12:49 | 10 | 015:51 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 20 EN T-543 SE REEMPLAZO PISTOLA | B21092000143 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 951 | 2021-09-20 | 9510 | keep | 0 | Sep | 2021 | 0.0064772 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-20 21:04 | 2021-09-21 11:43 | 1 | 014:39 | P | NO SE REPORTO CAUSA | 1 X 25 EN SWITCH UNIT | A21092000136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 879 | 2021-09-20 | 879 | keep | 0 | Sep | 2021 | 0.00059868 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-09-20 21:06 | 2021-09-21 21:31 | 200 | 024:25 | P | ESTRUCTURA AVERIADA | SE REMPLAZO DOS POSTES PARTIDOS EN EL FID 30702398 DE 45' METAL | M21092000210 | Additional_clients | Defective Pole | Include | Include | Equipment | 1465 | 2021-09-20 | 293000 | keep | 0 | Sep | 2021 | 0.19956 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-20 21:08 | 2021-09-21 10:55 | 25 | 013:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21092000126 | New_Event | Bad Weather | Include | Include | Weather | 827 | 2021-09-20 | 20675 | keep | 0 | Sep | 2021 | 0.014082 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-20 21:12 | 2021-09-20 21:13 | 225 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1303-05 | S21092000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 225 | keep | 0 | Sep | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-20 21:12 | 2021-09-20 21:13 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1303-04 | S21092000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-20 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-09-20 21:15 | 2021-09-21 01:11 | 225 | 003:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO AMARRE CON 1303-05 Y SE CERRO POR SCADA EL 1303-05 LLEVA EL 1303-04 | S21092000000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 236 | 2021-09-20 | 53100 | keep | 0 | Sep | 2021 | 0.036166 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-20 21:15 | 2021-09-21 00:37 | 870 | 003:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO AMARRE CON 1303-04 Y SE CERRO POR SCADA | S21092000000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 202 | 2021-09-20 | 175740 | keep | 0 | Sep | 2021 | 0.1197 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-09-20 21:26 | 2021-09-20 22:22 | 1844 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO | S21092000000 | New_Event | Wire Down | Include | Include | Equipment | 56 | 2021-09-20 | 103264 | keep | 0 | Sep | 2021 | 0.070333 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
BAYAMON | 2021-09-20 21:28 | 2021-09-21 16:24 | 20 | 018:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | S21092000331 | New_Event | Cutout Failure | Include | Include | Equipment | 1136 | 2021-09-20 | 22720 | keep | 0 | Sep | 2021 | 0.015474 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-20 21:42 | 2021-09-21 11:39 | 252 | 013:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO | P21092000203 | New_Event | Wire Down | Include | Include | Equipment | 837 | 2021-09-20 | 210924 | keep | 0 | Sep | 2021 | 0.14366 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
CANOVANAS | 2021-09-20 22:29 | 2021-09-21 09:18 | 1 | 010:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21092000075 | New_Event | Bad Weather | Include | Include | Weather | 649 | 2021-09-20 | 649 | keep | 0 | Sep | 2021 | 0.00044203 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-20 22:46 | 2021-09-21 01:58 | 50 | 003:12 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M21092000039 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 192 | 2021-09-20 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-20 22:48 | 2021-09-21 00:21 | 562 | 001:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21092000209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2021-09-20 | 52266 | keep | 0 | Sep | 2021 | 0.035598 | 0.00038278 | Sustained | FALSE | TRUE | Not_TMED_Event | 562
PONCE | 2021-09-20 22:48 | 2021-09-21 00:21 | 688 | 001:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21092000209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2021-09-20 | 63984 | keep | 0 | Sep | 2021 | 0.043579 | 0.00046859 | Sustained | FALSE | TRUE | Not_TMED_Event | 688
PONCE | 2021-09-20 22:48 | 2021-09-21 00:21 | 658 | 001:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21092000209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2021-09-20 | 61194 | keep | 0 | Sep | 2021 | 0.041679 | 0.00044816 | Sustained | FALSE | TRUE | Not_TMED_Event | 658
PONCE | 2021-09-20 22:48 | 2021-09-21 00:21 | 4009 | 001:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21092000209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 93 | 2021-09-20 | 372837 | keep | 0 | Sep | 2021 | 0.25394 | 0.0027305 | Sustained | FALSE | TRUE | Not_TMED_Event | 4009
BAYAMON | 2021-09-20 23:27 | 2021-09-22 18:18 | 50 | 042:51 | P | DESGANCHE | SE REALIZO DESHANCHE | S21092000367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2571 | 2021-09-20 | 128550 | keep | 0 | Sep | 2021 | 0.087555 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-21 00:12 | 2021-09-21 16:25 | 40 | 016:13 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 973 | 2021-09-21 | 38920 | keep | 0 | Sep | 2021 | 0.026508 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-09-21 00:16 | 2021-09-22 13:28 | 132 | 037:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE EN MACHETE DEL 7005-3 | M21092100000 | New_Event | Wire Down | Include | Include | Equipment | 2232 | 2021-09-21 | 294624 | keep | 0 | Sep | 2021 | 0.20067 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
AGUADILLA | 2021-09-21 00:16 | 2021-09-22 13:28 | 1157 | 037:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE DE MACHETE A INTERRUPTOR | M21092100000 | New_Event | Wire Down | Include | Include | Equipment | 2232 | 2021-09-21 | 2582424 | keep | 0 | Sep | 2021 | 1.7589 | 0.00078803 | Sustained | FALSE | FALSE | Not_TMED_Event | 1157
SAN JUAN | 2021-09-21 00:42 | 2021-09-21 01:11 | 870 | 000:29 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | HACIENDO OPERACIONES SE DISPARO Y SE CERRO POR SCADA LLEVA 1303-04 | S21092000000 | Partial_restoration | Wire Down | Include | Include | Equipment | 29 | 2021-09-21 | 25230 | keep | 0 | Sep | 2021 | 0.017184 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-21 00:52 | 2021-09-21 00:53 | 1399 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1399 | keep | 0 | Sep | 2021 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BARRANQUITAS | 2021-09-21 00:55 | 2021-09-21 14:43 | 40 | 013:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO DISCO | C21092100001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 828 | 2021-09-21 | 33120 | keep | 0 | Sep | 2021 | 0.022558 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-21 01:45 | 2021-09-21 18:13 | 22 | 016:28 | P | ESTRUCTURA AVERIADA | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO 2 POSTES PRIMARIO Y UN BANCO DE TRANSFORMADORES | R21092100001 | New_Event | Defective Pole | Include | Include | Equipment | 988 | 2021-09-21 | 21736 | keep | 0 | Sep | 2021 | 0.014804 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
CANOVANAS | 2021-09-21 03:44 | 2021-09-21 10:01 | 97 | 006:17 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R21092100002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 377 | 2021-09-21 | 36569 | keep | 0 | Sep | 2021 | 0.024907 | 6.6066e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 97
SAN JUAN | 2021-09-21 04:13 | 2021-09-23 18:23 | 20 | 062:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN RISER | S21092100011 | New_Event | Wire Down | Include | Include | Equipment | 3730 | 2021-09-21 | 74600 | keep | 0 | Sep | 2021 | 0.05081 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-21 04:19 | 2021-09-21 04:20 | 800 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA 95% DE LA CARGA SE ENCUENTRA POR EL 1119-04 | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 800 | keep | 0 | Sep | 2021 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2021-09-21 04:19 | 2021-09-21 04:20 | 2720 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA LLEVA 1115-05 | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 2720 | keep | 0 | Sep | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-09-21 04:36 | 2021-09-21 09:29 | 25 | 004:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21092100005 | New_Event | Bad Weather | Include | Include | Weather | 293 | 2021-09-21 | 7325 | keep | 0 | Sep | 2021 | 0.004989 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-21 04:53 | 2021-09-21 07:19 | 225 | 002:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA SECCIONALIZAR Y LEVANTAR LINEA PRIMARIA. CARGA A TRAVES DEL 1303-05 | S21092100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 146 | 2021-09-21 | 32850 | keep | 0 | Sep | 2021 | 0.022374 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-21 04:53 | 2021-09-21 07:19 | 870 | 002:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA SECCIONALIZAR Y LEVANTAR LINEA PRIMARIA | S21092100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 146 | 2021-09-21 | 127020 | keep | 0 | Sep | 2021 | 0.086513 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-21 05:27 | 2021-09-21 17:45 | 75 | 012:18 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 738 | 2021-09-21 | 55350 | keep | 0 | Sep | 2021 | 0.037699 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-09-21 06:22 | 2021-09-21 17:38 | 79 | 011:16 | P | HERRAJE ROTO O PODRIDO | 2 X 80 CORTE DE LINEA SE REMPLAZO CRUCETA | S21092100019 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 676 | 2021-09-21 | 53404 | keep | 0 | Sep | 2021 | 0.036373 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
MAYAGÃœEZ | 2021-09-21 06:23 | 2021-09-21 07:55 | 50 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100019 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2021-09-21 | 4600 | keep | 0 | Sep | 2021 | 0.003133 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-21 06:45 | 2021-09-21 10:30 | 70 | 003:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-09-21 | 15750 | keep | 0 | Sep | 2021 | 0.010727 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-09-21 06:46 | 2021-09-21 12:05 | 15 | 005:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN TRANSFORMADOR | A21092100008 | New_Event | Cutout Failure | Include | Include | Equipment | 319 | 2021-09-21 | 4785 | keep | 0 | Sep | 2021 | 0.003259 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-09-21 06:49 | 2021-09-21 06:50 | 3565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 3565 | keep | 0 | Sep | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
ARECIBO | 2021-09-21 06:58 | 2021-09-21 11:16 | 10 | 004:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | A21092100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2021-09-21 | 2580 | keep | 0 | Sep | 2021 | 0.0017572 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-21 07:06 | 2021-09-21 22:50 | 80 | 015:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21092100212 | New_Event | Wire Down | Include | Include | Equipment | 944 | 2021-09-21 | 75520 | keep | 0 | Sep | 2021 | 0.051436 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-09-21 07:17 | 2021-09-21 13:32 | 10 | 006:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA Y PARARRAYO DE TRANSFORMADOR | P21092100009 | New_Event | Cutout Failure | Include | Include | Equipment | 375 | 2021-09-21 | 3750 | keep | 0 | Sep | 2021 | 0.0025541 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-21 07:18 | 2021-09-21 22:43 | 92 | 015:25 | P | ESTRUCTURA AVERIADA | 1 X 40 EN CORTE DE LINEA SE ASEGURO POSTE PARTIDO | B21092100008 | New_Event | Defective Pole | Include | Include | Equipment | 925 | 2021-09-21 | 85100 | keep | 0 | Sep | 2021 | 0.057961 | 6.2661e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 92
SAN JUAN | 2021-09-21 07:24 | 2021-09-22 18:39 | 52 | 035:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2115 | 2021-09-21 | 109980 | keep | 0 | Sep | 2021 | 0.074907 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
ARECIBO | 2021-09-21 07:29 | 2021-09-21 10:02 | 50 | 002:33 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | A21092100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-09-21 | 7650 | keep | 0 | Sep | 2021 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-21 07:35 | 2021-09-21 21:50 | 40 | 014:15 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA DE PM-9 AL PM-8. SE ABRIO ENTRE ELLOS Y SE ENERGIZO PM-8 CERRANDO N/O CON EL SU-3. | M21092100036 | New_Event | UG Cable Fault | Include | Include | Equipment | 855 | 2021-09-21 | 34200 | keep | 0 | Sep | 2021 | 0.023293 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-09-21 07:43 | 2021-09-21 07:44 | 817 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21092100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 817 | keep | 0 | Sep | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
ARECIBO | 2021-09-21 07:45 | 2021-09-21 10:31 | 60 | 002:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA | A21092100013 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2021-09-21 | 9960 | keep | 0 | Sep | 2021 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-21 07:55 | 2021-09-21 07:56 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-21 07:55 | 2021-09-21 07:56 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-21 07:55 | 2021-09-21 07:56 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-21 07:56 | 2021-09-21 14:44 | 50 | 006:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100019 | Partial_restoration | Bad Weather | Include | Include | Weather | 408 | 2021-09-21 | 20400 | keep | 0 | Sep | 2021 | 0.013894 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-21 07:59 | 2021-09-21 15:15 | 10 | 007:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100039 | New_Event | Bad Weather | Include | Include | Weather | 436 | 2021-09-21 | 4360 | keep | 0 | Sep | 2021 | 0.0029696 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-09-21 08:07 | 2021-09-21 08:08 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
CAGUAS | 2021-09-21 08:12 | 2021-09-21 11:51 | 90 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA. | C21092100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2021-09-21 | 19710 | keep | 0 | Sep | 2021 | 0.013424 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-09-21 08:14 | 2021-09-21 14:18 | 5 | 006:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA CERRO PUENTE | C21092100009 | New_Event | Wire Down | Include | Include | Equipment | 364 | 2021-09-21 | 1820 | keep | 0 | Sep | 2021 | 0.0012396 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-09-21 08:16 | 2021-09-21 13:55 | 6 | 005:39 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE TRASPATIO | C21092100011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 339 | 2021-09-21 | 2034 | keep | 0 | Sep | 2021 | 0.0013853 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-09-21 08:29 | 2021-09-21 19:29 | 70 | 011:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA | A21092100021 | New_Event | Bad Weather | Include | Include | Weather | 660 | 2021-09-21 | 46200 | keep | 0 | Sep | 2021 | 0.031467 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
YAUCO | 2021-09-21 08:36 | 2021-09-21 08:37 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210921000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
CANOVANAS | 2021-09-21 08:50 | 2021-09-21 17:19 | 10 | 008:29 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R21092100022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 509 | 2021-09-21 | 5090 | keep | 0 | Sep | 2021 | 0.0034668 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-21 08:53 | 2021-09-21 20:52 | 300 | 011:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21092100054 | New_Event | Wire Down | Include | Include | Equipment | 719 | 2021-09-21 | 215700 | keep | 0 | Sep | 2021 | 0.14691 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-09-21 08:53 | 2021-09-21 11:30 | 1 | 002:37 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR CLIENTE TENIA AVERIA INTERNA | M21092100053 | New_Event | Other Causes | Include | Include | Other | 157 | 2021-09-21 | 157 | keep | 0 | Sep | 2021 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-21 08:55 | 2021-09-21 12:06 | 25 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | A21092100025 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2021-09-21 | 4775 | keep | 0 | Sep | 2021 | 0.0032522 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-21 09:04 | 2021-09-22 13:44 | 50 | 028:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTES TRONADAS Y LLUVIAS | B21092100021 | New_Event | Bad Weather | Include | Include | Weather | 1720 | 2021-09-21 | 86000 | keep | 0 | Sep | 2021 | 0.058574 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-21 09:27 | 2021-09-21 15:17 | 15 | 005:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO SECUNDARIA | P21092000025 | New_Event | Wire Down | Include | Include | Equipment | 350 | 2021-09-21 | 5250 | keep | 0 | Sep | 2021 | 0.0035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-09-21 09:27 | 2021-09-21 18:53 | 50 | 009:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100064 | New_Event | Bad Weather | Include | Include | Weather | 566 | 2021-09-21 | 28300 | keep | 0 | Sep | 2021 | 0.019275 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-21 09:33 | 2021-09-21 13:25 | 150 | 003:52 | P | ESTRUCTURA AVERIADA | SE ABRIERON MACHETES PARA RETIRAR POSTE PARTIDO TRASPATIO QUE SE SECCIONALIZO AYER. SE RETIRO POSTE Y SE CERRO MACHETES. TOD EL MUNDO EN SERVICIO Y MAÃ‘ANA CONTINUARAN LOS TRABAJOS | B21092100026 | New_Event | Defective Pole | Include | Include | Equipment | 232 | 2021-09-21 | 34800 | keep | 0 | Sep | 2021 | 0.023702 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-09-21 09:34 | 2021-09-21 09:44 | 200 | 000:10 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO 2 MACHETES QUEMADOS Y 5 DISCOS | R21092100004 | New_Event | Switch Failure | Include | Include | Equipment | 10 | 2021-09-21 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-21 09:38 | 2021-09-21 14:50 | 40 | 005:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21092100068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2021-09-21 | 12480 | keep | 0 | Sep | 2021 | 0.0085001 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-21 09:41 | 2021-09-21 11:15 | 100 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100034 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2021-09-21 | 9400 | keep | 0 | Sep | 2021 | 0.0064023 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-09-21 09:53 | 2021-09-21 09:54 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210912000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1475 | keep | 0 | Sep | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
AGUADILLA | 2021-09-21 09:53 | 2021-09-21 18:48 | 15 | 008:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | M21092100072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 535 | 2021-09-21 | 8025 | keep | 0 | Sep | 2021 | 0.0054658 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-21 09:57 | 2021-09-21 11:30 | 6 | 001:33 | P | HERRAJE ROTO O PODRIDO | SE ABRIO TRANSFORMADOR PARA FIJAR TRANSFORMADOR POR TORNILLO PARTIDO | A21092100048 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 93 | 2021-09-21 | 558 | keep | 0 | Sep | 2021 | 0.00038005 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-21 09:58 | 2021-09-21 09:59 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 2605 | keep | 0 | Sep | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
CANOVANAS | 2021-09-21 10:09 | 2021-09-21 10:10 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21092100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1894 | keep | 0 | Sep | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
ARECIBO | 2021-09-21 10:10 | 2021-09-21 12:57 | 2 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADO | A21092100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-09-21 | 334 | keep | 0 | Sep | 2021 | 0.00022749 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2021-09-21 10:14 | 2021-09-21 11:35 | 234 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2021-09-21 | 18954 | keep | 0 | Sep | 2021 | 0.012909 | 0.00015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 234
PONCE | 2021-09-21 10:14 | 2021-09-21 11:35 | 2468 | 001:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2021-09-21 | 199908 | keep | 0 | Sep | 2021 | 0.13616 | 0.0016809 | Sustained | FALSE | TRUE | Not_TMED_Event | 2468
BAYAMON | 2021-09-21 10:19 | 2021-09-21 10:48 | 10 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO NEUTRAL | S21092000041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-09-21 | 290 | keep | 0 | Sep | 2021 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-21 10:20 | 2021-09-21 14:43 | 40 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B21092100037 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2021-09-21 | 10520 | keep | 0 | Sep | 2021 | 0.0071651 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-21 10:40 | 2021-09-21 11:18 | 5 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | M21091900169 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-09-21 | 190 | keep | 0 | Sep | 2021 | 0.00012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-09-21 10:43 | 2021-09-21 15:22 | 20 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE DESPEGO BAJANTE PRIMARIO DE TENSOR | R21092100043 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2021-09-21 | 5580 | keep | 0 | Sep | 2021 | 0.0038005 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-09-21 10:52 | 2021-09-21 14:55 | 1 | 004:03 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR CLIENTE RETIRO EQUIPO DEFECTUOSO | M21092100084 | New_Event | Other Causes | Include | Include | Other | 243 | 2021-09-21 | 243 | keep | 0 | Sep | 2021 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-21 11:07 | 2021-09-21 13:03 | 4 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21092100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-21 | 464 | keep | 0 | Sep | 2021 | 0.00031603 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-09-21 11:23 | 2021-09-21 12:20 | 10 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECCIONES Y BAJANTE SECUNDARIO | A21092100046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-09-21 | 570 | keep | 0 | Sep | 2021 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-21 11:25 | 2021-09-22 13:58 | 80 | 026:33 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21092100112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1593 | 2021-09-21 | 127440 | keep | 0 | Sep | 2021 | 0.086799 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-21 11:34 | 2021-09-22 09:38 | 50 | 022:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21092100145 | New_Event | Cutout Failure | Include | Include | Equipment | 1324 | 2021-09-21 | 66200 | keep | 0 | Sep | 2021 | 0.045089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-21 11:43 | 2021-09-21 14:58 | 20 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEA PARTIDA | A21092100049 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2021-09-21 | 3900 | keep | 0 | Sep | 2021 | 0.0026563 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-21 11:45 | 2021-09-21 12:55 | 1 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C21092100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-09-21 | 70 | keep | 0 | Sep | 2021 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-09-21 11:47 | 2021-09-21 14:15 | 50 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21092100041 | New_Event |  |  | Include | Wildlife | 148 | 2021-09-21 | 7400 | keep | 0 | Sep | 2021 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-21 11:56 | 2021-09-21 15:11 | 40 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | C21092100031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-09-21 | 7800 | keep | 0 | Sep | 2021 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-09-21 11:58 | 2021-09-21 20:17 | 80 | 008:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21092100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 499 | 2021-09-21 | 39920 | keep | 0 | Sep | 2021 | 0.027189 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-21 12:01 | 2021-09-21 12:02 | 5063 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN CORTE DE LINEA MAL TIEMPO | P21092000045 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-21 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | TRUE | Not_TMED_Event | 5063
YAUCO | 2021-09-21 12:01 | 2021-09-21 16:57 | 75 | 004:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21092100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-09-21 | 22200 | keep | 0 | Sep | 2021 | 0.01512 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-09-21 12:02 | 2021-09-21 19:00 | 15 | 006:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN CORTE DE LINEA MAL TIEMPO | P21092000045 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 418 | 2021-09-21 | 6270 | keep | 0 | Sep | 2021 | 0.0042705 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-09-21 12:03 | 2021-09-21 14:25 | 4 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL | C21091700129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-09-21 | 568 | keep | 0 | Sep | 2021 | 0.00038686 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-21 12:34 | 2021-09-21 19:24 | 20 | 006:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES | S21092100130 | New_Event | Secondary Wire Down | Include | Include | Equipment | 410 | 2021-09-21 | 8200 | keep | 0 | Sep | 2021 | 0.005585 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-09-21 12:44 | 2021-09-21 15:50 | 15 | 003:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21092100050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 186 | 2021-09-21 | 2790 | keep | 0 | Sep | 2021 | 0.0019003 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-21 12:54 | 2021-09-21 13:02 | 653 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21092100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-09-21 | 5224 | keep | 0 | Sep | 2021 | 0.003558 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
SAN JUAN | 2021-09-21 13:06 | 2021-09-22 20:13 | 20 | 031:07 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO PROVICIONAL AEREO HACIA T - 269 | R21092100070 | New_Event | UG Cable Fault | Include | Include | Equipment | 1867 | 2021-09-21 | 37340 | keep | 0 | Sep | 2021 | 0.025432 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-21 13:06 | 2021-09-23 17:11 | 20 | 052:05 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVICIONAL DEL T - 269 AL T - 268 | R21092100070 | New_Event | UG Cable Fault | Include | Include | Equipment | 3125 | 2021-09-21 | 62500 | keep | 0 | Sep | 2021 | 0.042568 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-21 13:08 | 2021-09-21 14:47 | 653 | 001:39 | T | DESGANCHE | SE REALISO DESGANCHE | PPI092100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2021-09-21 | 64647 | keep | 0 | Sep | 2021 | 0.044031 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
CAGUAS | 2021-09-21 13:09 | 2021-09-21 15:03 | 40 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092100038 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2021-09-21 | 4560 | keep | 0 | Sep | 2021 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-21 13:18 | 2021-09-21 18:01 | 32 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092100138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2021-09-21 | 9056 | keep | 0 | Sep | 2021 | 0.006168 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
SAN JUAN | 2021-09-21 13:24 | 2021-09-21 13:25 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 225 | keep | 0 | Sep | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-21 13:24 | 2021-09-21 13:25 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-09-21 13:24 | 2021-09-23 11:52 | 45 | 046:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B21092100067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2788 | 2021-09-21 | 125460 | keep | 0 | Sep | 2021 | 0.08545 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CANOVANAS | 2021-09-21 13:33 | 2021-09-21 15:22 | 17 | 001:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | R21092100032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 109 | 2021-09-21 | 1853 | keep | 0 | Sep | 2021 | 0.0012621 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2021-09-21 13:57 | 2021-09-21 17:20 | 150 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65, 2 X 50 , 2 X 25 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100135 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-09-21 | 30450 | keep | 0 | Sep | 2021 | 0.020739 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-21 14:08 | 2021-09-21 20:18 | 20 | 006:10 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | M21092100139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2021-09-21 | 7400 | keep | 0 | Sep | 2021 | 0.0050401 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-21 14:12 | 2021-09-21 15:44 | 5 | 001:32 | P | OTRAS CAUSAS | SE ABRIO CORTE DE LINEA PARA ELIMINAR POSTES FUERA DE SERVICIO | P21092100070 | New_Event | Other Causes | Include | Include | Other | 92 | 2021-09-21 | 460 | keep | 0 | Sep | 2021 | 0.0003133 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-09-21 14:20 | 2021-09-21 17:49 | 200 | 003:29 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA Y 1 X 100 EN CORTE DE LINEA | S21092100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-09-21 | 41800 | keep | 0 | Sep | 2021 | 0.02847 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-21 14:45 | 2021-09-21 14:46 | 1746 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21092100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-21 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-09-21 14:46 | 2021-09-21 18:58 | 60 | 004:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092100095 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-09-21 | 15120 | keep | 0 | Sep | 2021 | 0.010298 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-21 14:49 | 2021-09-21 16:32 | 11 | 001:43 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEANDO 50 KVA X 50 KVA | C21092100045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 103 | 2021-09-21 | 1133 | keep | 0 | Sep | 2021 | 0.00077168 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-09-21 14:54 | 2021-09-21 14:55 | 327 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 5200 Y 6500 | C21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 327 | keep | 0 | Sep | 2021 | 0.00022272 | 0.00022272 | Momentary | FALSE | TRUE | Not_TMED_Event | 327
CAGUAS | 2021-09-21 14:54 | 2021-09-21 14:55 | 1843 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 5200 Y 6500 | C21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 1843 | keep | 0 | Sep | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | TRUE | Not_TMED_Event | 1843
CAGUAS | 2021-09-21 14:54 | 2021-09-21 14:55 | 2203 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 5200 Y 6500 | C21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 2203 | keep | 0 | Sep | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | TRUE | Not_TMED_Event | 2203
CAGUAS | 2021-09-21 14:54 | 2021-09-21 14:55 | 2457 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 5200 Y 6500 | C21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 2457 | keep | 0 | Sep | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | TRUE | Not_TMED_Event | 2457
SAN JUAN | 2021-09-21 14:56 | 2021-09-21 15:18 | 533 | 000:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE REMPLAZO MACHETE EN RISER DE SALIDA | S21092100172 | New_Event | Wire Down | Include | Include | Equipment | 22 | 2021-09-21 | 11726 | keep | 0 | Sep | 2021 | 0.0079865 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
UTUADO | 2021-09-21 15:00 | 2021-09-21 15:17 | 2 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092100101 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2021-09-21 | 34 | keep | 0 | Sep | 2021 | 2.3157e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-09-21 15:05 | 2021-09-21 16:20 | 60 | 001:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21092100149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-09-21 | 4500 | keep | 0 | Sep | 2021 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-21 15:08 | 2021-09-21 20:52 | 12 | 005:44 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEANDO DE 50 KVA X 50 KVA Y UNA CRUCETA | C21091900039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 344 | 2021-09-21 | 4128 | keep | 0 | Sep | 2021 | 0.0028116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-21 15:16 | 2021-09-21 15:17 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092100150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1097 | keep | 0 | Sep | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
SAN JUAN | 2021-09-21 15:19 | 2021-09-21 17:20 | 1021 | 002:01 | T | DESGANCHE | SE PATRULLO Y NO SE ENCONTRO CONDICION SE PROCEDIO A CERRAR POR SCADA | S21092100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-09-21 | 123541 | keep | 0 | Sep | 2021 | 0.084143 | 0.0006954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1021
UTUADO | 2021-09-21 15:24 | 2021-09-21 17:42 | 16 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092100105 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-09-21 | 2208 | keep | 0 | Sep | 2021 | 0.0015039 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
CAGUAS | 2021-09-21 15:31 | 2021-09-21 17:10 | 7 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL | C21092100047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2021-09-21 | 693 | keep | 0 | Sep | 2021 | 0.000472 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-09-21 15:35 | 2021-09-21 17:18 | 35 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE | B21092100084 | New_Event |  |  | Include | Wildlife | 103 | 2021-09-21 | 3605 | keep | 0 | Sep | 2021 | 0.0024553 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-09-21 15:39 | 2021-09-21 15:40 | 2106 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21092100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-21 | 2106 | keep | 0 | Sep | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-09-21 15:39 | 2021-09-21 15:40 | 635 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 635 | keep | 0 | Sep | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2021-09-21 15:40 | 2021-09-21 17:25 | 2 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN BANCO DE TRANSFORMADOR MAL TIEMPO | R21092100091 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 105 | 2021-09-21 | 210 | keep | 0 | Sep | 2021 | 0.00014303 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-09-21 15:41 | 2021-09-22 10:15 | 100 | 018:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100108 | New_Event | Bad Weather | Include | Include | Weather | 1114 | 2021-09-21 | 111400 | keep | 0 | Sep | 2021 | 0.075874 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-21 15:45 | 2021-09-21 16:20 | 80 | 000:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | M21092100153 | New_Event | Bad Weather | Include | Include | Weather | 35 | 2021-09-21 | 2800 | keep | 0 | Sep | 2021 | 0.0019071 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-21 15:54 | 2021-09-21 15:55 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21092100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 2179 | keep | 0 | Sep | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CAGUAS | 2021-09-21 15:57 | 2021-09-21 15:58 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1342 | keep | 0 | Sep | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
ARECIBO | 2021-09-21 16:04 | 2021-09-21 21:21 | 85 | 005:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR MAL TIEMPO | A21092100122 | New_Event | Bad Weather | Include | Include | Weather | 317 | 2021-09-21 | 26945 | keep | 0 | Sep | 2021 | 0.018352 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
MAYAGÃœEZ | 2021-09-21 16:07 | 2021-09-21 18:24 | 120 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 Y 1 X 80 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100166 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-09-21 | 16440 | keep | 0 | Sep | 2021 | 0.011197 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-09-21 16:08 | 2021-09-21 22:56 | 20 | 006:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092100167 | New_Event | Bad Weather | Include | Include | Weather | 408 | 2021-09-21 | 8160 | keep | 0 | Sep | 2021 | 0.0055577 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-21 16:20 | 2021-09-21 20:29 | 11 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092100172 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-09-21 | 2739 | keep | 0 | Sep | 2021 | 0.0018655 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
ARECIBO | 2021-09-21 16:20 | 2021-09-21 18:50 | 20 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | A21092100130 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2021-09-21 | 3000 | keep | 0 | Sep | 2021 | 0.0020433 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-09-21 16:26 | 2021-09-22 19:57 | 9 | 027:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADDO AVERIADO DE 50 KVA X 50 KVA | C21092100055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1651 | 2021-09-21 | 14859 | keep | 0 | Sep | 2021 | 0.01012 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-09-21 16:27 | 2021-09-21 22:28 | 50 | 006:01 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN CORTE DE LINEA AVERIA DEL T - 270 AL T - 269 | R21092100106 | New_Event | UG Cable Fault | Include | Include | Equipment | 361 | 2021-09-21 | 18050 | keep | 0 | Sep | 2021 | 0.012294 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-21 16:35 | 2021-09-21 20:35 | 80 | 004:00 | P | NO SE REPORTO CAUSA | SE REPUSO 1 X 80 EN CORTE DE LINEA | B21092100109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-09-21 | 19200 | keep | 0 | Sep | 2021 | 0.013077 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-21 16:38 | 2021-09-22 16:06 | 20 | 023:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR EN 3 TRANSFORMADORES DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A21092100142 | New_Event | Bad Weather | Include | Include | Weather | 1408 | 2021-09-21 | 28160 | keep | 0 | Sep | 2021 | 0.01918 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-09-21 16:40 | 2021-09-22 09:38 | 400 | 016:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR SE ABRIO INTERRUPTOR PARA REPARAR | A21092100145 | New_Event | Wire Down | Include | Include | Equipment | 1018 | 2021-09-21 | 407200 | keep | 0 | Sep | 2021 | 0.27734 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2021-09-21 16:58 | 2021-09-21 20:50 | 40 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092100183 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2021-09-21 | 9280 | keep | 0 | Sep | 2021 | 0.0063206 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-21 17:00 | 2021-09-22 17:57 | 1 | 024:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR LA MISMA CAPACIDAD EN FID:18420750 / MARCA: COOPER / #SERIE: 2055098931 / VOLTAJES 4.16/7.2KV 120-240V | M21092200184 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1497 | 2021-09-21 | 1497 | keep | 0 | Sep | 2021 | 0.0010196 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-21 17:03 | 2021-09-21 19:05 | 100 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | B21092100127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-09-21 | 12200 | keep | 0 | Sep | 2021 | 0.0083094 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-21 17:06 | 2021-09-21 20:52 | 40 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21092100128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2021-09-21 | 9040 | keep | 0 | Sep | 2021 | 0.0061571 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-21 17:18 | 2021-09-22 15:30 | 175 | 022:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092100191 | New_Event | Bad Weather | Include | Include | Weather | 1332 | 2021-09-21 | 233100 | keep | 0 | Sep | 2021 | 0.15876 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
UTUADO | 2021-09-21 17:18 | 2021-09-21 20:26 | 40 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR MAL TIEMPO | A21092100153 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-09-21 | 7520 | keep | 0 | Sep | 2021 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-09-21 17:22 | 2021-09-21 21:34 | 60 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092100138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2021-09-21 | 15120 | keep | 0 | Sep | 2021 | 0.010298 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-09-21 17:35 | 2021-09-21 20:48 | 200 | 003:13 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES | A21092100156 | New_Event | Switch Failure | Include | Include | Equipment | 193 | 2021-09-21 | 38600 | keep | 0 | Sep | 2021 | 0.02629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-09-21 17:49 | 2021-09-21 17:51 | 172 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-21 | 344 | keep | 0 | Sep | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
PONCE | 2021-09-21 17:52 | 2021-09-21 17:53 | 653 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210921000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 653 | keep | 0 | Sep | 2021 | 0.00044476 | 0.00044476 | Momentary | FALSE | FALSE | Not_TMED_Event | 653
UTUADO | 2021-09-21 17:52 | 2021-09-21 18:38 | 10 | 000:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092100159 | New_Event | Bad Weather | Include | Include | Weather | 46 | 2021-09-21 | 460 | keep | 0 | Sep | 2021 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-09-21 17:54 | 2021-09-21 17:55 | 50 | 000:01 | P | ESTRUCTURA AVERIADA | SE REMPLASO POSTE PRIMARIO | P21092100035 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-09-21 | 50 | keep | 0 | Sep | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-09-21 18:02 | 2021-09-21 20:00 | 10 | 001:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD EN EL FID31469069 / MARCA EATON / #SERIE 2055099370 / VOLTAJES 2.4/4.16KV 120/240V | M21092100202 | New_Event | Service Transformer Failure | Include | Include | Equipment | 118 | 2021-09-21 | 1180 | keep | 0 | Sep | 2021 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-21 18:04 | 2021-09-21 19:51 | 1026 | 001:47 | T | DESCONECTIVO DEFECTUOSO | RECERRO INTERRUPTOR 2 VECES QUEDO FUERA SE REALIZO PRUEBA PROBO MALO SE SECCIONALIZO TRAMOS SOTERRADO CERRADO POR CONTROL | R21092100128 | New_Event | Switch Failure | Include | Include | Equipment | 107 | 2021-09-21 | 109782 | keep | 0 | Sep | 2021 | 0.074772 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
UTUADO | 2021-09-21 18:06 | 2021-09-22 19:00 | 50 | 024:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO POSTE PRIMARIO SE CERRO CORTE DE LINEA | A21092100161 | New_Event | Wire Down | Include | Include | Equipment | 1494 | 2021-09-21 | 74700 | keep | 0 | Sep | 2021 | 0.050878 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-21 18:15 | 2021-09-22 10:36 | 11 | 016:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21092100065 | New_Event | Bad Weather | Include | Include | Weather | 981 | 2021-09-21 | 10791 | keep | 0 | Sep | 2021 | 0.0073497 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-09-21 18:19 | 2021-09-21 21:01 | 15 | 002:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 X 50 | S21092100107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 162 | 2021-09-21 | 2430 | keep | 0 | Sep | 2021 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-21 18:23 | 2021-09-21 20:50 | 3438 | 002:27 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR EN EL CAMPO | B21092100150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-09-21 | 505386 | keep | 0 | Sep | 2021 | 0.34422 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2021-09-21 18:26 | 2021-09-22 15:18 | 1 | 020:52 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S21092100230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1252 | 2021-09-21 | 1252 | keep | 0 | Sep | 2021 | 0.00085273 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-21 18:35 | 2021-09-21 18:36 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1570 | keep | 0 | Sep | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2021-09-21 18:35 | 2021-09-21 18:36 | 31 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 31 | keep | 0 | Sep | 2021 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2021-09-21 18:36 | 2021-09-21 20:17 | 40 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092000148 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-09-21 | 4040 | keep | 0 | Sep | 2021 | 0.0027516 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-21 18:37 | 2021-09-21 18:38 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1834 | keep | 0 | Sep | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
FAJARDO | 2021-09-21 18:42 | 2021-09-22 12:08 | 9 | 017:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | R21092100142 | New_Event | Cutout Failure | Include | Include | Equipment | 1046 | 2021-09-21 | 9414 | keep | 0 | Sep | 2021 | 0.0064118 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-09-21 18:48 | 2021-09-21 18:49 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092100209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 990 | keep | 0 | Sep | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2021-09-21 19:11 | 2021-09-21 22:49 | 1021 | 003:38 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S21092100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-09-21 | 222578 | keep | 0 | Sep | 2021 | 0.1516 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-21 19:11 | 2021-09-21 19:12 | 3798 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 3798 | keep | 0 | Sep | 2021 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
GUAYAMA | 2021-09-21 19:19 | 2021-09-22 10:44 | 29 | 015:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | P21092100099 | New_Event | Bad Weather | Include | Include | Weather | 925 | 2021-09-21 | 26825 | keep | 0 | Sep | 2021 | 0.01827 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2021-09-21 19:21 | 2021-09-22 01:16 | 50 | 005:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN AEREO PROVISIONAL SE REMPLAZO CAJA PRIMARIA | B21092100172 | New_Event | Cutout Failure | Include | Include | Equipment | 355 | 2021-09-21 | 17750 | keep | 0 | Sep | 2021 | 0.012089 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-09-21 19:28 | 2021-09-21 23:20 | 4 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | R21092100161 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2021-09-21 | 928 | keep | 0 | Sep | 2021 | 0.00063206 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-21 19:30 | 2021-09-22 18:54 | 25 | 023:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA | B21092100177 | New_Event | Cutout Failure | Include | Include | Equipment | 1404 | 2021-09-21 | 35100 | keep | 0 | Sep | 2021 | 0.023906 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-21 19:30 | 2021-09-22 16:04 | 40 | 020:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092100177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1234 | 2021-09-21 | 49360 | keep | 0 | Sep | 2021 | 0.033619 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-21 19:33 | 2021-09-21 23:04 | 120 | 003:31 | P | DESGANCHE | 1 X 50 Y 2 X 30 EN CORTES DE LINEA SE REALIZO DESGANCHE | B21092100179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-09-21 | 25320 | keep | 0 | Sep | 2021 | 0.017245 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
VEGA BAJA | 2021-09-21 19:37 | 2021-09-22 12:32 | 50 | 016:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA RAYO | B21092100181 | New_Event | Bad Weather | Include | Include | Weather | 1015 | 2021-09-21 | 50750 | keep | 0 | Sep | 2021 | 0.034566 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-21 19:39 | 2021-09-21 23:08 | 1271 | 003:29 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO EL ALIMENTADOR | R21092100251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2021-09-21 | 265639 | keep | 0 | Sep | 2021 | 0.18093 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2021-09-21 19:43 | 2021-09-22 10:02 | 65 | 014:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21092100071 | New_Event | Bad Weather | Include | Include | Weather | 859 | 2021-09-21 | 55835 | keep | 0 | Sep | 2021 | 0.038029 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-09-21 19:49 | 2021-09-22 20:39 | 2 | 024:50 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | M21092100217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1490 | 2021-09-21 | 2980 | keep | 0 | Sep | 2021 | 0.0020297 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
UTUADO | 2021-09-21 19:50 | 2021-09-22 14:30 | 40 | 018:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100181 | New_Event | Bad Weather | Include | Include | Weather | 1120 | 2021-09-21 | 44800 | keep | 0 | Sep | 2021 | 0.030513 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-21 19:50 | 2021-09-22 19:32 | 12 | 023:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092100182 | New_Event | Bad Weather | Include | Include | Weather | 1422 | 2021-09-21 | 17064 | keep | 0 | Sep | 2021 | 0.011622 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-21 19:51 | 2021-09-21 20:07 | 600 | 000:16 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | R21092100128 | Partial_restoration | Switch Failure | Include | Include | Equipment | 16 | 2021-09-21 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-21 19:51 | 2021-09-22 12:35 | 95 | 016:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 65 EN CORTES DE LINEAS SE REEMPLAZO AISLADOR | R21092100169 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1004 | 2021-09-21 | 95380 | keep | 0 | Sep | 2021 | 0.064963 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
PONCE | 2021-09-21 19:51 | 2021-09-22 13:43 | 4 | 017:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | P21092200100 | New_Event | Bad Weather | Include | Include | Weather | 1072 | 2021-09-21 | 4288 | keep | 0 | Sep | 2021 | 0.0029205 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-21 19:53 | 2021-09-23 15:01 | 30 | 043:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S21092100246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2588 | 2021-09-21 | 77640 | keep | 0 | Sep | 2021 | 0.05288 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-21 20:04 | 2021-09-22 19:50 | 30 | 023:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM T-22 AVERIADO 50KVA POR 50KVA @ 13KV | B21092100187 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1426 | 2021-09-21 | 42780 | keep | 0 | Sep | 2021 | 0.029137 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-21 20:07 | 2021-09-21 20:08 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR PERSONAL REALIZANDO PRUEBA CERRADO POR CONTROL | R21092100128 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-09-21 | 1026 | keep | 0 | Sep | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-21 20:08 | 2021-09-21 20:59 | 600 | 000:51 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | R21092100128 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 51 | 2021-09-21 | 30600 | keep | 0 | Sep | 2021 | 0.020842 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
ARECIBO | 2021-09-21 20:14 | 2021-09-22 15:35 | 100 | 019:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21092100187 | New_Event | Wire Down | Include | Include | Equipment | 1161 | 2021-09-21 | 116100 | keep | 0 | Sep | 2021 | 0.079075 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-21 20:15 | 2021-09-22 11:10 | 200 | 014:55 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100188 | New_Event | Bad Weather | Include | Include | Weather | 895 | 2021-09-21 | 179000 | keep | 0 | Sep | 2021 | 0.12192 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-21 20:20 | 2021-09-22 13:00 | 200 | 016:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A21092100303 | New_Event | Wire Down | Include | Include | Equipment | 1000 | 2021-09-21 | 200000 | keep | 0 | Sep | 2021 | 0.13622 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-21 20:20 | 2021-09-21 20:41 | 30 | 000:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21092100192 | New_Event | Cutout Failure | Include | Include | Equipment | 21 | 2021-09-21 | 630 | keep | 0 | Sep | 2021 | 0.00042909 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-21 20:31 | 2021-09-21 20:41 | 2777 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA NO CERRO POR SCADA SE CERRO MANUAL ELECTRICO | A21092100200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-09-21 | 27770 | keep | 0 | Sep | 2021 | 0.018914 | 0.0018914 | Sustained | FALSE | FALSE | Not_TMED_Event | 2777
BAYAMON | 2021-09-21 20:31 | 2021-09-23 14:47 | 10 | 042:16 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | B21092100196 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2536 | 2021-09-21 | 25360 | keep | 0 | Sep | 2021 | 0.017273 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-21 20:34 | 2021-09-22 10:29 | 30 | 013:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE AISLADOR ROTO | C21092100081 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 835 | 2021-09-21 | 25050 | keep | 0 | Sep | 2021 | 0.017061 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-09-21 20:36 | 2021-09-22 11:40 | 207 | 015:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE EN EL PISO | P21092100108 | New_Event | Wire Down | Include | Include | Equipment | 904 | 2021-09-21 | 187128 | keep | 0 | Sep | 2021 | 0.12745 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2021-09-21 20:40 | 2021-09-22 14:45 | 2 | 018:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092100207 | New_Event | Bad Weather | Include | Include | Weather | 1085 | 2021-09-21 | 2170 | keep | 0 | Sep | 2021 | 0.001478 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-09-21 20:41 | 2021-09-21 23:08 | 1879 | 002:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2021-09-21 | 276213 | keep | 0 | Sep | 2021 | 0.18813 | 0.0012798 | Sustained | FALSE | TRUE | Not_TMED_Event | 1879
ARECIBO | 2021-09-21 20:41 | 2021-09-21 23:08 | 2777 | 002:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2021-09-21 | 408219 | keep | 0 | Sep | 2021 | 0.27804 | 0.0018914 | Sustained | FALSE | TRUE | Not_TMED_Event | 2777
ARECIBO | 2021-09-21 20:41 | 2021-09-21 23:08 | 2 | 002:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2021-09-21 | 294 | keep | 0 | Sep | 2021 | 0.00020024 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
ARECIBO | 2021-09-21 20:41 | 2021-09-21 23:08 | 2839 | 002:27 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2021-09-21 | 417333 | keep | 0 | Sep | 2021 | 0.28424 | 0.0019336 | Sustained | FALSE | TRUE | Not_TMED_Event | 2839
ARECIBO | 2021-09-21 20:41 | 2021-09-21 23:08 | 1160 | 002:27 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2021-09-21 | 170520 | keep | 0 | Sep | 2021 | 0.11614 | 0.00079007 | Sustained | FALSE | TRUE | Not_TMED_Event | 1160
ARECIBO | 2021-09-21 20:41 | 2021-09-21 23:08 | 1860 | 002:27 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 147 | 2021-09-21 | 273420 | keep | 0 | Sep | 2021 | 0.18623 | 0.0012668 | Sustained | FALSE | TRUE | Not_TMED_Event | 1860
BAYAMON | 2021-09-21 20:41 | 2021-09-21 20:42 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 2735 | keep | 0 | Sep | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
VEGA BAJA | 2021-09-21 20:42 | 2021-09-21 20:43 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 3332 | keep | 0 | Sep | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
BAYAMON | 2021-09-21 20:42 | 2021-09-22 00:46 | 2735 | 004:04 | T | DESGANCHE | SE SECCIONALIZO PARA DESGANCHAR Y SE CERRO POR SCADA | B21092100200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-09-21 | 667340 | keep | 0 | Sep | 2021 | 0.45452 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
ARECIBO | 2021-09-21 20:43 | 2021-09-21 20:44 | 3157 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 11400 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 3157 | keep | 0 | Sep | 2021 | 0.0021502 | 0.0021502 | Momentary | FALSE | TRUE | Not_TMED_Event | 3157
ARECIBO | 2021-09-21 20:43 | 2021-09-21 20:44 | 35 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 11400 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 35 | keep | 0 | Sep | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-21 20:43 | 2021-09-21 20:44 | 2916 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 11400 | A21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 2916 | keep | 0 | Sep | 2021 | 0.0019861 | 0.0019861 | Momentary | FALSE | TRUE | Not_TMED_Event | 2916
ARECIBO | 2021-09-21 20:45 | 2021-09-22 01:20 | 500 | 004:35 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100216 | New_Event | Bad Weather | Include | Include | Weather | 275 | 2021-09-21 | 137500 | keep | 0 | Sep | 2021 | 0.093651 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-09-21 20:49 | 2021-09-22 00:51 | 3157 | 004:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 SE ENERGIZO A TRAVES DE LA LINEA 2200 | A21092100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2021-09-21 | 763994 | keep | 0 | Sep | 2021 | 0.52035 | 0.0021502 | Sustained | FALSE | TRUE | Not_TMED_Event | 3157
ARECIBO | 2021-09-21 20:49 | 2021-09-22 00:51 | 35 | 004:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 SE ENERGIZO A TRAVES DE LA LINEA 2200 | A21092100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2021-09-21 | 8470 | keep | 0 | Sep | 2021 | 0.0057689 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-21 20:49 | 2021-09-22 00:51 | 2916 | 004:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 SE ENERGIZO A TRAVES DE LA LINEA 2200 | A21092100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2021-09-21 | 705672 | keep | 0 | Sep | 2021 | 0.48063 | 0.0019861 | Sustained | FALSE | TRUE | Not_TMED_Event | 2916
HUMACAO | 2021-09-21 20:52 | 2021-09-21 20:53 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092100088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 1089 | keep | 0 | Sep | 2021 | 0.00074171 | 0.00074171 | Momentary | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-09-21 20:52 | 2021-09-21 20:53 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092100088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 3896 | keep | 0 | Sep | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-09-21 20:52 | 2021-09-21 20:53 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092100088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 1467 | keep | 0 | Sep | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
PONCE | 2021-09-21 20:52 | 2021-09-21 20:53 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 2751 | keep | 0 | Sep | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | TRUE | Not_TMED_Event | 2751
PONCE | 2021-09-21 20:52 | 2021-09-21 20:53 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 576 | keep | 0 | Sep | 2021 | 0.00039231 | 0.00039231 | Momentary | FALSE | TRUE | Not_TMED_Event | 576
PONCE | 2021-09-21 20:52 | 2021-09-21 20:53 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 2584 | keep | 0 | Sep | 2021 | 0.00176 | 0.00176 | Momentary | FALSE | TRUE | Not_TMED_Event | 2584
PONCE | 2021-09-21 20:52 | 2021-09-21 20:53 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 1606 | keep | 0 | Sep | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | TRUE | Not_TMED_Event | 1606
PONCE | 2021-09-21 20:52 | 2021-09-21 20:53 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P210921000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 29 | keep | 0 | Sep | 2021 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 29
HUMACAO | 2021-09-21 20:53 | 2021-09-21 23:18 | 1089 | 002:25 | S | NO SE REPORTO CAUSA | SISPARO LINEA 3000 | C21092100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-09-21 | 157905 | keep | 0 | Sep | 2021 | 0.10755 | 0.00074171 | Sustained | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-09-21 20:53 | 2021-09-21 23:18 | 3896 | 002:25 | S | NO SE REPORTO CAUSA | SISPARO LINEA 3000 | C21092100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-09-21 | 564920 | keep | 0 | Sep | 2021 | 0.38476 | 0.0026535 | Sustained | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-09-21 20:53 | 2021-09-21 23:18 | 1467 | 002:25 | S | NO SE REPORTO CAUSA | SISPARO LINEA 3000 | C21092100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-09-21 | 212715 | keep | 0 | Sep | 2021 | 0.14488 | 0.00099917 | Sustained | FALSE | TRUE | Not_TMED_Event | 1467
BARRANQUITAS | 2021-09-21 20:53 | 2021-09-21 20:54 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 Y 8500 | C21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 2565 | keep | 0 | Sep | 2021 | 0.001747 | 0.001747 | Momentary | FALSE | TRUE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-09-21 20:53 | 2021-09-21 20:54 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 Y 8500 | C21092100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-21 | 3565 | keep | 0 | Sep | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | TRUE | Not_TMED_Event | 3565
PONCE | 2021-09-21 20:53 | 2021-09-21 20:54 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 1606 | keep | 0 | Sep | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
VEGA BAJA | 2021-09-21 20:58 | 2021-09-21 20:59 | 3076 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 3076 | keep | 0 | Sep | 2021 | 0.002095 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
SAN JUAN | 2021-09-21 20:59 | 2021-09-21 21:00 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21092100128 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-09-21 | 1026 | keep | 0 | Sep | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-21 21:00 | 2021-09-21 21:19 | 600 | 000:19 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | R21092100128 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 19 | 2021-09-21 | 11400 | keep | 0 | Sep | 2021 | 0.0077645 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
VEGA BAJA | 2021-09-21 21:13 | 2021-09-21 21:14 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 3387 | keep | 0 | Sep | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
SAN JUAN | 2021-09-21 21:19 | 2021-09-21 21:21 | 1026 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR PERSONAL REALIZANDO OPERACIONES CERRADO POR CONTROL | R21092100128 | Additional_clients | Switch Failure | Include | Include | Equipment | 2 | 2021-09-21 | 2052 | keep | 0 | Sep | 2021 | 0.0013976 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-21 21:21 | 2021-09-22 16:42 | 600 | 019:21 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | R21092100128 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1161 | 2021-09-21 | 696600 | keep | 0 | Sep | 2021 | 0.47445 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
PONCE | 2021-09-21 21:24 | 2021-09-22 09:09 | 110 | 011:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REPARO CONDUCTOR EN EL PISO | P21092100115 | New_Event | Wire Down | Include | Include | Equipment | 705 | 2021-09-21 | 77550 | keep | 0 | Sep | 2021 | 0.052819 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
HUMACAO | 2021-09-21 21:25 | 2021-09-21 21:26 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 5630 | keep | 0 | Sep | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2021-09-21 21:29 | 2021-09-21 23:54 | 100 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 65 EN CORTES DE LINEA | B21092100223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-09-21 | 14500 | keep | 0 | Sep | 2021 | 0.0098759 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-21 21:32 | 2021-09-21 21:33 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210921000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 527 | keep | 0 | Sep | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
VEGA BAJA | 2021-09-21 21:40 | 2021-09-22 09:10 | 4702 | 011:30 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR ABRIENDO MACHETES EN CARR #2 ALMIRANTE NORTE | B21092100225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 690 | 2021-09-21 | 3244380 | keep | 0 | Sep | 2021 | 2.2097 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
HUMACAO | 2021-09-21 21:44 | 2021-09-22 00:35 | 5630 | 002:51 | T | MAL TIEMPO/RAYOS/WET ASH | SE FIJO INTELLIRUPTER 2603-08E PERNO PARTIDO POR RAYO | C21092100106 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2021-09-21 | 962730 | keep | 0 | Sep | 2021 | 0.65571 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
CANOVANAS | 2021-09-21 21:47 | 2021-09-22 11:08 | 5 | 013:21 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR | R21092100182 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 801 | 2021-09-21 | 4005 | keep | 0 | Sep | 2021 | 0.0027278 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-09-21 21:50 | 2021-09-22 11:39 | 286 | 013:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21092100108 | New_Event | Bad Weather | Include | Include | Weather | 829 | 2021-09-21 | 237094 | keep | 0 | Sep | 2021 | 0.16148 | 0.00019479 | Sustained | FALSE | TRUE | Not_TMED_Event | 286
YAUCO | 2021-09-21 22:00 | 2021-09-21 22:49 | 200 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CONVERTIDOR POR MAL TIEMPO | P21092100118 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-09-21 | 9800 | keep | 0 | Sep | 2021 | 0.0066747 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-09-21 22:00 | 2021-09-21 22:15 | 250 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092100289 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2021-09-21 | 3750 | keep | 0 | Sep | 2021 | 0.0025541 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
VEGA BAJA | 2021-09-21 22:31 | 2021-09-22 21:23 | 20 | 022:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092100249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1372 | 2021-09-21 | 27440 | keep | 0 | Sep | 2021 | 0.018689 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-21 22:42 | 2021-09-22 17:41 | 20 | 018:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21092100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1139 | 2021-09-21 | 22780 | keep | 0 | Sep | 2021 | 0.015515 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-21 22:44 | 2021-09-22 15:30 | 225 | 016:46 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21092100122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1006 | 2021-09-21 | 226350 | keep | 0 | Sep | 2021 | 0.15417 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
SAN JUAN | 2021-09-21 22:49 | 2021-09-22 00:29 | 200 | 001:40 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S21092100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 100 | 2021-09-21 | 20000 | keep | 0 | Sep | 2021 | 0.013622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-21 23:00 | 2021-09-22 10:44 | 130 | 011:44 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | R21092100190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 704 | 2021-09-21 | 91520 | keep | 0 | Sep | 2021 | 0.062334 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
ARECIBO | 2021-09-21 23:08 | 2021-09-23 17:58 | 5 | 042:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092100304 | New_Event | Bad Weather | Include | Include | Weather | 2570 | 2021-09-21 | 12850 | keep | 0 | Sep | 2021 | 0.0087521 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-21 23:08 | 2021-09-22 00:15 | 2777 | 001:07 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA NO CERO POR SCADA SE CERRO MANUAL ELECTRICO | A21092100200 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-09-21 | 186059 | keep | 0 | Sep | 2021 | 0.12672 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-21 23:08 | 2021-09-22 10:55 | 30 | 011:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A21092100192 | New_Event | Wire Down | Include | Include | Equipment | 707 | 2021-09-21 | 21210 | keep | 0 | Sep | 2021 | 0.014446 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-21 23:10 | 2021-09-21 23:11 | 533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1330-05 CARGA POR EL 1330-02 | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 533 | keep | 0 | Sep | 2021 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
VEGA BAJA | 2021-09-21 23:10 | 2021-09-21 23:11 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 2704 | keep | 0 | Sep | 2021 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2021-09-21 23:28 | 2021-09-21 23:29 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21092100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-21 | 2203 | keep | 0 | Sep | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
HUMACAO | 2021-09-22 00:14 | 2021-09-22 00:15 | 519 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21092200002 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-22 | 519 | keep | 0 | Sep | 2021 | 0.00035349 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2021-09-22 00:15 | 2021-09-22 16:52 | 7 | 016:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR REPTIL | C21092200176 | 1st_after_momentary |  |  | Include | Wildlife | 997 | 2021-09-22 | 6979 | keep | 0 | Sep | 2021 | 0.0047534 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-09-22 00:34 | 2021-09-22 10:12 | 20 | 009:38 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21092200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 578 | 2021-09-22 | 11560 | keep | 0 | Sep | 2021 | 0.0078735 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-09-22 00:35 | 2021-09-22 12:01 | 1866 | 011:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE FIJO INTELLIRUPTER 2603-08 PERNO PARTIDO POR RAYO | C21092200006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 686 | 2021-09-22 | 1280076 | keep | 0 | Sep | 2021 | 0.87185 | 0.0012709 | Sustained | FALSE | FALSE | Not_TMED_Event | 1866
BAYAMON | 2021-09-22 00:46 | 2021-09-22 01:29 | 2000 | 000:43 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | B21092100200 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-09-22 | 86000 | keep | 0 | Sep | 2021 | 0.058574 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-09-22 01:02 | 2021-09-22 10:55 | 145 | 009:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | P21090000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 593 | 2021-09-22 | 85985 | keep | 0 | Sep | 2021 | 0.058564 | 9.8759e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 145
SAN JUAN | 2021-09-22 03:12 | 2021-09-22 03:15 | 5620 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA EL 90% DEL 1336-07 ESTA POR EL 1620-04 | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-22 | 16860 | keep | 0 | Sep | 2021 | 0.011483 | 0.0038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-09-22 03:12 | 2021-09-22 03:15 | 343 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA EL 85% DEL 1336-10 ESTA POR EL 1620-04 | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-22 | 1029 | keep | 0 | Sep | 2021 | 0.00070085 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2021-09-22 03:12 | 2021-09-22 03:15 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA CARGA DEL 1620-01 SE ENCUENTRA POR EL 1620-04 | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-22 | 108 | keep | 0 | Sep | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-09-22 03:12 | 2021-09-22 03:15 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01, 85% DEL 1336-10 Y 90% 1336-07 | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-22 | 516 | keep | 0 | Sep | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
FAJARDO | 2021-09-22 03:35 | 2021-09-22 10:49 | 60 | 007:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21092200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 434 | 2021-09-22 | 26040 | keep | 0 | Sep | 2021 | 0.017736 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-22 04:50 | 2021-09-22 09:47 | 110 | 004:57 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | R21092200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-09-22 | 32670 | keep | 0 | Sep | 2021 | 0.022251 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
ARECIBO | 2021-09-22 05:01 | 2021-09-24 14:10 | 20 | 057:09 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21092200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3429 | 2021-09-22 | 68580 | keep | 0 | Sep | 2021 | 0.04671 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-22 05:17 | 2021-09-24 19:31 | 10 | 062:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37 KVA POR 37 KVA | B21092200036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3734 | 2021-09-22 | 37340 | keep | 0 | Sep | 2021 | 0.025432 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-22 05:28 | 2021-09-22 13:49 | 16 | 008:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21092200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2021-09-22 | 8016 | keep | 0 | Sep | 2021 | 0.0054597 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-09-22 05:31 | 2021-09-22 17:00 | 78 | 011:29 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21092200021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 689 | 2021-09-22 | 53742 | keep | 0 | Sep | 2021 | 0.036603 | 5.3125e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 78
BAYAMON | 2021-09-22 05:46 | 2021-09-22 05:47 | 252 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 252 | keep | 0 | Sep | 2021 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-09-22 05:47 | 2021-09-22 17:34 | 75 | 011:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082200217 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 707 | 2021-09-22 | 53025 | keep | 0 | Sep | 2021 | 0.036115 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-09-22 06:18 | 2021-09-22 21:36 | 10 | 015:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | A21092200038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 918 | 2021-09-22 | 9180 | keep | 0 | Sep | 2021 | 0.0062525 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-22 06:20 | 2021-09-22 14:26 | 4 | 008:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092200018 | New_Event | Bad Weather | Include | Include | Weather | 486 | 2021-09-22 | 1944 | keep | 0 | Sep | 2021 | 0.001324 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-09-22 06:33 | 2021-09-22 06:34 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
UTUADO | 2021-09-22 06:37 | 2021-09-22 15:53 | 30 | 009:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200040 | New_Event | Bad Weather | Include | Include | Weather | 556 | 2021-09-22 | 16680 | keep | 0 | Sep | 2021 | 0.011361 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-22 06:39 | 2021-09-22 10:40 | 50 | 004:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200043 | New_Event | Bad Weather | Include | Include | Weather | 241 | 2021-09-22 | 12050 | keep | 0 | Sep | 2021 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-22 06:42 | 2021-09-22 18:10 | 50 | 011:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200044 | New_Event | Bad Weather | Include | Include | Weather | 688 | 2021-09-22 | 34400 | keep | 0 | Sep | 2021 | 0.02343 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-22 06:46 | 2021-09-22 11:06 | 35 | 004:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21092100026 | New_Event | Wire Down | Include | Include | Equipment | 260 | 2021-09-22 | 9100 | keep | 0 | Sep | 2021 | 0.006198 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BARRANQUITAS | 2021-09-22 06:46 | 2021-09-22 11:55 | 60 | 005:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21092200021 | New_Event | Cutout Failure | Include | Include | Equipment | 309 | 2021-09-22 | 18540 | keep | 0 | Sep | 2021 | 0.012628 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-22 06:54 | 2021-09-22 12:29 | 40 | 005:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21092200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-09-22 | 13400 | keep | 0 | Sep | 2021 | 0.0091267 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-22 07:14 | 2021-09-22 10:49 | 100 | 003:35 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO BAMBÃšS SOBRE LAS LINEAS | A21092200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-09-22 | 21500 | keep | 0 | Sep | 2021 | 0.014644 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-22 07:19 | 2021-09-22 17:34 | 80 | 010:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21092200053 | New_Event | Wire Down | Include | Include | Equipment | 615 | 2021-09-22 | 49200 | keep | 0 | Sep | 2021 | 0.03351 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-09-22 07:22 | 2021-09-22 17:52 | 75 | 010:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M21092200074 | New_Event |  |  | Include | Wildlife | 630 | 2021-09-22 | 47250 | keep | 0 | Sep | 2021 | 0.032182 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
HUMACAO | 2021-09-22 07:25 | 2021-09-22 15:30 | 35 | 008:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092200031 | New_Event | Bad Weather | Include | Include | Weather | 485 | 2021-09-22 | 16975 | keep | 0 | Sep | 2021 | 0.011562 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-09-22 07:33 | 2021-09-22 11:57 | 93 | 004:24 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21092200033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2021-09-22 | 24552 | keep | 0 | Sep | 2021 | 0.016722 | 6.3342e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 93
CAGUAS | 2021-09-22 07:34 | 2021-09-22 17:03 | 175 | 009:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA, POLIMERO, SE DESGANCHO Y PORTAFUSIBLE | C21092200034 | New_Event | Cutout Failure | Include | Include | Equipment | 569 | 2021-09-22 | 99575 | keep | 0 | Sep | 2021 | 0.06782 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
MAYAGÃœEZ | 2021-09-22 07:36 | 2021-09-22 19:37 | 50 | 012:01 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | M21092200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 721 | 2021-09-22 | 36050 | keep | 0 | Sep | 2021 | 0.024553 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-22 07:37 | 2021-09-22 18:00 | 120 | 010:23 | P | DESGANCHE | 1 X 40 EN RISER Y 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21092200036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2021-09-22 | 74760 | keep | 0 | Sep | 2021 | 0.050919 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
VEGA BAJA | 2021-09-22 07:45 | 2021-09-22 15:49 | 30 | 008:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21092200103 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 484 | 2021-09-22 | 14520 | keep | 0 | Sep | 2021 | 0.0098895 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-22 07:46 | 2021-09-22 13:09 | 55 | 005:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21092200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2021-09-22 | 17765 | keep | 0 | Sep | 2021 | 0.0121 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-09-22 07:48 | 2021-09-22 11:47 | 85 | 003:59 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE | S21092200079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-09-22 | 20315 | keep | 0 | Sep | 2021 | 0.013836 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2021-09-22 07:54 | 2021-09-22 07:55 | 837 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 837 | keep | 0 | Sep | 2021 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-09-22 07:54 | 2021-09-22 07:55 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 908 | keep | 0 | Sep | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
ARECIBO | 2021-09-22 07:56 | 2021-09-22 17:30 | 10 | 009:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA PARTIDA | A21092200061 | New_Event | Wire Down | Include | Include | Equipment | 574 | 2021-09-22 | 5740 | keep | 0 | Sep | 2021 | 0.0039095 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-09-22 07:57 | 2021-09-22 07:58 | 128 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C21092200044 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-22 | 128 | keep | 0 | Sep | 2021 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2021-09-22 07:57 | 2021-09-22 07:58 | 273 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR CARGA POR EL 3009-02 | C21092200044 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-22 | 273 | keep | 0 | Sep | 2021 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2021-09-22 07:57 | 2021-09-22 07:58 | 1772 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR CARGA POR EL 3009-02 | C21092200044 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-22 | 1772 | keep | 0 | Sep | 2021 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
CAGUAS | 2021-09-22 07:58 | 2021-09-22 11:30 | 366 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO | C21092200046 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 212 | 2021-09-22 | 77592 | keep | 0 | Sep | 2021 | 0.052848 | 0.00024928 | Sustained | FALSE | TRUE | Not_TMED_Event | 366
VEGA BAJA | 2021-09-22 08:01 | 2021-09-23 17:02 | 10 | 033:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 25 X 25 KVA S.N 012-OJ319 | B21092200128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1981 | 2021-09-22 | 19810 | keep | 0 | Sep | 2021 | 0.013493 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-22 08:05 | 2021-09-22 12:53 | 100 | 004:48 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | S21092200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2021-09-22 | 28800 | keep | 0 | Sep | 2021 | 0.019616 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-09-22 08:08 | 2021-09-22 11:17 | 127 | 003:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P20109220000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-09-22 | 24003 | keep | 0 | Sep | 2021 | 0.016348 | 8.6499e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 127
BARRANQUITAS | 2021-09-22 08:11 | 2021-09-22 20:12 | 325 | 012:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80, 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21092200052 | New_Event | Wire Down | Include | Include | Equipment | 721 | 2021-09-22 | 234325 | keep | 0 | Sep | 2021 | 0.1596 | 0.00022136 | Sustained | FALSE | TRUE | Not_TMED_Event | 325
BARRANQUITAS | 2021-09-22 08:14 | 2021-09-22 12:09 | 8 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO | C21092200055 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2021-09-22 | 1880 | keep | 0 | Sep | 2021 | 0.0012805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-22 08:19 | 2021-09-22 14:49 | 35 | 006:30 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-15 SE SECCIONALIZO DEL T-49 AL T-50 | C21092200059 | New_Event | UG Cable Fault | Include | Include | Equipment | 390 | 2021-09-22 | 13650 | keep | 0 | Sep | 2021 | 0.009297 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2021-09-22 08:29 | 2021-09-22 17:04 | 8 | 008:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN MONTURA DE TRANSFORMADOR AVE PALOMA ENTRE LINEA | P21092200105 | New_Event |  |  | Include | Wildlife | 515 | 2021-09-22 | 4120 | keep | 0 | Sep | 2021 | 0.0028061 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
ARECIBO | 2021-09-22 08:34 | 2021-09-22 09:30 | 200 | 000:56 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200076 | New_Event | Bad Weather | Include | Include | Weather | 56 | 2021-09-22 | 11200 | keep | 0 | Sep | 2021 | 0.0076283 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-22 08:48 | 2021-09-22 11:43 | 300 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200080 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2021-09-22 | 52500 | keep | 0 | Sep | 2021 | 0.035758 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 849 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 16980 | keep | 0 | Sep | 2021 | 0.011565 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 893 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 17860 | keep | 0 | Sep | 2021 | 0.012164 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 602 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 12040 | keep | 0 | Sep | 2021 | 0.0082004 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 43 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 860 | keep | 0 | Sep | 2021 | 0.00058574 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 1389 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 27780 | keep | 0 | Sep | 2021 | 0.018921 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 673 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 13460 | keep | 0 | Sep | 2021 | 0.0091675 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 372 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 7440 | keep | 0 | Sep | 2021 | 0.0050674 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 732 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 14640 | keep | 0 | Sep | 2021 | 0.0099712 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 637 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 12740 | keep | 0 | Sep | 2021 | 0.0086772 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 721 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 14420 | keep | 0 | Sep | 2021 | 0.0098214 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 325 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 6500 | keep | 0 | Sep | 2021 | 0.0044271 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 600 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 12000 | keep | 0 | Sep | 2021 | 0.0081731 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 267 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 5340 | keep | 0 | Sep | 2021 | 0.003637 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 621 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 12420 | keep | 0 | Sep | 2021 | 0.0084592 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 2203 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 44060 | keep | 0 | Sep | 2021 | 0.030009 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 246 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 4920 | keep | 0 | Sep | 2021 | 0.003351 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2021-09-22 08:50 | 2021-09-22 09:10 | 9 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH 38KV | S21092200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2021-09-22 | 180 | keep | 0 | Sep | 2021 | 0.0001226 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2021-09-22 08:58 | 2021-09-22 11:44 | 16 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | C21092200071 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2021-09-22 | 2656 | keep | 0 | Sep | 2021 | 0.001809 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2021-09-22 09:03 | 2021-09-22 16:46 | 100 | 007:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21092200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2021-09-22 | 46300 | keep | 0 | Sep | 2021 | 0.031535 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-22 09:03 | 2021-09-22 12:26 | 3 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200086 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-09-22 | 609 | keep | 0 | Sep | 2021 | 0.00041479 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
PONCE | 2021-09-22 09:09 | 2021-09-22 14:00 | 397 | 004:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CORTE DE LINEA ABIERTO POR CABLE EN EL PISO | P21092200019 | Additional_clients | Wire Down | Include | Include | Equipment | 291 | 2021-09-22 | 115527 | keep | 0 | Sep | 2021 | 0.078685 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-22 09:10 | 2021-09-22 09:44 | 2500 | 000:34 | P | DESGANCHE | SE ABRIERON MACHETES EN CARR 690 ESQ CARR 689 Y SE CERRARON MACHETES EN CARR #2 ALMIRANTE NORTE | B21092100225 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 34 | 2021-09-22 | 85000 | keep | 0 | Sep | 2021 | 0.057893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-22 09:14 | 2021-09-24 12:05 | 10 | 050:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37 5 KVA POR 37 5 KVA | B21092200128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3051 | 2021-09-22 | 30510 | keep | 0 | Sep | 2021 | 0.02078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-22 09:16 | 2021-09-22 16:45 | 40 | 007:29 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21092200040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 449 | 2021-09-22 | 17960 | keep | 0 | Sep | 2021 | 0.012232 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-22 09:17 | 2021-09-23 15:37 | 12 | 030:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092200311 | New_Event | Bad Weather | Include | Include | Weather | 1820 | 2021-09-22 | 21840 | keep | 0 | Sep | 2021 | 0.014875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-22 09:23 | 2021-09-22 09:24 | 6197 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21092200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 6197 | keep | 0 | Sep | 2021 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
VEGA BAJA | 2021-09-22 09:23 | 2021-09-22 16:41 | 60 | 007:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21092200131 | New_Event | Cutout Failure | Include | Include | Equipment | 438 | 2021-09-22 | 26280 | keep | 0 | Sep | 2021 | 0.017899 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-22 09:33 | 2021-09-22 16:20 | 80 | 006:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200096 | New_Event | Bad Weather | Include | Include | Weather | 407 | 2021-09-22 | 32560 | keep | 0 | Sep | 2021 | 0.022176 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-22 09:38 | 2021-09-22 11:34 | 1185 | 001:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO SE CERRO INTERRUPTOR | A21092200098 | Additional_clients | Wire Down | Include | Include | Equipment | 116 | 2021-09-22 | 137460 | keep | 0 | Sep | 2021 | 0.093623 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-22 09:40 | 2021-09-22 09:43 | 651 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-22 | 1953 | keep | 0 | Sep | 2021 | 0.0013302 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2021-09-22 09:42 | 2021-09-22 19:57 | 50 | 010:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 615 | 2021-09-22 | 30750 | keep | 0 | Sep | 2021 | 0.020944 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-22 09:44 | 2021-09-22 15:12 | 30 | 005:28 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B21092200141 | New_Event | Defective Pole | Include | Include | Equipment | 328 | 2021-09-22 | 9840 | keep | 0 | Sep | 2021 | 0.006702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-22 09:44 | 2021-09-22 10:24 | 1000 | 000:40 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA Y SE CERRARON MACHETES EN CARR 690 ESQ CARR 689 | B21092100225 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 40 | 2021-09-22 | 40000 | keep | 0 | Sep | 2021 | 0.027244 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-09-22 09:52 | 2021-09-22 11:02 | 60 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21092200044 | New_Event |  |  | Include | Wildlife | 70 | 2021-09-22 | 4200 | keep | 0 | Sep | 2021 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-22 10:04 | 2021-09-23 18:23 | 7 | 032:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092200103 | New_Event | Bad Weather | Include | Include | Weather | 1939 | 2021-09-22 | 13573 | keep | 0 | Sep | 2021 | 0.0092445 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-22 10:05 | 2021-09-22 18:53 | 35 | 008:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092200083 | New_Event | Bad Weather | Include | Include | Weather | 528 | 2021-09-22 | 18480 | keep | 0 | Sep | 2021 | 0.012587 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-09-22 10:07 | 2021-09-25 09:25 | 13 | 071:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21092200047 | New_Event | Bad Weather | Include | Include | Weather | 4278 | 2021-09-22 | 55614 | keep | 0 | Sep | 2021 | 0.037878 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-09-22 10:13 | 2021-09-22 17:14 | 30 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21092200153 | New_Event | Wire Down | Include | Include | Equipment | 421 | 2021-09-22 | 12630 | keep | 0 | Sep | 2021 | 0.0086022 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-09-22 10:13 | 2021-09-24 14:43 | 40 | 052:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21092200108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3150 | 2021-09-22 | 126000 | keep | 0 | Sep | 2021 | 0.085818 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-22 10:16 | 2021-09-22 19:27 | 50 | 009:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092200154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 551 | 2021-09-22 | 27550 | keep | 0 | Sep | 2021 | 0.018764 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-22 10:24 | 2021-09-22 12:56 | 75 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTE DE LINEA SE REEMPLAZARON CAJAS AVERIADAS | B21092200162 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-09-22 | 11400 | keep | 0 | Sep | 2021 | 0.0077645 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-22 10:26 | 2021-09-22 10:27 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-02 LLEVANDO EL 1720-08 | B21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 2402 | keep | 0 | Sep | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-09-22 10:26 | 2021-09-22 10:27 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-02 LLEVANDO EL 1720-08 | B21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-22 10:26 | 2021-09-22 14:30 | 60 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092200093 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-09-22 | 14640 | keep | 0 | Sep | 2021 | 0.0099712 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-22 10:33 | 2021-09-22 17:15 | 100 | 006:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200114 | New_Event | Bad Weather | Include | Include | Weather | 402 | 2021-09-22 | 40200 | keep | 0 | Sep | 2021 | 0.02738 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-22 10:37 | 2021-09-22 12:25 | 16 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 100 PIES DE SECUNDARIA | C21092100080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2021-09-22 | 1728 | keep | 0 | Sep | 2021 | 0.0011769 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-09-22 10:41 | 2021-09-22 10:42 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
CAGUAS | 2021-09-22 10:49 | 2021-09-22 10:50 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 2302 | keep | 0 | Sep | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CANOVANAS | 2021-09-22 10:55 | 2021-09-22 10:56 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 4188 | keep | 0 | Sep | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-09-22 10:56 | 2021-09-22 14:34 | 40 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21092200068 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 218 | 2021-09-22 | 8720 | keep | 0 | Sep | 2021 | 0.0059392 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-22 11:01 | 2021-09-23 20:54 | 80 | 033:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA FUERTES LLUVIAS Y RAYOS | B21092200168 | New_Event | Bad Weather | Include | Include | Weather | 2033 | 2021-09-22 | 162640 | keep | 0 | Sep | 2021 | 0.11077 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-22 11:03 | 2021-09-22 12:51 | 1615 | 001:48 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES EN CALLE URUGUAY ESQ CARR 8860 ROLLING HILLS | R21092200055 | New_Event | Switch Failure | Include | Include | Equipment | 108 | 2021-09-22 | 174420 | keep | 0 | Sep | 2021 | 0.1188 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
FAJARDO | 2021-09-22 11:10 | 2021-09-22 13:40 | 7 | 002:30 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA DESGANCHO Y RETEZO LINEA | R21092200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-09-22 | 1050 | keep | 0 | Sep | 2021 | 0.00071515 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
GUAYAMA | 2021-09-22 11:15 | 2021-09-22 11:16 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092200031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 1945 | keep | 0 | Sep | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
ARECIBO | 2021-09-22 11:15 | 2021-09-22 16:36 | 20 | 005:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21092200121 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2021-09-22 | 6420 | keep | 0 | Sep | 2021 | 0.0043726 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-22 11:26 | 2021-09-22 17:11 | 7 | 005:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 5 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092200125 | New_Event | Bad Weather | Include | Include | Weather | 345 | 2021-09-22 | 2415 | keep | 0 | Sep | 2021 | 0.0016448 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-09-22 11:30 | 2021-09-22 16:35 | 25 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21092200103 | New_Event | Bad Weather | Include | Include | Weather | 305 | 2021-09-22 | 7625 | keep | 0 | Sep | 2021 | 0.0051934 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-22 11:32 | 2021-09-23 10:50 | 10 | 023:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092200127 | New_Event | Bad Weather | Include | Include | Weather | 1398 | 2021-09-22 | 13980 | keep | 0 | Sep | 2021 | 0.0095217 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-22 11:34 | 2021-09-22 13:40 | 50 | 002:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21092100145 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 126 | 2021-09-22 | 6300 | keep | 0 | Sep | 2021 | 0.0042909 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-22 11:38 | 2021-09-26 08:52 | 195 | 093:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21092200071 | New_Event | Cutout Failure | Include | Include | Equipment | 5594 | 2021-09-22 | 1090830 | keep | 0 | Sep | 2021 | 0.74296 | 0.00013281 | Sustained | FALSE | TRUE | Not_TMED_Event | 195
YAUCO | 2021-09-22 11:40 | 2021-09-22 19:10 | 169 | 007:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA EN EL PISO | 21092100063 | Partial_restoration | Wire Down | Include | Include | Equipment | 450 | 2021-09-22 | 76050 | keep | 0 | Sep | 2021 | 0.051797 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-22 11:44 | 2021-09-22 17:52 | 50 | 006:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21092200132 | New_Event | Cutout Failure | Include | Include | Equipment | 368 | 2021-09-22 | 18400 | keep | 0 | Sep | 2021 | 0.012532 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-22 11:45 | 2021-09-22 17:05 | 1 | 005:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN MONTURA DE TRANSFORMADORES CULEBRA CRUZO FASE A TIERRA | M21092200112 | New_Event |  |  | Include | Wildlife | 320 | 2021-09-22 | 320 | keep | 0 | Sep | 2021 | 0.00021795 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-22 11:49 | 2021-09-22 18:26 | 20 | 006:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 X 37.5 | B21092200178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 397 | 2021-09-22 | 7940 | keep | 0 | Sep | 2021 | 0.0054079 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-09-22 11:50 | 2021-09-22 11:51 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21092200116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 1702 | keep | 0 | Sep | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
HUMACAO | 2021-09-22 12:01 | 2021-09-22 12:06 | 5630 | 000:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR DISCOS Y AISLADOR AVERIADO CERRADO POR CONTROL | C21092200116 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2021-09-22 | 28150 | keep | 0 | Sep | 2021 | 0.019173 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-22 12:05 | 2021-09-22 15:33 | 25 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092200143 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2021-09-22 | 5200 | keep | 0 | Sep | 2021 | 0.0035417 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-09-22 12:06 | 2021-09-22 15:41 | 1866 | 003:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO 5 DISCOS Y 3 AISLADORES SE CERRO MACHETES DEL RISER | C21092200006 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 215 | 2021-09-22 | 401190 | keep | 0 | Sep | 2021 | 0.27325 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-22 12:10 | 2021-09-22 12:11 | 1510 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21092200120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-22 | 1510 | keep | 0 | Sep | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-09-22 12:11 | 2021-09-22 15:50 | 156 | 003:39 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21092200126 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-09-22 | 34164 | keep | 0 | Sep | 2021 | 0.023269 | 0.00010625 | Sustained | FALSE | TRUE | Not_TMED_Event | 156
CANOVANAS | 2021-09-22 12:18 | 2021-09-22 16:52 | 40 | 004:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR | R21092200086 | New_Event | Wire Down | Include | Include | Equipment | 274 | 2021-09-22 | 10960 | keep | 0 | Sep | 2021 | 0.0074648 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-22 12:24 | 2021-09-22 15:50 | 40 | 003:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M21092200125 | New_Event |  |  | Include | Wildlife | 206 | 2021-09-22 | 8240 | keep | 0 | Sep | 2021 | 0.0056122 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-22 12:33 | 2021-09-22 17:30 | 60 | 004:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 ENTRADA DEL RISER Y 1 X 40 EN SALIDA DEL RISER MAL TIEMPO | C21092200130 | New_Event | Bad Weather | Include | Include | Weather | 297 | 2021-09-22 | 17820 | keep | 0 | Sep | 2021 | 0.012137 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-09-22 12:37 | 2021-09-22 12:38 | 2450 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | C21092200133 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-22 | 2450 | keep | 0 | Sep | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
CAGUAS | 2021-09-22 12:37 | 2021-09-23 11:00 | 40 | 022:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 40 AMP EN SU - 1 CRUCE POR AVE | C21092200132 | New_Event |  |  | Include | Wildlife | 1343 | 2021-09-22 | 53720 | keep | 0 | Sep | 2021 | 0.036588 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-09-22 12:38 | 2021-09-22 17:14 | 478 | 004:36 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN LA ENTRADA DEL CONVERTIDOR | C21092200020 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 276 | 2021-09-22 | 131928 | keep | 0 | Sep | 2021 | 0.089856 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
PONCE | 2021-09-22 12:40 | 2021-09-22 17:00 | 12 | 004:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21092200040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 260 | 2021-09-22 | 3120 | keep | 0 | Sep | 2021 | 0.002125 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
VEGA BAJA | 2021-09-22 12:41 | 2021-09-22 20:06 | 200 | 007:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SUBIR LINEA PRIMARIA DE TRONCAL | B21092200199 | New_Event | Wire Down | Include | Include | Equipment | 445 | 2021-09-22 | 89000 | keep | 0 | Sep | 2021 | 0.060617 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-22 12:42 | 2021-09-22 17:36 | 22 | 004:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200160 | New_Event | Bad Weather | Include | Include | Weather | 294 | 2021-09-22 | 6468 | keep | 0 | Sep | 2021 | 0.0044053 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
ARECIBO | 2021-09-22 12:50 | 2021-09-22 20:03 | 7 | 007:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21092200029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 433 | 2021-09-22 | 3031 | keep | 0 | Sep | 2021 | 0.0020644 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-22 12:51 | 2021-09-22 15:55 | 500 | 003:04 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE QUEMADO | R21092200055 | Partial_restoration | Switch Failure | Include | Include | Equipment | 184 | 2021-09-22 | 92000 | keep | 0 | Sep | 2021 | 0.062661 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-22 12:52 | 2021-09-25 13:05 | 40 | 072:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21092200163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4333 | 2021-09-22 | 173320 | keep | 0 | Sep | 2021 | 0.11805 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-22 12:53 | 2021-09-22 12:54 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 2704 | keep | 0 | Sep | 2021 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
GUAYAMA | 2021-09-22 13:00 | 2021-09-22 13:22 | 187 | 000:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR AISLADOR | P21092200026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 22 | 2021-09-22 | 4114 | keep | 0 | Sep | 2021 | 0.002802 | 0.00012736 | Sustained | FALSE | TRUE | Not_TMED_Event | 187
CAGUAS | 2021-09-22 13:03 | 2021-09-22 13:04 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21092200140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 1307 | keep | 0 | Sep | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
UTUADO | 2021-09-22 13:04 | 2021-09-23 11:59 | 6 | 022:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR UNO DE 37.5KVA EN EL FID: 20800234 / MARCA: HOWARD / #SERIE: 1880851418 / VOLTAJE: 4.16/7.2KV 120-240V | A21092200170 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1375 | 2021-09-22 | 8250 | keep | 0 | Sep | 2021 | 0.005619 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-22 13:09 | 2021-09-22 15:41 | 30 | 002:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21092200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-09-22 | 4560 | keep | 0 | Sep | 2021 | 0.0031058 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-22 13:19 | 2021-09-22 16:08 | 45 | 002:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21092200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-09-22 | 7605 | keep | 0 | Sep | 2021 | 0.0051797 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-22 13:26 | 2021-09-23 13:12 | 25 | 023:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR Y SE REMPLAZO CAJA OPEN TIPE EN TRANSFORMADOR | B21092200212 | New_Event | Cutout Failure | Include | Include | Equipment | 1426 | 2021-09-22 | 35650 | keep | 0 | Sep | 2021 | 0.024281 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-09-22 13:27 | 2021-09-22 13:40 | 6197 | 000:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | C21092200149 | New_Event | Wire Down | Include | Include | Equipment | 13 | 2021-09-22 | 80561 | keep | 0 | Sep | 2021 | 0.05487 | 0.0042207 | Sustained | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2021-09-22 13:27 | 2021-09-23 11:36 | 10 | 022:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21092200145 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1329 | 2021-09-22 | 13290 | keep | 0 | Sep | 2021 | 0.0090518 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-22 13:49 | 2021-09-22 19:07 | 33 | 005:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE CERRO PUENTE | C21092200153 | New_Event | Wire Down | Include | Include | Equipment | 318 | 2021-09-22 | 10494 | keep | 0 | Sep | 2021 | 0.0071474 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
CAGUAS | 2021-09-22 13:51 | 2021-09-22 13:53 | 1565 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO ORDENES CERRADAS SE CERRO POR CONTROL | C21092200155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-22 | 3130 | keep | 0 | Sep | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
SAN JUAN | 2021-09-22 13:59 | 2021-09-22 17:21 | 175 | 003:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R21092200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-09-22 | 35350 | keep | 0 | Sep | 2021 | 0.024077 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
MAYAGÃœEZ | 2021-09-22 14:02 | 2021-09-22 22:38 | 200 | 008:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092200153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2021-09-22 | 103200 | keep | 0 | Sep | 2021 | 0.070289 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
GUAYAMA | 2021-09-22 14:15 | 2021-09-22 15:15 | 6 | 001:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA | P21092200049 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2021-09-22 | 360 | keep | 0 | Sep | 2021 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-22 14:16 | 2021-09-23 12:25 | 6 | 022:09 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21092200163 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1329 | 2021-09-22 | 7974 | keep | 0 | Sep | 2021 | 0.0054311 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-09-22 14:16 | 2021-09-23 10:33 | 75 | 020:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN MACHETES DE SALIDA ALIMENTADOR | B21092200168 | New_Event | Wire Down | Include | Include | Equipment | 1217 | 2021-09-22 | 91275 | keep | 0 | Sep | 2021 | 0.062167 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-09-22 14:42 | 2021-09-22 17:51 | 15 | 003:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 25KVA CON DERRAME | B21092200002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 189 | 2021-09-22 | 2835 | keep | 0 | Sep | 2021 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-09-22 14:47 | 2021-09-23 11:49 | 100 | 021:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21092200170 | New_Event | Bad Weather | Include | Include | Weather | 1262 | 2021-09-22 | 126200 | keep | 0 | Sep | 2021 | 0.085954 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-22 14:49 | 2021-09-22 21:35 | 8 | 006:46 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA EL T-50 | C21092200059 | New_Event | UG Cable Fault | Include | Include | Equipment | 406 | 2021-09-22 | 3248 | keep | 0 | Sep | 2021 | 0.0022122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-09-22 14:51 | 2021-09-23 21:45 | 10 | 030:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR FUERTES RAYOS Y LLUVIAS | B21092200239 | New_Event | Bad Weather | Include | Include | Weather | 1854 | 2021-09-22 | 18540 | keep | 0 | Sep | 2021 | 0.012628 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-22 14:59 | 2021-09-22 16:40 | 32 | 001:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21092200173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-09-22 | 3232 | keep | 0 | Sep | 2021 | 0.0022013 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
CAGUAS | 2021-09-22 15:00 | 2021-09-22 15:52 | 85 | 000:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE POR BAMBUA | C21092200183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-09-22 | 4420 | keep | 0 | Sep | 2021 | 0.0030104 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
ARECIBO | 2021-09-22 15:05 | 2021-09-22 17:40 | 7 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21092200207 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-09-22 | 1085 | keep | 0 | Sep | 2021 | 0.00073899 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-22 15:11 | 2021-09-22 15:13 | 225 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1303-05 | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-22 | 450 | keep | 0 | Sep | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-22 15:11 | 2021-09-22 15:13 | 870 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1303-04 | S21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-22 | 1740 | keep | 0 | Sep | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2021-09-22 15:25 | 2021-09-22 18:27 | 80 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200215 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2021-09-22 | 14560 | keep | 0 | Sep | 2021 | 0.0099167 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-22 15:34 | 2021-09-22 20:25 | 75 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092200247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-09-22 | 21825 | keep | 0 | Sep | 2021 | 0.014865 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-22 15:34 | 2021-09-22 17:35 | 60 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092200250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2021-09-22 | 7260 | keep | 0 | Sep | 2021 | 0.0049448 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-22 15:36 | 2021-09-22 20:17 | 70 | 004:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | R21092200123 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 281 | 2021-09-22 | 19670 | keep | 0 | Sep | 2021 | 0.013397 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-09-22 15:39 | 2021-09-22 17:05 | 100 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 65 EN CORTE DE LINEA EXCAVADORA TOCO LINEAS | R21092200125 | New_Event |  |  | Include | Wildlife | 86 | 2021-09-22 | 8600 | keep | 0 | Sep | 2021 | 0.0058574 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-22 15:41 | 2021-09-22 18:14 | 20 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200218 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-09-22 | 3060 | keep | 0 | Sep | 2021 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-22 15:42 | 2021-09-22 18:50 | 30 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A21092200219 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-09-22 | 5640 | keep | 0 | Sep | 2021 | 0.0038414 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-22 15:45 | 2021-09-24 11:40 | 10 | 043:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR ITON 15 KVA 4160/7200 # 667861 FID-18409754 X LO MISMO | M21092200174 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2635 | 2021-09-22 | 26350 | keep | 0 | Sep | 2021 | 0.017947 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-22 15:47 | 2021-09-22 18:36 | 40 | 002:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21092200189 | New_Event |  |  | Include | Wildlife | 169 | 2021-09-22 | 6760 | keep | 0 | Sep | 2021 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-22 16:05 | 2021-09-22 17:15 | 20 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21092100260 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-09-22 | 1400 | keep | 0 | Sep | 2021 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-22 16:10 | 2021-09-22 21:21 | 15 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21092200261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-09-22 | 4665 | keep | 0 | Sep | 2021 | 0.0031773 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-22 16:13 | 2021-09-22 16:14 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21092200176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 3458 | keep | 0 | Sep | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | TRUE | Not_TMED_Event | 3458
BAYAMON | 2021-09-22 16:16 | 2021-09-23 10:06 | 45 | 017:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092200264 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1070 | 2021-09-22 | 48150 | keep | 0 | Sep | 2021 | 0.032795 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-09-22 16:32 | 2021-09-22 17:14 | 12 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092200200 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2021-09-22 | 504 | keep | 0 | Sep | 2021 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-09-22 16:38 | 2021-09-22 20:04 | 7 | 003:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21092100106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 206 | 2021-09-22 | 1442 | keep | 0 | Sep | 2021 | 0.00098214 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
SAN JUAN | 2021-09-22 16:42 | 2021-09-22 16:44 | 1026 | 000:02 | T | DESCONECTIVO DEFECTUOSO | PERSONAL REALIZANDO PRUEBAS | R21092100128 | Additional_clients | Switch Failure | Include | Include | Equipment | 2 | 2021-09-22 | 2052 | keep | 0 | Sep | 2021 | 0.0013976 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-22 16:42 | 2021-09-22 16:43 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 7621 | keep | 0 | Sep | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2021-09-22 16:44 | 2021-09-23 16:19 | 100 | 023:35 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO CAJA SECA EN EL MH - 2 Y HIZO BY PASS AL MH - 1 QUE ESTA INOPERANTE | R21092100128 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1415 | 2021-09-22 | 141500 | keep | 0 | Sep | 2021 | 0.096375 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-09-22 16:52 | 2021-09-22 20:16 | 76 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21092200136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-09-22 | 15504 | keep | 0 | Sep | 2021 | 0.01056 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
CAGUAS | 2021-09-22 16:54 | 2021-09-23 09:39 | 81 | 016:45 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21092200206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1005 | 2021-09-22 | 81405 | keep | 0 | Sep | 2021 | 0.055445 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
HUMACAO | 2021-09-22 16:59 | 2021-09-22 19:15 | 1 | 002:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21092200209 | New_Event | Bad Weather | Include | Include | Weather | 136 | 2021-09-22 | 136 | keep | 0 | Sep | 2021 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-22 17:11 | 2021-09-22 19:02 | 65 | 001:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21092200212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-09-22 | 7215 | keep | 0 | Sep | 2021 | 0.0049141 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
UTUADO | 2021-09-22 17:13 | 2021-09-23 12:43 | 100 | 019:30 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092200246 | New_Event | Bad Weather | Include | Include | Weather | 1170 | 2021-09-22 | 117000 | keep | 0 | Sep | 2021 | 0.079688 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-22 17:14 | 2021-09-22 21:22 | 120 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092200247 | New_Event | Bad Weather | Include | Include | Weather | 248 | 2021-09-22 | 29760 | keep | 0 | Sep | 2021 | 0.020269 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
ARECIBO | 2021-09-22 17:17 | 2021-09-23 19:55 | 10 | 026:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 50 KVA | A21092200250 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1598 | 2021-09-22 | 15980 | keep | 0 | Sep | 2021 | 0.010884 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-22 17:20 | 2021-09-23 16:57 | 8 | 023:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 25 KVA | A21092200254 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1417 | 2021-09-22 | 11336 | keep | 0 | Sep | 2021 | 0.0077209 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-22 17:24 | 2021-09-22 20:56 | 50 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21092200183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-09-22 | 10600 | keep | 0 | Sep | 2021 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-22 17:28 | 2021-09-23 10:58 | 80 | 017:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA | B21092200291 | New_Event | Wire Down | Include | Include | Equipment | 1050 | 2021-09-22 | 84000 | keep | 0 | Sep | 2021 | 0.057212 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-22 17:30 | 2021-09-22 20:07 | 100 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65, 1 X 50 Y 1 X 40 EN CORTES DE LINEAS DIFERENTES MAL TIEMPO DESCARGAS ELECTRICAS | A21092200261 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-09-22 | 15700 | keep | 0 | Sep | 2021 | 0.010693 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-22 17:45 | 2021-09-22 18:45 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21092200133 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-09-22 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-22 17:50 | 2021-09-22 19:38 | 10 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21092200069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2021-09-22 | 1080 | keep | 0 | Sep | 2021 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-22 17:57 | 2021-09-23 12:31 | 250 | 018:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092200272 | New_Event | Bad Weather | Include | Include | Weather | 1114 | 2021-09-22 | 278500 | keep | 0 | Sep | 2021 | 0.18969 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-09-22 18:03 | 2021-09-22 22:55 | 5 | 004:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE CORRIGIO LINEA PRIMARIA CRUZADA CON TENSOR | M21092200191 | New_Event | Wire Down | Include | Include | Equipment | 292 | 2021-09-22 | 1460 | keep | 0 | Sep | 2021 | 0.0009944 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-09-22 18:20 | 2021-09-23 13:42 | 12 | 019:22 | P | NO SE REPORTO CAUSA | 1 X 12 EN TRANSFORMADOR NX | S21092200176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1162 | 2021-09-22 | 13944 | keep | 0 | Sep | 2021 | 0.0094972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-22 18:20 | 2021-09-23 10:39 | 150 | 016:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | A21092200276 | New_Event | Wire Down | Include | Include | Equipment | 979 | 2021-09-22 | 146850 | keep | 0 | Sep | 2021 | 0.10002 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-22 18:30 | 2021-09-23 15:40 | 1 | 021:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21092200159 | New_Event | Bad Weather | Include | Include | Weather | 1270 | 2021-09-22 | 1270 | keep | 0 | Sep | 2021 | 0.00086499 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-22 18:34 | 2021-09-22 18:35 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 312 | keep | 0 | Sep | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2021-09-22 18:46 | 2021-09-23 15:30 | 15 | 020:44 | P | NO SE REPORTO CAUSA | SE HIZO PRUEBAS A CABLE DE T-14 @ T-15 PROBO BUENO SE DEJO CLIENTES CON SERVICIO | M21092200197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1244 | 2021-09-22 | 18660 | keep | 0 | Sep | 2021 | 0.012709 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-22 19:01 | 2021-09-23 10:57 | 65 | 015:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21092200235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2021-09-22 | 62140 | keep | 0 | Sep | 2021 | 0.042323 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-09-22 19:11 | 2021-09-23 11:33 | 50 | 016:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21092200239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 982 | 2021-09-22 | 49100 | keep | 0 | Sep | 2021 | 0.033442 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-22 19:18 | 2021-09-23 14:54 | 55 | 019:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21092300083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1176 | 2021-09-22 | 64680 | keep | 0 | Sep | 2021 | 0.044053 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
YAUCO | 2021-09-22 19:18 | 2021-09-23 20:37 | 75 | 025:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P21092200081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1519 | 2021-09-22 | 113925 | keep | 0 | Sep | 2021 | 0.077594 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-09-22 19:20 | 2021-09-23 17:04 | 200 | 021:44 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21092200240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1304 | 2021-09-22 | 260800 | keep | 0 | Sep | 2021 | 0.17763 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-09-22 19:27 | 2021-09-23 16:10 | 35 | 020:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE ABIERTO | P21092200085 | New_Event | Wire Down | Include | Include | Equipment | 1243 | 2021-09-22 | 43505 | keep | 0 | Sep | 2021 | 0.029631 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-09-22 19:42 | 2021-09-22 22:47 | 40 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092200204 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2021-09-22 | 7400 | keep | 0 | Sep | 2021 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-22 19:47 | 2021-09-23 09:30 | 100 | 013:43 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | A21092200289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2021-09-22 | 82300 | keep | 0 | Sep | 2021 | 0.056054 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-22 20:00 | 2021-09-23 16:53 | 11 | 020:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 50 KVA | A21092300090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1253 | 2021-09-22 | 13783 | keep | 0 | Sep | 2021 | 0.0093875 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2021-09-22 20:06 | 2021-09-22 22:28 | 1310 | 002:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SUBIR LINEA PRIMARIA DE TRONCAL | B21092200199 | Additional_clients | Wire Down | Include | Include | Equipment | 142 | 2021-09-22 | 186020 | keep | 0 | Sep | 2021 | 0.1267 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-22 20:30 | 2021-09-22 22:26 | 462 | 001:56 | P | NO SE REPORTO CAUSA | SE RETIRO LA CARGA PARA REPONER FUSIBLE EN LA ALTA 125 HS | B21092200188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-22 | 53592 | keep | 0 | Sep | 2021 | 0.036501 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
BAYAMON | 2021-09-22 20:30 | 2021-09-22 22:26 | 100 | 001:56 | P | NO SE REPORTO CAUSA | SE RETIRO LA CARGA PARA REPONER FUSIBLE EN LA ALTA 125 HS | B21092200188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-22 | 11600 | keep | 0 | Sep | 2021 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-09-22 20:30 | 2021-09-22 22:26 | 330 | 001:56 | P | NO SE REPORTO CAUSA | SE RETIRO LA CARGA PARA REPONER FUSIBLE EN LA ALTA 125 HS | B21092200188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-22 | 38280 | keep | 0 | Sep | 2021 | 0.026072 | 0.00022476 | Sustained | FALSE | FALSE | Not_TMED_Event | 330
BAYAMON | 2021-09-22 20:30 | 2021-09-22 22:26 | 189 | 001:56 | P | NO SE REPORTO CAUSA | SE RETIRO LA CARGA PARA REPONER FUSIBLE EN LA ALTA 125 HS | B21092200188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-22 | 21924 | keep | 0 | Sep | 2021 | 0.014932 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
BAYAMON | 2021-09-22 20:30 | 2021-09-22 22:26 | 433 | 001:56 | P | NO SE REPORTO CAUSA | SE RETIRO LA CARGA PARA REPONER FUSIBLE EN LA ALTA 125 HS | B21092200188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-09-22 | 50228 | keep | 0 | Sep | 2021 | 0.03421 | 0.00029491 | Sustained | FALSE | FALSE | Not_TMED_Event | 433
CANOVANAS | 2021-09-22 20:36 | 2021-09-22 20:37 | 4188 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21092200242 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-22 | 4188 | keep | 0 | Sep | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-09-22 20:37 | 2021-09-22 23:07 | 100 | 002:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR ZAFADO HACIA MACHETES SE DEJARON ABIERTO Y SE CERRO N/O CARR 187 KM 20.8 HACIA PUENTE HERRERA PENDIENTE PARA MAÃ‘ANA REPARAR | R21092200284 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 150 | 2021-09-22 | 15000 | keep | 0 | Sep | 2021 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-09-22 20:46 | 2021-09-23 09:24 | 5 | 012:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092200301 | New_Event | Bad Weather | Include | Include | Weather | 758 | 2021-09-22 | 3790 | keep | 0 | Sep | 2021 | 0.0025814 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-22 20:50 | 2021-09-23 14:53 | 50 | 018:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21092200258 | New_Event | Bad Weather | Include | Include | Weather | 1083 | 2021-09-22 | 54150 | keep | 0 | Sep | 2021 | 0.036881 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-22 21:00 | 2021-09-23 12:01 | 100 | 015:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CONVERTIDOR SE REMPLAZO CAJA EN CONVERTIDOR EN EL FID:32071692 / MARCA: ABB 200AMP | A21092200307 | New_Event | Cutout Failure | Include | Include | Equipment | 901 | 2021-09-22 | 90100 | keep | 0 | Sep | 2021 | 0.061367 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-09-22 21:38 | 2021-09-23 13:01 | 8 | 015:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD EN EL FID: 31411244 / MARCA: PROLEC / #SERIE: M20110333 / VOLTAJE 13.2KV 120-240V | A21092200313 | New_Event | Service Transformer Failure | Include | Include | Equipment | 923 | 2021-09-22 | 7384 | keep | 0 | Sep | 2021 | 0.0050292 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-22 21:42 | 2021-09-23 11:59 | 40 | 014:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARAR PUENTE PRIMARIO DE LINEA A CAJA EN CORTE DE LINEA | S21092200193 | New_Event | Wire Down | Include | Include | Equipment | 857 | 2021-09-22 | 34280 | keep | 0 | Sep | 2021 | 0.023348 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-22 21:44 | 2021-09-22 22:26 | 7621 | 000:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR BAJANTE ZAFADO EN RISER | R21092200000 | New_Event | Wire Down | Include | Include | Equipment | 42 | 2021-09-22 | 320082 | keep | 0 | Sep | 2021 | 0.21801 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
BAYAMON | 2021-09-22 21:46 | 2021-09-23 22:10 | 12 | 024:24 | P | NO SE REPORTO CAUSA | 1 X 10 EN T-216 @ T-217 | B21092300326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1464 | 2021-09-22 | 17568 | keep | 0 | Sep | 2021 | 0.011965 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-22 21:46 | 2021-09-23 14:56 | 100 | 017:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA CERRO RISER | R21092200273 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1030 | 2021-09-22 | 103000 | keep | 0 | Sep | 2021 | 0.070153 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-22 21:52 | 2021-09-23 16:45 | 30 | 018:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21092200195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1133 | 2021-09-22 | 33990 | keep | 0 | Sep | 2021 | 0.02315 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-22 21:56 | 2021-09-23 19:07 | 80 | 021:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | S21092200196 | New_Event | Cutout Failure | Include | Include | Equipment | 1271 | 2021-09-22 | 101680 | keep | 0 | Sep | 2021 | 0.069254 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-22 22:07 | 2021-09-23 13:20 | 30 | 015:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21092200235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 913 | 2021-09-22 | 27390 | keep | 0 | Sep | 2021 | 0.018655 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-22 22:26 | 2021-09-22 23:00 | 1399 | 000:34 | S | LINEA DE TRANSMISION 38KV | SE REMPLAZO UN FUSIBLE EN LA ALTA HAY PUNTO CALIENTE EN MACHETE DE DISTRIBUCION PERO EL MISMO SE SOLDO SE ENERGIZO Y SE REPUSO LA CARGA | B21092200188 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 34 | 2021-09-22 | 47566 | keep | 0 | Sep | 2021 | 0.032397 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-09-22 22:26 | 2021-09-22 23:00 | 302 | 000:34 | S | NO SE REPORTO CAUSA | SE REMPLAZO UN FUSIBLE EN LA ALTA HAY PUNTO CALIENTE EN MACHETE DE DISTRIBUCION PERO EL MISMO SE SOLDO SE ENERGIZO Y SE REPUSO LA CARGA | B21092200188 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-09-22 | 10268 | keep | 0 | Sep | 2021 | 0.0069935 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-22 22:26 | 2021-09-22 23:00 | 1048 | 000:34 | S | NO SE REPORTO CAUSA | SE REMPLAZO UN FUSIBLE EN LA ALTA HAY PUNTO CALIENTE EN MACHETE DE DISTRIBUCION PERO EL MISMO SE SOLDO SE ENERGIZO Y SE REPUSO LA CARGA | B21092200188 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-09-22 | 35632 | keep | 0 | Sep | 2021 | 0.024269 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-22 22:26 | 2021-09-22 23:00 | 573 | 000:34 | S | NO SE REPORTO CAUSA | SE REMPLAZO UN FUSIBLE EN LA ALTA HAY PUNTO CALIENTE EN MACHETE DE DISTRIBUCION PERO EL MISMO SE SOLDO SE ENERGIZO Y SE REPUSO LA CARGA | B21092200188 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-09-22 | 19482 | keep | 0 | Sep | 2021 | 0.013269 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-22 22:26 | 2021-09-22 23:00 | 1313 | 000:34 | S | NO SE REPORTO CAUSA | SE REMPLAZO UN FUSIBLE EN LA ALTA HAY PUNTO CALIENTE EN MACHETE DE DISTRIBUCION PERO EL MISMO SE SOLDO SE ENERGIZO Y SE REPUSO LA CARGA | B21092200188 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-09-22 | 44642 | keep | 0 | Sep | 2021 | 0.030405 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-22 22:30 | 2021-09-23 10:45 | 75 | 012:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21092200237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 735 | 2021-09-22 | 55125 | keep | 0 | Sep | 2021 | 0.037545 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-22 22:34 | 2021-09-23 15:28 | 40 | 016:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR Y 1 X 50 EN CORTE DE LINEA | B21092200445 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1014 | 2021-09-22 | 40560 | keep | 0 | Sep | 2021 | 0.027625 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-22 22:36 | 2021-09-23 10:31 | 8 | 011:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092200119 | New_Event | Bad Weather | Include | Include | Weather | 715 | 2021-09-22 | 5720 | keep | 0 | Sep | 2021 | 0.0038959 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-22 23:22 | 2021-09-23 00:08 | 30 | 000:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | R21092200325 | New_Event | Wire Down | Include | Include | Equipment | 46 | 2021-09-22 | 1380 | keep | 0 | Sep | 2021 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-22 23:26 | 2021-09-22 23:27 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA CARGA DEL 1346-05 POR EL 1401-08 | S21092200200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 922 | keep | 0 | Sep | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-09-22 23:26 | 2021-09-22 23:27 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA PARTE DE LA CARGA DEL 1348-08 ESTA POR EL 1401-08 | S21092200200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 300 | keep | 0 | Sep | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-09-22 23:26 | 2021-09-22 23:27 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 Y PARTE DEL 1348-08 | S21092200200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-22 | 135 | keep | 0 | Sep | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2021-09-23 00:38 | 2021-09-23 13:43 | 50 | 013:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHO Y REMPLAZO PORTAFUSIBLE | C21092300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 785 | 2021-09-23 | 39250 | keep | 0 | Sep | 2021 | 0.026733 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-23 01:03 | 2021-09-23 18:42 | 45 | 017:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1059 | 2021-09-23 | 47655 | keep | 0 | Sep | 2021 | 0.032458 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
YAUCO | 2021-09-23 01:07 | 2021-09-23 07:26 | 1924 | 006:19 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE ALIMENTADOR CAMION IMPACTO Y PARTIO DOS POSTES PRIMARIOS | P21092300001 | New_Event |  |  | Include | Wildlife | 379 | 2021-09-23 | 729196 | keep | 0 | Sep | 2021 | 0.49665 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-09-23 01:13 | 2021-09-23 01:14 | 2440 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 2440 | keep | 0 | Sep | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
UTUADO | 2021-09-23 02:59 | 2021-09-23 11:03 | 10 | 008:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA EN EL FID: 1001209633 / MARCA: ABB DE 100AMP | A21092300003 | New_Event | Cutout Failure | Include | Include | Equipment | 484 | 2021-09-23 | 4840 | keep | 0 | Sep | 2021 | 0.0032965 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-09-23 03:18 | 2021-09-23 03:19 | 4154 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R21092300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-23 | 4154 | keep | 0 | Sep | 2021 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2021-09-23 03:19 | 2021-09-23 10:27 | 190 | 007:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21092300017 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 428 | 2021-09-23 | 81320 | keep | 0 | Sep | 2021 | 0.055387 | 0.00012941 | Sustained | FALSE | TRUE | Not_TMED_Event | 190
BAYAMON | 2021-09-23 03:37 | 2021-09-23 13:43 | 35 | 010:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 606 | 2021-09-23 | 21210 | keep | 0 | Sep | 2021 | 0.014446 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-09-23 04:38 | 2021-09-23 04:39 | 329 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 329 | keep | 0 | Sep | 2021 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
ARECIBO | 2021-09-23 05:24 | 2021-09-23 12:49 | 40 | 007:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO CONECTORES EN LINEA SECUNDARIA | A21092300005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 445 | 2021-09-23 | 17800 | keep | 0 | Sep | 2021 | 0.012123 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-23 05:45 | 2021-09-23 22:38 | 120 | 016:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092300106 | New_Event | Bad Weather | Include | Include | Weather | 1013 | 2021-09-23 | 121560 | keep | 0 | Sep | 2021 | 0.082794 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
ARECIBO | 2021-09-23 06:08 | 2021-09-24 10:26 | 8 | 028:18 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | A21092300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1698 | 2021-09-23 | 13584 | keep | 0 | Sep | 2021 | 0.009252 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-23 06:18 | 2021-09-24 11:35 | 95 | 029:17 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN CORTE DE LINEA REEMPLAZO PARARRAYO AVERIADO | C21092300002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1757 | 2021-09-23 | 166915 | keep | 0 | Sep | 2021 | 0.11369 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
SAN JUAN | 2021-09-23 06:24 | 2021-09-23 19:08 | 30 | 012:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 764 | 2021-09-23 | 22920 | keep | 0 | Sep | 2021 | 0.015611 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-23 06:26 | 2021-09-23 06:27 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 1702 | keep | 0 | Sep | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
SAN JUAN | 2021-09-23 06:51 | 2021-09-23 17:13 | 10 | 010:22 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | R21092300020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 622 | 2021-09-23 | 6220 | keep | 0 | Sep | 2021 | 0.0042364 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-23 06:56 | 2021-09-23 18:08 | 80 | 011:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE NECESITA RETEZAR LAS FASES PARA CREAR MAYOR DESPEJE | B21092300020 | New_Event | Wire Down | Include | Include | Equipment | 672 | 2021-09-23 | 53760 | keep | 0 | Sep | 2021 | 0.036616 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-23 07:10 | 2021-09-23 16:32 | 30 | 009:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092300021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 562 | 2021-09-23 | 16860 | keep | 0 | Sep | 2021 | 0.011483 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-09-23 07:14 | 2021-09-24 11:30 | 40 | 028:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21092300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1696 | 2021-09-23 | 67840 | keep | 0 | Sep | 2021 | 0.046206 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-09-23 07:23 | 2021-09-23 07:24 | 4132 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE | P210923000XX | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-23 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
YAUCO | 2021-09-23 07:26 | 2021-09-24 17:00 | 150 | 033:34 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO PUENTE | P21092300014 | New_Event | Defective Pole | Include | Include | Equipment | 2014 | 2021-09-23 | 302100 | keep | 0 | Sep | 2021 | 0.20576 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2021-09-23 07:28 | 2021-09-23 07:29 | 4132 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE | P21092300017 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-23 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 14:43 | 5 | 007:14 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR 25KVA 7620V QUEMADO POR LO MISMO | P21092300033 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 434 | 2021-09-23 | 2170 | keep | 0 | Sep | 2021 | 0.001478 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2100 | keep | 0 | Sep | 2021 | 0.0014303 | 0.0014303 | Momentary | FALSE | TRUE | Not_TMED_Event | 2100
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 922 | keep | 0 | Sep | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | TRUE | Not_TMED_Event | 922
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1676 | keep | 0 | Sep | 2021 | 0.0011415 | 0.0011415 | Momentary | FALSE | TRUE | Not_TMED_Event | 1676
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2844 | keep | 0 | Sep | 2021 | 0.001937 | 0.001937 | Momentary | FALSE | TRUE | Not_TMED_Event | 2844
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2775 | keep | 0 | Sep | 2021 | 0.00189 | 0.00189 | Momentary | FALSE | TRUE | Not_TMED_Event | 2775
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1457 | keep | 0 | Sep | 2021 | 0.00099236 | 0.00099236 | Momentary | FALSE | TRUE | Not_TMED_Event | 1457
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1086 | keep | 0 | Sep | 2021 | 0.00073967 | 0.00073967 | Momentary | FALSE | TRUE | Not_TMED_Event | 1086
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2134 | keep | 0 | Sep | 2021 | 0.0014535 | 0.0014535 | Momentary | FALSE | TRUE | Not_TMED_Event | 2134
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1464 | keep | 0 | Sep | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1833 | keep | 0 | Sep | 2021 | 0.0012484 | 0.0012484 | Momentary | FALSE | TRUE | Not_TMED_Event | 1833
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1565 | keep | 0 | Sep | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
GUAYAMA | 2021-09-23 07:29 | 2021-09-23 07:30 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P210923000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 977 | keep | 0 | Sep | 2021 | 0.00066543 | 0.00066543 | Momentary | FALSE | TRUE | Not_TMED_Event | 977
GUAYAMA | 2021-09-23 07:30 | 2021-09-23 07:31 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092300018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 4279 | keep | 0 | Sep | 2021 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2021-09-23 07:34 | 2021-09-23 09:04 | 1945 | 1:30 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR Y QUEDO FUERA | P21092300012 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2021-09-23 | 175050 | keep | 0 | Sep | 2021 | 0.11923 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
MAYAGÃœEZ | 2021-09-23 07:35 | 2021-09-23 22:09 | 20 | 014:34 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO LINEA PROVISIONAL AEREA ENTRE EL PM-08 Y EL PM-09 | M21092300009 | New_Event | UG Cable Fault | Include | Include | Equipment | 874 | 2021-09-23 | 17480 | keep | 0 | Sep | 2021 | 0.011906 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-09-23 07:42 | 2021-09-23 07:43 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | B21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 2234 | keep | 0 | Sep | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2021-09-23 07:43 | 2021-09-23 17:11 | 1 | 009:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21092300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 568 | 2021-09-23 | 568 | keep | 0 | Sep | 2021 | 0.00038686 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-09-23 07:49 | 2021-09-23 10:23 | 75 | 002:34 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B21092200104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-09-23 | 11550 | keep | 0 | Sep | 2021 | 0.0078667 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-23 07:56 | 2021-09-23 18:30 | 5 | 010:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21092200061 | New_Event | Wire Down | Include | Include | Equipment | 634 | 2021-09-23 | 3170 | keep | 0 | Sep | 2021 | 0.0021591 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
ARECIBO | 2021-09-23 08:05 | 2021-09-23 10:06 | 100 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 30 EN CORTES DE LINEA Y 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092300021 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-09-23 | 12100 | keep | 0 | Sep | 2021 | 0.0082413 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-23 08:09 | 2021-09-23 20:04 | 30 | 011:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | S21092200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2021-09-23 | 21450 | keep | 0 | Sep | 2021 | 0.014609 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-23 08:11 | 2021-09-23 10:19 | 10 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO AISLADOR Y UNA CAJA EN EL FID:27470028 / MARCA: CNHT / 100AMP | A21092300022 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2021-09-23 | 1280 | keep | 0 | Sep | 2021 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-23 08:13 | 2021-09-23 18:08 | 45 | 009:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21092300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 595 | 2021-09-23 | 26775 | keep | 0 | Sep | 2021 | 0.018236 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-23 08:14 | 2021-09-23 15:00 | 80 | 006:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092300037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 406 | 2021-09-23 | 32480 | keep | 0 | Sep | 2021 | 0.022122 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-09-23 08:16 | 2021-09-23 16:27 | 40 | 008:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092300016 | New_Event | Bad Weather | Include | Include | Weather | 491 | 2021-09-23 | 19640 | keep | 0 | Sep | 2021 | 0.013377 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-09-23 08:39 | 2021-09-23 20:50 | 15 | 012:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | P21092300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 731 | 2021-09-23 | 10965 | keep | 0 | Sep | 2021 | 0.0074682 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-23 08:45 | 2021-09-24 09:33 | 120 | 024:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA FUERTES LLUVIAS Y RAYOS | B21092300290 | New_Event | Bad Weather | Include | Include | Weather | 1488 | 2021-09-23 | 178560 | keep | 0 | Sep | 2021 | 0.12162 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
AGUADILLA | 2021-09-23 08:46 | 2021-09-23 19:30 | 100 | 010:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21092300063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2021-09-23 | 64400 | keep | 0 | Sep | 2021 | 0.043863 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-23 08:47 | 2021-09-23 16:28 | 6 | 007:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092300027 | New_Event | Bad Weather | Include | Include | Weather | 461 | 2021-09-23 | 2766 | keep | 0 | Sep | 2021 | 0.0018839 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-09-23 08:53 | 2021-09-23 12:25 | 50 | 003:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA 1 X 40 EN RISER A T-21 | B21092300047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2021-09-23 | 10600 | keep | 0 | Sep | 2021 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-23 09:00 | 2021-09-23 17:10 | 6 | 008:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA POR LO MISMO | M21092300014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 490 | 2021-09-23 | 2940 | keep | 0 | Sep | 2021 | 0.0020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-09-23 09:04 | 2021-09-23 09:40 | 900 | 000:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | MACHETES ABIERTOS PARA SECCIONALIZAR AVERIA | P21092300034 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 36 | 2021-09-23 | 32400 | keep | 0 | Sep | 2021 | 0.022067 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-23 09:19 | 2021-09-23 09:20 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 2354 | keep | 0 | Sep | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2021-09-23 09:29 | 2021-09-23 09:30 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1709-5 | S21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 1533 | keep | 0 | Sep | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-09-23 09:29 | 2021-09-23 09:30 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1709-03 | S21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 2364 | keep | 0 | Sep | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
PONCE | 2021-09-23 09:30 | 2021-09-23 13:50 | 19 | 004:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21092300034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 260 | 2021-09-23 | 4940 | keep | 0 | Sep | 2021 | 0.0033646 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
CANOVANAS | 2021-09-23 09:33 | 2021-09-23 10:01 | 100 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R21092300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2021-09-23 | 2800 | keep | 0 | Sep | 2021 | 0.0019071 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-23 09:39 | 2021-09-23 15:15 | 15 | 005:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092300034 | New_Event | Bad Weather | Include | Include | Weather | 336 | 2021-09-23 | 5040 | keep | 0 | Sep | 2021 | 0.0034327 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-09-23 09:40 | 2021-09-23 17:00 | 900 | 007:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA Y PARARRAYO | P21092300038 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 440 | 2021-09-23 | 396000 | keep | 0 | Sep | 2021 | 0.26971 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-09-23 09:41 | 2021-09-23 09:42 | 1827 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21092300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-23 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2021-09-23 09:41 | 2021-09-23 15:45 | 50 | 006:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092300035 | New_Event | Bad Weather | Include | Include | Weather | 364 | 2021-09-23 | 18200 | keep | 0 | Sep | 2021 | 0.012396 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-23 09:42 | 2021-09-23 15:10 | 60 | 005:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21092300045 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-09-23 | 19680 | keep | 0 | Sep | 2021 | 0.013404 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-23 09:44 | 2021-09-23 19:10 | 1 | 009:26 | P | DESGANCHE | 1 X 30 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21092300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 566 | 2021-09-23 | 566 | keep | 0 | Sep | 2021 | 0.0003855 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-09-23 09:48 | 2021-09-23 11:04 | 50 | 001:16 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA SECCIONALIZARON TRANSFORMADOR AVERIADO | R21092300047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 76 | 2021-09-23 | 3800 | keep | 0 | Sep | 2021 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-09-23 09:58 | 2021-09-23 18:46 | 5 | 008:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA EN EL PISO | P21092300040 | New_Event | Wire Down | Include | Include | Equipment | 528 | 2021-09-23 | 2640 | keep | 0 | Sep | 2021 | 0.0017981 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-09-23 10:01 | 2021-09-23 10:02 | 225 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 225 | keep | 0 | Sep | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-23 10:01 | 2021-09-23 10:02 | 870 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-09-23 10:04 | 2021-09-23 17:38 | 10 | 007:34 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | B21092300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 454 | 2021-09-23 | 4540 | keep | 0 | Sep | 2021 | 0.0030922 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-23 10:07 | 2021-09-23 18:35 | 3 | 008:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A21092300106 | New_Event | Bad Weather | Include | Include | Weather | 508 | 2021-09-23 | 1524 | keep | 0 | Sep | 2021 | 0.001038 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-09-23 10:10 | 2021-09-23 18:35 | 10 | 008:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | C21092300033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 505 | 2021-09-23 | 5050 | keep | 0 | Sep | 2021 | 0.0034395 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-23 10:11 | 2021-09-23 19:23 | 7 | 009:12 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA POR POSTE PARTIDO | S21092000044 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 552 | 2021-09-23 | 3864 | keep | 0 | Sep | 2021 | 0.0026318 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-23 10:17 | 2021-09-23 14:57 | 25 | 004:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21092300021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-09-23 | 7000 | keep | 0 | Sep | 2021 | 0.0047677 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-23 10:19 | 2021-09-23 17:05 | 50 | 006:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA GLOBO CRUZO LINEAS | A21092300045 | New_Event |  |  | Include | Wildlife | 406 | 2021-09-23 | 20300 | keep | 0 | Sep | 2021 | 0.013826 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-09-23 10:33 | 2021-09-23 18:19 | 18 | 007:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO TRANSFORMADORES PARA REEMPLAZO DE POSTE PARTIDO POR VEHICULO | R21092300021 | New_Event |  |  | Include | Wildlife | 466 | 2021-09-23 | 8388 | keep | 0 | Sep | 2021 | 0.005713 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2021-09-23 10:33 | 2021-09-24 16:44 | 8 | 030:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21092300047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1811 | 2021-09-23 | 14488 | keep | 0 | Sep | 2021 | 0.0098677 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-09-23 10:33 | 2021-09-23 11:01 | 325 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON R/R OFF HABIA PERSONAL REALIZANDO DESGANCHE Y SE VERIFICO EN CAMPO E INDICAN QUE NO CRUZARON FASE Y SE CERRO POR CONTROL. COMPAÃ‘IA PRIVADA DRC | B21092300071 | Additional_clients | Wire Down | Include | Include | Equipment | 28 | 2021-09-23 | 9100 | keep | 0 | Sep | 2021 | 0.006198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-23 10:38 | 2021-09-23 12:35 | 60 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092300073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2021-09-23 | 7020 | keep | 0 | Sep | 2021 | 0.0047813 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-23 10:54 | 2021-09-24 15:46 | 60 | 028:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO Y SE REMPLAZO CONDUCTOR QUEMADO EN AEREO PROVISIONAL | B21092300083 | New_Event | Wire Down | Include | Include | Equipment | 1732 | 2021-09-23 | 103920 | keep | 0 | Sep | 2021 | 0.070779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-09-23 10:54 | 2021-09-23 16:06 | 10 | 005:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-09-23 | 3120 | keep | 0 | Sep | 2021 | 0.002125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-23 11:01 | 2021-09-24 14:13 | 75 | 027:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN MACHETES DE SALIDA ALIMENTADOR | B21092200168 | Partial_restoration | Wire Down | Include | Include | Equipment | 1632 | 2021-09-23 | 122400 | keep | 0 | Sep | 2021 | 0.083366 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-23 11:02 | 2021-09-23 17:10 | 1 | 006:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 5 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21092300035 | New_Event | Bad Weather | Include | Include | Weather | 368 | 2021-09-23 | 368 | keep | 0 | Sep | 2021 | 0.00025064 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-09-23 11:04 | 2021-09-23 18:10 | 10 | 007:06 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | R21092300047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 426 | 2021-09-23 | 4260 | keep | 0 | Sep | 2021 | 0.0029015 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-23 11:05 | 2021-09-23 17:26 | 30 | 006:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21092300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2021-09-23 | 11430 | keep | 0 | Sep | 2021 | 0.0077849 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-23 11:10 | 2021-09-24 15:20 | 10 | 028:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21092300047 | New_Event | Bad Weather | Include | Include | Weather | 1690 | 2021-09-23 | 16900 | keep | 0 | Sep | 2021 | 0.011511 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-23 11:20 | 2021-09-23 19:05 | 1 | 007:45 | P | DESGANCHE | 1 X 20 EN RISER SE RETIRO ENREDADERA | M21092300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2021-09-23 | 465 | keep | 0 | Sep | 2021 | 0.00031671 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-09-23 11:26 | 2021-09-23 15:20 | 8 | 003:54 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | P21092300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2021-09-23 | 1872 | keep | 0 | Sep | 2021 | 0.001275 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
SAN JUAN | 2021-09-23 11:31 | 2021-09-23 11:32 | 225 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-05 Y SE CERRO POR SCADA LA CARGA DEL 1303-04 SE ENCUENTRA POR EL 1303-05 | S21092300000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 225 | keep | 0 | Sep | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-23 11:31 | 2021-09-23 11:32 | 870 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-05 Y SE CERRO POR SCADA LLEVA EL 1303-04 | S21092300000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2021-09-23 11:39 | 2021-09-23 16:14 | 51 | 004:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER | C21092300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-09-23 | 14025 | keep | 0 | Sep | 2021 | 0.0095524 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
BAYAMON | 2021-09-23 11:46 | 2021-09-26 11:47 | 10 | 072:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092300098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4321 | 2021-09-23 | 43210 | keep | 0 | Sep | 2021 | 0.02943 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-23 11:55 | 2021-09-24 22:50 | 32 | 034:55 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE REALIZO DESGANCHE | M21092300092 | New_Event | Defective Pole | Include | Include | Equipment | 2095 | 2021-09-23 | 67040 | keep | 0 | Sep | 2021 | 0.045661 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2021-09-23 12:04 | 2021-09-23 18:26 | 15 | 006:22 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA LA CARGA ESTA POR EL 1206-03 | S21092300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-09-23 | 5730 | keep | 0 | Sep | 2021 | 0.0039027 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-23 12:10 | 2021-09-23 17:43 | 10 | 005:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092300064 | New_Event | Bad Weather | Include | Include | Weather | 333 | 2021-09-23 | 3330 | keep | 0 | Sep | 2021 | 0.002268 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-23 12:19 | 2021-09-23 15:19 | 10 | 003:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092300067 | New_Event | Bad Weather | Include | Include | Weather | 180 | 2021-09-23 | 1800 | keep | 0 | Sep | 2021 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-23 12:37 | 2021-09-23 17:05 | 20 | 004:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21092300070 | New_Event | Cutout Failure | Include | Include | Equipment | 268 | 2021-09-23 | 5360 | keep | 0 | Sep | 2021 | 0.0036507 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-23 12:38 | 2021-09-23 15:47 | 150 | 003:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21092300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-09-23 | 28350 | keep | 0 | Sep | 2021 | 0.019309 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-09-23 12:43 | 2021-09-23 17:03 | 40 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092300065 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-09-23 | 10400 | keep | 0 | Sep | 2021 | 0.0070834 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-23 12:44 | 2021-09-23 17:40 | 40 | 004:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-09-23 | 11840 | keep | 0 | Sep | 2021 | 0.0080642 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-23 12:46 | 2021-09-25 15:37 | 10 | 050:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR UNO DE 25KVA FID 8317636 HC MON73281-1 | B21092300113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3051 | 2021-09-23 | 30510 | keep | 0 | Sep | 2021 | 0.02078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-23 12:55 | 2021-09-23 17:32 | 10 | 004:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092300074 | New_Event | Bad Weather | Include | Include | Weather | 277 | 2021-09-23 | 2770 | keep | 0 | Sep | 2021 | 0.0018866 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-09-23 13:09 | 2021-09-23 15:41 | 51 | 002:32 | P | DESGANCHE | 1 X 50 Y 2 X 40 EN CORTES DE LINEA | C21092300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-09-23 | 7752 | keep | 0 | Sep | 2021 | 0.0052799 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
BAYAMON | 2021-09-23 13:14 | 2021-09-23 16:31 | 4431 | 003:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICIO PUENTE ABIERTO EN MACHETES, SE ABRIO MACHETES ANTES Y SE CERRO INTERRUPTOR | B21092300000 | New_Event | Wire Down | Include | Include | Equipment | 197 | 2021-09-23 | 872907 | keep | 0 | Sep | 2021 | 0.59453 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
CANOVANAS | 2021-09-23 13:14 | 2021-09-23 16:45 | 810 | 003:31 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE QUEMADO | R21092300063 | New_Event | Switch Failure | Include | Include | Equipment | 211 | 2021-09-23 | 170910 | keep | 0 | Sep | 2021 | 0.11641 | 0.00055169 | Sustained | FALSE | FALSE | Not_TMED_Event | 810
BAYAMON | 2021-09-23 13:18 | 2021-09-23 13:19 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B2109230000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
VEGA BAJA | 2021-09-23 13:18 | 2021-09-23 15:01 | 80 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092300121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-09-23 | 8240 | keep | 0 | Sep | 2021 | 0.0056122 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-23 13:20 | 2021-09-23 13:21 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-09-23 13:24 | 2021-09-23 13:25 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-09-23 13:26 | 2021-09-23 13:27 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BARRANQUITAS | 2021-09-23 13:34 | 2021-09-23 21:22 | 65 | 007:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21092300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 468 | 2021-09-23 | 30420 | keep | 0 | Sep | 2021 | 0.020719 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-09-23 13:48 | 2021-09-23 14:10 | 4 | 000:22 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA | P21096220004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2021-09-23 | 88 | keep | 0 | Sep | 2021 | 5.9936e-05 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
PONCE | 2021-09-23 13:50 | 2021-09-23 17:25 | 35 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE EN EL PISO | P21092300061 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2021-09-23 | 7525 | keep | 0 | Sep | 2021 | 0.0051252 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-09-23 13:54 | 2021-09-23 14:12 | 40 | 000:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA MAQUINA CRUZO LINEAS | C21092300069 | New_Event |  |  | Include | Wildlife | 18 | 2021-09-23 | 720 | keep | 0 | Sep | 2021 | 0.00049039 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-23 14:00 | 2021-09-23 18:51 | 50 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092300163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-09-23 | 14550 | keep | 0 | Sep | 2021 | 0.0099099 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-23 14:04 | 2021-09-23 18:37 | 80 | 004:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092300082 | New_Event |  |  | Include | Wildlife | 273 | 2021-09-23 | 21840 | keep | 0 | Sep | 2021 | 0.014875 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-09-23 14:22 | 2021-09-23 18:59 | 10 | 004:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21092300171 | New_Event | Secondary Wire Down | Include | Include | Equipment | 277 | 2021-09-23 | 2770 | keep | 0 | Sep | 2021 | 0.0018866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-23 14:23 | 2021-09-23 16:48 | 100 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | R21092300075 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2021-09-23 | 14500 | keep | 0 | Sep | 2021 | 0.0098759 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-23 14:28 | 2021-09-24 11:54 | 12 | 021:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO CAJA DE TRANSFORMADOR AVERIADA Y BAJANTE SECUNDARIO DE TRANSFORMADOR | C21092300083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1286 | 2021-09-23 | 15432 | keep | 0 | Sep | 2021 | 0.010511 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-23 14:34 | 2021-09-23 17:52 | 10 | 003:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARO SECUNDARIA | C21092300165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 198 | 2021-09-23 | 1980 | keep | 0 | Sep | 2021 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-23 14:34 | 2021-09-23 17:40 | 30 | 003:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21092300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-09-23 | 5580 | keep | 0 | Sep | 2021 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-23 14:36 | 2021-09-23 14:37 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | B2109230000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 651 | keep | 0 | Sep | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CANOVANAS | 2021-09-23 14:38 | 2021-09-23 17:06 | 80 | 002:28 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | R21092300082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-09-23 | 11840 | keep | 0 | Sep | 2021 | 0.0080642 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-23 14:38 | 2021-09-23 15:00 | 6 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21092300023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2021-09-23 | 132 | keep | 0 | Sep | 2021 | 8.9905e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-23 14:47 | 2021-09-24 09:19 | 6 | 018:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21092300086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1112 | 2021-09-23 | 6672 | keep | 0 | Sep | 2021 | 0.0045443 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-09-23 15:05 | 2021-09-23 16:20 | 111 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | P21092300067 | New_Event |  |  | Include | Wildlife | 75 | 2021-09-23 | 8325 | keep | 0 | Sep | 2021 | 0.0056701 | 7.5602e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 111
SAN JUAN | 2021-09-23 15:07 | 2021-09-24 17:16 | 14 | 026:09 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO T-160 DE 50KVA X 100KVA | R21092300088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1569 | 2021-09-23 | 21966 | keep | 0 | Sep | 2021 | 0.014961 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2021-09-23 15:08 | 2021-09-23 17:25 | 25 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21092300091 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-09-23 | 3425 | keep | 0 | Sep | 2021 | 0.0023328 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-09-23 15:09 | 2021-09-23 18:17 | 59 | 003:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA LINEAS FUERA DEL AISLADOR | P21092300068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 188 | 2021-09-23 | 11092 | keep | 0 | Sep | 2021 | 0.0075547 | 4.0185e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 59
VEGA BAJA | 2021-09-23 15:32 | 2021-09-23 17:02 | 40 | 001:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-09-23 | 3600 | keep | 0 | Sep | 2021 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-23 15:43 | 2021-09-23 15:44 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1825 | keep | 0 | Sep | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-09-23 15:43 | 2021-09-23 15:44 | 47 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 47 | keep | 0 | Sep | 2021 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-09-23 15:43 | 2021-09-23 15:44 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 315 | keep | 0 | Sep | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-09-23 15:43 | 2021-09-23 15:44 | 2 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2 | keep | 0 | Sep | 2021 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-09-23 15:43 | 2021-09-23 15:44 | 2391 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2391 | keep | 0 | Sep | 2021 | 0.0016285 | 0.0016285 | Momentary | FALSE | TRUE | Not_TMED_Event | 2391
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:47 | 817 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO | C21092300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-23 | 3268 | keep | 0 | Sep | 2021 | 0.0022258 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 1153 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1153 | keep | 0 | Sep | 2021 | 0.0007853 | 0.0007853 | Momentary | FALSE | TRUE | Not_TMED_Event | 1153
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 1709 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1709 | keep | 0 | Sep | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | TRUE | Not_TMED_Event | 1709
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 1320 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1320 | keep | 0 | Sep | 2021 | 0.00089905 | 0.00089905 | Momentary | FALSE | TRUE | Not_TMED_Event | 1320
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 2276 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 2276 | keep | 0 | Sep | 2021 | 0.0015502 | 0.0015502 | Momentary | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 777 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 777 | keep | 0 | Sep | 2021 | 0.00052921 | 0.00052921 | Momentary | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 12 | keep | 0 | Sep | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-09-23 15:43 | 2021-09-23 15:44 | 1290 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21092300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-23 | 1290 | keep | 0 | Sep | 2021 | 0.00087861 | 0.00087861 | Momentary | FALSE | TRUE | Not_TMED_Event | 1290
BAYAMON | 2021-09-23 15:48 | 2021-09-24 15:40 | 30 | 023:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | B21092300211 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1432 | 2021-09-23 | 42960 | keep | 0 | Sep | 2021 | 0.02926 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-23 15:49 | 2021-09-23 16:47 | 1277 | 000:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR PARA CORREGIR LINEAS CRUZADAS | A21092100028 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2021-09-23 | 74066 | keep | 0 | Sep | 2021 | 0.050446 | 0.00086976 | Sustained | FALSE | TRUE | Not_TMED_Event | 1277
CAGUAS | 2021-09-23 15:56 | 2021-09-23 19:31 | 40 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | C21092300094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-09-23 | 8600 | keep | 0 | Sep | 2021 | 0.0058574 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-09-23 16:03 | 2021-09-23 19:16 | 15 | 003:13 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REMPLAZO PARARRAYO | C21092300097 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 193 | 2021-09-23 | 2895 | keep | 0 | Sep | 2021 | 0.0019718 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BARRANQUITAS | 2021-09-23 16:07 | 2021-09-23 19:49 | 5 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21092300098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2021-09-23 | 1110 | keep | 0 | Sep | 2021 | 0.00075602 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-09-23 16:09 | 2021-09-25 14:41 | 10 | 046:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | B21092300224 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2792 | 2021-09-23 | 27920 | keep | 0 | Sep | 2021 | 0.019016 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-09-23 16:26 | 2021-09-24 15:20 | 50 | 022:54 | P | DESGANCHE | 1 X 5 EN TRANSFORMADOR DESGANCHE | P21092300033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1374 | 2021-09-23 | 68700 | keep | 0 | Sep | 2021 | 0.046791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-09-23 16:27 | 2021-09-23 17:38 | 10 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRALES SECUNDARIOS | S21092300068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-09-23 | 710 | keep | 0 | Sep | 2021 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-23 16:31 | 2021-09-23 17:25 | 2000 | 000:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES DESPUES DEL PUENTE ABIERTO Y SE CERRO MACHETES N/O CONTRA EL 1719-19 | B21092300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 54 | 2021-09-23 | 108000 | keep | 0 | Sep | 2021 | 0.073558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-09-23 16:40 | 2021-09-23 18:26 | 40 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21092300099 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-09-23 | 4240 | keep | 0 | Sep | 2021 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-23 16:42 | 2021-09-23 18:52 | 175 | 002:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21092300106 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2021-09-23 | 22750 | keep | 0 | Sep | 2021 | 0.015495 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
HUMACAO | 2021-09-23 16:58 | 2021-09-23 20:17 | 40 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21092300111 | New_Event | Wire Down | Include | Include | Equipment | 199 | 2021-09-23 | 7960 | keep | 0 | Sep | 2021 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-23 16:59 | 2021-09-23 17:32 | 7 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REGULARLO QUEDO 124/248V | C21092300007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-09-23 | 231 | keep | 0 | Sep | 2021 | 0.00015733 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-23 17:00 | 2021-09-23 19:53 | 45 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092300277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2021-09-23 | 7785 | keep | 0 | Sep | 2021 | 0.0053023 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-23 17:09 | 2021-09-23 17:10 | 2678 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21092300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-23 | 2678 | keep | 0 | Sep | 2021 | 0.001824 | 0.001824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2678
BAYAMON | 2021-09-23 17:10 | 2021-09-24 16:55 | 20 | 023:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO PUENTE LINEA A CAJA EN CORTE DE LINEA | B21092300305 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1425 | 2021-09-23 | 28500 | keep | 0 | Sep | 2021 | 0.019411 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-23 17:12 | 2021-09-23 20:07 | 60 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 25 EN SU | S21092300076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2021-09-23 | 10500 | keep | 0 | Sep | 2021 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-09-23 17:16 | 2021-09-23 20:34 | 25 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A21092300113 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2021-09-23 | 4950 | keep | 0 | Sep | 2021 | 0.0033714 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-09-23 17:19 | 2021-09-23 18:40 | 10 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092300114 | Partial_restoration | Bad Weather | Include | Include | Weather | 81 | 2021-09-23 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-23 17:24 | 2021-09-23 23:08 | 1 | 005:44 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE AISLO PUENTE PEGADO A ESTRUCTURA SE REMPLAZO FUSIBLE DE LA ALTA Y SE NORMALIZO LA CARGA | B21092300000 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-09-23 | 344 | keep | 0 | Sep | 2021 | 0.0002343 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-23 17:24 | 2021-09-23 23:08 | 81 | 005:44 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE AISLO PUENTE PEGADO A ESTRUCTURA SE REMPLAZO FUSIBLE DE LA ALTA Y SE NORMALIZO LA CARGA | B21092300000 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-09-23 | 27864 | keep | 0 | Sep | 2021 | 0.018978 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2021-09-23 17:25 | 2021-09-23 23:25 | 100 | 006:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO MACHETES Y SE CERRARON PUENTES Y SE NORMALIZO LA CARGA | B21092300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 360 | 2021-09-23 | 36000 | keep | 0 | Sep | 2021 | 0.024519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-23 17:34 | 2021-09-23 17:35 | 1250 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092300126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 1250 | keep | 0 | Sep | 2021 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
ARECIBO | 2021-09-23 17:41 | 2021-09-23 20:42 | 10 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092300116 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-09-23 | 1810 | keep | 0 | Sep | 2021 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-23 17:41 | 2021-09-23 19:59 | 200 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092300116 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-09-23 | 27600 | keep | 0 | Sep | 2021 | 0.018798 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-23 17:42 | 2021-09-24 10:42 | 1 | 017:00 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFROMADOR | S21092300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1020 | 2021-09-23 | 1020 | keep | 0 | Sep | 2021 | 0.00069472 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-23 17:42 | 2021-09-23 18:59 | 10 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092300117 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-09-23 | 770 | keep | 0 | Sep | 2021 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-23 17:46 | 2021-09-23 17:47 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 99% DEL 1909-09 | S21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 222 | keep | 0 | Sep | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-09-23 17:46 | 2021-09-23 17:47 | 4412 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA EL 99% DEL 1909-09 POR EL 1907-03 | S21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 4412 | keep | 0 | Sep | 2021 | 0.003005 | 0.003005 | Momentary | FALSE | FALSE | Not_TMED_Event | 4412
PONCE | 2021-09-23 17:53 | 2021-09-23 17:54 | 1979 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER SUBESTACION PORTATIL | P210923000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-09-23 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-23 17:53 | 2021-09-23 17:54 | 5069 | 000:01 | S | OTRAS CAUSAS | RECIERRE BREAKER SUBESTACION PORTATIL | P210923000XX | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-23 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-23 17:53 | 2021-09-23 17:54 | 5063 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER SUBESTACION PORTATIL | P210923000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-09-23 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2021-09-23 17:54 | 2021-09-23 19:20 | 50 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PALOMA CRUZO FASE | P21092300085 | New_Event |  |  | Include | Wildlife | 86 | 2021-09-23 | 4300 | keep | 0 | Sep | 2021 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-23 18:00 | 2021-09-24 14:00 | 15 | 020:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 50KVA 4160/7200V 120/240V HOWARD SER:1660591118 X 50 KVA | A21092300119 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1200 | 2021-09-23 | 18000 | keep | 0 | Sep | 2021 | 0.01226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-09-23 18:01 | 2021-09-24 17:05 | 20 | 023:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21092300120 | New_Event | Bad Weather | Include | Include | Weather | 1384 | 2021-09-23 | 27680 | keep | 0 | Sep | 2021 | 0.018853 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-23 18:05 | 2021-09-24 10:00 | 70 | 015:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21092300072 | New_Event | Bad Weather | Include | Include | Weather | 955 | 2021-09-23 | 66850 | keep | 0 | Sep | 2021 | 0.045531 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-09-23 18:14 | 2021-09-23 19:21 | 30 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN 3 TRANSFORMADORES DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A21092300121 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-09-23 | 2010 | keep | 0 | Sep | 2021 | 0.001369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-23 18:17 | 2021-09-23 18:19 | 225 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE CERRO POR SCADA LA CARGA ESTA POR EL 1303-05 | S21092300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-09-23 | 450 | keep | 0 | Sep | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-23 18:17 | 2021-09-23 18:19 | 870 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA CARGA 1303-04 | S21092300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-09-23 | 1740 | keep | 0 | Sep | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
UTUADO | 2021-09-23 18:29 | 2021-09-24 18:15 | 80 | 023:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21092300124 | New_Event | Bad Weather | Include | Include | Weather | 1426 | 2021-09-23 | 114080 | keep | 0 | Sep | 2021 | 0.077699 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-09-23 18:37 | 2021-09-23 19:39 | 4 | 001:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR REMPLAZO CAJA QUEMADA | C21092300129 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2021-09-23 | 248 | keep | 0 | Sep | 2021 | 0.00016891 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-09-23 18:43 | 2021-09-23 18:49 | 5620 | 000:06 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA ESTA POR 1620-04 | S21092300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-09-23 | 33720 | keep | 0 | Sep | 2021 | 0.022967 | 0.0038278 | Sustained | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-09-23 18:43 | 2021-09-23 18:49 | 360 | 000:06 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA ESTA POR EL 1620-04 | S21092300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-09-23 | 2160 | keep | 0 | Sep | 2021 | 0.0014712 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
SAN JUAN | 2021-09-23 18:43 | 2021-09-23 18:49 | 36 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LA CARGA ESTA POR EL 1620-04 | S21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-09-23 | 216 | keep | 0 | Sep | 2021 | 0.00014712 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-09-23 18:43 | 2021-09-23 18:50 | 172 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1620-01, PARTE DEL 1336-10 Y EL 1336-07 | S21092300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-09-23 | 1204 | keep | 0 | Sep | 2021 | 0.00082004 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-09-23 18:46 | 2021-09-23 18:47 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21092300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-23 | 3957 | keep | 0 | Sep | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
VEGA BAJA | 2021-09-23 18:52 | 2021-09-24 11:18 | 50 | 016:26 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21092300276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 986 | 2021-09-23 | 49300 | keep | 0 | Sep | 2021 | 0.033578 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-23 18:58 | 2021-09-23 19:01 | 225 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE CERRO POR SCADA LA CARGA ESTA POR 1303-05 | S21092300000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-09-23 | 675 | keep | 0 | Sep | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-23 18:58 | 2021-09-23 19:01 | 870 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1303-04 | S21092300000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-09-23 | 2610 | keep | 0 | Sep | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-09-23 18:58 | 2021-09-26 18:38 | 10 | 071:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21092300078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4300 | 2021-09-23 | 43000 | keep | 0 | Sep | 2021 | 0.029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-23 19:00 | 2021-09-24 16:30 | 40 | 021:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21092300127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1290 | 2021-09-23 | 51600 | keep | 0 | Sep | 2021 | 0.035145 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-23 19:01 | 2021-09-23 23:50 | 225 | 004:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DISCO PARTIDO Y SE CERRO POR SCADA 1303-05 LA CARGA DEL 1303-04 ESTA POR EL 1303-05 | S21092300000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 289 | 2021-09-23 | 65025 | keep | 0 | Sep | 2021 | 0.044288 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-23 19:01 | 2021-09-23 23:50 | 870 | 004:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DISCO PARTIDO Y SE CERRO POR SCADA LLEVA 1303-04 | S21092300000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 289 | 2021-09-23 | 251430 | keep | 0 | Sep | 2021 | 0.17125 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-09-23 19:09 | 2021-09-23 19:52 | 50 | 000:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR FUERTES LLUVIAS | B21092300281 | New_Event | Bad Weather | Include | Include | Weather | 43 | 2021-09-23 | 2150 | keep | 0 | Sep | 2021 | 0.0014644 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-09-23 19:13 | 2021-09-23 22:22 | 40 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | P21092300099 | New_Event |  |  | Include | Wildlife | 189 | 2021-09-23 | 7560 | keep | 0 | Sep | 2021 | 0.0051491 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-23 19:18 | 2021-09-23 19:51 | 293 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7900 | P21092300116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-09-23 | 9669 | keep | 0 | Sep | 2021 | 0.0065855 | 0.00019956 | Sustained | FALSE | TRUE | Not_TMED_Event | 293
PONCE | 2021-09-23 19:18 | 2021-09-23 19:51 | 253 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7900 | P21092300116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-09-23 | 8349 | keep | 0 | Sep | 2021 | 0.0056865 | 0.00017232 | Sustained | FALSE | TRUE | Not_TMED_Event | 253
PONCE | 2021-09-23 19:18 | 2021-09-23 19:51 | 900 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7900 | P21092300116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-09-23 | 29700 | keep | 0 | Sep | 2021 | 0.020229 | 0.00061299 | Sustained | FALSE | TRUE | Not_TMED_Event | 900
PONCE | 2021-09-23 19:18 | 2021-09-23 19:51 | 1615 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7900 | P21092300116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-09-23 | 53295 | keep | 0 | Sep | 2021 | 0.036299 | 0.0011 | Sustained | FALSE | TRUE | Not_TMED_Event | 1615
PONCE | 2021-09-23 19:18 | 2021-09-23 19:51 | 3 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7900 | P21092300116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-09-23 | 99 | keep | 0 | Sep | 2021 | 6.7428e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-09-23 19:19 | 2021-09-23 23:59 | 60 | 004:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092400188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-09-23 | 16800 | keep | 0 | Sep | 2021 | 0.011442 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-23 19:20 | 2021-09-23 20:19 | 828 | 000:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR Y SE CERRO POR SCADA 1206-04 EL 60% DE LA CARGA SE ENCUENTRA POR EL 1206-04 | S21092300107 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 59 | 2021-09-23 | 48852 | keep | 0 | Sep | 2021 | 0.033273 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2021-09-23 19:20 | 2021-09-23 22:05 | 1977 | 002:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE LLEVO LINEA A SU SITIO Y SE CERRO MACHETES DE AMARRE CONTRA 1206-04 EL 40% DE LA CARGA ESTA POR EL 1206-04 | S21092300107 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 165 | 2021-09-23 | 326205 | keep | 0 | Sep | 2021 | 0.22218 | 0.0013465 | Sustained | FALSE | TRUE | Not_TMED_Event | 1977
SAN JUAN | 2021-09-23 19:20 | 2021-09-23 20:19 | 1799 | 000:59 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADO Y SE CERRO POR SCADA 1206-04 QUE LLEVA 40% DEL 1204-04 60% DEL 1204-03 Y PARTE DEL 1303-02 | S21092300107 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 59 | 2021-09-23 | 106141 | keep | 0 | Sep | 2021 | 0.072292 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-09-23 19:20 | 2021-09-23 20:19 | 500 | 000:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR Y SE CERRO POR SCADA 1206-04 PARTE DE LA CARGA DEL 1303-02 ESTA POR EL 1206-04 | S21092300107 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 59 | 2021-09-23 | 29500 | keep | 0 | Sep | 2021 | 0.020092 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-09-23 19:32 | 2021-09-24 13:55 | 1 | 018:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR SE RETIRO RATON CRUZANDO LINEAS | B21092200319 | New_Event |  |  | Include | Wildlife | 1103 | 2021-09-23 | 1103 | keep | 0 | Sep | 2021 | 0.00075125 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-23 19:40 | 2021-09-24 14:09 | 80 | 018:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092300091 | New_Event | Bad Weather | Include | Include | Weather | 1109 | 2021-09-23 | 88720 | keep | 0 | Sep | 2021 | 0.060427 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-23 19:42 | 2021-09-24 10:53 | 80 | 015:11 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | A21092300137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 911 | 2021-09-23 | 72880 | keep | 0 | Sep | 2021 | 0.049638 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-23 19:50 | 2021-09-23 20:35 | 8 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21092300088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-09-23 | 360 | keep | 0 | Sep | 2021 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-23 20:13 | 2021-09-24 09:50 | 70 | 013:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21092300145 | New_Event | Bad Weather | Include | Include | Weather | 817 | 2021-09-23 | 57190 | keep | 0 | Sep | 2021 | 0.038952 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-09-23 20:16 | 2021-09-23 22:16 | 100 | 002:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZARON DISCOS | R21092300129 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2021-09-23 | 12000 | keep | 0 | Sep | 2021 | 0.0081731 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-23 20:39 | 2021-09-24 14:13 | 7 | 017:34 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C21092300139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1054 | 2021-09-23 | 7378 | keep | 0 | Sep | 2021 | 0.0050251 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-09-23 20:49 | 2021-09-24 11:20 | 125 | 014:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21092300112 | New_Event | Bad Weather | Include | Include | Weather | 871 | 2021-09-23 | 108875 | keep | 0 | Sep | 2021 | 0.074154 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
SAN JUAN | 2021-09-23 20:51 | 2021-09-24 12:49 | 50 | 015:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21092300198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 958 | 2021-09-23 | 47900 | keep | 0 | Sep | 2021 | 0.032624 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-23 20:55 | 2021-09-24 10:56 | 20 | 014:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21092300149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 841 | 2021-09-23 | 16820 | keep | 0 | Sep | 2021 | 0.011456 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-23 20:55 | 2021-09-24 18:00 | 45 | 021:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21092300312 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1265 | 2021-09-23 | 56925 | keep | 0 | Sep | 2021 | 0.038771 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-23 20:56 | 2021-09-24 13:58 | 30 | 017:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21092300313 | New_Event | Cutout Failure | Include | Include | Equipment | 1022 | 2021-09-23 | 30660 | keep | 0 | Sep | 2021 | 0.020882 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-23 21:08 | 2021-09-23 21:09 | 828 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES RECERRO 1206-04 QUE LLEVA EL 60% DEL 1204-03 | S21092300107 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-23 21:08 | 2021-09-23 21:09 | 1799 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES RECERRO 1206-04 LLEVA 60% DEL 1204-03 Y PARTE DEL 1303-02 | S21092300107 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 1799 | keep | 0 | Sep | 2021 | 0.0012253 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-23 21:08 | 2021-09-23 21:09 | 500 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES RECERRO 1206-04 PARTE DE LA CARGA DEL 1303-02 ESTA POR EL 1206-04 | S21092300107 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-23 | 500 | keep | 0 | Sep | 2021 | 0.00034055 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-23 21:28 | 2021-09-24 19:09 | 6 | 021:41 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B21092300322 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1301 | 2021-09-23 | 7806 | keep | 0 | Sep | 2021 | 0.0053166 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-23 21:58 | 2021-09-24 19:30 | 10 | 021:32 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA X 37.5KVA | C21092300143 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1292 | 2021-09-23 | 12920 | keep | 0 | Sep | 2021 | 0.0087998 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-23 22:41 | 2021-09-23 22:42 | 40 | 000:01 | P | OTRAS CAUSAS | SE ABRIO MACHETES Y SE CERRO NORMALLY-OPEN PARA TRANSFERIR CARGA DEJAR ALIMENTADOR EN SERVICIO HACIA SAN GERMAN | M21092300124 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-23 | 40 | keep | 0 | Sep | 2021 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-23 22:52 | 2021-09-24 14:13 | 12 | 015:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21092300144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 921 | 2021-09-23 | 11052 | keep | 0 | Sep | 2021 | 0.0075275 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-23 23:04 | 2021-09-24 12:22 | 10 | 013:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092200332 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 798 | 2021-09-23 | 7980 | keep | 0 | Sep | 2021 | 0.0054351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-24 00:32 | 2021-09-24 17:13 | 50 | 016:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21092400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1001 | 2021-09-24 | 50050 | keep | 0 | Sep | 2021 | 0.034089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-24 00:52 | 2021-09-24 11:45 | 100 | 010:53 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21092400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2021-09-24 | 65300 | keep | 0 | Sep | 2021 | 0.044476 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-09-24 00:55 | 2021-09-24 16:55 | 10 | 016:00 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 37.5KVA | R21092400001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 960 | 2021-09-24 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-24 02:44 | 2021-09-24 13:03 | 80 | 010:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21092400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 619 | 2021-09-24 | 49520 | keep | 0 | Sep | 2021 | 0.033728 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-24 03:03 | 2021-09-24 12:53 | 50 | 009:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA DE 100AMP. MARCA:CHINT | A21092400002 | New_Event | Cutout Failure | Include | Include | Equipment | 590 | 2021-09-24 | 29500 | keep | 0 | Sep | 2021 | 0.020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-09-24 03:12 | 2021-09-24 16:03 | 90 | 012:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21092400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 771 | 2021-09-24 | 69390 | keep | 0 | Sep | 2021 | 0.047261 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-09-24 06:01 | 2021-09-24 06:02 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 3438 | keep | 0 | Sep | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
PONCE | 2021-09-24 06:07 | 2021-09-24 06:08 | 1067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21092400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 1067 | keep | 0 | Sep | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
BAYAMON | 2021-09-24 06:14 | 2021-09-25 20:25 | 10 | 038:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE 50KVA FID 23355351 HC MON73283-1 | B21092400012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2291 | 2021-09-24 | 22910 | keep | 0 | Sep | 2021 | 0.015604 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-24 06:17 | 2021-09-24 10:27 | 20 | 004:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PRIMARIO QUEMADO | A21092400008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 250 | 2021-09-24 | 5000 | keep | 0 | Sep | 2021 | 0.0034055 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-24 06:34 | 2021-09-24 13:25 | 50 | 006:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21092400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2021-09-24 | 20550 | keep | 0 | Sep | 2021 | 0.013997 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-24 06:58 | 2021-09-24 19:28 | 15 | 012:30 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | A21092400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2021-09-24 | 11250 | keep | 0 | Sep | 2021 | 0.0076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-24 07:11 | 2021-09-24 07:12 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 922 | keep | 0 | Sep | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-09-24 07:11 | 2021-09-24 07:12 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 135 | keep | 0 | Sep | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2021-09-24 07:17 | 2021-09-24 13:30 | 40 | 006:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21092400016 | New_Event | Bad Weather | Include | Include | Weather | 373 | 2021-09-24 | 14920 | keep | 0 | Sep | 2021 | 0.010162 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-24 07:51 | 2021-09-24 18:44 | 15 | 010:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2021-09-24 | 9795 | keep | 0 | Sep | 2021 | 0.0066713 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-24 07:58 | 2021-09-25 14:16 | 50 | 030:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO EN TRONCAL | B21092400026 | New_Event | Wire Down | Include | Include | Equipment | 1818 | 2021-09-24 | 90900 | keep | 0 | Sep | 2021 | 0.061912 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-09-24 08:09 | 2021-09-24 16:02 | 30 | 007:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B21092400027 | New_Event |  |  | Include | Wildlife | 473 | 2021-09-24 | 14190 | keep | 0 | Sep | 2021 | 0.0096647 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-24 08:18 | 2021-09-24 10:21 | 12 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-09-24 | 1476 | keep | 0 | Sep | 2021 | 0.0010053 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-24 08:34 | 2021-09-24 15:37 | 30 | 007:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2021-09-24 | 12690 | keep | 0 | Sep | 2021 | 0.0086431 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-24 08:44 | 2021-09-24 08:46 | 5620 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA EL 90% DE LA CARGA SE ENCUENTRA POR EL 1620-04 | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-24 | 11240 | keep | 0 | Sep | 2021 | 0.0076555 | 0.0038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-09-24 08:44 | 2021-09-24 08:46 | 343 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA EL 85% DE LA CARGA ESTA POR EL 1620-04 | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-24 | 686 | keep | 0 | Sep | 2021 | 0.00046723 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2021-09-24 08:44 | 2021-09-24 08:46 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 85% DEL 1336-10Y EL 90% DEL 1336-07 | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-24 | 344 | keep | 0 | Sep | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
YAUCO | 2021-09-24 08:47 | 2021-09-24 13:56 | 400 | 005:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21092400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-09-24 | 123600 | keep | 0 | Sep | 2021 | 0.084183 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
SAN JUAN | 2021-09-24 09:29 | 2021-09-24 12:55 | 35 | 003:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER PRONCIPAL Y 1 X 65 EN CORTE DE LINEA RAMAL | S21092400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2021-09-24 | 7210 | keep | 0 | Sep | 2021 | 0.0049107 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-09-24 09:49 | 2021-09-24 12:07 | 11 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21092400013 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2021-09-24 | 1518 | keep | 0 | Sep | 2021 | 0.0010339 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
BARRANQUITAS | 2021-09-24 09:54 | 2021-09-24 18:26 | 45 | 008:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 512 | 2021-09-24 | 23040 | keep | 0 | Sep | 2021 | 0.015692 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-24 09:58 | 2021-09-24 16:42 | 30 | 006:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | S21092400033 | New_Event | Cutout Failure | Include | Include | Equipment | 404 | 2021-09-24 | 12120 | keep | 0 | Sep | 2021 | 0.0082549 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-24 10:03 | 2021-09-24 11:55 | 810 | 001:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092400041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-09-24 | 90720 | keep | 0 | Sep | 2021 | 0.061789 | 0.00055169 | Sustained | FALSE | TRUE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-09-24 10:03 | 2021-09-24 11:55 | 1235 | 001:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092400041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-09-24 | 138320 | keep | 0 | Sep | 2021 | 0.094209 | 0.00084115 | Sustained | FALSE | TRUE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-09-24 10:03 | 2021-09-24 11:55 | 93 | 001:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092400041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-09-24 | 10416 | keep | 0 | Sep | 2021 | 0.0070943 | 6.3342e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-09-24 10:03 | 2021-09-24 13:03 | 1825 | 003:00 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO CIERRA POR SCADA CERRADO MANUAL ELECTRICO | M21092400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2021-09-24 | 328500 | keep | 0 | Sep | 2021 | 0.22374 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-09-24 10:03 | 2021-09-24 11:55 | 3230 | 001:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092400041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-09-24 | 361760 | keep | 0 | Sep | 2021 | 0.24639 | 0.0021999 | Sustained | FALSE | TRUE | Not_TMED_Event | 3230
SAN JUAN | 2021-09-24 10:07 | 2021-09-24 11:20 | 143 | 001:13 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. SE RETIRO IGUANA DE LA LINEA Y SE CERRO PUENTE PRIMARIO | S21092400036 | New_Event |  |  | Include | Wildlife | 73 | 2021-09-24 | 10439 | keep | 0 | Sep | 2021 | 0.00711 | 9.7397e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 143
ARECIBO | 2021-09-24 10:14 | 2021-09-24 15:54 | 10 | 005:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 25KVA MARCA:PROLEC TE 4160/7200V 120/240V SER:M18B15627 FID:33986379 X 25 KVA | A21092400025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 340 | 2021-09-24 | 3400 | keep | 0 | Sep | 2021 | 0.0023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-24 10:14 | 2021-09-24 14:14 | 30 | 004:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 25KVA 4800/7620V 120/240V COOPER POWER SER:1955005851 FID:33589887 | A21092400025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 240 | 2021-09-24 | 7200 | keep | 0 | Sep | 2021 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-09-24 10:19 | 2021-09-24 13:24 | 11 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092400015 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2021-09-24 | 2035 | keep | 0 | Sep | 2021 | 0.001386 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-09-24 10:25 | 2021-09-24 18:22 | 200 | 007:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092400049 | New_Event | Bad Weather | Include | Include | Weather | 477 | 2021-09-24 | 95400 | keep | 0 | Sep | 2021 | 0.064977 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-09-24 10:29 | 2021-09-24 17:18 | 20 | 006:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2021-09-24 | 8180 | keep | 0 | Sep | 2021 | 0.0055714 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-24 10:30 | 2021-09-24 12:50 | 75 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | M21092400057 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-09-24 | 10500 | keep | 0 | Sep | 2021 | 0.0071515 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-24 10:34 | 2021-09-24 15:15 | 12 | 004:41 | P | DESGANCHE | 2 X 20 EN TRANSFORMADOR POR DESGANCHE | A21092400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-09-24 | 3372 | keep | 0 | Sep | 2021 | 0.0022967 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-09-24 10:41 | 2021-09-25 12:06 | 12 | 025:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092500098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1525 | 2021-09-24 | 18300 | keep | 0 | Sep | 2021 | 0.012464 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-24 10:51 | 2021-09-25 16:08 | 30 | 029:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S21092400046 | New_Event | Cutout Failure | Include | Include | Equipment | 1757 | 2021-09-24 | 52710 | keep | 0 | Sep | 2021 | 0.035901 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-24 10:53 | 2021-09-24 15:37 | 15 | 004:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2021-09-24 | 4260 | keep | 0 | Sep | 2021 | 0.0029015 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-09-24 10:56 | 2021-09-24 16:48 | 110 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REPARO PUENTE ABIERTO | R21092400017 | New_Event | Wire Down | Include | Include | Equipment | 352 | 2021-09-24 | 38720 | keep | 0 | Sep | 2021 | 0.026372 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
CAGUAS | 2021-09-24 11:12 | 2021-09-25 10:26 | 40 | 023:14 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25AMP EN SU - 3 NO CAUSA | C21092400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1394 | 2021-09-24 | 55760 | keep | 0 | Sep | 2021 | 0.037978 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-09-24 11:24 | 2021-09-24 11:25 | 60 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-24 | 60 | keep | 0 | Sep | 2021 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-09-24 11:28 | 2021-09-25 18:25 | 10 | 030:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | B21092400069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1857 | 2021-09-24 | 18570 | keep | 0 | Sep | 2021 | 0.012648 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-24 11:30 | 2021-09-25 03:44 | 83 | 016:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEA POR POSTE PRIMARIO PARTIDO EN ACCIDENTE DE AUTO SE ABREN PUENTES PARA SECCIONALIZAR AVERIA | P21092500008 | New_Event |  |  | Include | Wildlife | 974 | 2021-09-24 | 80842 | keep | 0 | Sep | 2021 | 0.055061 | 5.6531e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 83
BAYAMON | 2021-09-24 11:31 | 2021-09-24 21:31 | 30 | 010:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN AEREO PROVISIONAL | B21092300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 600 | 2021-09-24 | 18000 | keep | 0 | Sep | 2021 | 0.01226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-09-24 11:50 | 2021-09-24 15:51 | 50 | 004:01 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA POR DESGANCHE | A21092400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-09-24 | 12050 | keep | 0 | Sep | 2021 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-24 12:01 | 2021-09-24 22:36 | 12 | 010:35 | P | ESTRUCTURA AVERIADA | SE ASEGURO POSTE PRIMARIO | B21092400079 | New_Event | Defective Pole | Include | Include | Equipment | 635 | 2021-09-24 | 7620 | keep | 0 | Sep | 2021 | 0.0051899 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-24 12:05 | 2021-09-24 16:42 | 10 | 004:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 37.5 X 37.5 KVA HAY OTRO TRANSFORMADOR AVERIADO EN EL AREA | B21092200128 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 277 | 2021-09-24 | 2770 | keep | 0 | Sep | 2021 | 0.0018866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-24 12:09 | 2021-09-25 15:10 | 80 | 027:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21092500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1621 | 2021-09-24 | 129680 | keep | 0 | Sep | 2021 | 0.088324 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-09-24 12:15 | 2021-09-24 16:47 | 200 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN C/L SE REPARO ALAMBRE PRIMARIO | P21092400033 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2021-09-24 | 54400 | keep | 0 | Sep | 2021 | 0.037052 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-09-24 12:17 | 2021-09-24 14:38 | 60 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21092400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-09-24 | 8460 | keep | 0 | Sep | 2021 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-09-24 12:24 | 2021-09-25 10:17 | 12 | 021:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR Y SE REMPLAZO CAJA OPEN TIPE EN TRANSFORMADOR | S21092400082 | New_Event | Cutout Failure | Include | Include | Equipment | 1313 | 2021-09-24 | 15756 | keep | 0 | Sep | 2021 | 0.010731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-24 12:29 | 2021-09-24 15:45 | 2500 | 003:16 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO SE ENCONTRO CAUSA SE CERRO POR CONTROL PARTE DE SU CARGA POR 9405 05 | B21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2021-09-24 | 490000 | keep | 0 | Sep | 2021 | 0.33374 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
BAYAMON | 2021-09-24 12:29 | 2021-09-25 15:11 | 10 | 026:42 | P | NO SE REPORTO CAUSA | 1 X 10 NX | B21092400085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1602 | 2021-09-24 | 16020 | keep | 0 | Sep | 2021 | 0.010911 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-24 12:29 | 2021-09-24 16:30 | 3511 | 004:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO SE ENCONTRO CAUSA SE CERRO POR CONTROL LLEVA PARTE DE LA CARGA 1710 05 | B21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2021-09-24 | 846151 | keep | 0 | Sep | 2021 | 0.57631 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
VEGA BAJA | 2021-09-24 12:31 | 2021-09-25 12:55 | 45 | 024:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B21092400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1464 | 2021-09-24 | 65880 | keep | 0 | Sep | 2021 | 0.044871 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-09-24 12:32 | 2021-09-24 14:27 | 20 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21092400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-09-24 | 2300 | keep | 0 | Sep | 2021 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-24 12:59 | 2021-09-24 15:43 | 30 | 002:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21092400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-09-24 | 4920 | keep | 0 | Sep | 2021 | 0.003351 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-24 13:00 | 2021-09-24 13:01 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
BAYAMON | 2021-09-24 13:05 | 2021-09-24 16:50 | 20 | 003:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092400144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2021-09-24 | 4500 | keep | 0 | Sep | 2021 | 0.0030649 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-24 13:09 | 2021-09-24 13:10 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 225 | keep | 0 | Sep | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-24 13:09 | 2021-09-24 13:10 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2021-09-24 13:21 | 2021-09-25 14:35 | 10 | 025:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21092400081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1514 | 2021-09-24 | 15140 | keep | 0 | Sep | 2021 | 0.010312 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-24 13:23 | 2021-09-24 16:27 | 1447 | 003:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO DE SU-1 A SU-3 DETRAS DE CONDOMINIO BAYSIDE Y SE CERRO DE SU-38 A SU-1 QUEDO 100% EN SERVICIO 1112-04 Y CONTINUA FUERA EL 1419-09 | S21092400082 | New_Event |  |  | Include | Wildlife | 184 | 2021-09-24 | 266248 | keep | 0 | Sep | 2021 | 0.18134 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
CAGUAS | 2021-09-24 13:37 | 2021-09-25 16:07 | 40 | 026:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1590 | 2021-09-24 | 63600 | keep | 0 | Sep | 2021 | 0.043318 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-24 13:52 | 2021-09-24 13:53 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 225 | keep | 0 | Sep | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-09-24 13:52 | 2021-09-24 13:53 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-09-24 13:55 | 2021-09-24 14:51 | 4882 | 000:56 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RECIERRE EN OFF MAL TIEMPO DESCARGAS ELECTRICAS SE CERRO INTERRUPTOR | M21092400127 | New_Event | Bad Weather | Include | Include | Weather | 56 | 2021-09-24 | 273392 | keep | 0 | Sep | 2021 | 0.18621 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
ARECIBO | 2021-09-24 14:03 | 2021-09-24 17:47 | 6 | 003:44 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | A21092400056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-09-24 | 1344 | keep | 0 | Sep | 2021 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-24 14:04 | 2021-09-25 14:19 | 15 | 024:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S21092400106 | New_Event | Wire Down | Include | Include | Equipment | 1455 | 2021-09-24 | 21825 | keep | 0 | Sep | 2021 | 0.014865 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-24 14:09 | 2021-09-24 14:10 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21092400178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 2234 | keep | 0 | Sep | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-09-24 14:10 | 2021-09-25 13:15 | 12 | 023:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092400227 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1385 | 2021-09-24 | 16620 | keep | 0 | Sep | 2021 | 0.01132 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-24 14:11 | 2021-09-24 18:32 | 150 | 004:21 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | A21092400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-09-24 | 39150 | keep | 0 | Sep | 2021 | 0.026665 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-09-24 14:13 | 2021-09-24 15:25 | 325 | 001:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE PRIMARIO ABIERTO LINEA A MACHETE A LA SALIDA DE ALIMENTADOR | B21092400183 | Additional_clients | Wire Down | Include | Include | Equipment | 72 | 2021-09-24 | 23400 | keep | 0 | Sep | 2021 | 0.015938 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
GUAYAMA | 2021-09-24 14:20 | 2021-09-24 23:00 | 140 | 008:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA DEL PISO | P21092400048 | New_Event | Wire Down | Include | Include | Equipment | 520 | 2021-09-24 | 72800 | keep | 0 | Sep | 2021 | 0.049584 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
CAGUAS | 2021-09-24 14:27 | 2021-09-25 17:03 | 40 | 026:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092500084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1596 | 2021-09-24 | 63840 | keep | 0 | Sep | 2021 | 0.043481 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-24 14:27 | 2021-09-24 19:01 | 60 | 004:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092400136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2021-09-24 | 16440 | keep | 0 | Sep | 2021 | 0.011197 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-24 14:47 | 2021-09-24 17:35 | 30 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R21092400030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2021-09-24 | 5040 | keep | 0 | Sep | 2021 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-24 14:57 | 2021-09-24 14:58 | 1565 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21092400044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 1565 | keep | 0 | Sep | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
AGUADILLA | 2021-09-24 14:58 | 2021-09-24 18:46 | 60 | 003:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-09-24 | 13680 | keep | 0 | Sep | 2021 | 0.0093174 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-24 15:06 | 2021-09-24 15:07 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | S21092400124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 199 | keep | 0 | Sep | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
BARRANQUITAS | 2021-09-24 15:16 | 2021-09-24 15:17 | 1617 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21092400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-24 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2021-09-24 15:17 | 2021-09-25 13:47 | 50 | 022:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR MAL TIEMPO | C21092400098 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1350 | 2021-09-24 | 67500 | keep | 0 | Sep | 2021 | 0.045974 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 863 | keep | 0 | Sep | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 309 | keep | 0 | Sep | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 176 | keep | 0 | Sep | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 974 | keep | 0 | Sep | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21092400150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 770 | keep | 0 | Sep | 2021 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2021-09-24 15:27 | 2021-09-24 15:28 | 2225 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21092400149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 2225 | keep | 0 | Sep | 2021 | 0.0015154 | 0.0015154 | Momentary | FALSE | FALSE | Not_TMED_Event | 2225
BARRANQUITAS | 2021-09-24 15:42 | 2021-09-24 16:59 | 265 | 001:17 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR BANCO DE TRANSFORMADOR AVERIADO | C21092400043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 77 | 2021-09-24 | 20405 | keep | 0 | Sep | 2021 | 0.013898 | 0.00018049 | Sustained | FALSE | TRUE | Not_TMED_Event | 265
ARECIBO | 2021-09-24 15:42 | 2021-09-25 09:20 | 10 | 017:38 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | A21092400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1058 | 2021-09-24 | 10580 | keep | 0 | Sep | 2021 | 0.007206 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-24 15:42 | 2021-09-24 19:18 | 80 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21092400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-09-24 | 17280 | keep | 0 | Sep | 2021 | 0.011769 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-24 15:47 | 2021-09-25 11:35 | 165 | 019:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092400052 | New_Event |  |  | Include | Wildlife | 1188 | 2021-09-24 | 196020 | keep | 0 | Sep | 2021 | 0.13351 | 0.00011238 | Sustained | FALSE | TRUE | Not_TMED_Event | 165
MAYAGÃœEZ | 2021-09-24 15:51 | 2021-09-24 15:52 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21092400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-24 15:51 | 2021-09-24 15:52 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21092400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 1235 | keep | 0 | Sep | 2021 | 0.00084115 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-24 15:51 | 2021-09-24 15:52 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21092400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 93 | keep | 0 | Sep | 2021 | 6.3342e-05 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-24 15:51 | 2021-09-24 15:52 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21092400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 1825 | keep | 0 | Sep | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | TRUE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-09-24 15:51 | 2021-09-24 15:52 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21092400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-24 | 3230 | keep | 0 | Sep | 2021 | 0.0021999 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-24 16:07 | 2021-09-24 22:30 | 100 | 006:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21092400161 | New_Event | Wire Down | Include | Include | Equipment | 383 | 2021-09-24 | 38300 | keep | 0 | Sep | 2021 | 0.026086 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-24 16:11 | 2021-09-24 17:03 | 130 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R21092400038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2021-09-24 | 6760 | keep | 0 | Sep | 2021 | 0.0046042 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
GUAYAMA | 2021-09-24 16:11 | 2021-09-24 17:46 | 50 | 001:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21092400060 | New_Event |  |  | Include | Wildlife | 95 | 2021-09-24 | 4750 | keep | 0 | Sep | 2021 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-24 16:21 | 2021-09-25 14:36 | 15 | 022:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFROMADOR QUEMADO DE 37.5 KVA POR LO MISMO | A21092400077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1335 | 2021-09-24 | 20025 | keep | 0 | Sep | 2021 | 0.013639 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-09-24 16:32 | 2021-09-24 19:28 | 6 | 002:56 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR DE 50KVA QUEMADO SE TRANSFIRIO CARGA A TRANSFORMADOR ADYACENTE | R21092400042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 176 | 2021-09-24 | 1056 | keep | 0 | Sep | 2021 | 0.00071924 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-24 16:46 | 2021-09-25 15:15 | 80 | 022:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21092400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1349 | 2021-09-24 | 107920 | keep | 0 | Sep | 2021 | 0.073504 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-24 16:47 | 2021-09-24 20:34 | 75 | 003:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21092400080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-09-24 | 17025 | keep | 0 | Sep | 2021 | 0.011596 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BARRANQUITAS | 2021-09-24 16:59 | 2021-09-24 17:53 | 1 | 000:54 | P | TRANSFORMADOR AVERIADO | REEMPLAZARON DOS TRANSFORMADORES DE 25KVA X 25KVA EN BANCO DE TRANSFORMADOR | C21092400043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 54 | 2021-09-24 | 54 | keep | 0 | Sep | 2021 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-09-24 17:01 | 2021-09-25 16:57 | 80 | 023:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 2 X 30 EN CORTES DE LINEA Y 3 X 15 EN BANCO DE TRANSFORMADORES MAL TIEMPO | C21092400068 | New_Event | Bad Weather | Include | Include | Weather | 1436 | 2021-09-24 | 114880 | keep | 0 | Sep | 2021 | 0.078244 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-24 17:10 | 2021-09-25 11:26 | 25 | 018:16 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | S21092400170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1096 | 2021-09-24 | 27400 | keep | 0 | Sep | 2021 | 0.018662 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-24 17:13 | 2021-09-24 20:03 | 60 | 002:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTE HACIA PROVISIONAL AEREO ROTO | C21092400071 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-09-24 | 10200 | keep | 0 | Sep | 2021 | 0.0069472 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-24 17:20 | 2021-09-25 10:00 | 5 | 016:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A21092400082 | New_Event | Wire Down | Include | Include | Equipment | 1000 | 2021-09-24 | 5000 | keep | 0 | Sep | 2021 | 0.0034055 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-09-24 17:29 | 2021-09-24 21:47 | 85 | 004:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21092400172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2021-09-24 | 21930 | keep | 0 | Sep | 2021 | 0.014936 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
SAN JUAN | 2021-09-24 17:32 | 2021-09-25 13:18 | 25 | 019:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092400173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1186 | 2021-09-24 | 29650 | keep | 0 | Sep | 2021 | 0.020194 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-24 17:35 | 2021-09-24 17:36 | 1447 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO AL CERRAR SU-3 A SU-4 | S21092400082 | Partial_restoration |  |  | Include | Wildlife | 1 | 2021-09-24 | 1447 | keep | 0 | Sep | 2021 | 0.00098555 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-24 17:35 | 2021-09-24 17:36 | 266 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | 95% EN 1419-09 SE ENCONTRO SU-4 LAGARTO CRUZO FASE | S21092400082 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-24 | 266 | keep | 0 | Sep | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-09-24 17:36 | 2021-09-24 17:52 | 40 | 000:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO LAGARTO QUE CRUZO FASE Y SE CERRO SU-3 A SU-4 100% EN SERVICIO | S21092400082 | 1st_after_momentary |  |  | Include | Wildlife | 16 | 2021-09-24 | 640 | keep | 0 | Sep | 2021 | 0.0004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-09-24 17:49 | 2021-09-25 12:00 | 1 | 018:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P21092400073 | New_Event | Bad Weather | Include | Include | Weather | 1091 | 2021-09-24 | 1091 | keep | 0 | Sep | 2021 | 0.00074308 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-24 17:54 | 2021-09-25 12:19 | 25 | 018:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y SE RETIRO PALOMA | S21092400181 | New_Event |  |  | Include | Wildlife | 1105 | 2021-09-24 | 27625 | keep | 0 | Sep | 2021 | 0.018815 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-09-24 17:57 | 2021-09-24 18:25 | 60 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE SALIDA DE ALIMENTADOR | S21092400182 | New_Event | Wire Down | Include | Include | Equipment | 28 | 2021-09-24 | 1680 | keep | 0 | Sep | 2021 | 0.0011442 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-09-24 18:12 | 2021-09-24 18:13 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092400079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 2302 | keep | 0 | Sep | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
ARECIBO | 2021-09-24 18:13 | 2021-09-25 10:10 | 100 | 015:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA CNHP 100 AMP FID-33576640 | A21092400089 | New_Event | Cutout Failure | Include | Include | Equipment | 957 | 2021-09-24 | 95700 | keep | 0 | Sep | 2021 | 0.065181 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-09-24 18:15 | 2021-09-25 19:55 | 15 | 025:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO Y SE AJUSTO CAJA PRIMARIA | S21092400186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1540 | 2021-09-24 | 23100 | keep | 0 | Sep | 2021 | 0.015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-24 18:16 | 2021-09-25 14:27 | 40 | 020:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21092400177 | New_Event | Wire Down | Include | Include | Equipment | 1211 | 2021-09-24 | 48440 | keep | 0 | Sep | 2021 | 0.032992 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-24 18:25 | 2021-09-24 18:26 | 60 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | HACER PRUEBA DE BREAKER Y QUEDO EN SERVICIO | S21092400000 | Partial_restoration | Wire Down | Include | Include | Equipment | 1 | 2021-09-24 | 60 | keep | 0 | Sep | 2021 | 4.0866e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-24 18:39 | 2021-09-25 19:03 | 30 | 024:24 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S21092400190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1464 | 2021-09-24 | 43920 | keep | 0 | Sep | 2021 | 0.029914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-09-24 19:19 | 2021-09-25 11:04 | 10 | 015:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO | A21092400052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 945 | 2021-09-24 | 9450 | keep | 0 | Sep | 2021 | 0.0064364 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-24 19:28 | 2021-09-25 17:53 | 40 | 022:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO TRANSFORMADOR IMPACTADO POR AUTO KVA X KVA | C21092400091 | New_Event |  |  | Include | Wildlife | 1345 | 2021-09-24 | 53800 | keep | 0 | Sep | 2021 | 0.036643 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-24 19:28 | 2021-09-25 09:14 | 80 | 013:46 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA | B21092400243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 826 | 2021-09-24 | 66080 | keep | 0 | Sep | 2021 | 0.045007 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-24 19:38 | 2021-09-25 09:35 | 4 | 013:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092400093 | New_Event | Bad Weather | Include | Include | Weather | 837 | 2021-09-24 | 3348 | keep | 0 | Sep | 2021 | 0.0022803 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-24 19:42 | 2021-09-24 19:54 | 15 | 000:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN AEREO PROVISIONAL | B21092400246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2021-09-24 | 180 | keep | 0 | Sep | 2021 | 0.0001226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-09-24 19:43 | 2021-09-25 13:01 | 8 | 017:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21092400092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1038 | 2021-09-24 | 8304 | keep | 0 | Sep | 2021 | 0.0056558 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-09-24 19:56 | 2021-09-25 10:08 | 2 | 014:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN MONTURA TRIFASICA NEUTRAL CRUZADO | P21092400089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 852 | 2021-09-24 | 1704 | keep | 0 | Sep | 2021 | 0.0011606 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-09-24 20:40 | 2021-09-25 11:37 | 6 | 014:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21092400100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 897 | 2021-09-24 | 5382 | keep | 0 | Sep | 2021 | 0.0036657 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-24 21:03 | 2021-09-25 14:10 | 1 | 017:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN SU-2 ROEDOR CRUZO FASE | P21092400095 | New_Event |  |  | Include | Wildlife | 1027 | 2021-09-24 | 1027 | keep | 0 | Sep | 2021 | 0.00069949 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-24 21:12 | 2021-09-25 11:59 | 15 | 014:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21092400204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 887 | 2021-09-24 | 13305 | keep | 0 | Sep | 2021 | 0.009062 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-24 21:14 | 2021-09-24 21:15 | 3708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21092400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 3708 | keep | 0 | Sep | 2021 | 0.0025255 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
PONCE | 2021-09-24 21:19 | 2021-09-24 21:20 | 100 | 000:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21092400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-24 | 100 | keep | 0 | Sep | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-24 22:11 | 2021-09-25 12:07 | 50 | 013:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M21092400231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 836 | 2021-09-24 | 41800 | keep | 0 | Sep | 2021 | 0.02847 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-24 22:23 | 2021-09-25 12:07 | 50 | 013:44 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO PARRARAYO | S21092300254 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 824 | 2021-09-24 | 41200 | keep | 0 | Sep | 2021 | 0.028061 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-24 22:37 | 2021-09-25 10:12 | 17 | 011:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21092400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2021-09-24 | 11815 | keep | 0 | Sep | 2021 | 0.0080471 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
GUAYAMA | 2021-09-24 22:44 | 2021-09-24 22:45 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092400099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-24 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-09-25 02:21 | 2021-09-25 02:24 | 1945 | 000:03 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR | P21092500005 | New_Event |  |  | Include | Wildlife | 3 | 2021-09-25 | 5835 | keep | 0 | Sep | 2021 | 0.0039742 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2021-09-25 02:24 | 2021-09-25 12:39 | 50 | 010:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21092500012 | 1st_after_momentary |  |  | Include | Wildlife | 615 | 2021-09-25 | 30750 | keep | 0 | Sep | 2021 | 0.020944 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-25 02:57 | 2021-09-25 02:58 | 2859 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21092500000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-09-25 | 2859 | keep | 0 | Sep | 2021 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2021-09-25 02:58 | 2021-09-25 16:33 | 8 | 013:35 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN BANCO DE TRANSFORMADORES REMPLAZO PARARRAYO | C21092500087 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 815 | 2021-09-25 | 6520 | keep | 0 | Sep | 2021 | 0.0044407 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-09-25 03:44 | 2021-09-25 20:30 | 3 | 016:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PRIMARIO PARTIDO SE RELOCALIZO TRANSFORMADOR Y SE CERRO PUENTE PRIMARIO | P21092500008 | Partial_restoration |  |  | Include | Wildlife | 1006 | 2021-09-25 | 3018 | keep | 0 | Sep | 2021 | 0.0020555 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-09-25 04:12 | 2021-09-25 10:57 | 150 | 006:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZO 3 CAJAS PRIMARIAS AVERIADAS | P21092500009 | New_Event | Cutout Failure | Include | Include | Equipment | 405 | 2021-09-25 | 60750 | keep | 0 | Sep | 2021 | 0.041377 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-25 04:31 | 2021-09-25 11:49 | 50 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2021-09-25 | 21900 | keep | 0 | Sep | 2021 | 0.014916 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-25 04:37 | 2021-09-25 08:55 | 68 | 004:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21092500004 | New_Event |  |  | Include | Wildlife | 258 | 2021-09-25 | 17544 | keep | 0 | Sep | 2021 | 0.011949 | 4.6314e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 68
YAUCO | 2021-09-25 05:43 | 2021-09-25 11:37 | 300 | 005:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA DE 200 AMP | P21092500011 | New_Event | Cutout Failure | Include | Include | Equipment | 354 | 2021-09-25 | 106200 | keep | 0 | Sep | 2021 | 0.072332 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BARRANQUITAS | 2021-09-25 06:00 | 2021-09-25 10:34 | 60 | 004:34 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21092500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2021-09-25 | 16440 | keep | 0 | Sep | 2021 | 0.011197 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-25 06:53 | 2021-09-25 13:10 | 50 | 006:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO AISLADOR | S21092500016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 377 | 2021-09-25 | 18850 | keep | 0 | Sep | 2021 | 0.012839 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-25 07:01 | 2021-09-25 18:36 | 100 | 011:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA FIJO BAJANTE DE LINEA A CAJA | C21092500006 | New_Event | Wire Down | Include | Include | Equipment | 695 | 2021-09-25 | 69500 | keep | 0 | Sep | 2021 | 0.047336 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-25 07:22 | 2021-09-25 19:09 | 30 | 011:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | A21092500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 707 | 2021-09-25 | 21210 | keep | 0 | Sep | 2021 | 0.014446 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-25 07:25 | 2021-09-25 15:26 | 6 | 008:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092500007 | New_Event | Bad Weather | Include | Include | Weather | 481 | 2021-09-25 | 2886 | keep | 0 | Sep | 2021 | 0.0019656 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-09-25 07:47 | 2021-09-25 11:54 | 40 | 004:07 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21092500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2021-09-25 | 9880 | keep | 0 | Sep | 2021 | 0.0067292 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-25 07:54 | 2021-09-25 17:12 | 15 | 009:18 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFOMADOR DE 37.5 KVA QUEMADO POR LO MISMO | A21092500009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 558 | 2021-09-25 | 8370 | keep | 0 | Sep | 2021 | 0.0057008 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-25 07:59 | 2021-09-25 17:25 | 30 | 009:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21092500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 566 | 2021-09-25 | 16980 | keep | 0 | Sep | 2021 | 0.011565 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-25 08:03 | 2021-09-25 17:53 | 10 | 009:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE RISER A SU 5 | S21092500009 | New_Event | Cutout Failure | Include | Include | Equipment | 590 | 2021-09-25 | 5900 | keep | 0 | Sep | 2021 | 0.0040185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-25 08:08 | 2021-09-25 08:09 | 320 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | B21092500012 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-25 | 320 | keep | 0 | Sep | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-09-25 08:09 | 2021-09-25 14:07 | 10 | 005:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE RETIRO AVE | B21092500014 | 1st_after_momentary |  |  | Include | Wildlife | 358 | 2021-09-25 | 3580 | keep | 0 | Sep | 2021 | 0.0024383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-25 08:20 | 2021-09-25 10:59 | 23 | 002:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21092500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-09-25 | 3657 | keep | 0 | Sep | 2021 | 0.0024908 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
UTUADO | 2021-09-25 08:30 | 2021-09-25 10:35 | 60 | 002:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21092500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-09-25 | 7500 | keep | 0 | Sep | 2021 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-09-25 08:31 | 2021-09-25 08:32 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 1310 | keep | 0 | Sep | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-09-25 08:58 | 2021-09-25 18:16 | 2 | 009:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | A21092500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 558 | 2021-09-25 | 1116 | keep | 0 | Sep | 2021 | 0.0007601 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-09-25 09:02 | 2021-09-25 09:30 | 80 | 000:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21092400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2021-09-25 | 2240 | keep | 0 | Sep | 2021 | 0.0015257 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-25 09:08 | 2021-09-25 18:38 | 10 | 009:30 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO TRANSFORMADOR 25 KVA QUE CAYO AL PISO POR UNO DE 25KVA | S21092500033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 570 | 2021-09-25 | 5700 | keep | 0 | Sep | 2021 | 0.0038822 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-25 09:15 | 2021-09-25 09:58 | 12 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | B21092300070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-09-25 | 516 | keep | 0 | Sep | 2021 | 0.00035145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-25 09:32 | 2021-09-25 10:04 | 3000 | 000:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO CON R/R OFF PERSONAL COMPAÃ‘IA DRC REALIZANDO DESGANCHE TUMBO ARBOL CRUZO 3 FASES SE VERIFICO CON PERSONAL A CARGO INDICO HAY VARIOS PUNTOS CRITICOS EN TOA ALTA HEIGHTS CARGA TRANSFERIDA AL 9405-05 | B21092500032 | New_Event |  |  | Include | Wildlife | 32 | 2021-09-25 | 96000 | keep | 0 | Sep | 2021 | 0.065385 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2021-09-25 09:32 | 2021-09-25 10:04 | 3511 | 000:32 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO CON R/R OFF PERSONAL COMPAÃ‘IA DRC REALIZANDO DESGANCHE TUMBO ARBOL CRUZO 3 FASES SE VERIFICO CON PERSONAL A CARGO INDICO HAY VARIOS PUNTOS CRITICOS EN TOA ALTA HEIGHTS | B21092500032 | New_Event |  |  | Include | Wildlife | 32 | 2021-09-25 | 112352 | keep | 0 | Sep | 2021 | 0.076522 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2021-09-25 09:37 | 2021-09-25 17:14 | 5 | 007:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA EN MONTURA DE TRANSFORMADORES POR UNO DE 100KVA | S21092500039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 457 | 2021-09-25 | 2285 | keep | 0 | Sep | 2021 | 0.0015563 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-09-25 09:37 | 2021-09-25 09:58 | 8 | 000:21 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR AJUSTARON BARRA EN PEDESTAL Y LIMPIARON BUSHING SECUNDARIOS | R21092400046 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 21 | 2021-09-25 | 168 | keep | 0 | Sep | 2021 | 0.00011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-25 09:42 | 2021-09-25 18:02 | 25 | 008:20 | P | OTRAS CAUSAS | 1 X 100 EN RISER PROBLEMA INTERNO DEL CONDOMINIO | S21092500040 | New_Event | Other Causes | Include | Include | Other | 500 | 2021-09-25 | 12500 | keep | 0 | Sep | 2021 | 0.0085137 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-25 09:51 | 2021-09-25 20:27 | 1825 | 010:36 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA REPARAR TRAMO DE LA 9200 AUT ING CRISTIAN FELICIANO | M21092500017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 636 | 2021-09-25 | 1160700 | keep | 0 | Sep | 2021 | 0.79055 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
CAGUAS | 2021-09-25 09:52 | 2021-09-25 10:41 | 20 | 000:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR Y LEVANTAR CONDUCTOR | C21092500037 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 49 | 2021-09-25 | 980 | keep | 0 | Sep | 2021 | 0.00066747 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-25 09:55 | 2021-09-25 12:20 | 30 | 002:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21092500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2021-09-25 | 4350 | keep | 0 | Sep | 2021 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-25 10:19 | 2021-09-26 16:15 | 8 | 029:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | C21092500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1796 | 2021-09-25 | 14368 | keep | 0 | Sep | 2021 | 0.009786 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-09-25 10:25 | 2021-09-25 11:15 | 12 | 000:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE DE LINEA A CAJA TRANSFORMADOR | B21092500004 | New_Event | Wire Down | Include | Include | Equipment | 50 | 2021-09-25 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-09-25 10:26 | 2021-09-25 12:21 | 12 | 001:55 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | R21092300043 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 115 | 2021-09-25 | 1380 | keep | 0 | Sep | 2021 | 0.00093991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-25 10:26 | 2021-09-25 15:45 | 70 | 005:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA | A21092500024 | New_Event | Cutout Failure | Include | Include | Equipment | 319 | 2021-09-25 | 22330 | keep | 0 | Sep | 2021 | 0.015209 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-09-25 10:30 | 2021-09-25 16:00 | 8 | 005:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA AVERIADO POR LO MISMO | M21092500025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 330 | 2021-09-25 | 2640 | keep | 0 | Sep | 2021 | 0.0017981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-09-25 10:40 | 2021-09-25 13:11 | 9 | 002:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | R21092500019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 151 | 2021-09-25 | 1359 | keep | 0 | Sep | 2021 | 0.00092561 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2021-09-25 10:44 | 2021-09-25 16:12 | 69 | 005:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA. CLIENTE REALIZANDO DESGANCHE CRUZO FASES. | P21092500049 | New_Event |  |  | Include | Wildlife | 328 | 2021-09-25 | 22632 | keep | 0 | Sep | 2021 | 0.015415 | 4.6996e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 69
CANOVANAS | 2021-09-25 10:48 | 2021-09-25 18:00 | 6 | 007:12 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | R21092500020 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 432 | 2021-09-25 | 2592 | keep | 0 | Sep | 2021 | 0.0017654 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-09-25 10:57 | 2021-09-25 10:58 | 4132 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR POR CAJAS AVERIADAS | P21092500009 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-25 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-09-25 10:58 | 2021-09-25 11:04 | 150 | 000:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZO 3 CAJAS PRIMARIAS AVERIADAS | P21092500009 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 6 | 2021-09-25 | 900 | keep | 0 | Sep | 2021 | 0.00061299 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-09-25 11:00 | 2021-09-25 15:36 | 80 | 004:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21092500087 | New_Event | Bad Weather | Include | Include | Weather | 276 | 2021-09-25 | 22080 | keep | 0 | Sep | 2021 | 0.015039 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-09-25 11:04 | 2021-09-25 11:06 | 4132 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE INTERRUPTOR A PETICION DE SUP OSVALDO GALIO PARA ABRIR CAJA EN FUEGO | P21092500009 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2021-09-25 | 8264 | keep | 0 | Sep | 2021 | 0.0056286 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-09-25 11:06 | 2021-09-25 11:57 | 150 | 000:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZO 3 CAJAS PRIMARIAS AVERIADAS | P21092500009 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 51 | 2021-09-25 | 7650 | keep | 0 | Sep | 2021 | 0.0052104 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-25 11:07 | 2021-09-25 21:10 | 18 | 010:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA QUEMADO LO MISMO | A21092500029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 603 | 2021-09-25 | 10854 | keep | 0 | Sep | 2021 | 0.0073926 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2021-09-25 11:18 | 2021-09-25 11:25 | 3 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37800 | S21092500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-25 | 21 | keep | 0 | Sep | 2021 | 1.4303e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-09-25 11:18 | 2021-09-25 11:25 | 3957 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37800 | S21092500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-25 | 27699 | keep | 0 | Sep | 2021 | 0.018866 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-25 11:18 | 2021-09-25 11:25 | 58 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE L-37800 | S21092500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-25 | 406 | keep | 0 | Sep | 2021 | 0.00027652 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2021-09-25 11:18 | 2021-09-25 11:25 | 386 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37800 | S21092500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-09-25 | 2702 | keep | 0 | Sep | 2021 | 0.0018403 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
BAYAMON | 2021-09-25 11:33 | 2021-09-25 14:36 | 10 | 003:03 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE Y REPARAR BAJANTE SECUNDARIO | B21092500073 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 183 | 2021-09-25 | 1830 | keep | 0 | Sep | 2021 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-25 11:33 | 2021-09-25 18:07 | 80 | 006:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE | C21092500049 | New_Event | Cutout Failure | Include | Include | Equipment | 394 | 2021-09-25 | 31520 | keep | 0 | Sep | 2021 | 0.021468 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-09-25 11:54 | 2021-09-25 12:20 | 4085 | 000:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE SECCIONALIZO CAJA PRIMARIA QUEMADA | R21092500030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 26 | 2021-09-25 | 106210 | keep | 0 | Sep | 2021 | 0.072339 | 0.0027823 | Sustained | FALSE | FALSE | Not_TMED_Event | 4085
VEGA BAJA | 2021-09-25 12:03 | 2021-09-25 17:58 | 776 | 005:55 | T | HERRAJE ROTO O PODRIDO | SE REPARO CRUCETA PARTIDA Y SE CERRO INTERRUPTOR | B21092500110 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 355 | 2021-09-25 | 275480 | keep | 0 | Sep | 2021 | 0.18763 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
YAUCO | 2021-09-25 12:17 | 2021-09-25 18:40 | 50 | 006:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21092500066 | New_Event | Bad Weather | Include | Include | Weather | 383 | 2021-09-25 | 19150 | keep | 0 | Sep | 2021 | 0.013043 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-25 12:20 | 2021-09-25 12:44 | 2226 | 000:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO MACHETE Y DISCO ROTO SE CERRO MACHETES | R21092500044 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 24 | 2021-09-25 | 53424 | keep | 0 | Sep | 2021 | 0.036387 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-25 12:20 | 2021-09-25 12:21 | 1604 | 000:01 | T | DESGANCHE | RECIERRE | C21092500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-25 | 1604 | keep | 0 | Sep | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-09-25 12:21 | 2021-09-25 17:44 | 30 | 005:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21092500039 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 323 | 2021-09-25 | 9690 | keep | 0 | Sep | 2021 | 0.0065998 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-25 12:21 | 2021-09-25 17:43 | 200 | 005:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21092500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-09-25 | 64400 | keep | 0 | Sep | 2021 | 0.043863 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-25 12:31 | 2021-09-25 15:49 | 40 | 003:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21092500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-09-25 | 7920 | keep | 0 | Sep | 2021 | 0.0053943 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-25 12:42 | 2021-09-25 12:43 | 4369 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21092500068 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-25 | 4369 | keep | 0 | Sep | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-09-25 12:43 | 2021-09-25 14:50 | 5 | 002:07 | P | CABLE SOTERRADO AVERIADO | 1 X 10 EN TRANSFORMADOR DESPEGO TENSOR DEL BAJANTE | C21092500052 | New_Event | UG Cable Fault | Include | Include | Equipment | 127 | 2021-09-25 | 635 | keep | 0 | Sep | 2021 | 0.0004325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-09-25 12:44 | 2021-09-25 13:17 | 4085 | 000:33 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR MACHETE Y DISCO ROTO SE DEJO SECCIONALIZADO CERRADO POR CONTROL | R21092500039 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 33 | 2021-09-25 | 134805 | keep | 0 | Sep | 2021 | 0.091815 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-25 12:47 | 2021-09-25 18:34 | 100 | 005:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | A21092500033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2021-09-25 | 34700 | keep | 0 | Sep | 2021 | 0.023634 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-25 12:48 | 2021-09-25 15:12 | 12 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21092500041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2021-09-25 | 1728 | keep | 0 | Sep | 2021 | 0.0011769 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-25 12:51 | 2021-09-26 09:54 | 50 | 021:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21092500043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1263 | 2021-09-25 | 63150 | keep | 0 | Sep | 2021 | 0.043011 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-25 13:01 | 2021-09-25 18:55 | 35 | 005:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21092500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-09-25 | 12390 | keep | 0 | Sep | 2021 | 0.0084388 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-09-25 13:17 | 2021-09-25 14:11 | 2226 | 000:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO MACHETE Y DISCO ROTO SE CERRO MACHETES | R21092500044 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 54 | 2021-09-25 | 120204 | keep | 0 | Sep | 2021 | 0.08187 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-25 13:21 | 2021-09-26 14:50 | 12 | 025:29 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 75 KVA X 75 KVA | C21092500076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1529 | 2021-09-25 | 18348 | keep | 0 | Sep | 2021 | 0.012497 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-09-25 13:27 | 2021-09-25 14:10 | 10 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES | A21092500034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-09-25 | 430 | keep | 0 | Sep | 2021 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-25 13:29 | 2021-09-25 15:11 | 24 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21092500046 | New_Event |  |  | Include | Wildlife | 102 | 2021-09-25 | 2448 | keep | 0 | Sep | 2021 | 0.0016673 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
MAYAGÃœEZ | 2021-09-25 13:34 | 2021-09-25 15:02 | 25 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21092400109 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-09-25 | 2200 | keep | 0 | Sep | 2021 | 0.0014984 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-25 13:41 | 2021-09-25 13:42 | 1854 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 1854 | keep | 0 | Sep | 2021 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2021-09-25 13:49 | 2021-09-25 15:58 | 15 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA | C21092500081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2021-09-25 | 1935 | keep | 0 | Sep | 2021 | 0.0013179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-25 13:54 | 2021-09-25 18:41 | 100 | 004:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR GLOBOS CRUZANDO LA LINEA | M21092500036 | New_Event |  |  | Include | Wildlife | 287 | 2021-09-25 | 28700 | keep | 0 | Sep | 2021 | 0.019547 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-25 14:07 | 2021-09-25 18:37 | 74 | 004:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR SE CERRO CORTE DE LINEA | R21092500073 | New_Event | Wire Down | Include | Include | Equipment | 270 | 2021-09-25 | 19980 | keep | 0 | Sep | 2021 | 0.013608 | 5.0401e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 74
BAYAMON | 2021-09-25 14:07 | 2021-09-25 16:38 | 10 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21092500134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2021-09-25 | 1510 | keep | 0 | Sep | 2021 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-25 14:09 | 2021-09-25 16:32 | 30 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR MAL TIEMPO | A21092500035 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2021-09-25 | 4290 | keep | 0 | Sep | 2021 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-09-25 14:11 | 2021-09-25 14:14 | 4085 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR MACHETE Y DISCO AVERIADO SE DEJO SECCIONALIZADO | R21092500044 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-09-25 | 12255 | keep | 0 | Sep | 2021 | 0.0083468 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-25 14:14 | 2021-09-25 16:37 | 2226 | 002:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO MACHETE Y DISCO ROTO SE CERRO MACHETES | R21092500044 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 143 | 2021-09-25 | 318318 | keep | 0 | Sep | 2021 | 0.2168 | 0.0015161 | Sustained | FALSE | FALSE | Not_TMED_Event | 2226
BAYAMON | 2021-09-25 14:16 | 2021-09-25 16:15 | 200 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES Y SE CERRO PUENTE ABIERTO EN TRONCAL | B21092400026 | Additional_clients | Wire Down | Include | Include | Equipment | 119 | 2021-09-25 | 23800 | keep | 0 | Sep | 2021 | 0.01621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-25 14:17 | 2021-09-25 15:14 | 8 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092500138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2021-09-25 | 456 | keep | 0 | Sep | 2021 | 0.00031058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-25 14:32 | 2021-09-26 11:12 | 41 | 020:40 | P | CABLE SOTERRADO AVERIADO | REPARO TRAMO ENTRE EL SU - 1 Y EL T - 23 | C21092500086 | New_Event | UG Cable Fault | Include | Include | Equipment | 1240 | 2021-09-25 | 50840 | keep | 0 | Sep | 2021 | 0.034627 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
SAN JUAN | 2021-09-25 14:36 | 2021-09-25 14:37 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 30% POR EL 1619-02 | R21092500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
UTUADO | 2021-09-25 14:37 | 2021-09-25 16:00 | 40 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | A21092300125 | New_Event | Wire Down | Include | Include | Equipment | 83 | 2021-09-25 | 3320 | keep | 0 | Sep | 2021 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-09-25 14:43 | 2021-09-25 18:51 | 275 | 004:08 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE EN VARIOS PUNTOS | R21092500056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2021-09-25 | 68200 | keep | 0 | Sep | 2021 | 0.046451 | 0.0001873 | Sustained | FALSE | TRUE | Not_TMED_Event | 275
BAYAMON | 2021-09-25 14:47 | 2021-09-25 15:37 | 10 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO | B21092500147 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-09-25 | 500 | keep | 0 | Sep | 2021 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-09-25 14:53 | 2021-09-25 15:22 | 17 | 000:29 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE DESGANCHO ARBOL DE PANA | R21092500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-09-25 | 493 | keep | 0 | Sep | 2021 | 0.00033578 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
SAN JUAN | 2021-09-25 14:54 | 2021-09-26 08:52 | 1 | 017:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO Y ELIMINO PARARRAYO PRIVADO | R21092500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1078 | 2021-09-25 | 1078 | keep | 0 | Sep | 2021 | 0.00073422 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-25 15:04 | 2021-09-25 16:04 | 160 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETIRAR NEUTRAL PARTIDO DE 1204-04 PARTE DE SU CARGA POR 1342-04 | S21092500078 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-09-25 | 9600 | keep | 0 | Sep | 2021 | 0.0065385 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
SAN JUAN | 2021-09-25 15:04 | 2021-09-25 16:04 | 356 | 001:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETIRAR NEUTRAL PARTIDO DE 1204-04 CARGA POR 1342-04 | S21092500078 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-09-25 | 21360 | keep | 0 | Sep | 2021 | 0.014548 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
SAN JUAN | 2021-09-25 15:04 | 2021-09-25 16:04 | 390 | 001:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETIRAR NEUTRAL PARTIDO DE 1204-04 LLEVA CARGA 1342-01 Y PARTE 1203-03 | S21092500078 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-09-25 | 23400 | keep | 0 | Sep | 2021 | 0.015938 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
ARECIBO | 2021-09-25 15:04 | 2021-09-25 19:19 | 35 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | A21092500040 | New_Event | Bad Weather | Include | Include | Weather | 255 | 2021-09-25 | 8925 | keep | 0 | Sep | 2021 | 0.0060788 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-25 15:08 | 2021-09-25 16:08 | 8 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE A TRANSFOMADOR | A21092500041 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-09-25 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-09-25 15:16 | 2021-09-25 15:21 | 3316 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21092500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-25 | 16580 | keep | 0 | Sep | 2021 | 0.011293 | 0.0022585 | Momentary | FALSE | FALSE | Not_TMED_Event | 3316
VEGA BAJA | 2021-09-25 15:18 | 2021-09-25 16:54 | 10 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21092300119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2021-09-25 | 960 | keep | 0 | Sep | 2021 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-25 15:21 | 2021-09-25 15:49 | 21 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | R21092400048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-09-25 | 588 | keep | 0 | Sep | 2021 | 0.00040048 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
UTUADO | 2021-09-25 15:21 | 2021-09-25 20:07 | 225 | 004:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 140 EN CORTE DE LINEA Y 1 X 80 EN CONVERTIDOR SE SECCIONALIZO AVERIA DE LINEA PRIMARIA | A21092500046 | New_Event | Wire Down | Include | Include | Equipment | 286 | 2021-09-25 | 64350 | keep | 0 | Sep | 2021 | 0.043828 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
BAYAMON | 2021-09-25 15:27 | 2021-09-26 10:46 | 30 | 019:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092500163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1159 | 2021-09-25 | 34770 | keep | 0 | Sep | 2021 | 0.023682 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-25 15:32 | 2021-09-26 12:30 | 25 | 020:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21092500045 | New_Event | Bad Weather | Include | Include | Weather | 1258 | 2021-09-25 | 31450 | keep | 0 | Sep | 2021 | 0.02142 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-25 15:34 | 2021-09-26 10:27 | 10 | 018:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR TIPO NX | B21092500166 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1133 | 2021-09-25 | 11330 | keep | 0 | Sep | 2021 | 0.0077168 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-25 16:18 | 2021-09-25 20:27 | 25 | 004:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S21092500103 | New_Event | Cutout Failure | Include | Include | Equipment | 249 | 2021-09-25 | 6225 | keep | 0 | Sep | 2021 | 0.0042398 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-09-25 16:40 | 2021-09-25 19:24 | 55 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21092500100 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2021-09-25 | 9020 | keep | 0 | Sep | 2021 | 0.0061435 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BARRANQUITAS | 2021-09-25 16:41 | 2021-09-26 11:38 | 5 | 018:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092500107 | New_Event | Bad Weather | Include | Include | Weather | 1137 | 2021-09-25 | 5685 | keep | 0 | Sep | 2021 | 0.003872 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-09-25 16:49 | 2021-09-25 18:40 | 10 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21092500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2021-09-25 | 1110 | keep | 0 | Sep | 2021 | 0.00075602 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-09-25 16:49 | 2021-09-25 17:23 | 10 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y CONEXIONES | S21092500024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-09-25 | 340 | keep | 0 | Sep | 2021 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-09-25 16:56 | 2021-09-25 16:57 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092500103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
ARECIBO | 2021-09-25 16:58 | 2021-09-25 18:29 | 30 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21092500054 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2021-09-25 | 2730 | keep | 0 | Sep | 2021 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-25 17:02 | 2021-09-25 17:03 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21092500120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 315 | keep | 0 | Sep | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
HUMACAO | 2021-09-25 17:04 | 2021-09-25 18:36 | 1 | 001:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092500113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-09-25 | 92 | keep | 0 | Sep | 2021 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-25 17:13 | 2021-09-25 17:14 | 6197 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092500121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 6197 | keep | 0 | Sep | 2021 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
BAYAMON | 2021-09-25 17:14 | 2021-09-26 13:28 | 13 | 020:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 KVA POR 100 KVA | S21092500039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1214 | 2021-09-25 | 15782 | keep | 0 | Sep | 2021 | 0.010749 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-09-25 17:44 | 2021-09-26 17:26 | 40 | 023:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21092500114 | New_Event | Cutout Failure | Include | Include | Equipment | 1422 | 2021-09-25 | 56880 | keep | 0 | Sep | 2021 | 0.038741 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-25 17:45 | 2021-09-25 17:46 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092500112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-25 | 732 | keep | 0 | Sep | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
CANOVANAS | 2021-09-25 17:55 | 2021-09-25 19:31 | 50 | 001:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R21092500074 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2021-09-25 | 4800 | keep | 0 | Sep | 2021 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-25 18:11 | 2021-09-25 18:13 | 4381 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | M21092500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-25 | 8762 | keep | 0 | Sep | 2021 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
BAYAMON | 2021-09-25 18:13 | 2021-09-25 23:01 | 40 | 004:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | S21092500120 | New_Event | Cutout Failure | Include | Include | Equipment | 288 | 2021-09-25 | 11520 | keep | 0 | Sep | 2021 | 0.0078462 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-25 18:13 | 2021-09-26 09:13 | 30 | 015:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092500184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 900 | 2021-09-25 | 27000 | keep | 0 | Sep | 2021 | 0.01839 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-25 18:14 | 2021-09-26 10:11 | 31 | 015:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092500121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 957 | 2021-09-25 | 29667 | keep | 0 | Sep | 2021 | 0.020206 | 2.1114e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 31
BAYAMON | 2021-09-25 18:17 | 2021-09-25 21:11 | 40 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092500186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-09-25 | 6960 | keep | 0 | Sep | 2021 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-09-25 18:28 | 2021-09-25 20:30 | 50 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21092500115 | New_Event |  |  | Include | Wildlife | 122 | 2021-09-25 | 6100 | keep | 0 | Sep | 2021 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-25 18:34 | 2021-09-25 20:43 | 30 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092500189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-09-25 | 3870 | keep | 0 | Sep | 2021 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-25 18:35 | 2021-09-26 08:52 | 122 | 014:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | R21092500078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 857 | 2021-09-25 | 104554 | keep | 0 | Sep | 2021 | 0.071211 | 8.3094e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 122
BAYAMON | 2021-09-25 18:57 | 2021-09-26 15:47 | 10 | 020:50 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21092500196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1250 | 2021-09-25 | 12500 | keep | 0 | Sep | 2021 | 0.0085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-25 19:25 | 2021-09-26 12:05 | 30 | 016:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 Y 2 X 65 EN CORTES DE LINEAS SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | B21092500202 | New_Event | Cutout Failure | Include | Include | Equipment | 1000 | 2021-09-25 | 30000 | keep | 0 | Sep | 2021 | 0.020433 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-25 19:38 | 2021-09-26 10:15 | 10 | 014:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092500068 | New_Event | Bad Weather | Include | Include | Weather | 877 | 2021-09-25 | 8770 | keep | 0 | Sep | 2021 | 0.0059732 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-25 19:41 | 2021-09-26 11:28 | 8 | 015:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092500128 | New_Event | Bad Weather | Include | Include | Weather | 947 | 2021-09-25 | 7576 | keep | 0 | Sep | 2021 | 0.00516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-25 19:46 | 2021-09-25 21:46 | 10 | 002:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL SECUNDARIO | A21092400031 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 120 | 2021-09-25 | 1200 | keep | 0 | Sep | 2021 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-25 19:48 | 2021-09-25 20:58 | 15 | 001:10 | P | NO SE REPORTO CAUSA | 2 X 20 EN CORTE DE LINEA | S21092500131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-09-25 | 1050 | keep | 0 | Sep | 2021 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-09-25 20:12 | 2021-09-26 18:14 | 15 | 022:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 1 X 25 EN CORTES DE LINEA Y 1 X 25 EN TRANSFORMADOR REPARO SECUNDARIA CRUZADA | C21092500131 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1322 | 2021-09-25 | 19830 | keep | 0 | Sep | 2021 | 0.013506 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-25 20:19 | 2021-09-25 20:43 | 50 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092500210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2021-09-25 | 1200 | keep | 0 | Sep | 2021 | 0.00081731 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-25 20:26 | 2021-09-26 08:49 | 65 | 012:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21092500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 743 | 2021-09-25 | 48295 | keep | 0 | Sep | 2021 | 0.032894 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 4027 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 8054 | keep | 0 | Sep | 2021 | 0.0054855 | 0.0027428 | Momentary | FALSE | TRUE | Not_TMED_Event | 4027
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 2468 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 4936 | keep | 0 | Sep | 2021 | 0.0033619 | 0.0016809 | Momentary | FALSE | TRUE | Not_TMED_Event | 2468
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 1494 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 2988 | keep | 0 | Sep | 2021 | 0.0020351 | 0.0010176 | Momentary | FALSE | TRUE | Not_TMED_Event | 1494
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 2368 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 4736 | keep | 0 | Sep | 2021 | 0.0032257 | 0.0016128 | Momentary | FALSE | TRUE | Not_TMED_Event | 2368
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 538 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 1076 | keep | 0 | Sep | 2021 | 0.00073286 | 0.00036643 | Momentary | FALSE | TRUE | Not_TMED_Event | 538
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 1284 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 2568 | keep | 0 | Sep | 2021 | 0.0017491 | 0.00087453 | Momentary | FALSE | TRUE | Not_TMED_Event | 1284
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 1310 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 2620 | keep | 0 | Sep | 2021 | 0.0017845 | 0.00089224 | Momentary | FALSE | TRUE | Not_TMED_Event | 1310
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 215 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 430 | keep | 0 | Sep | 2021 | 0.00029287 | 0.00014644 | Momentary | FALSE | TRUE | Not_TMED_Event | 215
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 1 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 2 | keep | 0 | Sep | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 652 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 1304 | keep | 0 | Sep | 2021 | 0.00088815 | 0.00044407 | Momentary | FALSE | TRUE | Not_TMED_Event | 652
VEGA BAJA | 2021-09-25 20:43 | 2021-09-25 20:45 | 2704 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 AFECTANDO BARRA VEGA ALTA | B21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-25 | 5408 | keep | 0 | Sep | 2021 | 0.0036834 | 0.0018417 | Momentary | FALSE | TRUE | Not_TMED_Event | 2704
VEGA BAJA | 2021-09-25 20:45 | 2021-09-26 09:40 | 30 | 012:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092500189 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 775 | 2021-09-25 | 23250 | keep | 0 | Sep | 2021 | 0.015835 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-25 20:45 | 2021-09-25 21:18 | 50 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092500210 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-09-25 | 1650 | keep | 0 | Sep | 2021 | 0.0011238 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-25 20:58 | 2021-09-25 20:59 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3000 | C21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 1089 | keep | 0 | Sep | 2021 | 0.00074171 | 0.00074171 | Momentary | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-09-25 20:58 | 2021-09-25 20:59 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3000 | C21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 3896 | keep | 0 | Sep | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-09-25 20:58 | 2021-09-25 20:59 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3000 | C21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 1467 | keep | 0 | Sep | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
BARRANQUITAS | 2021-09-25 21:01 | 2021-09-26 14:56 | 2 | 017:55 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 15 KVA | C21092500136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1075 | 2021-09-25 | 2150 | keep | 0 | Sep | 2021 | 0.0014644 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-09-25 21:02 | 2021-09-26 11:38 | 1 | 014:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE REPORTO CAUSA | P21092600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 876 | 2021-09-25 | 876 | keep | 0 | Sep | 2021 | 0.00059664 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-09-25 22:00 | 2021-09-26 09:40 | 250 | 011:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21092500126 | New_Event | Wire Down | Include | Include | Equipment | 700 | 2021-09-25 | 175000 | keep | 0 | Sep | 2021 | 0.11919 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
YAUCO | 2021-09-25 22:01 | 2021-09-26 11:05 | 100 | 013:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA Y DESCARGAS ELECTRICAS | P21092500072 | New_Event | Bad Weather | Include | Include | Weather | 784 | 2021-09-25 | 78400 | keep | 0 | Sep | 2021 | 0.053398 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-25 22:16 | 2021-09-26 11:26 | 10 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21092500079 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-09-25 | 7900 | keep | 0 | Sep | 2021 | 0.0053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-25 22:46 | 2021-09-25 22:47 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 0.00055169 | Momentary | FALSE | TRUE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-09-25 22:46 | 2021-09-25 22:47 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 1235 | keep | 0 | Sep | 2021 | 0.00084115 | 0.00084115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-09-25 22:46 | 2021-09-25 22:47 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 93 | keep | 0 | Sep | 2021 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-09-25 22:46 | 2021-09-25 22:47 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 1825 | keep | 0 | Sep | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | TRUE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-09-25 22:46 | 2021-09-25 22:47 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21092500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-25 | 3230 | keep | 0 | Sep | 2021 | 0.0021999 | 0.0021999 | Momentary | FALSE | TRUE | Not_TMED_Event | 3230
UTUADO | 2021-09-25 23:52 | 2021-09-26 17:47 | 30 | 017:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21092500081 | New_Event | Wire Down | Include | Include | Equipment | 1075 | 2021-09-25 | 32250 | keep | 0 | Sep | 2021 | 0.021965 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-26 00:36 | 2021-09-26 14:20 | 100 | 013:44 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21092600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 824 | 2021-09-26 | 82400 | keep | 0 | Sep | 2021 | 0.056122 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-26 01:21 | 2021-09-26 09:45 | 137 | 008:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092600001 | New_Event |  |  | Include | Wildlife | 504 | 2021-09-26 | 69048 | keep | 0 | Sep | 2021 | 0.047028 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-09-26 01:26 | 2021-09-26 01:27 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-09-26 01:36 | 2021-09-26 13:31 | 15 | 011:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21092600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 715 | 2021-09-26 | 10725 | keep | 0 | Sep | 2021 | 0.0073047 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-09-26 01:54 | 2021-09-26 09:11 | 200 | 007:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | A21092600001 | New_Event | Bad Weather | Include | Include | Weather | 437 | 2021-09-26 | 87400 | keep | 0 | Sep | 2021 | 0.059528 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-26 03:11 | 2021-09-26 09:20 | 100 | 006:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21092600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-09-26 | 36900 | keep | 0 | Sep | 2021 | 0.025132 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-26 03:31 | 2021-09-26 06:49 | 1089 | 003:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C21092600005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-09-26 | 215622 | keep | 0 | Sep | 2021 | 0.14686 | 0.00074171 | Sustained | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-09-26 03:31 | 2021-09-26 06:49 | 3896 | 003:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C21092600005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-09-26 | 771408 | keep | 0 | Sep | 2021 | 0.5254 | 0.0026535 | Sustained | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-09-26 03:31 | 2021-09-26 06:49 | 1467 | 003:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C21092600005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-09-26 | 290466 | keep | 0 | Sep | 2021 | 0.19784 | 0.00099917 | Sustained | FALSE | TRUE | Not_TMED_Event | 1467
CAGUAS | 2021-09-26 04:20 | 2021-09-26 04:21 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092600019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 1342 | keep | 0 | Sep | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
PONCE | 2021-09-26 05:47 | 2021-09-26 09:45 | 100 | 003:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21092600001 | New_Event |  |  | Include | Wildlife | 238 | 2021-09-26 | 23800 | keep | 0 | Sep | 2021 | 0.01621 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-26 05:48 | 2021-09-26 09:57 | 40 | 004:09 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SMU 20 DE 40AMP Y 1 X 10 EN TRANSFORMADOR CONTAMINACION | R21092600003 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 249 | 2021-09-26 | 9960 | keep | 0 | Sep | 2021 | 0.0067837 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-09-26 05:53 | 2021-09-26 05:54 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 271 | keep | 0 | Sep | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CAGUAS | 2021-09-26 05:53 | 2021-09-26 12:32 | 130 | 006:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21092600029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 399 | 2021-09-26 | 51870 | keep | 0 | Sep | 2021 | 0.035328 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
ARECIBO | 2021-09-26 06:11 | 2021-09-26 11:00 | 15 | 004:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21092600004 | New_Event | Bad Weather | Include | Include | Weather | 289 | 2021-09-26 | 4335 | keep | 0 | Sep | 2021 | 0.0029525 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-09-26 06:23 | 2021-09-26 08:52 | 100 | 002:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21092600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-09-26 | 14900 | keep | 0 | Sep | 2021 | 0.010148 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-26 06:44 | 2021-09-26 06:45 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21092600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 1879 | keep | 0 | Sep | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
SAN JUAN | 2021-09-26 06:44 | 2021-09-26 13:18 | 23 | 006:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21092600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 394 | 2021-09-26 | 9062 | keep | 0 | Sep | 2021 | 0.0061721 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
AGUADILLA | 2021-09-26 07:03 | 2021-09-26 12:45 | 60 | 005:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21092600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-09-26 | 20520 | keep | 0 | Sep | 2021 | 0.013976 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-26 07:08 | 2021-09-26 07:09 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 58 | keep | 0 | Sep | 2021 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2021-09-26 07:30 | 2021-09-26 07:31 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B21092600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-09-26 07:31 | 2021-09-26 18:35 | 150 | 011:04 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU 13A | B21092600033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 664 | 2021-09-26 | 99600 | keep | 0 | Sep | 2021 | 0.067837 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-09-26 07:35 | 2021-09-26 09:27 | 40 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-09-26 | 4480 | keep | 0 | Sep | 2021 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-26 07:38 | 2021-09-26 10:36 | 10 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21092600007 | New_Event |  |  | Include | Wildlife | 178 | 2021-09-26 | 1780 | keep | 0 | Sep | 2021 | 0.0012123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-26 07:38 | 2021-09-26 07:39 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 3000 | keep | 0 | Sep | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2021-09-26 07:44 | 2021-09-26 07:58 | 200 | 000:14 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL PARTE DE SU CARGA POR 9405 05 | B21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2021-09-26 | 2800 | keep | 0 | Sep | 2021 | 0.0019071 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-09-26 07:44 | 2021-09-26 11:54 | 10 | 004:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-09-26 | 2500 | keep | 0 | Sep | 2021 | 0.0017027 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-26 07:44 | 2021-09-26 07:58 | 3511 | 000:14 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA PARTE DE LA CARGA 1710 05 | B21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2021-09-26 | 49154 | keep | 0 | Sep | 2021 | 0.033479 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
SAN JUAN | 2021-09-26 07:56 | 2021-09-26 11:19 | 16 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21092600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-09-26 | 3248 | keep | 0 | Sep | 2021 | 0.0022122 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
HUMACAO | 2021-09-26 08:05 | 2021-09-26 13:55 | 6 | 005:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 15 EN BANCO DE TRANSFORMADORES CRUCE CON TIERRA DEL TRANSFORMADOR | C21092600041 | New_Event | Wire Down | Include | Include | Equipment | 350 | 2021-09-26 | 2100 | keep | 0 | Sep | 2021 | 0.0014303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-26 08:08 | 2021-09-26 16:40 | 10 | 008:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | B21092600037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 512 | 2021-09-26 | 5120 | keep | 0 | Sep | 2021 | 0.0034872 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-26 08:14 | 2021-09-26 09:47 | 15 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA DE 100 AMP | P21092600010 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2021-09-26 | 1395 | keep | 0 | Sep | 2021 | 0.00095013 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-26 08:22 | 2021-09-26 12:28 | 40 | 004:06 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | A21092600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-09-26 | 9840 | keep | 0 | Sep | 2021 | 0.006702 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-26 08:39 | 2021-09-26 16:45 | 60 | 008:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092600010 | New_Event | Bad Weather | Include | Include | Weather | 486 | 2021-09-26 | 29160 | keep | 0 | Sep | 2021 | 0.019861 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-26 08:42 | 2021-09-26 08:43 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
GUAYAMA | 2021-09-26 08:47 | 2021-09-26 12:04 | 50 | 003:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P21092600012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 197 | 2021-09-26 | 9850 | keep | 0 | Sep | 2021 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-26 08:51 | 2021-09-26 09:29 | 2450 | 000:38 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SUBESTACION SIN RTU SE CERRO EN LA SUBESTACION | C21092600049 | New_Event |  |  | Include | Wildlife | 38 | 2021-09-26 | 93100 | keep | 0 | Sep | 2021 | 0.06341 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
AGUADILLA | 2021-09-26 08:52 | 2021-09-26 21:59 | 60 | 013:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092600024 | New_Event | Bad Weather | Include | Include | Weather | 787 | 2021-09-26 | 47220 | keep | 0 | Sep | 2021 | 0.032161 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-26 08:57 | 2021-09-27 13:53 | 195 | 028:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21092200071 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 1736 | 2021-09-26 | 338520 | keep | 0 | Sep | 2021 | 0.23056 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-26 08:57 | 2021-09-26 10:19 | 100 | 001:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21092600007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-09-26 | 8200 | keep | 0 | Sep | 2021 | 0.005585 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-26 08:57 | 2021-09-27 13:05 | 122 | 028:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | R21092500078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1688 | 2021-09-26 | 205936 | keep | 0 | Sep | 2021 | 0.14026 | 8.3094e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 122
ARECIBO | 2021-09-26 09:02 | 2021-09-26 17:15 | 50 | 008:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092300030 | New_Event | Bad Weather | Include | Include | Weather | 493 | 2021-09-26 | 24650 | keep | 0 | Sep | 2021 | 0.016789 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-26 09:05 | 2021-09-26 15:45 | 1 | 006:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHO Y ELIMINO PARARRAYO PRIVADO | R21092500059 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 400 | 2021-09-26 | 400 | keep | 0 | Sep | 2021 | 0.00027244 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
FAJARDO | 2021-09-26 09:19 | 2021-09-26 12:23 | 8 | 003:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21092600028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 184 | 2021-09-26 | 1472 | keep | 0 | Sep | 2021 | 0.0010026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-09-26 09:29 | 2021-09-26 12:27 | 100 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21092600071 | Partial_restoration |  |  | Include | Wildlife | 178 | 2021-09-26 | 17800 | keep | 0 | Sep | 2021 | 0.012123 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-26 09:54 | 2021-09-26 09:56 | 2053 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R21092600033 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-26 | 4106 | keep | 0 | Sep | 2021 | 0.0027966 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-26 09:56 | 2021-09-26 10:16 | 4 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA DE PEDESTAL | R21092600034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-09-26 | 80 | keep | 0 | Sep | 2021 | 5.4488e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-09-26 09:56 | 2021-09-26 16:55 | 50 | 006:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21092500043 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 419 | 2021-09-26 | 20950 | keep | 0 | Sep | 2021 | 0.014269 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-26 10:05 | 2021-09-26 12:30 | 7 | 002:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 190 PIES DE SECUNDARIA Y SE DESGANCHO | C21092500102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 145 | 2021-09-26 | 1015 | keep | 0 | Sep | 2021 | 0.00069131 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-09-26 10:21 | 2021-09-26 12:40 | 664 | 002:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON CAJAS PRIMARIAS Y MACHETE AVERIADO | C21092600064 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2021-09-26 | 92296 | keep | 0 | Sep | 2021 | 0.062862 | 0.00045225 | Sustained | FALSE | FALSE | Not_TMED_Event | 664
CANOVANAS | 2021-09-26 10:31 | 2021-09-26 12:38 | 30 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21092600037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2021-09-26 | 3810 | keep | 0 | Sep | 2021 | 0.002595 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-09-26 10:32 | 2021-09-26 13:02 | 12 | 002:30 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | B21092600006 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 150 | 2021-09-26 | 1800 | keep | 0 | Sep | 2021 | 0.001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-09-26 10:35 | 2021-09-26 18:56 | 10 | 008:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 501 | 2021-09-26 | 5010 | keep | 0 | Sep | 2021 | 0.0034123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-26 10:36 | 2021-09-26 12:05 | 12 | 001:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO Y BAJANTE SECUNDARIO DEL TRANSFORMADOR | C21092600117 | New_Event | Wire Down | Include | Include | Equipment | 89 | 2021-09-26 | 1068 | keep | 0 | Sep | 2021 | 0.00072741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-26 10:45 | 2021-09-26 11:19 | 49 | 000:34 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-09-26 | 1666 | keep | 0 | Sep | 2021 | 0.0011347 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
BAYAMON | 2021-09-26 11:07 | 2021-09-26 15:39 | 15 | 004:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21092600039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-09-26 | 4080 | keep | 0 | Sep | 2021 | 0.0027789 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-09-26 11:12 | 2021-09-26 11:13 | 4369 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21092600074 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-26 | 4369 | keep | 0 | Sep | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
SAN JUAN | 2021-09-26 11:17 | 2021-09-26 18:03 | 12 | 006:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR IGUANA CRUZO FASE | S21092600041 | New_Event |  |  | Include | Wildlife | 406 | 2021-09-26 | 4872 | keep | 0 | Sep | 2021 | 0.0033183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-26 11:29 | 2021-09-26 11:30 | 4369 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR PERSONAL REALIZANDO PRUEBAS | C21092600076 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-09-26 | 4369 | keep | 0 | Sep | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-09-26 11:30 | 2021-09-27 07:59 | 41 | 020:29 | P | CABLE SOTERRADO AVERIADO | REPARO TRAMO ENTRE EL SU - 1 Y EL T - 23 | C21092500086 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1229 | 2021-09-26 | 50389 | keep | 0 | Sep | 2021 | 0.03432 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2021-09-26 11:39 | 2021-09-26 11:41 | 1879 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21092600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-26 | 3758 | keep | 0 | Sep | 2021 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
PONCE | 2021-09-26 11:40 | 2021-09-26 11:41 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE SUB PORTATIL 10 | P21092600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-26 11:40 | 2021-09-26 11:41 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE SUB PORTATIL 10 | P21092600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-26 11:40 | 2021-09-26 11:41 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE SUB PORTATIL 10 | P21092600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
SAN JUAN | 2021-09-26 11:56 | 2021-09-26 16:28 | 50 | 004:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21092600047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-09-26 | 13600 | keep | 0 | Sep | 2021 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-26 12:13 | 2021-09-26 12:14 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 4085 | keep | 0 | Sep | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
ARECIBO | 2021-09-26 12:55 | 2021-09-27 11:29 | 10 | 022:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA PARTIDA | A21092600028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1354 | 2021-09-26 | 13540 | keep | 0 | Sep | 2021 | 0.009222 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-26 13:11 | 2021-09-26 15:54 | 50 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | A21092600030 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-09-26 | 8150 | keep | 0 | Sep | 2021 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-26 13:21 | 2021-09-26 13:22 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21092600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 2675 | keep | 0 | Sep | 2021 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BARRANQUITAS | 2021-09-26 13:23 | 2021-09-26 19:12 | 80 | 005:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21092600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2021-09-26 | 27920 | keep | 0 | Sep | 2021 | 0.019016 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-26 13:36 | 2021-09-26 16:34 | 50 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092600032 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-09-26 | 8900 | keep | 0 | Sep | 2021 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-26 13:37 | 2021-09-26 18:16 | 100 | 004:39 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | M21092600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2021-09-26 | 27900 | keep | 0 | Sep | 2021 | 0.019003 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-26 13:44 | 2021-09-26 15:53 | 70 | 002:09 | P | DESGANCHE | CERRO INTELIRRUPTER 2603-8E | C21092600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-09-26 | 9030 | keep | 0 | Sep | 2021 | 0.0061503 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2021-09-26 13:45 | 2021-09-26 15:54 | 100 | 002:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA | M21092600017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2021-09-26 | 12900 | keep | 0 | Sep | 2021 | 0.0087861 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-26 13:48 | 2021-09-26 17:00 | 10 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092600034 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-09-26 | 1920 | keep | 0 | Sep | 2021 | 0.0013077 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-09-26 14:19 | 2021-09-26 14:20 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 539 | keep | 0 | Sep | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
CAGUAS | 2021-09-26 14:24 | 2021-09-26 16:26 | 5 | 002:02 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21092600094 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 122 | 2021-09-26 | 610 | keep | 0 | Sep | 2021 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-09-26 14:26 | 2021-09-26 20:22 | 40 | 005:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2021-09-26 | 14240 | keep | 0 | Sep | 2021 | 0.0096988 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-26 14:26 | 2021-09-27 21:28 | 100 | 031:02 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21092600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1862 | 2021-09-26 | 186200 | keep | 0 | Sep | 2021 | 0.12682 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-26 14:39 | 2021-09-26 21:52 | 1825 | 007:13 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA TRABAJOS DE TRANSMISION 9200 | M21092400082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 433 | 2021-09-26 | 790225 | keep | 0 | Sep | 2021 | 0.53822 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
ARECIBO | 2021-09-26 14:39 | 2021-09-26 17:00 | 70 | 002:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | A21092600039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-09-26 | 9870 | keep | 0 | Sep | 2021 | 0.0067224 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-09-26 14:40 | 2021-09-26 18:03 | 45 | 003:23 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21092600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-09-26 | 9135 | keep | 0 | Sep | 2021 | 0.0062218 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-09-26 14:46 | 2021-09-28 15:08 | 35 | 048:22 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21092600062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2902 | 2021-09-26 | 101570 | keep | 0 | Sep | 2021 | 0.069179 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BARRANQUITAS | 2021-09-26 14:50 | 2021-09-26 14:51 | 2410 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE | C21092600000 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-26 | 2410 | keep | 0 | Sep | 2021 | 0.0016414 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-26 14:51 | 2021-09-27 10:54 | 12 | 020:03 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 75 KVA X 75 KVA | C21092500076 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1203 | 2021-09-26 | 14436 | keep | 0 | Sep | 2021 | 0.0098323 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-09-26 14:56 | 2021-09-26 16:31 | 54 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21092600103 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-09-26 | 5130 | keep | 0 | Sep | 2021 | 0.003494 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
BARRANQUITAS | 2021-09-26 15:02 | 2021-09-26 16:13 | 100 | 001:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21092600072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-09-26 | 7100 | keep | 0 | Sep | 2021 | 0.0048358 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-26 15:47 | 2021-09-26 19:04 | 10 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21092600041 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2021-09-26 | 1970 | keep | 0 | Sep | 2021 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-26 15:57 | 2021-09-26 15:59 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE VERIFICO CON COD CAROLINA NO TENIAN PERSONAL SE PROBO POR CONTROL QUEDO EN SERVICIO | R21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-26 | 3230 | keep | 0 | Sep | 2021 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-09-26 16:02 | 2021-09-26 18:15 | 1 | 002:13 | P | DESGANCHE | 1 SMU 20 DE 40AMP EN EL SU - 1 | R21092500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2021-09-26 | 133 | keep | 0 | Sep | 2021 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-26 16:13 | 2021-09-26 17:15 | 2694 | 001:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR POR CENTRO DE CONTROL | A21092600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-09-26 | 167028 | keep | 0 | Sep | 2021 | 0.11376 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-09-26 16:13 | 2021-09-26 17:15 | 438 | 001:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR POR CENTRO DE CONTROL | A21092600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-09-26 | 27156 | keep | 0 | Sep | 2021 | 0.018496 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
BARRANQUITAS | 2021-09-26 16:13 | 2021-09-26 19:55 | 80 | 003:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21092600117 | New_Event | Bad Weather | Include | Include | Weather | 222 | 2021-09-26 | 17760 | keep | 0 | Sep | 2021 | 0.012096 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-26 16:15 | 2021-09-26 19:23 | 40 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21092600119 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2021-09-26 | 7520 | keep | 0 | Sep | 2021 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-26 16:16 | 2021-09-26 16:17 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 2234 | keep | 0 | Sep | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-09-26 16:29 | 2021-09-26 16:30 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21092600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 2234 | keep | 0 | Sep | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-09-26 16:33 | 2021-09-27 15:42 | 60 | 023:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092600106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1389 | 2021-09-26 | 83340 | keep | 0 | Sep | 2021 | 0.056762 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-09-26 16:43 | 2021-09-26 16:44 | 3744 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P21092600048 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-26 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-26 16:43 | 2021-09-26 16:44 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-09-26 16:44 | 2021-09-26 21:53 | 50 | 005:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 4 X 50 EN CORTE DE LINEA | P21092600051 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 309 | 2021-09-26 | 15450 | keep | 0 | Sep | 2021 | 0.010523 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-26 16:51 | 2021-09-27 11:20 | 200 | 018:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M21092600066 | New_Event | Cutout Failure | Include | Include | Equipment | 1109 | 2021-09-26 | 221800 | keep | 0 | Sep | 2021 | 0.15107 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-09-26 16:51 | 2021-09-27 19:30 | 1 | 026:39 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO CORTE DE LINEA | M21092600066 | New_Event | Defective Pole | Include | Include | Equipment | 1599 | 2021-09-26 | 1599 | keep | 0 | Sep | 2021 | 0.0010891 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-09-26 17:02 | 2021-09-26 17:05 | 200 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA POR 9405 05 | B21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-26 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-09-26 17:02 | 2021-09-26 17:05 | 3511 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA PARTE DE LA CARGA DE 1710 05 | B21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-26 | 10533 | keep | 0 | Sep | 2021 | 0.007174 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
PONCE | 2021-09-26 17:04 | 2021-09-27 14:45 | 29 | 021:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES LLUVIAS | P21092600052 | New_Event | Bad Weather | Include | Include | Weather | 1301 | 2021-09-26 | 37729 | keep | 0 | Sep | 2021 | 0.025697 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
BAYAMON | 2021-09-26 17:05 | 2021-09-26 21:27 | 45 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092600188 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-09-26 | 11790 | keep | 0 | Sep | 2021 | 0.0080301 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-09-26 17:07 | 2021-09-27 20:59 | 10 | 027:52 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR DE 50 KVA 4160VOLTS QUEMADO POR LO MISMO | P21092600053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1672 | 2021-09-26 | 16720 | keep | 0 | Sep | 2021 | 0.011388 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-26 17:14 | 2021-09-26 17:15 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE BREAKER PORTATIL #10 | P21092600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-26 17:14 | 2021-09-26 17:15 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE BREAKER PORTATIL #10 | P21092600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-26 17:14 | 2021-09-26 17:15 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE BREAKER PORTATIL #10 | P21092600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
ARECIBO | 2021-09-26 17:34 | 2021-09-26 17:35 | 3 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21092600019 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-26 | 3 | keep | 0 | Sep | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-09-26 17:46 | 2021-09-26 17:47 | 2751 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P21092600059 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-26 | 2751 | keep | 0 | Sep | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2021-09-26 17:47 | 2021-09-27 07:56 | 200 | 014:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | P21092600112 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 849 | 2021-09-26 | 169800 | keep | 0 | Sep | 2021 | 0.11565 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-26 18:04 | 2021-09-27 10:26 | 150 | 016:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 80 EN CORTES DE LINEA CRUCE X AVE | C21092600149 | New_Event |  |  | Include | Wildlife | 982 | 2021-09-26 | 147300 | keep | 0 | Sep | 2021 | 0.10033 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-09-26 18:33 | 2021-09-27 12:16 | 15 | 017:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092600153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1063 | 2021-09-26 | 15945 | keep | 0 | Sep | 2021 | 0.01086 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-26 18:41 | 2021-09-27 10:50 | 50 | 016:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21092600097 | New_Event | Bad Weather | Include | Include | Weather | 969 | 2021-09-26 | 48450 | keep | 0 | Sep | 2021 | 0.032999 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-26 18:42 | 2021-09-27 15:00 | 4664 | 020:18 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO SALIDA SOTERRADA DEL ALIMENTADOR Y SE AMARRO CON 6012-03 | M21092600101 | New_Event | UG Cable Fault | Include | Include | Equipment | 1218 | 2021-09-26 | 5680752 | keep | 0 | Sep | 2021 | 3.8691 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
VEGA BAJA | 2021-09-26 18:44 | 2021-09-27 10:52 | 20 | 016:08 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21092600159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 968 | 2021-09-26 | 19360 | keep | 0 | Sep | 2021 | 0.013186 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-26 18:46 | 2021-09-26 22:17 | 1712 | 003:31 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DESCARGAS ELECTRICAS SE PUSO EN SERVICIO ELECTRICAMENTE | P21092600111 | New_Event | Bad Weather | Include | Include | Weather | 211 | 2021-09-26 | 361232 | keep | 0 | Sep | 2021 | 0.24603 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-09-26 18:46 | 2021-09-26 22:17 | 7 | 003:31 | T | MAL TIEMPO/RAYOS/WET ASH | DESCARGAS ELECTRICAS | P21092600111 | New_Event | Bad Weather | Include | Include | Weather | 211 | 2021-09-26 | 1477 | keep | 0 | Sep | 2021 | 0.001006 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-09-26 18:46 | 2021-09-27 17:50 | 10 | 023:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1X10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | P21092600089 | New_Event | Bad Weather | Include | Include | Weather | 1384 | 2021-09-26 | 13840 | keep | 0 | Sep | 2021 | 0.0094264 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-26 18:55 | 2021-09-26 21:16 | 20 | 002:21 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | M21092600111 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 141 | 2021-09-26 | 2820 | keep | 0 | Sep | 2021 | 0.0019207 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-09-26 19:00 | 2021-09-26 21:15 | 2011 | 002:15 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE ALIMENTADOR NO HAY RTU | P21092600123 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-09-26 | 271485 | keep | 0 | Sep | 2021 | 0.18491 | 0.0013697 | Sustained | FALSE | FALSE | Not_TMED_Event | 2011
AGUADILLA | 2021-09-26 19:31 | 2021-10-08 19:45 | 5 | 288:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092600125 | New_Event | Bad Weather | Include | Include | Weather | 17294 | 2021-09-26 | 86470 | keep | 0 | Sep | 2021 | 0.058894 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-09-26 19:35 | 2021-09-27 10:40 | 100 | 015:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21092600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 905 | 2021-09-26 | 90500 | keep | 0 | Sep | 2021 | 0.061639 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-26 19:40 | 2021-09-26 21:35 | 50 | 001:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21092600059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-09-26 | 5750 | keep | 0 | Sep | 2021 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-26 19:48 | 2021-09-26 20:32 | 10 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA TRASPATIO | S21092600103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-09-26 | 440 | keep | 0 | Sep | 2021 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-26 19:54 | 2021-09-26 20:23 | 2234 | 000:29 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21092600193 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 29 | 2021-09-26 | 64786 | keep | 0 | Sep | 2021 | 0.044125 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-09-26 19:56 | 2021-09-27 19:32 | 15 | 023:36 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | B21092600186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1416 | 2021-09-26 | 21240 | keep | 0 | Sep | 2021 | 0.014466 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-26 21:03 | 2021-09-27 08:05 | 50 | 011:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092600151 | New_Event | Bad Weather | Include | Include | Weather | 662 | 2021-09-26 | 33100 | keep | 0 | Sep | 2021 | 0.022544 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-26 21:17 | 2021-09-26 21:18 | 351 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21092600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 351 | keep | 0 | Sep | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
MAYAGÃœEZ | 2021-09-26 21:26 | 2021-09-27 08:05 | 85 | 010:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092600154 | New_Event | Bad Weather | Include | Include | Weather | 639 | 2021-09-26 | 54315 | keep | 0 | Sep | 2021 | 0.036994 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
CAGUAS | 2021-09-26 21:54 | 2021-09-27 10:54 | 40 | 013:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21092600119 | Partial_restoration | Wire Down | Include | Include | Equipment | 780 | 2021-09-26 | 31200 | keep | 0 | Sep | 2021 | 0.02125 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-26 22:15 | 2021-09-27 11:18 | 70 | 013:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA MARCA-THNT 100AMP. | A21092600096 | New_Event | Cutout Failure | Include | Include | Equipment | 783 | 2021-09-26 | 54810 | keep | 0 | Sep | 2021 | 0.037331 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-26 22:17 | 2021-09-26 22:18 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092600172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-26 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
FAJARDO | 2021-09-26 22:18 | 2021-09-27 09:28 | 235 | 011:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR IGUANA | R21092600141 | New_Event |  |  | Include | Wildlife | 670 | 2021-09-26 | 157450 | keep | 0 | Sep | 2021 | 0.10724 | 0.00016006 | Sustained | FALSE | TRUE | Not_TMED_Event | 235
BAYAMON | 2021-09-26 23:26 | 2021-09-27 04:57 | 60 | 005:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 50 EN RISER | B21092600302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 331 | 2021-09-26 | 19860 | keep | 0 | Sep | 2021 | 0.013527 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-26 23:32 | 2021-09-27 14:03 | 20 | 014:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21092600241 | New_Event | Wire Down | Include | Include | Equipment | 871 | 2021-09-26 | 17420 | keep | 0 | Sep | 2021 | 0.011865 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-26 23:34 | 2021-09-27 11:44 | 15 | 012:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANFORMADOR | B21092600191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 730 | 2021-09-26 | 10950 | keep | 0 | Sep | 2021 | 0.007458 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-27 01:35 | 2021-09-28 10:41 | 80 | 033:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092700009 | New_Event | Bad Weather | Include | Include | Weather | 1986 | 2021-09-27 | 158880 | keep | 0 | Sep | 2021 | 0.10821 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-27 02:11 | 2021-09-27 10:03 | 50 | 007:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO CAUSA | C21092700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2021-09-27 | 23600 | keep | 0 | Sep | 2021 | 0.016074 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-27 03:26 | 2021-09-27 11:54 | 100 | 008:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21092700007 | New_Event | Bad Weather | Include | Include | Weather | 508 | 2021-09-27 | 50800 | keep | 0 | Sep | 2021 | 0.0346 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-27 04:21 | 2021-09-27 04:22 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092700016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-27 | 113 | keep | 0 | Sep | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
ARECIBO | 2021-09-27 04:48 | 2021-09-27 04:50 | 2888 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21092700004 | New_Event |  |  | Include | Wildlife | 2 | 2021-09-27 | 5776 | keep | 0 | Sep | 2021 | 0.003934 | 0.001967 | Momentary | FALSE | TRUE | Not_TMED_Event | 2888
ARECIBO | 2021-09-27 04:50 | 2021-09-27 14:22 | 12 | 009:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CAUSA POR CULEBRA | A21009270006 | 1st_after_momentary |  |  | Include | Wildlife | 572 | 2021-09-27 | 6864 | keep | 0 | Sep | 2021 | 0.004675 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-27 05:04 | 2021-09-27 11:26 | 60 | 006:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 50 EN RISER | B21092600302 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 382 | 2021-09-27 | 22920 | keep | 0 | Sep | 2021 | 0.015611 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-27 05:29 | 2021-09-27 06:56 | 1983 | 001:27 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1801 02 | B21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-09-27 | 172521 | keep | 0 | Sep | 2021 | 0.1175 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-09-27 05:29 | 2021-09-27 06:56 | 186 | 001:27 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1711 04 | B21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-09-27 | 16182 | keep | 0 | Sep | 2021 | 0.011021 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
CAGUAS | 2021-09-27 05:31 | 2021-09-27 09:17 | 1403 | 003:46 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO CABLE SOTERRADO AVERIADO | C21092700014 | New_Event | UG Cable Fault | Include | Include | Equipment | 226 | 2021-09-27 | 317078 | keep | 0 | Sep | 2021 | 0.21596 | 0.00095558 | Sustained | FALSE | FALSE | Not_TMED_Event | 1403
MAYAGÃœEZ | 2021-09-27 06:29 | 2021-09-27 14:44 | 30 | 008:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | M21092700024 | New_Event | Wire Down | Include | Include | Equipment | 495 | 2021-09-27 | 14850 | keep | 0 | Sep | 2021 | 0.010114 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-09-27 06:45 | 2021-09-27 06:46 | 5630 | 000:01 | T | DESGANCHE | RECIERRE | C21092700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-27 | 5630 | keep | 0 | Sep | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-09-27 06:46 | 2021-09-27 20:53 | 70 | 014:07 | P | DESGANCHE | CERRO INTELIRRUPTER 2603-8E | C21092700404 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 847 | 2021-09-27 | 59290 | keep | 0 | Sep | 2021 | 0.040382 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2021-09-27 06:50 | 2021-09-27 11:00 | 150 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21092700027 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2021-09-27 | 37500 | keep | 0 | Sep | 2021 | 0.025541 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-09-27 06:57 | 2021-09-27 06:58 | 726 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1346-04 | S21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-27 | 726 | keep | 0 | Sep | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-09-27 06:57 | 2021-09-27 06:58 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1303-03 | S21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-27 | 3932 | keep | 0 | Sep | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
HUMACAO | 2021-09-27 07:04 | 2021-09-27 11:30 | 60 | 004:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTES DE LINEA MAL TIEMPO | C21092700022 | New_Event | Bad Weather | Include | Include | Weather | 266 | 2021-09-27 | 15960 | keep | 0 | Sep | 2021 | 0.01087 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-27 07:28 | 2021-09-27 08:00 | 1983 | 000:32 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1801 02 | B21092700054 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 32 | 2021-09-27 | 63456 | keep | 0 | Sep | 2021 | 0.04322 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-27 07:28 | 2021-09-27 08:00 | 186 | 000:32 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1711 04 | B21092700054 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 32 | 2021-09-27 | 5952 | keep | 0 | Sep | 2021 | 0.0040539 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-27 07:45 | 2021-09-27 12:36 | 20 | 004:51 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA 1 X 65 EN RISER SE REPARO TERMINACION SOTERRADA | B21092700060 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 291 | 2021-09-27 | 5820 | keep | 0 | Sep | 2021 | 0.003964 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-27 08:23 | 2021-09-27 12:54 | 888 | 004:31 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR CONTINGENCIA | M21092700000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 271 | 2021-09-27 | 240648 | keep | 0 | Sep | 2021 | 0.1639 | 0.00060481 | Sustained | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2021-09-27 08:23 | 2021-09-27 12:54 | 393 | 004:31 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR CONTINGENCIA | M21092700000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 271 | 2021-09-27 | 106503 | keep | 0 | Sep | 2021 | 0.072539 | 0.00026767 | Sustained | FALSE | FALSE | Not_TMED_Event | 393
UTUADO | 2021-09-27 09:07 | 2021-09-27 11:59 | 6 | 002:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA | A21092700028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 172 | 2021-09-27 | 1032 | keep | 0 | Sep | 2021 | 0.00070289 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-27 09:10 | 2021-09-27 17:44 | 100 | 008:34 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS SE CERRO CORTE DE LINEA | M21092700093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2021-09-27 | 51400 | keep | 0 | Sep | 2021 | 0.035008 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-09-27 09:35 | 2021-09-27 09:58 | 2450 | 000:23 | T | NO SE REPORTO CAUSA | DISPARO | C21092700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-09-27 | 56350 | keep | 0 | Sep | 2021 | 0.03838 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2021-09-27 09:36 | 2021-09-27 10:29 | 12 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21092600038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2021-09-27 | 636 | keep | 0 | Sep | 2021 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-27 09:37 | 2021-09-27 12:53 | 150 | 003:16 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21092700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-09-27 | 29400 | keep | 0 | Sep | 2021 | 0.020024 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-09-27 09:39 | 2021-09-27 15:05 | 6 | 005:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE POSTE SECUNDARIO | R21092700088 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 326 | 2021-09-27 | 1956 | keep | 0 | Sep | 2021 | 0.0013322 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-27 09:48 | 2021-09-27 13:22 | 20 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21092700149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2021-09-27 | 4280 | keep | 0 | Sep | 2021 | 0.0029151 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-27 09:55 | 2021-09-27 11:04 | 154 | 001:09 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE | R21092700090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-09-27 | 10626 | keep | 0 | Sep | 2021 | 0.0072373 | 0.00010489 | Sustained | FALSE | TRUE | Not_TMED_Event | 154
BAYAMON | 2021-09-27 09:55 | 2021-09-27 11:42 | 1 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER SE RETIRO AVE CRUZANDO LINEAS | B21092700150 | New_Event |  |  | Include | Wildlife | 107 | 2021-09-27 | 107 | keep | 0 | Sep | 2021 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-09-27 10:23 | 2021-09-27 15:23 | 2 | 005:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA AVERIADO POR LO MISMO | A21092700045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 300 | 2021-09-27 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-09-27 10:29 | 2021-09-27 21:05 | 50 | 010:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092700442 | New_Event | Bad Weather | Include | Include | Weather | 636 | 2021-09-27 | 31800 | keep | 0 | Sep | 2021 | 0.021659 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-27 10:34 | 2021-09-28 11:39 | 20 | 025:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092700446 | New_Event | Bad Weather | Include | Include | Weather | 1505 | 2021-09-27 | 30100 | keep | 0 | Sep | 2021 | 0.020501 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-27 10:36 | 2021-09-27 14:58 | 10 | 004:22 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | C21092600069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 262 | 2021-09-27 | 2620 | keep | 0 | Sep | 2021 | 0.0017845 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-27 10:40 | 2021-09-27 15:59 | 9 | 005:19 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA PASARLO A POSTE NUEVO EXISTENTE | A21092700000 | New_Event | Other Causes | Include | Include | Other | 319 | 2021-09-27 | 2871 | keep | 0 | Sep | 2021 | 0.0019554 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-09-27 10:43 | 2021-09-27 13:21 | 5 | 002:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21092700162 | New_Event | Secondary Wire Down | Include | Include | Equipment | 158 | 2021-09-27 | 790 | keep | 0 | Sep | 2021 | 0.00053807 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-09-27 10:55 | 2021-09-27 12:47 | 200 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | P21092600112 | Partial_restoration | Wire Down | Include | Include | Equipment | 112 | 2021-09-27 | 22400 | keep | 0 | Sep | 2021 | 0.015257 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-27 11:02 | 2021-09-27 13:25 | 35 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR 1 X 40 EN CORTE DE LINEA | B21092700190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2021-09-27 | 5005 | keep | 0 | Sep | 2021 | 0.0034089 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-09-27 11:07 | 2021-09-27 13:22 | 60 | 002:15 | P | DESGANCHE | SE REEMPLAZO CAJA PRIMARIA Y DESGANCHE | B21092700420 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-09-27 | 8100 | keep | 0 | Sep | 2021 | 0.0055169 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-09-27 11:20 | 2021-09-27 12:28 | 1 | 001:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | R21092700108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-09-27 | 68 | keep | 0 | Sep | 2021 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-09-27 11:22 | 2021-09-27 12:50 | 40 | 001:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | R21092700109 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2021-09-27 | 3520 | keep | 0 | Sep | 2021 | 0.0023975 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-27 11:41 | 2021-09-27 15:01 | 2 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092700064 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-09-27 | 400 | keep | 0 | Sep | 2021 | 0.00027244 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-09-27 11:46 | 2021-09-27 15:45 | 200 | 003:59 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092700153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-09-27 | 47800 | keep | 0 | Sep | 2021 | 0.032556 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-09-27 12:03 | 2021-09-27 14:50 | 25 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21092700076 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-09-27 | 4175 | keep | 0 | Sep | 2021 | 0.0028436 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-27 12:06 | 2021-09-27 20:41 | 41 | 008:35 | P | CABLE SOTERRADO AVERIADO | REPARO TRAMO ENTRE EL SU - 1 Y EL T - 23 | C21092500086 | New_Event | UG Cable Fault | Include | Include | Equipment | 515 | 2021-09-27 | 21115 | keep | 0 | Sep | 2021 | 0.014381 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
MAYAGÃœEZ | 2021-09-27 12:15 | 2021-09-27 14:03 | 50 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092600151 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-09-27 | 5400 | keep | 0 | Sep | 2021 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-27 12:22 | 2021-09-27 17:18 | 10 | 004:56 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | B21092700201 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 296 | 2021-09-27 | 2960 | keep | 0 | Sep | 2021 | 0.002016 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-27 12:25 | 2021-09-27 21:32 | 100 | 009:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21092600072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2021-09-27 | 54700 | keep | 0 | Sep | 2021 | 0.037256 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-27 12:29 | 2021-09-27 21:14 | 1382 | 008:45 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA CARGA DEL 1706-03 Y 1715-03 | B21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 525 | 2021-09-27 | 725550 | keep | 0 | Sep | 2021 | 0.49417 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-09-27 12:29 | 2021-09-27 21:14 | 663 | 008:45 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1706-02 | B21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 525 | 2021-09-27 | 348075 | keep | 0 | Sep | 2021 | 0.23707 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
ARECIBO | 2021-09-27 12:36 | 2021-09-27 15:06 | 4 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIAS | A21092700072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2021-09-27 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-09-27 12:37 | 2021-09-27 16:55 | 2 | 004:18 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 15 KVA | C21092500136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 258 | 2021-09-27 | 516 | keep | 0 | Sep | 2021 | 0.00035145 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-09-27 12:37 | 2021-09-27 20:11 | 20 | 007:34 | P | TRANSFORMADOR AVERIADO | REMPLAZO 2 TRANSFORMADORES 25 KVA X 25 KVA Y 37.5 KVA X 37.5 KVA | C21092700137 | New_Event | Service Transformer Failure | Include | Include | Equipment | 454 | 2021-09-27 | 9080 | keep | 0 | Sep | 2021 | 0.0061843 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-27 12:38 | 2021-09-27 12:41 | 3 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21092700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-27 | 9 | keep | 0 | Sep | 2021 | 6.1299e-06 | 2.0433e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-09-27 12:38 | 2021-09-27 12:41 | 3957 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21092700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-27 | 11871 | keep | 0 | Sep | 2021 | 0.0080853 | 0.0026951 | Momentary | FALSE | TRUE | Not_TMED_Event | 3957
BAYAMON | 2021-09-27 12:38 | 2021-09-27 12:41 | 58 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S2109270000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-27 | 174 | keep | 0 | Sep | 2021 | 0.00011851 | 3.9504e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 58
SAN JUAN | 2021-09-27 12:38 | 2021-09-27 12:41 | 386 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21092700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-09-27 | 1158 | keep | 0 | Sep | 2021 | 0.00078871 | 0.0002629 | Momentary | FALSE | TRUE | Not_TMED_Event | 386
ARECIBO | 2021-09-27 13:58 | 2021-09-27 17:15 | 15 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092700106 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2021-09-27 | 2955 | keep | 0 | Sep | 2021 | 0.0020126 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-09-27 14:18 | 2021-09-27 15:25 | 11 | 001:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R21092700175 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2021-09-27 | 737 | keep | 0 | Sep | 2021 | 0.00050197 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-09-27 14:20 | 2021-09-27 14:34 | 160 | 000:14 | P | NO SE REPORTO CAUSA | 2 X 125 EN SU-9 | B21092700294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2021-09-27 | 2240 | keep | 0 | Sep | 2021 | 0.0015257 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
UTUADO | 2021-09-27 15:09 | 2021-09-27 15:10 | 650 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21092700136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-27 | 650 | keep | 0 | Sep | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
BARRANQUITAS | 2021-09-27 15:14 | 2021-09-27 19:54 | 30 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21092700297 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2021-09-27 | 8400 | keep | 0 | Sep | 2021 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-27 15:23 | 2021-09-27 15:25 | 281 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LIMEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 562 | keep | 0 | Sep | 2021 | 0.00038278 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-27 15:23 | 2021-09-27 15:25 | 1252 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LIMEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 2504 | keep | 0 | Sep | 2021 | 0.0017055 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-09-27 15:23 | 2021-09-27 15:25 | 595 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LIMEA 8100 | M21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1190 | keep | 0 | Sep | 2021 | 0.0008105 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-09-27 15:23 | 2021-09-27 15:25 | 51 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LIMEA 8100 | M21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 102 | keep | 0 | Sep | 2021 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-09-27 15:23 | 2021-09-27 15:25 | 721 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LIMEA 8100 | M21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1442 | keep | 0 | Sep | 2021 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2021-09-27 15:23 | 2021-09-27 15:25 | 3316 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 6632 | keep | 0 | Sep | 2021 | 0.004517 | 0.0022585 | Momentary | FALSE | TRUE | Not_TMED_Event | 3316
UTUADO | 2021-09-27 15:23 | 2021-09-27 15:25 | 1241 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 2482 | keep | 0 | Sep | 2021 | 0.0016905 | 0.00084524 | Momentary | FALSE | TRUE | Not_TMED_Event | 1241
UTUADO | 2021-09-27 15:23 | 2021-09-27 15:25 | 650 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1300 | keep | 0 | Sep | 2021 | 0.00088542 | 0.00044271 | Momentary | FALSE | TRUE | Not_TMED_Event | 650
UTUADO | 2021-09-27 15:23 | 2021-09-27 15:25 | 1382 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 2764 | keep | 0 | Sep | 2021 | 0.0018825 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-27 15:23 | 2021-09-27 15:25 | 654 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21092700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1308 | keep | 0 | Sep | 2021 | 0.00089087 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
UTUADO | 2021-09-27 15:25 | 2021-09-27 17:16 | 12 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092000119 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2021-09-27 | 1332 | keep | 0 | Sep | 2021 | 0.00090722 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
ARECIBO | 2021-09-27 15:40 | 2021-09-27 20:59 | 400 | 005:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA LINEAS PARTIDAS | A21092700148 | New_Event | Wire Down | Include | Include | Equipment | 319 | 2021-09-27 | 127600 | keep | 0 | Sep | 2021 | 0.086908 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
SAN JUAN | 2021-09-27 15:46 | 2021-09-27 15:47 | 351 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-27 | 351 | keep | 0 | Sep | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
BAYAMON | 2021-09-27 15:53 | 2021-09-28 13:00 | 8 | 021:07 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21092700487 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1267 | 2021-09-27 | 10136 | keep | 0 | Sep | 2021 | 0.0069036 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-27 16:59 | 2021-09-27 17:01 | 281 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 562 | keep | 0 | Sep | 2021 | 0.00038278 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-27 16:59 | 2021-09-27 17:01 | 1252 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 2504 | keep | 0 | Sep | 2021 | 0.0017055 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-09-27 16:59 | 2021-09-27 17:01 | 595 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1190 | keep | 0 | Sep | 2021 | 0.0008105 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-09-27 16:59 | 2021-09-27 17:01 | 51 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 102 | keep | 0 | Sep | 2021 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-09-27 16:59 | 2021-09-27 17:01 | 721 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1442 | keep | 0 | Sep | 2021 | 0.00098214 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-09-27 16:59 | 2021-09-27 17:01 | 1382 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 2764 | keep | 0 | Sep | 2021 | 0.0018825 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-27 16:59 | 2021-09-27 17:01 | 654 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21092700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-27 | 1308 | keep | 0 | Sep | 2021 | 0.00089087 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
CAGUAS | 2021-09-27 17:22 | 2021-09-27 17:42 | 5 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21092700162 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-09-27 | 100 | keep | 0 | Sep | 2021 | 6.811e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-09-27 18:03 | 2021-09-27 22:10 | 60 | 004:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR Y REPARAR CONDUCTOR VIVO EN EL SUELO NO FUNDIO FUSIBLE | R21092700229 | New_Event | Wire Down | Include | Include | Equipment | 247 | 2021-09-27 | 14820 | keep | 0 | Sep | 2021 | 0.010094 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-27 18:59 | 2021-09-27 21:23 | 200 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA REMPLAZO CAJA | A21092700224 | New_Event | Cutout Failure | Include | Include | Equipment | 144 | 2021-09-27 | 28800 | keep | 0 | Sep | 2021 | 0.019616 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-09-27 19:09 | 2021-09-27 21:04 | 35 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21092700462 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-09-27 | 4025 | keep | 0 | Sep | 2021 | 0.0027414 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-27 19:13 | 2021-09-27 21:20 | 70 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER DESCARGAS ELECTRICAS | P21092700330 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2021-09-27 | 8890 | keep | 0 | Sep | 2021 | 0.0060549 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2021-09-27 19:15 | 2021-09-28 09:39 | 140 | 014:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21092700333 | New_Event | Vegetation Contact | Include | Include | Vegetation | 864 | 2021-09-27 | 120960 | keep | 0 | Sep | 2021 | 0.082385 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
PONCE | 2021-09-27 19:45 | 2021-09-27 19:53 | 653 | 000:08 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO ALIMENTADOR POR MAL TIEMPO | P21092700344 | New_Event | Bad Weather | Include | Include | Weather | 8 | 2021-09-27 | 5224 | keep | 0 | Sep | 2021 | 0.003558 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
ARECIBO | 2021-09-27 19:57 | 2021-09-28 00:02 | 140 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | A21092700248 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-09-27 | 34300 | keep | 0 | Sep | 2021 | 0.023362 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
ARECIBO | 2021-09-27 20:04 | 2021-09-27 21:37 | 18 | 001:33 | P | SOBRECARGA | 1 X 20 EN RISER PERSONAL INDICO QUE EL MISMO FUNDIO POR CARGA | A21092700252 | New_Event | Trip Due To Overload | Include | Include | Other | 93 | 2021-09-27 | 1674 | keep | 0 | Sep | 2021 | 0.0011402 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2021-09-27 20:12 | 2021-09-27 21:28 | 20 | 001:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR LIQUEANDO DE 50KVA LO MISMO | A21092100167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 76 | 2021-09-27 | 1520 | keep | 0 | Sep | 2021 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-27 20:17 | 2021-09-28 11:06 | 1746 | 014:49 | T | DESGANCHE | SE REALIZO DESGANCHE EN CALLE WASHINGTON Y SE CERRO AMARRE CON 5011-05 | P21092700403 | New_Event | Vegetation Contact | Include | Include | Vegetation | 889 | 2021-09-27 | 1552194 | keep | 0 | Sep | 2021 | 1.0572 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-09-27 20:17 | 2021-09-27 23:17 | 113 | 003:00 | T | NO SE REPORTO CAUSA | DISPARO DEL ALIMENTADOR RECERRO TRES VECES | P21092700364 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2021-09-27 | 20340 | keep | 0 | Sep | 2021 | 0.013853 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
MAYAGÃœEZ | 2021-09-27 20:29 | 2021-09-28 09:45 | 150 | 013:16 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092700404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 796 | 2021-09-27 | 119400 | keep | 0 | Sep | 2021 | 0.081323 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-09-27 21:17 | 2021-09-27 21:18 | 713 | 000:01 | T | SOBRECARGA | SE ABRE INTERRUPTOR PARA TRANSFERIR CARGA DEL INTERRUPTOR 2 POR SOBRE CARGA | P210927000XX | New_Event | Trip Due To Overload | Include | Include | Other | 1 | 2021-09-27 | 713 | keep | 0 | Sep | 2021 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
ARECIBO | 2021-09-27 21:21 | 2021-09-28 15:00 | 30 | 017:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21092700266 | New_Event | Wire Down | Include | Include | Equipment | 1059 | 2021-09-27 | 31770 | keep | 0 | Sep | 2021 | 0.021638 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-27 21:24 | 2021-09-29 11:57 | 12 | 038:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092000119 | New_Event | Bad Weather | Include | Include | Weather | 2313 | 2021-09-27 | 27756 | keep | 0 | Sep | 2021 | 0.018904 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
ARECIBO | 2021-09-27 21:29 | 2021-09-28 00:18 | 2231 | 002:49 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700267 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 169 | 2021-09-27 | 377039 | keep | 0 | Sep | 2021 | 0.2568 | 0.0015195 | Sustained | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2021-09-27 21:29 | 2021-09-28 00:18 | 1923 | 002:49 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700268 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 169 | 2021-09-27 | 324987 | keep | 0 | Sep | 2021 | 0.22135 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
ARECIBO | 2021-09-27 21:29 | 2021-09-28 00:18 | 1066 | 002:49 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 169 | 2021-09-27 | 180154 | keep | 0 | Sep | 2021 | 0.1227 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2021-09-27 21:29 | 2021-09-28 00:18 | 141 | 002:49 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700269 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 169 | 2021-09-27 | 23829 | keep | 0 | Sep | 2021 | 0.01623 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
ARECIBO | 2021-09-27 21:34 | 2021-09-28 00:27 | 1798 | 002:53 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700270 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 173 | 2021-09-27 | 311054 | keep | 0 | Sep | 2021 | 0.21186 | 0.0012246 | Sustained | FALSE | FALSE | Not_TMED_Event | 1798
ARECIBO | 2021-09-27 21:34 | 2021-09-28 00:27 | 3309 | 002:53 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700271 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 173 | 2021-09-27 | 572457 | keep | 0 | Sep | 2021 | 0.3899 | 0.0022537 | Sustained | FALSE | FALSE | Not_TMED_Event | 3309
ARECIBO | 2021-09-27 21:34 | 2021-09-28 00:28 | 713 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700272 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 124062 | keep | 0 | Sep | 2021 | 0.084498 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
ARECIBO | 2021-09-27 21:37 | 2021-09-28 00:31 | 2791 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700275 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 485634 | keep | 0 | Sep | 2021 | 0.33076 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-09-27 21:37 | 2021-09-28 00:31 | 759 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700277 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 132066 | keep | 0 | Sep | 2021 | 0.08995 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-09-27 21:37 | 2021-09-28 00:31 | 1500 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700278 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 261000 | keep | 0 | Sep | 2021 | 0.17777 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-09-27 21:37 | 2021-09-28 00:31 | 2132 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 370968 | keep | 0 | Sep | 2021 | 0.25266 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-09-27 21:37 | 2021-09-28 00:31 | 2366 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700274 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 411684 | keep | 0 | Sep | 2021 | 0.2804 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-09-27 21:37 | 2021-09-28 00:31 | 1976 | 002:54 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | A21092700276 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 174 | 2021-09-27 | 343824 | keep | 0 | Sep | 2021 | 0.23418 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
GUAYAMA | 2021-09-27 21:39 | 2021-09-27 23:59 | 241 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER ROEDOR | P21092700396 | New_Event |  |  | Include | Wildlife | 140 | 2021-09-27 | 33740 | keep | 0 | Sep | 2021 | 0.02298 | 0.00016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 241
CAGUAS | 2021-09-27 22:13 | 2021-09-27 22:14 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21092700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-27 | 2178 | keep | 0 | Sep | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
VEGA BAJA | 2021-09-27 22:13 | 2021-09-28 10:00 | 40 | 011:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 707 | 2021-09-27 | 28280 | keep | 0 | Sep | 2021 | 0.019261 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-27 22:13 | 2021-09-28 12:15 | 60 | 014:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092700540 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 842 | 2021-09-27 | 50520 | keep | 0 | Sep | 2021 | 0.034409 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-27 22:18 | 2021-09-28 01:10 | 824 | 002:52 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | M21092700000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 172 | 2021-09-27 | 141728 | keep | 0 | Sep | 2021 | 0.09653 | 0.00056122 | Sustained | FALSE | FALSE | Not_TMED_Event | 824
MAYAGÃœEZ | 2021-09-27 22:18 | 2021-09-28 01:10 | 146 | 002:52 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | M21092700000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 172 | 2021-09-27 | 25112 | keep | 0 | Sep | 2021 | 0.017104 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
MAYAGÃœEZ | 2021-09-27 22:18 | 2021-09-28 01:10 | 667 | 002:52 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA | M21092700000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 172 | 2021-09-27 | 114724 | keep | 0 | Sep | 2021 | 0.078138 | 0.00045429 | Sustained | FALSE | FALSE | Not_TMED_Event | 667
YAUCO | 2021-09-27 22:20 | 2021-09-28 01:12 | 1924 | 002:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTIGENCIA | P21092700412 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 172 | 2021-09-27 | 330928 | keep | 0 | Sep | 2021 | 0.22539 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-09-27 22:20 | 2021-09-28 01:12 | 968 | 002:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTIGENCIA | P21092700412 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 172 | 2021-09-27 | 166496 | keep | 0 | Sep | 2021 | 0.1134 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2021-09-27 22:20 | 2021-09-28 01:12 | 2246 | 002:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTIGENCIA | P21092700412 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 172 | 2021-09-27 | 386312 | keep | 0 | Sep | 2021 | 0.26312 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
BAYAMON | 2021-09-27 22:21 | 2021-09-28 05:13 | 10 | 006:52 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REPARARON DOS TERMINACIONES DE RISER A T-11 | B21092700546 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 412 | 2021-09-27 | 4120 | keep | 0 | Sep | 2021 | 0.0028061 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-09-27 22:46 | 2021-09-28 11:00 | 60 | 012:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21092700288 | New_Event | Bad Weather | Include | Include | Weather | 734 | 2021-09-27 | 44040 | keep | 0 | Sep | 2021 | 0.029995 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-27 22:49 | 2021-09-28 09:52 | 10 | 011:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092700289 | New_Event | Bad Weather | Include | Include | Weather | 663 | 2021-09-27 | 6630 | keep | 0 | Sep | 2021 | 0.0045157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-27 23:06 | 2021-09-27 23:18 | 80 | 000:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092700566 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2021-09-27 | 960 | keep | 0 | Sep | 2021 | 0.00065385 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-27 23:28 | 2021-09-28 13:30 | 50 | 014:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092700575 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 842 | 2021-09-27 | 42100 | keep | 0 | Sep | 2021 | 0.028674 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-27 23:48 | 2021-09-28 11:45 | 50 | 011:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092700442 | Partial_restoration | Bad Weather | Include | Include | Weather | 717 | 2021-09-27 | 35850 | keep | 0 | Sep | 2021 | 0.024417 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-28 00:02 | 2021-09-28 01:11 | 2201 | 001:09 | T | MAL TIEMPO/RAYOS/WET ASH | ABIMELEC ACEVEDO VERIFICO TODO NORMAL Y CERRO EL INTERRUPTOR EN LA SUBESTACION | A21092800002 | Additional_clients | Bad Weather | Include | Include | Weather | 69 | 2021-09-28 | 151869 | keep | 0 | Sep | 2021 | 0.10344 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-28 00:55 | 2021-09-28 07:09 | 10 | 006:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | LEVANTO SECUNDARIA Y CERRO CORTE DE LINEA | S21092800005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 374 | 2021-09-28 | 3740 | keep | 0 | Sep | 2021 | 0.0025473 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-28 01:11 | 2021-09-28 09:10 | 140 | 007:59 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | A21092700248 | New_Event | Bad Weather | Include | Include | Weather | 479 | 2021-09-28 | 67060 | keep | 0 | Sep | 2021 | 0.045674 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
MAYAGÃœEZ | 2021-09-28 01:29 | 2021-09-28 01:30 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 990 | keep | 0 | Sep | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
PONCE | 2021-09-28 01:30 | 2021-09-28 07:09 | 70 | 005:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER DESCARGAS ELECTRICAS | P21092700330 | New_Event | Bad Weather | Include | Include | Weather | 339 | 2021-09-28 | 23730 | keep | 0 | Sep | 2021 | 0.016162 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2021-09-28 04:08 | 2021-09-28 10:55 | 8 | 006:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21092800010 | New_Event | Bad Weather | Include | Include | Weather | 407 | 2021-09-28 | 3256 | keep | 0 | Sep | 2021 | 0.0022176 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-09-28 04:12 | 2021-09-28 14:42 | 40 | 010:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092800009 | New_Event | Bad Weather | Include | Include | Weather | 630 | 2021-09-28 | 25200 | keep | 0 | Sep | 2021 | 0.017164 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-28 04:28 | 2021-09-28 07:05 | 5 | 002:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CAMION PARTELINEA SECUNDARIA | P21092800026 | New_Event |  |  | Include | Wildlife | 157 | 2021-09-28 | 785 | keep | 0 | Sep | 2021 | 0.00053466 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CANOVANAS | 2021-09-28 04:58 | 2021-09-28 10:53 | 150 | 005:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 Y 1 X 65 EN CORTES DE LINEA REEMPLAZO CAJA QUEMADA | R21092800016 | New_Event | Cutout Failure | Include | Include | Equipment | 355 | 2021-09-28 | 53250 | keep | 0 | Sep | 2021 | 0.036268 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-28 05:01 | 2021-09-28 11:29 | 10 | 006:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21082800004 | New_Event | Bad Weather | Include | Include | Weather | 388 | 2021-09-28 | 3880 | keep | 0 | Sep | 2021 | 0.0026427 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-28 05:20 | 2021-09-28 16:08 | 10 | 010:48 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REPARARON DOS TERMINACIONES DE RISER A T-11 | B21092700546 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 648 | 2021-09-28 | 6480 | keep | 0 | Sep | 2021 | 0.0044135 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-09-28 05:39 | 2021-09-28 05:40 | 1428 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 1428 | keep | 0 | Sep | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
BAYAMON | 2021-09-28 05:47 | 2021-09-28 15:51 | 15 | 010:04 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 10KVA POR UNO DE 37.5KVA FID 8328485 | B21092800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 604 | 2021-09-28 | 9060 | keep | 0 | Sep | 2021 | 0.0061707 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-28 05:57 | 2021-09-28 05:58 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21092800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 449 | keep | 0 | Sep | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2021-09-28 06:01 | 2021-09-28 14:30 | 50 | 008:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21092800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 509 | 2021-09-28 | 25450 | keep | 0 | Sep | 2021 | 0.017334 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-28 06:09 | 2021-09-28 13:55 | 45 | 007:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | S21092800025 | New_Event | Cutout Failure | Include | Include | Equipment | 466 | 2021-09-28 | 20970 | keep | 0 | Sep | 2021 | 0.014283 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-09-28 06:16 | 2021-09-28 10:00 | 65 | 003:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2021-09-28 | 14560 | keep | 0 | Sep | 2021 | 0.0099167 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-09-28 06:17 | 2021-09-28 06:18 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 2782 | keep | 0 | Sep | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CAGUAS | 2021-09-28 06:21 | 2021-09-28 19:26 | 150 | 013:05 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | C21092800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 785 | 2021-09-28 | 117750 | keep | 0 | Sep | 2021 | 0.080199 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-28 06:28 | 2021-09-28 06:30 | 5191 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1710-05 Y SE CERRO POR SCADA LLEVA 1719-15 | B21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-28 | 10382 | keep | 0 | Sep | 2021 | 0.0070711 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2021-09-28 06:28 | 2021-09-28 06:30 | 3597 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1710-05 Y SE CERRO POR SCADA LLEVA 1719-15 | B21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-28 | 7194 | keep | 0 | Sep | 2021 | 0.0048998 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-09-28 06:30 | 2021-09-29 21:00 | 10 | 038:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21092800066 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2310 | 2021-09-28 | 23100 | keep | 0 | Sep | 2021 | 0.015733 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-28 06:49 | 2021-09-28 16:25 | 23 | 009:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO | P21092800042 | New_Event | Wire Down | Include | Include | Equipment | 576 | 2021-09-28 | 13248 | keep | 0 | Sep | 2021 | 0.0090232 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
SAN JUAN | 2021-09-28 07:09 | 2021-09-28 07:14 | 3 | 000:05 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-28 | 15 | keep | 0 | Sep | 2021 | 1.0216e-05 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-09-28 07:09 | 2021-09-28 12:14 | 70 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER DESCARGAS ELECTRICAS | P21092700330 | Partial_restoration | Bad Weather | Include | Include | Weather | 305 | 2021-09-28 | 21350 | keep | 0 | Sep | 2021 | 0.014541 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-09-28 07:21 | 2021-09-28 07:22 | 661 | 000:01 | T | RELEVO DE CARGA AUTOMATICO | RECIERRE INTERRUPTOR | P21092800051 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 1 | 2021-09-28 | 661 | keep | 0 | Sep | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2021-09-28 07:54 | 2021-09-28 20:13 | 50 | 012:19 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21092800110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 739 | 2021-09-28 | 36950 | keep | 0 | Sep | 2021 | 0.025166 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-28 08:04 | 2021-09-28 11:17 | 5 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | P21092800067 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-09-28 | 965 | keep | 0 | Sep | 2021 | 0.00065726 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-28 08:10 | 2021-09-28 15:31 | 10 | 007:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA AVERIADO POR LO MISMO | A21092800037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 441 | 2021-09-28 | 4410 | keep | 0 | Sep | 2021 | 0.0030036 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-28 08:12 | 2021-09-28 11:31 | 50 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092800139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2021-09-28 | 9950 | keep | 0 | Sep | 2021 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-28 08:13 | 2021-09-28 09:03 | 20 | 000:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21092800064 | New_Event | Bad Weather | Include | Include | Weather | 50 | 2021-09-28 | 1000 | keep | 0 | Sep | 2021 | 0.0006811 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-09-28 08:38 | 2021-09-28 11:35 | 15 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21092800032 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-28 | 2655 | keep | 0 | Sep | 2021 | 0.0018083 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-28 08:51 | 2021-09-28 10:19 | 2201 | 001:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DEL SERVICE TRANSFORMER | A21092800035 | New_Event | Wire Down | Include | Include | Equipment | 88 | 2021-09-28 | 193688 | keep | 0 | Sep | 2021 | 0.13192 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-09-28 08:54 | 2021-09-28 15:31 | 500 | 006:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO DOS PUENTES ABIERTOS | A21092800037 | New_Event | Wire Down | Include | Include | Equipment | 397 | 2021-09-28 | 198500 | keep | 0 | Sep | 2021 | 0.1352 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-09-28 09:00 | 2021-09-28 10:00 | 3 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21092800060 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-09-28 | 180 | keep | 0 | Sep | 2021 | 0.0001226 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
YAUCO | 2021-09-28 09:02 | 2021-09-28 16:56 | 10 | 007:54 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR AVERIADO | P21092800079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 474 | 2021-09-28 | 4740 | keep | 0 | Sep | 2021 | 0.0032284 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-28 09:02 | 2021-09-28 16:02 | 80 | 007:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21092800092 | New_Event | Bad Weather | Include | Include | Weather | 420 | 2021-09-28 | 33600 | keep | 0 | Sep | 2021 | 0.022885 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
FAJARDO | 2021-09-28 09:04 | 2021-09-28 10:51 | 6 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21092800068 | New_Event |  |  | Include | Wildlife | 107 | 2021-09-28 | 642 | keep | 0 | Sep | 2021 | 0.00043726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-28 09:09 | 2021-09-29 12:57 | 12 | 027:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M21092800106 | New_Event | Cutout Failure | Include | Include | Equipment | 1668 | 2021-09-28 | 20016 | keep | 0 | Sep | 2021 | 0.013633 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-09-28 09:10 | 2021-09-28 09:18 | 20 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO | A21092800045 | New_Event | Bad Weather | Include | Include | Weather | 8 | 2021-09-28 | 160 | keep | 0 | Sep | 2021 | 0.00010898 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-28 09:10 | 2021-09-28 16:12 | 10 | 007:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SECUNDARIO | A21092800025 | New_Event | Wire Down | Include | Include | Equipment | 422 | 2021-09-28 | 4220 | keep | 0 | Sep | 2021 | 0.0028742 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-28 09:12 | 2021-09-28 09:17 | 2565 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21092800071 | New_Event | Wire Down | Include | Include | Equipment | 5 | 2021-09-28 | 12825 | keep | 0 | Sep | 2021 | 0.008735 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BAYAMON | 2021-09-28 09:13 | 2021-09-28 11:11 | 1 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 15 HACIA SUBESTACION PRIVADA | S21092800191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2021-09-28 | 118 | keep | 0 | Sep | 2021 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-28 09:13 | 2021-09-28 11:58 | 40 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21092800046 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2021-09-28 | 6600 | keep | 0 | Sep | 2021 | 0.0044952 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-28 09:18 | 2021-09-28 09:20 | 1494 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | A21092800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-28 | 2988 | keep | 0 | Sep | 2021 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2021-09-28 09:26 | 2021-09-28 09:29 | 2916 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | A21092800052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-28 | 8748 | keep | 0 | Sep | 2021 | 0.0059582 | 0.0019861 | Momentary | FALSE | FALSE | Not_TMED_Event | 2916
BARRANQUITAS | 2021-09-28 09:32 | 2021-09-28 11:57 | 9 | 002:25 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C21092800077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2021-09-28 | 1305 | keep | 0 | Sep | 2021 | 0.00088883 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
CAGUAS | 2021-09-28 09:36 | 2021-09-28 11:26 | 1 | 001:50 | P | PARARRAYOS DEFECTUOSO | 3 X 40 EN RISER PARARRAYO PRIVADO AVERIADO | C21092800081 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 110 | 2021-09-28 | 110 | keep | 0 | Sep | 2021 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-28 09:36 | 2021-09-28 11:05 | 50 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21092800056 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-09-28 | 4450 | keep | 0 | Sep | 2021 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-28 09:55 | 2021-09-29 17:04 | 13 | 031:09 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PODRIDO | R21092800023 | New_Event | Defective Pole | Include | Include | Equipment | 1869 | 2021-09-28 | 24297 | keep | 0 | Sep | 2021 | 0.016549 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-09-28 10:01 | 2021-09-30 23:04 | 100 | 061:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21092800132 | New_Event | Bad Weather | Include | Include | Weather | 3663 | 2021-09-28 | 366300 | keep | 0 | Sep | 2021 | 0.24949 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-28 10:05 | 2021-09-28 10:59 | 35 | 000:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21092800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-09-28 | 1890 | keep | 0 | Sep | 2021 | 0.0012873 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-28 10:05 | 2021-09-28 10:44 | 1 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO | A21092800062 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-09-28 | 39 | keep | 0 | Sep | 2021 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-28 10:07 | 2021-09-28 10:42 | 36 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | C21092800089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-09-28 | 1260 | keep | 0 | Sep | 2021 | 0.00085818 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
PONCE | 2021-09-28 10:08 | 2021-09-28 10:09 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21092800096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 1478 | keep | 0 | Sep | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
UTUADO | 2021-09-28 10:16 | 2021-09-28 13:13 | 12 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO | A21092800064 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-28 | 2124 | keep | 0 | Sep | 2021 | 0.0014466 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-09-28 10:58 | 2021-09-28 12:15 | 11 | 001:17 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21092800093 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 77 | 2021-09-28 | 847 | keep | 0 | Sep | 2021 | 0.00057689 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-09-28 11:01 | 2021-09-28 11:05 | 4398 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-28 | 17592 | keep | 0 | Sep | 2021 | 0.011982 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
MAYAGÃœEZ | 2021-09-28 11:06 | 2021-09-28 12:00 | 20 | 000:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | M21092800172 | New_Event | Bad Weather | Include | Include | Weather | 54 | 2021-09-28 | 1080 | keep | 0 | Sep | 2021 | 0.00073558 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-09-28 11:07 | 2021-09-28 15:50 | 4 | 004:43 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHO Y REMPLAZO 2 CAJAS QUEMADAS | C21092800116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-09-28 | 1132 | keep | 0 | Sep | 2021 | 0.000771 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
FAJARDO | 2021-09-28 11:10 | 2021-09-28 17:27 | 20 | 006:17 | P | DESGANCHE | ABRIO CORTE DE LINEA PARA DESGANCHAR Y REMPLAZAR POSTE PARTIDO | R21092800098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2021-09-28 | 7540 | keep | 0 | Sep | 2021 | 0.0051355 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-28 11:19 | 2021-09-28 11:58 | 15 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092800181 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-09-28 | 585 | keep | 0 | Sep | 2021 | 0.00039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-28 11:26 | 2021-09-28 14:55 | 30 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CORTE DE LINEA | A21092800107 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2021-09-28 | 6270 | keep | 0 | Sep | 2021 | 0.0042705 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-28 11:28 | 2021-09-28 17:04 | 10 | 005:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | LEVANTO SECUNDARIA Y CERRO CORTE DE LINEA | S21092800005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 336 | 2021-09-28 | 3360 | keep | 0 | Sep | 2021 | 0.0022885 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-09-28 11:28 | 2021-09-28 15:56 | 40 | 004:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800081 | New_Event | Bad Weather | Include | Include | Weather | 268 | 2021-09-28 | 10720 | keep | 0 | Sep | 2021 | 0.0073013 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-28 11:35 | 2021-09-28 18:50 | 20 | 007:15 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | C21092800127 | New_Event | Defective Pole | Include | Include | Equipment | 435 | 2021-09-28 | 8700 | keep | 0 | Sep | 2021 | 0.0059255 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-28 11:40 | 2021-09-28 11:41 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21092800146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2021-09-28 11:41 | 2021-09-28 19:05 | 25 | 007:24 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUZETA PODRIDA | M21092800194 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 444 | 2021-09-28 | 11100 | keep | 0 | Sep | 2021 | 0.0075602 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-28 11:48 | 2021-09-29 17:30 | 50 | 029:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092800389 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1782 | 2021-09-28 | 89100 | keep | 0 | Sep | 2021 | 0.060686 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-28 12:00 | 2021-09-28 12:10 | 40 | 000:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21092800118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2021-09-28 | 400 | keep | 0 | Sep | 2021 | 0.00027244 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-28 12:10 | 2021-09-28 16:47 | 50 | 004:37 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | A21092800144 | New_Event | Bad Weather | Include | Include | Weather | 277 | 2021-09-28 | 13850 | keep | 0 | Sep | 2021 | 0.0094332 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-28 12:23 | 2021-09-28 12:24 | 4028 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21092800166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 4028 | keep | 0 | Sep | 2021 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2021-09-28 12:28 | 2021-09-28 12:29 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 4176 | keep | 0 | Sep | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
UTUADO | 2021-09-28 12:35 | 2021-09-28 12:55 | 1382 | 000:20 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA PARA REALIZAR OPERACIONES EN LINEA 8100 A PETICION CCE-PONCE | A21092800105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2021-09-28 | 27640 | keep | 0 | Sep | 2021 | 0.018825 | 0.00094127 | Sustained | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-28 12:35 | 2021-09-28 12:55 | 654 | 000:20 | T | LINEA DE TRANSMISION 38KV | RETIRAR CARGA A PETICION DE C.C.E PONCE | A21092800106 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2021-09-28 | 13080 | keep | 0 | Sep | 2021 | 0.0089087 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
FAJARDO | 2021-09-28 12:40 | 2021-09-28 12:41 | 970 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | R21092800172 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-28 | 970 | keep | 0 | Sep | 2021 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2021-09-28 12:41 | 2021-09-28 16:06 | 9 | 003:25 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 15 EN TRANSFORMADOR CONTAMINACION | R21092800239 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 205 | 2021-09-28 | 1845 | keep | 0 | Sep | 2021 | 0.0012566 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-09-28 12:55 | 2021-09-28 14:33 | 427 | 001:38 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092800000 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2021-09-28 | 41846 | keep | 0 | Sep | 2021 | 0.028501 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
UTUADO | 2021-09-28 12:55 | 2021-09-29 12:57 | 2 | 024:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21092700000 | New_Event | Bad Weather | Include | Include | Weather | 1442 | 2021-09-28 | 2884 | keep | 0 | Sep | 2021 | 0.0019643 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-09-28 12:55 | 2021-09-28 14:49 | 160 | 001:54 | P | ESTRUCTURA AVERIADA | SE ENDEREZO POSTE VIRADO | A21092800079 | New_Event | Defective Pole | Include | Include | Equipment | 114 | 2021-09-28 | 18240 | keep | 0 | Sep | 2021 | 0.012423 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2021-09-28 12:55 | 2021-09-28 15:06 | 10 | 002:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37.5 X 37.5 KVA | B21092800195 | New_Event | Service Transformer Failure | Include | Include | Equipment | 131 | 2021-09-28 | 1310 | keep | 0 | Sep | 2021 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-28 13:00 | 2021-09-28 18:03 | 50 | 005:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800144 | New_Event | Bad Weather | Include | Include | Weather | 303 | 2021-09-28 | 15150 | keep | 0 | Sep | 2021 | 0.010319 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-09-28 13:10 | 2021-09-28 17:16 | 45 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21092800170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-09-28 | 11070 | keep | 0 | Sep | 2021 | 0.0075397 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-09-28 13:10 | 2021-09-28 17:55 | 15 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800126 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2021-09-28 | 4275 | keep | 0 | Sep | 2021 | 0.0029117 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-28 13:13 | 2021-09-28 13:19 | 20 | 000:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21092800064 | New_Event | Bad Weather | Include | Include | Weather | 6 | 2021-09-28 | 120 | keep | 0 | Sep | 2021 | 8.1731e-05 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-28 13:13 | 2021-09-28 18:43 | 25 | 005:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21092800226 | New_Event | Wire Down | Include | Include | Equipment | 330 | 2021-09-28 | 8250 | keep | 0 | Sep | 2021 | 0.005619 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-28 13:14 | 2021-09-28 18:00 | 30 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800198 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2021-09-28 | 8580 | keep | 0 | Sep | 2021 | 0.0058438 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-28 13:33 | 2021-09-28 14:58 | 290 | 001:25 | P | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR DE PORTATIL 8 PARA CORREGIR PUNTO CALIENTE EN SALIDA DE MACHETES DE PORTATIL 8 | S21092800000 | New_Event | Defective Pole | Include | Include | Equipment | 85 | 2021-09-28 | 24650 | keep | 0 | Sep | 2021 | 0.016789 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
SAN JUAN | 2021-09-28 13:33 | 2021-09-28 14:58 | 251 | 001:25 | P | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR DE PORTATIL 8 PARA CORREGIR PUNTO CALIENTE EN MACHETES DE SALIDA PORTATIL 8 | S21092800000 | New_Event | Defective Pole | Include | Include | Equipment | 85 | 2021-09-28 | 21335 | keep | 0 | Sep | 2021 | 0.014531 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
SAN JUAN | 2021-09-28 13:33 | 2021-09-28 14:58 | 290 | 001:25 | P | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR DE PORTATIL 8 PARA CORREGIR PUNTO CALIENTE EN MACHETES DE SALIDA DE PORTATIL 8 | S21092800000 | New_Event | Defective Pole | Include | Include | Equipment | 85 | 2021-09-28 | 24650 | keep | 0 | Sep | 2021 | 0.016789 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
ARECIBO | 2021-09-28 14:10 | 2021-09-28 15:32 | 10 | 001:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA AVERIADO POR LO MISMO | A21092800000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 82 | 2021-09-28 | 820 | keep | 0 | Sep | 2021 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-28 14:11 | 2021-09-28 16:24 | 40 | 002:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2021-09-28 | 5320 | keep | 0 | Sep | 2021 | 0.0036234 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-28 14:11 | 2021-09-28 18:02 | 65 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2021-09-28 | 15015 | keep | 0 | Sep | 2021 | 0.010227 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-09-28 14:18 | 2021-09-28 15:39 | 75 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21092800054 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2021-09-28 | 6075 | keep | 0 | Sep | 2021 | 0.0041377 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-09-28 14:22 | 2021-09-28 19:53 | 50 | 005:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21092800239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2021-09-28 | 16550 | keep | 0 | Sep | 2021 | 0.011272 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-28 14:26 | 2021-09-28 14:42 | 867 | 000:16 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2021-09-28 | 13872 | keep | 0 | Sep | 2021 | 0.0094482 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
HUMACAO | 2021-09-28 14:31 | 2021-09-28 14:32 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092800252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 1467 | keep | 0 | Sep | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2021-09-28 14:33 | 2021-09-28 18:33 | 35 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S21092800527 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 240 | 2021-09-28 | 8400 | keep | 0 | Sep | 2021 | 0.0057212 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-09-28 14:36 | 2021-09-28 16:58 | 47 | 002:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21092800251 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-09-28 | 6674 | keep | 0 | Sep | 2021 | 0.0045456 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
ARECIBO | 2021-09-28 14:37 | 2021-09-29 09:56 | 25 | 019:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21092800140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1159 | 2021-09-28 | 28975 | keep | 0 | Sep | 2021 | 0.019735 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-09-28 14:44 | 2021-09-28 16:35 | 2565 | 001:51 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE | C21092800074 | New_Event | Wire Down | Include | Include | Equipment | 111 | 2021-09-28 | 284715 | keep | 0 | Sep | 2021 | 0.19392 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
BAYAMON | 2021-09-28 15:08 | 2021-09-29 12:50 | 30 | 021:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092900317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1302 | 2021-09-28 | 39060 | keep | 0 | Sep | 2021 | 0.026604 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-28 15:08 | 2021-09-29 12:50 | 60 | 021:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092900046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1302 | 2021-09-28 | 78120 | keep | 0 | Sep | 2021 | 0.053207 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-28 15:29 | 2021-09-29 11:16 | 6 | 019:47 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | C21092800273 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1187 | 2021-09-28 | 7122 | keep | 0 | Sep | 2021 | 0.0048508 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-09-28 15:32 | 2021-09-28 15:33 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 6 | keep | 0 | Sep | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-09-28 15:39 | 2021-09-29 13:13 | 40 | 021:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21092900105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1294 | 2021-09-28 | 51760 | keep | 0 | Sep | 2021 | 0.035254 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-28 15:54 | 2021-09-28 19:31 | 150 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 Y 2 X 50 EN CORTES DE LINEAS RETEZO LINEAS | C21092800302 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2021-09-28 | 32550 | keep | 0 | Sep | 2021 | 0.02217 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-09-28 16:10 | 2021-09-28 18:00 | 15 | 001:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21092800188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-09-28 | 1650 | keep | 0 | Sep | 2021 | 0.0011238 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-28 16:35 | 2021-09-28 18:43 | 70 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092800389 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2021-09-28 | 8960 | keep | 0 | Sep | 2021 | 0.0061026 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-09-28 17:00 | 2021-09-28 19:37 | 1 | 002:37 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA. RTU DOWN PERO MAS TARDE SUBIO Y SE CERRO POR CONTROL | B21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2021-09-28 | 157 | keep | 0 | Sep | 2021 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-28 17:10 | 2021-09-28 23:30 | 200 | 006:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21092800221 | New_Event | Wire Down | Include | Include | Equipment | 380 | 2021-09-28 | 76000 | keep | 0 | Sep | 2021 | 0.051763 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-09-28 17:10 | 2021-09-28 20:54 | 150 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800226 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-09-28 | 33600 | keep | 0 | Sep | 2021 | 0.022885 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-28 17:10 | 2021-09-28 18:50 | 10 | 001:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21092800240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2021-09-28 | 1000 | keep | 0 | Sep | 2021 | 0.0006811 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-09-28 17:12 | 2021-09-28 21:39 | 6 | 004:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO PORTAFUSIBLE QUEMADO | C21092800346 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2021-09-28 | 1602 | keep | 0 | Sep | 2021 | 0.0010911 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-09-28 17:12 | 2021-09-29 10:01 | 30 | 016:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21092800409 | New_Event | Bad Weather | Include | Include | Weather | 1009 | 2021-09-28 | 30270 | keep | 0 | Sep | 2021 | 0.020617 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-28 17:32 | 2021-09-28 20:07 | 30 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21092800415 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-09-28 | 4650 | keep | 0 | Sep | 2021 | 0.0031671 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-28 17:48 | 2021-09-28 19:06 | 50 | 001:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X65 EN CORTE DE LINEA. SE LEVANTO ALAMBRE PRIMARIO | P21092800301 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-09-28 | 3900 | keep | 0 | Sep | 2021 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-28 18:00 | 2021-09-28 20:34 | 40 | 002:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO AISLADOR | R21092800224 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 154 | 2021-09-28 | 6160 | keep | 0 | Sep | 2021 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-28 18:10 | 2021-09-28 19:30 | 100 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800265 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-09-28 | 8000 | keep | 0 | Sep | 2021 | 0.0054488 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-09-28 18:14 | 2021-09-28 22:05 | 11 | 003:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REEMPLAZO CAJA DE TRANSFORMADOR | R21092800225 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2021-09-28 | 2541 | keep | 0 | Sep | 2021 | 0.0017307 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-09-28 18:53 | 2021-09-28 18:54 | 4634 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21092800372 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-28 | 4634 | keep | 0 | Sep | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2021-09-28 18:58 | 2021-09-28 18:59 | 4634 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21092800372 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-28 | 4634 | keep | 0 | Sep | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2021-09-28 19:05 | 2021-09-28 19:06 | 4634 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21092800372 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-28 | 4634 | keep | 0 | Sep | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2021-09-28 19:06 | 2021-09-28 22:06 | 50 | 003:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21092800378 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 180 | 2021-09-28 | 9000 | keep | 0 | Sep | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-28 19:20 | 2021-09-28 21:00 | 15 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21092800259 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-09-28 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-28 19:59 | 2021-09-29 10:30 | 60 | 014:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092800473 | New_Event | Bad Weather | Include | Include | Weather | 871 | 2021-09-28 | 52260 | keep | 0 | Sep | 2021 | 0.035594 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-09-28 20:12 | 2021-09-28 20:24 | 4132 | 000:12 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR CON EL RR EN OFF. SE CONSULTO CON EL CCE Y AUTORIZARON A DARLE PRUEBA. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21092800367 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2021-09-28 | 49584 | keep | 0 | Sep | 2021 | 0.033771 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
ARECIBO | 2021-09-28 20:13 | 2021-09-28 22:00 | 500 | 001:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO DOS PUENTES ABIERTOS | A21092800037 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2021-09-28 | 53500 | keep | 0 | Sep | 2021 | 0.036439 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
BAYAMON | 2021-09-28 20:13 | 2021-09-28 20:46 | 15 | 000:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 10KVA POR UNO DE 37.5KVA FID 8328485 | B21092800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 33 | 2021-09-28 | 495 | keep | 0 | Sep | 2021 | 0.00033714 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-09-28 20:15 | 2021-09-29 12:07 | 9 | 015:52 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 15 EN TRANSFORMADOR CONTAMINACION | R21092800239 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 952 | 2021-09-28 | 8568 | keep | 0 | Sep | 2021 | 0.0058356 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-09-28 20:18 | 2021-09-28 21:09 | 10 | 000:51 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REPARARON DOS TERMINACIONES DE RISER A T-11 | B21092700546 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 51 | 2021-09-28 | 510 | keep | 0 | Sep | 2021 | 0.00034736 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-28 20:27 | 2021-09-28 20:28 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1909-08 CARGA DEL 1907-05 POR EL 1909-08 | S21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 2435 | keep | 0 | Sep | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-09-28 20:27 | 2021-09-28 20:28 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1907-05 | S21092800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-28 | 2956 | keep | 0 | Sep | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-09-28 20:46 | 2021-09-28 22:47 | 50 | 002:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21092800479 | New_Event | Wire Down | Include | Include | Equipment | 121 | 2021-09-28 | 6050 | keep | 0 | Sep | 2021 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-09-28 21:37 | 2021-09-28 22:37 | 125 | 001:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21092800291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-09-28 | 7500 | keep | 0 | Sep | 2021 | 0.0051082 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CANOVANAS | 2021-09-28 21:43 | 2021-09-28 23:24 | 10 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR REEMPLAZO CAJA DE TRANSFORMADOR | R21092800249 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2021-09-28 | 1010 | keep | 0 | Sep | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-28 21:46 | 2021-09-29 13:08 | 40 | 015:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092800415 | New_Event | Bad Weather | Include | Include | Weather | 922 | 2021-09-28 | 36880 | keep | 0 | Sep | 2021 | 0.025119 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-28 21:50 | 2021-09-29 11:49 | 60 | 013:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092800269 | New_Event | Bad Weather | Include | Include | Weather | 839 | 2021-09-28 | 50340 | keep | 0 | Sep | 2021 | 0.034286 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-28 22:00 | 2021-09-29 14:00 | 25 | 016:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21092800226 | Partial_restoration | Wire Down | Include | Include | Equipment | 960 | 2021-09-28 | 24000 | keep | 0 | Sep | 2021 | 0.016346 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-28 22:00 | 2021-09-29 10:00 | 70 | 012:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092800389 | Partial_restoration | Bad Weather | Include | Include | Weather | 720 | 2021-09-28 | 50400 | keep | 0 | Sep | 2021 | 0.034327 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-28 22:07 | 2021-09-29 11:55 | 178 | 013:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21092800463 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 828 | 2021-09-28 | 147384 | keep | 0 | Sep | 2021 | 0.10038 | 0.00012123 | Sustained | FALSE | TRUE | Not_TMED_Event | 178
HUMACAO | 2021-09-28 22:16 | 2021-09-29 15:10 | 10 | 016:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092800470 | New_Event | Bad Weather | Include | Include | Weather | 1014 | 2021-09-28 | 10140 | keep | 0 | Sep | 2021 | 0.0069063 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-28 22:26 | 2021-09-28 22:28 | 1863 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 3726 | keep | 0 | Sep | 2021 | 0.0025378 | 0.0012689 | Momentary | FALSE | TRUE | Not_TMED_Event | 1863
PONCE | 2021-09-28 22:26 | 2021-09-28 22:28 | 708 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 1416 | keep | 0 | Sep | 2021 | 0.00096443 | 0.00048222 | Momentary | FALSE | TRUE | Not_TMED_Event | 708
YAUCO | 2021-09-28 22:26 | 2021-09-28 22:28 | 502 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 1004 | keep | 0 | Sep | 2021 | 0.00068382 | 0.00034191 | Momentary | FALSE | TRUE | Not_TMED_Event | 502
YAUCO | 2021-09-28 22:26 | 2021-09-28 22:28 | 2747 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 5494 | keep | 0 | Sep | 2021 | 0.0037419 | 0.001871 | Momentary | FALSE | TRUE | Not_TMED_Event | 2747
YAUCO | 2021-09-28 22:26 | 2021-09-28 22:28 | 1587 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 3174 | keep | 0 | Sep | 2021 | 0.0021618 | 0.0010809 | Momentary | FALSE | TRUE | Not_TMED_Event | 1587
YAUCO | 2021-09-28 22:26 | 2021-09-28 22:28 | 2671 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 5342 | keep | 0 | Sep | 2021 | 0.0036384 | 0.0018192 | Momentary | FALSE | TRUE | Not_TMED_Event | 2671
YAUCO | 2021-09-28 22:26 | 2021-09-28 22:28 | 508 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 1016 | keep | 0 | Sep | 2021 | 0.00069199 | 0.000346 | Momentary | FALSE | TRUE | Not_TMED_Event | 508
YAUCO | 2021-09-28 22:26 | 2021-09-28 22:28 | 64 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21092800407 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-28 | 128 | keep | 0 | Sep | 2021 | 8.718e-05 | 4.359e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 64
CAGUAS | 2021-09-28 22:29 | 2021-09-29 12:09 | 150 | 013:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 Y 2 X 50 EN CORTES DE LINEAS RETEZO LINEAS | C21092800302 | Partial_restoration | Wire Down | Include | Include | Equipment | 820 | 2021-09-28 | 123000 | keep | 0 | Sep | 2021 | 0.083775 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-28 22:47 | 2021-09-28 22:50 | 1180 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR | B21092800479 | Additional_clients | Wire Down | Include | Include | Equipment | 3 | 2021-09-28 | 3540 | keep | 0 | Sep | 2021 | 0.0024111 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-28 22:50 | 2021-09-29 00:31 | 50 | 001:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21092800490 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 101 | 2021-09-28 | 5050 | keep | 0 | Sep | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-28 23:04 | 2021-09-29 08:52 | 50 | 009:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092800106 | New_Event | Bad Weather | Include | Include | Weather | 588 | 2021-09-28 | 29400 | keep | 0 | Sep | 2021 | 0.020024 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-28 23:19 | 2021-09-29 19:29 | 15 | 020:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A21092800304 | New_Event | Cutout Failure | Include | Include | Equipment | 1210 | 2021-09-28 | 18150 | keep | 0 | Sep | 2021 | 0.012362 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-28 23:35 | 2021-09-29 09:40 | 3 | 010:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092800305 | New_Event | Bad Weather | Include | Include | Weather | 605 | 2021-09-28 | 1815 | keep | 0 | Sep | 2021 | 0.0012362 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2021-09-28 23:48 | 2021-09-29 13:06 | 30 | 013:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21092800454 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 798 | 2021-09-28 | 23940 | keep | 0 | Sep | 2021 | 0.016305 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-28 23:54 | 2021-09-29 11:07 | 100 | 011:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21092800551 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 673 | 2021-09-28 | 67300 | keep | 0 | Sep | 2021 | 0.045838 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-29 00:07 | 2021-09-29 11:41 | 50 | 011:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21092800378 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 694 | 2021-09-29 | 34700 | keep | 0 | Sep | 2021 | 0.023634 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-29 00:15 | 2021-09-29 21:55 | 25 | 021:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S21092900017 | New_Event | Cutout Failure | Include | Include | Equipment | 1300 | 2021-09-29 | 32500 | keep | 0 | Sep | 2021 | 0.022136 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-29 00:31 | 2021-09-29 00:34 | 1180 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES | B21092900000 | Additional_clients | Wire Down | Include | Include | Equipment | 3 | 2021-09-29 | 3540 | keep | 0 | Sep | 2021 | 0.0024111 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-29 00:38 | 2021-09-29 02:33 | 1 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REMPLAZO CAJA | B21092900008 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2021-09-29 | 115 | keep | 0 | Sep | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-09-29 01:03 | 2021-09-29 08:52 | 60 | 007:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR | B21092900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2021-09-29 | 28140 | keep | 0 | Sep | 2021 | 0.019166 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-29 01:15 | 2021-09-29 08:15 | 34 | 007:00 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU - 13 REPARO TRAMO ENTRE EL SU - 13 Y EL T - 23 | C21092900003 | New_Event | UG Cable Fault | Include | Include | Equipment | 420 | 2021-09-29 | 14280 | keep | 0 | Sep | 2021 | 0.009726 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
ARECIBO | 2021-09-29 01:42 | 2021-09-29 09:56 | 7 | 008:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21092900003 | New_Event | Bad Weather | Include | Include | Weather | 494 | 2021-09-29 | 3458 | keep | 0 | Sep | 2021 | 0.0023552 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-09-29 02:08 | 2021-09-29 02:09 | 3003 | 000:01 | T | DESGANCHE | RECIERRE | R21092900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-29 | 3003 | keep | 0 | Sep | 2021 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2021-09-29 02:09 | 2021-09-29 17:19 | 50 | 015:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21092900099 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 910 | 2021-09-29 | 45500 | keep | 0 | Sep | 2021 | 0.03099 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-29 02:39 | 2021-09-29 02:40 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21092900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 990 | keep | 0 | Sep | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
PONCE | 2021-09-29 05:06 | 2021-09-29 05:07 | 778 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | P2109290014 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-29 | 778 | keep | 0 | Sep | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-09-29 05:06 | 2021-09-29 05:07 | 1746 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | P21092900014 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-29 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-09-29 05:06 | 2021-09-29 05:07 | 113 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE LLEVA LA CARGA DEL 5004-08 Y 5004-09 | P21092900014 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-29 | 113 | keep | 0 | Sep | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
PONCE | 2021-09-29 05:09 | 2021-09-29 05:10 | 778 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | P21092900015 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-29 | 778 | keep | 0 | Sep | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-09-29 05:09 | 2021-09-29 05:10 | 1746 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | P21092900015 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-29 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-09-29 05:09 | 2021-09-29 05:10 | 113 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE LLEVA LA CARGA DEL 5004-08 Y 5004-09 | P21092900015 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-09-29 | 113 | keep | 0 | Sep | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
BAYAMON | 2021-09-29 05:13 | 2021-09-29 14:51 | 80 | 009:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 80 EN RISER | S21092900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 578 | 2021-09-29 | 46240 | keep | 0 | Sep | 2021 | 0.031494 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-29 05:23 | 2021-09-29 15:23 | 15 | 010:00 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21092900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 600 | 2021-09-29 | 9000 | keep | 0 | Sep | 2021 | 0.0061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-09-29 05:43 | 2021-09-29 11:17 | 39 | 005:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | R21092900002 | New_Event |  |  | Include | Wildlife | 334 | 2021-09-29 | 13026 | keep | 0 | Sep | 2021 | 0.0088719 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
PONCE | 2021-09-29 05:52 | 2021-09-29 06:44 | 778 | 000:52 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | AVERIA EN MH 50 LA CARGA POR EL 5011-05 SE REMPLAZO INTERRUPTOR DE VACIO (VACUMM SWITCH) | P21092900021 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 52 | 2021-09-29 | 40456 | keep | 0 | Sep | 2021 | 0.027554 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-09-29 05:52 | 2021-09-29 06:44 | 1746 | 000:52 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | AVERIA EN MH 50 SE REAMPLZAO INTERRUPTOR DE VACIO (VACUUM SWITCH) | P21092900021 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 52 | 2021-09-29 | 90792 | keep | 0 | Sep | 2021 | 0.061838 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-09-29 05:52 | 2021-09-29 06:44 | 113 | 000:52 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | AVERIA EN MH 50 LLEVA LA CARGA DEL 5004-08 Y 5004-09 SE REMPLAZO DE INTERRUPTOR DE VACIO(VACUUM SWITCH) | P21092900021 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 52 | 2021-09-29 | 5876 | keep | 0 | Sep | 2021 | 0.0040021 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BAYAMON | 2021-09-29 06:14 | 2021-09-29 15:23 | 40 | 009:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21092800021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 549 | 2021-09-29 | 21960 | keep | 0 | Sep | 2021 | 0.014957 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-29 06:15 | 2021-09-29 13:26 | 10 | 007:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZO UNA CAJA AVERIADA EN EL FID:33971533 MARCA:CHNT 100AMP | A21092900006 | New_Event | Cutout Failure | Include | Include | Equipment | 431 | 2021-09-29 | 4310 | keep | 0 | Sep | 2021 | 0.0029355 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-29 06:18 | 2021-09-29 12:55 | 4 | 006:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092900019 | New_Event | Bad Weather | Include | Include | Weather | 397 | 2021-09-29 | 1588 | keep | 0 | Sep | 2021 | 0.0010816 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-09-29 06:20 | 2021-09-29 14:50 | 10 | 008:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1X10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | P21092900030 | New_Event | Bad Weather | Include | Include | Weather | 510 | 2021-09-29 | 5100 | keep | 0 | Sep | 2021 | 0.0034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-29 06:25 | 2021-09-30 00:36 | 30 | 018:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ENDEREZO POSTE VIRADO POR IMPACTO DE CAMION | B21092900030 | New_Event |  |  | Include | Wildlife | 1091 | 2021-09-29 | 32730 | keep | 0 | Sep | 2021 | 0.022292 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-09-29 06:29 | 2021-09-29 10:58 | 30 | 004:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A21092900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2021-09-29 | 8070 | keep | 0 | Sep | 2021 | 0.0054964 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-29 06:35 | 2021-09-29 10:01 | 7 | 003:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA AVERIADA EN TRANSFORMADOR EN EL FID:31408860 MARCA:CHNT 100AMP | A21092900008 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2021-09-29 | 1442 | keep | 0 | Sep | 2021 | 0.00098214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-09-29 06:43 | 2021-09-29 11:49 | 40 | 005:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2021-09-29 | 12240 | keep | 0 | Sep | 2021 | 0.0083366 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-29 06:46 | 2021-09-29 10:54 | 7 | 004:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21092900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2021-09-29 | 1736 | keep | 0 | Sep | 2021 | 0.0011824 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-09-29 06:58 | 2021-09-29 10:09 | 7 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZO 2 CAJAS AVERIADAS EN TRANSFORMADOR EN EL FID:33987458 MARCA:CHNT 100AMP | A21092900009 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2021-09-29 | 1337 | keep | 0 | Sep | 2021 | 0.00091062 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-29 07:00 | 2021-09-29 15:00 | 100 | 008:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21092900111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2021-09-29 | 48000 | keep | 0 | Sep | 2021 | 0.032693 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-29 07:00 | 2021-09-30 15:38 | 10 | 032:38 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21092900015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1958 | 2021-09-29 | 19580 | keep | 0 | Sep | 2021 | 0.013336 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-29 07:05 | 2021-09-29 13:19 | 50 | 006:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21092900017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2021-09-29 | 18700 | keep | 0 | Sep | 2021 | 0.012736 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-29 07:05 | 2021-09-29 14:51 | 40 | 007:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092900017 | New_Event | Bad Weather | Include | Include | Weather | 466 | 2021-09-29 | 18640 | keep | 0 | Sep | 2021 | 0.012696 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-29 07:12 | 2021-09-29 07:13 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 3025 | keep | 0 | Sep | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
ARECIBO | 2021-09-29 07:14 | 2021-09-29 10:57 | 60 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900011 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2021-09-29 | 13380 | keep | 0 | Sep | 2021 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-29 07:17 | 2021-09-29 14:20 | 12 | 007:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092900024 | New_Event | Bad Weather | Include | Include | Weather | 423 | 2021-09-29 | 5076 | keep | 0 | Sep | 2021 | 0.0034572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-09-29 07:17 | 2021-09-29 12:57 | 6 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900012 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2021-09-29 | 2040 | keep | 0 | Sep | 2021 | 0.0013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-09-29 07:20 | 2021-09-29 07:21 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21092900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-09-29 07:21 | 2021-09-29 08:02 | 80 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21092900073 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-09-29 | 3280 | keep | 0 | Sep | 2021 | 0.002234 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-29 07:22 | 2021-09-30 13:00 | 50 | 029:38 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21092900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1778 | 2021-09-29 | 88900 | keep | 0 | Sep | 2021 | 0.060549 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-29 07:27 | 2021-09-29 11:27 | 100 | 004:00 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-09-29 | 24000 | keep | 0 | Sep | 2021 | 0.016346 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-29 07:28 | 2021-09-29 13:12 | 2 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21092900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2021-09-29 | 688 | keep | 0 | Sep | 2021 | 0.00046859 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-09-29 07:29 | 2021-09-29 23:43 | 20 | 016:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 974 | 2021-09-29 | 19480 | keep | 0 | Sep | 2021 | 0.013268 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-29 07:35 | 2021-09-29 12:27 | 60 | 004:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900029 | New_Event | Bad Weather | Include | Include | Weather | 292 | 2021-09-29 | 17520 | keep | 0 | Sep | 2021 | 0.011933 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-09-29 07:42 | 2021-09-29 11:16 | 5 | 003:34 | P | OTRAS CAUSAS | 2 X 50 EN CORTE DE LINEA SE DEJO FUERA TRANSCLOSURE DEL REST. CHINO Y SE LE ORIENTO | R21092900006 | New_Event | Other Causes | Include | Include | Other | 214 | 2021-09-29 | 1070 | keep | 0 | Sep | 2021 | 0.00072877 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
ARECIBO | 2021-09-29 07:44 | 2021-09-29 10:39 | 10 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SEREPORTO CAUSA | A21092900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2021-09-29 | 1750 | keep | 0 | Sep | 2021 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-29 07:47 | 2021-09-29 07:48 | 619 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21092900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 619 | keep | 0 | Sep | 2021 | 0.0004216 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
HUMACAO | 2021-09-29 07:51 | 2021-09-29 12:31 | 18 | 004:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21092900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-09-29 | 5040 | keep | 0 | Sep | 2021 | 0.0034327 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
ARECIBO | 2021-09-29 08:01 | 2021-09-29 08:02 | 3431 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A21092900025 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-29 | 3431 | keep | 0 | Sep | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-09-29 08:02 | 2021-09-29 11:01 | 100 | 002:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA EN CORTE DE LINEA FID:30652110 MARCA:CHNT 100AMP | A21092900033 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 179 | 2021-09-29 | 17900 | keep | 0 | Sep | 2021 | 0.012192 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-09-29 08:04 | 2021-09-29 10:43 | 12 | 002:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21092900026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 159 | 2021-09-29 | 1908 | keep | 0 | Sep | 2021 | 0.0012995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-09-29 08:14 | 2021-09-29 16:37 | 100 | 008:23 | P | DESGANCHE | 1X100 EN CORTE DE LINEA POR DESGANCHE | P21092900046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2021-09-29 | 50300 | keep | 0 | Sep | 2021 | 0.034259 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-29 08:15 | 2021-09-29 09:57 | 1153 | 001:42 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO POR CONTINGENCIA | C21092900028 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 102 | 2021-09-29 | 117606 | keep | 0 | Sep | 2021 | 0.080101 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2021-09-29 08:15 | 2021-09-29 09:57 | 1709 | 001:42 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO POR CONTINGENCIA | C21092900029 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 102 | 2021-09-29 | 174318 | keep | 0 | Sep | 2021 | 0.11873 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2021-09-29 08:15 | 2021-09-29 09:57 | 1320 | 001:42 | T | RELEVO DE CARGA POR CONTINGENCIA | RELEVO POR CONTINGENCIA | C21092900030 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 102 | 2021-09-29 | 134640 | keep | 0 | Sep | 2021 | 0.091703 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
MAYAGÃœEZ | 2021-09-29 08:17 | 2021-09-29 12:40 | 8 | 004:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA POR LO MISMO | M21092900045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 263 | 2021-09-29 | 2104 | keep | 0 | Sep | 2021 | 0.001433 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-09-29 08:23 | 2021-09-29 11:17 | 1 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | C21092900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-09-29 | 174 | keep | 0 | Sep | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-29 08:35 | 2021-09-29 10:00 | 50 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900051 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-09-29 | 4250 | keep | 0 | Sep | 2021 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-29 08:40 | 2021-09-29 10:15 | 85 | 001:35 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTES DE LINEA | C21092900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-09-29 | 8075 | keep | 0 | Sep | 2021 | 0.0054998 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
AGUADILLA | 2021-09-29 08:51 | 2021-09-29 12:35 | 13 | 003:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21092900056 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2021-09-29 | 2912 | keep | 0 | Sep | 2021 | 0.0019833 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-09-29 08:52 | 2021-09-29 08:53 | 4381 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR MAL TIEMPO | M21092900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-29 | 4381 | keep | 0 | Sep | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-09-29 08:53 | 2021-09-29 15:38 | 50 | 006:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092800106 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 405 | 2021-09-29 | 20250 | keep | 0 | Sep | 2021 | 0.013792 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-29 08:58 | 2021-09-29 14:30 | 15 | 005:32 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 37.5 A 4160 POR LO MISMO | P21092900061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 332 | 2021-09-29 | 4980 | keep | 0 | Sep | 2021 | 0.0033919 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-29 09:00 | 2021-09-29 10:23 | 20 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER Y 1 X 10 NX EN T-21 | B21092600316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2021-09-29 | 1660 | keep | 0 | Sep | 2021 | 0.0011306 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-29 09:00 | 2021-09-29 11:15 | 80 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | P21092800339 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-09-29 | 10800 | keep | 0 | Sep | 2021 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-29 09:00 | 2021-09-29 10:00 | 75 | 001:00 | P | DESGANCHE | 1 X 80 EN CORE DE LINEA | P21092800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-09-29 | 4500 | keep | 0 | Sep | 2021 | 0.0030649 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-09-29 09:07 | 2021-09-29 21:19 | 40 | 012:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA 2 X 15 EN TRANSFORMADOR SE REEMPLAZARON DOS CAJAS QUEMADAS | B21092800073 | New_Event | Cutout Failure | Include | Include | Equipment | 732 | 2021-09-29 | 29280 | keep | 0 | Sep | 2021 | 0.019942 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-29 09:19 | 2021-09-29 10:57 | 32 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092900054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2021-09-29 | 3136 | keep | 0 | Sep | 2021 | 0.0021359 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
CAGUAS | 2021-09-29 09:19 | 2021-09-29 15:55 | 4 | 006:36 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE EN MALAS CONDICIONES | C21092900042 | New_Event | Defective Pole | Include | Include | Equipment | 396 | 2021-09-29 | 1584 | keep | 0 | Sep | 2021 | 0.0010789 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
CANOVANAS | 2021-09-29 09:22 | 2021-09-29 10:30 | 41 | 001:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R21092900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-09-29 | 2788 | keep | 0 | Sep | 2021 | 0.0018989 | 2.7925e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 41
CAGUAS | 2021-09-29 09:38 | 2021-09-29 14:26 | 80 | 004:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21092900047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2021-09-29 | 23040 | keep | 0 | Sep | 2021 | 0.015692 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-29 09:39 | 2021-09-29 12:57 | 2 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900055 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-09-29 | 396 | keep | 0 | Sep | 2021 | 0.00026971 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-09-29 09:44 | 2021-09-29 11:06 | 8 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21092900066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2021-09-29 | 656 | keep | 0 | Sep | 2021 | 0.0004468 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-09-29 09:45 | 2021-09-29 09:48 | 726 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-29 | 2178 | keep | 0 | Sep | 2021 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-09-29 09:45 | 2021-09-29 10:46 | 5 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21092500048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-09-29 | 305 | keep | 0 | Sep | 2021 | 0.00020773 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-29 09:47 | 2021-09-30 13:09 | 6 | 027:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEL TRANSFORMADOR AVERIADO | A21092900058 | New_Event | Cutout Failure | Include | Include | Equipment | 1642 | 2021-09-29 | 9852 | keep | 0 | Sep | 2021 | 0.0067102 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-09-29 09:49 | 2021-09-29 16:04 | 10 | 006:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA | R21092900040 | New_Event | Cutout Failure | Include | Include | Equipment | 375 | 2021-09-29 | 3750 | keep | 0 | Sep | 2021 | 0.0025541 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-29 09:52 | 2021-09-29 13:45 | 6 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900060 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-09-29 | 1398 | keep | 0 | Sep | 2021 | 0.00095217 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-09-29 09:54 | 2021-09-29 17:53 | 80 | 007:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21092900073 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 479 | 2021-09-29 | 38320 | keep | 0 | Sep | 2021 | 0.0261 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-29 09:56 | 2021-09-29 11:19 | 200 | 001:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A21092900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-09-29 | 16600 | keep | 0 | Sep | 2021 | 0.011306 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-29 09:57 | 2021-09-29 14:06 | 34 | 004:09 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU - 13 REPARO TRAMO ENTRE EL SU - 13 Y EL T - 23 | C21092900003 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 249 | 2021-09-29 | 8466 | keep | 0 | Sep | 2021 | 0.0057662 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-29 09:59 | 2021-09-29 18:15 | 30 | 008:16 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO PRIMARIA | S21092500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 496 | 2021-09-29 | 14880 | keep | 0 | Sep | 2021 | 0.010135 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-29 10:00 | 2021-09-29 12:44 | 25 | 002:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN RAISER AVE CRUZO LINEAS | P21092800414 | New_Event |  |  | Include | Wildlife | 164 | 2021-09-29 | 4100 | keep | 0 | Sep | 2021 | 0.0027925 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-09-29 10:00 | 2021-09-29 12:15 | 25 | 002:15 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN RAICER SE REPARO TERMINACION EN CABLE SOTERRADO | P21092800015 | New_Event | UG Cable Fault | Include | Include | Equipment | 135 | 2021-09-29 | 3375 | keep | 0 | Sep | 2021 | 0.0022987 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-29 10:16 | 2021-09-30 14:19 | 65 | 028:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA 1 X 50 EN OTRO CORTE DE LINEA SE REEMPLAZO CAJA Y SE LEVANTO CONDUCTOR | B21092900072 | New_Event | Wire Down | Include | Include | Equipment | 1683 | 2021-09-29 | 109395 | keep | 0 | Sep | 2021 | 0.074508 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
HUMACAO | 2021-09-29 10:19 | 2021-09-29 16:14 | 1 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21092900054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2021-09-29 | 355 | keep | 0 | Sep | 2021 | 0.00024179 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-29 10:20 | 2021-09-29 13:00 | 200 | 002:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | A21092900076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2021-09-29 | 32000 | keep | 0 | Sep | 2021 | 0.021795 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-09-29 10:22 | 2021-09-29 11:53 | 24 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21092900068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-09-29 | 2184 | keep | 0 | Sep | 2021 | 0.0014875 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
MAYAGÃœEZ | 2021-09-29 10:43 | 2021-09-30 10:45 | 12 | 024:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | M21092900087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1442 | 2021-09-29 | 17304 | keep | 0 | Sep | 2021 | 0.011786 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-09-29 10:44 | 2021-09-29 12:57 | 10 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900079 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-09-29 | 1330 | keep | 0 | Sep | 2021 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-29 10:46 | 2021-09-29 12:52 | 53 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092900075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-09-29 | 6678 | keep | 0 | Sep | 2021 | 0.0045484 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
GUAYAMA | 2021-09-29 10:52 | 2021-09-29 18:41 | 10 | 007:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON 80 PIES DE LINEA SECUNDARIA | P21092900088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 469 | 2021-09-29 | 4690 | keep | 0 | Sep | 2021 | 0.0031943 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-09-29 10:53 | 2021-09-29 17:55 | 35 | 007:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21092900084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 422 | 2021-09-29 | 14770 | keep | 0 | Sep | 2021 | 0.01006 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-09-29 10:59 | 2021-09-29 11:58 | 4 | 000:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900082 | New_Event | Bad Weather | Include | Include | Weather | 59 | 2021-09-29 | 236 | keep | 0 | Sep | 2021 | 0.00016074 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-09-29 11:03 | 2021-09-29 20:39 | 150 | 009:36 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA Y 2 X 40 EN OTRO CORTE DE LINEA | B21092900090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 576 | 2021-09-29 | 86400 | keep | 0 | Sep | 2021 | 0.058847 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-09-29 11:04 | 2021-09-29 16:23 | 50 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21092900091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2021-09-29 | 15950 | keep | 0 | Sep | 2021 | 0.010863 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-29 11:19 | 2021-09-29 18:00 | 75 | 006:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900091 | New_Event | Bad Weather | Include | Include | Weather | 401 | 2021-09-29 | 30075 | keep | 0 | Sep | 2021 | 0.020484 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-09-29 11:19 | 2021-09-30 18:50 | 7 | 031:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA MARCA:HOWARD SER:182458131H 4160/7200V 120/240V FID:33678131 POR LA MISMA CAPACIDAD | A21092900084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1891 | 2021-09-29 | 13237 | keep | 0 | Sep | 2021 | 0.0090157 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-09-29 11:19 | 2021-09-29 14:24 | 7 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21092900003 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2021-09-29 | 1295 | keep | 0 | Sep | 2021 | 0.00088202 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-09-29 11:20 | 2021-09-29 13:25 | 6 | 002:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | R21092900004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-09-29 | 750 | keep | 0 | Sep | 2021 | 0.00051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-09-29 11:28 | 2021-09-29 13:05 | 51 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-09-29 | 4947 | keep | 0 | Sep | 2021 | 0.0033694 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
CANOVANAS | 2021-09-29 11:31 | 2021-09-29 17:35 | 1 | 006:04 | P | OTRAS CAUSAS | 1 X 20 EN RISER SE HIZO BY PASS A LA MEDICION | R21092900057 | New_Event | Other Causes | Include | Include | Other | 364 | 2021-09-29 | 364 | keep | 0 | Sep | 2021 | 0.00024792 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-09-29 11:31 | 2021-09-29 15:51 | 50 | 004:20 | P | DESGANCHE | REPARTO DEL CARMEN CALLE 2 SE REALIZO DESGANCHE | P21092800124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2021-09-29 | 13000 | keep | 0 | Sep | 2021 | 0.0088542 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-09-29 11:37 | 2021-09-29 16:01 | 40 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | S21092900081 | New_Event | Wire Down | Include | Include | Equipment | 264 | 2021-09-29 | 10560 | keep | 0 | Sep | 2021 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-29 11:47 | 2021-09-29 17:11 | 5 | 005:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA POR CAMION | R21092900059 | New_Event |  |  | Include | Wildlife | 324 | 2021-09-29 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-09-29 11:56 | 2021-09-29 11:58 | 281 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-29 | 562 | keep | 0 | Sep | 2021 | 0.00038278 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-29 11:56 | 2021-09-29 11:58 | 1252 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-09-29 | 2504 | keep | 0 | Sep | 2021 | 0.0017055 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
PONCE | 2021-09-29 11:58 | 2021-09-29 11:59 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210929000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 449 | keep | 0 | Sep | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2021-09-29 11:59 | 2021-09-29 12:00 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2109290000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 112 | keep | 0 | Sep | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
HUMACAO | 2021-09-29 12:01 | 2021-09-29 15:51 | 100 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21092900064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2021-09-29 | 23000 | keep | 0 | Sep | 2021 | 0.015665 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-09-29 12:02 | 2021-09-29 12:03 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210929000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 449 | keep | 0 | Sep | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2021-09-29 12:07 | 2021-09-29 14:49 | 81 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R21092900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2021-09-29 | 13122 | keep | 0 | Sep | 2021 | 0.0089373 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
CANOVANAS | 2021-09-29 12:24 | 2021-09-29 18:16 | 6 | 005:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | R21092900065 | New_Event | Bad Weather | Include | Include | Weather | 352 | 2021-09-29 | 2112 | keep | 0 | Sep | 2021 | 0.0014385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-29 12:38 | 2021-09-29 12:39 | 3630 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21092900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-29 | 3630 | keep | 0 | Sep | 2021 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2021-09-29 12:39 | 2021-09-29 19:11 | 30 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900154 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 392 | 2021-09-29 | 11760 | keep | 0 | Sep | 2021 | 0.0080097 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-29 12:46 | 2021-09-29 13:11 | 100 | 000:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21092900068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-09-29 | 2500 | keep | 0 | Sep | 2021 | 0.0017027 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-29 12:55 | 2021-09-29 14:19 | 50 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900118 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-09-29 | 4200 | keep | 0 | Sep | 2021 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-29 12:57 | 2021-09-29 12:58 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 595 | keep | 0 | Sep | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-09-29 12:57 | 2021-09-29 12:58 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 51 | keep | 0 | Sep | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-09-29 12:57 | 2021-09-29 12:58 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 721 | keep | 0 | Sep | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-09-29 12:57 | 2021-09-29 12:58 | 3316 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | A21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 3316 | keep | 0 | Sep | 2021 | 0.0022585 | 0.0022585 | Momentary | FALSE | TRUE | Not_TMED_Event | 3316
UTUADO | 2021-09-29 12:57 | 2021-09-29 12:58 | 1241 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | A21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1241 | keep | 0 | Sep | 2021 | 0.00084524 | 0.00084524 | Momentary | FALSE | TRUE | Not_TMED_Event | 1241
UTUADO | 2021-09-29 12:57 | 2021-09-29 12:58 | 650 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | A21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 650 | keep | 0 | Sep | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | TRUE | Not_TMED_Event | 650
UTUADO | 2021-09-29 12:57 | 2021-09-29 12:58 | 1382 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | A21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-29 12:57 | 2021-09-29 12:58 | 654 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4700 | A21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 654 | keep | 0 | Sep | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
MAYAGÃœEZ | 2021-09-29 12:58 | 2021-09-29 18:20 | 12 | 005:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M21092800106 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 322 | 2021-09-29 | 3864 | keep | 0 | Sep | 2021 | 0.0026318 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-29 12:58 | 2021-09-29 13:13 | 10 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900079 | Partial_restoration | Bad Weather | Include | Include | Weather | 15 | 2021-09-29 | 150 | keep | 0 | Sep | 2021 | 0.00010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-29 12:58 | 2021-09-29 13:13 | 6 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900012 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2021-09-29 | 90 | keep | 0 | Sep | 2021 | 6.1299e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-09-29 12:58 | 2021-09-29 13:13 | 2 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21092700000 | Partial_restoration | Bad Weather | Include | Include | Weather | 15 | 2021-09-29 | 30 | keep | 0 | Sep | 2021 | 2.0433e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-29 12:59 | 2021-09-29 16:14 | 50 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900120 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2021-09-29 | 9750 | keep | 0 | Sep | 2021 | 0.0066407 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-29 13:01 | 2021-09-29 13:13 | 35 | 000:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CONVERTIDOR MAL TIEMPO | A21092900101 | New_Event | Bad Weather | Include | Include | Weather | 12 | 2021-09-29 | 420 | keep | 0 | Sep | 2021 | 0.00028606 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2021-09-29 13:05 | 2021-09-29 13:06 | 1863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1863 | keep | 0 | Sep | 2021 | 0.0012689 | 0.0012689 | Momentary | FALSE | TRUE | Not_TMED_Event | 1863
PONCE | 2021-09-29 13:05 | 2021-09-29 13:06 | 708 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 708 | keep | 0 | Sep | 2021 | 0.00048222 | 0.00048222 | Momentary | FALSE | TRUE | Not_TMED_Event | 708
YAUCO | 2021-09-29 13:05 | 2021-09-29 13:06 | 502 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 502 | keep | 0 | Sep | 2021 | 0.00034191 | 0.00034191 | Momentary | FALSE | TRUE | Not_TMED_Event | 502
YAUCO | 2021-09-29 13:05 | 2021-09-29 13:06 | 2747 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 2747 | keep | 0 | Sep | 2021 | 0.001871 | 0.001871 | Momentary | FALSE | TRUE | Not_TMED_Event | 2747
YAUCO | 2021-09-29 13:05 | 2021-09-29 13:06 | 1587 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1587 | keep | 0 | Sep | 2021 | 0.0010809 | 0.0010809 | Momentary | FALSE | TRUE | Not_TMED_Event | 1587
YAUCO | 2021-09-29 13:05 | 2021-09-29 13:06 | 2671 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 2671 | keep | 0 | Sep | 2021 | 0.0018192 | 0.0018192 | Momentary | FALSE | TRUE | Not_TMED_Event | 2671
YAUCO | 2021-09-29 13:05 | 2021-09-29 13:06 | 508 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 508 | keep | 0 | Sep | 2021 | 0.000346 | 0.000346 | Momentary | FALSE | TRUE | Not_TMED_Event | 508
YAUCO | 2021-09-29 13:05 | 2021-09-29 13:06 | 64 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 | P210929000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 64 | keep | 0 | Sep | 2021 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 64
HUMACAO | 2021-09-29 13:08 | 2021-09-29 19:44 | 5 | 006:36 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR REPARAR BAJANTE SECUNDARIO Y REGULARLO SUBIO TAP A AL B QUEDO 124/248V | C21092900072 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 396 | 2021-09-29 | 1980 | keep | 0 | Sep | 2021 | 0.0013486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-09-29 13:08 | 2021-09-29 14:44 | 50 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA RETESARON LINEAS | C21092900073 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2021-09-29 | 4800 | keep | 0 | Sep | 2021 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-29 13:08 | 2021-09-29 15:47 | 75 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21092900102 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2021-09-29 | 11925 | keep | 0 | Sep | 2021 | 0.0081221 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-09-29 13:11 | 2021-09-29 13:12 | 3699 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR | R21092900074 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-29 | 3699 | keep | 0 | Sep | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2021-09-29 13:12 | 2021-09-29 20:35 | 60 | 007:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA Y 14 X 25 EN RISER REEMPLAZO CAJA AVERIADA | R21092900079 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 443 | 2021-09-29 | 26580 | keep | 0 | Sep | 2021 | 0.018104 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-29 13:12 | 2021-09-29 18:25 | 100 | 005:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21092900068 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 313 | 2021-09-29 | 31300 | keep | 0 | Sep | 2021 | 0.021318 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-29 13:12 | 2021-09-29 13:13 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21092900124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 4176 | keep | 0 | Sep | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
UTUADO | 2021-09-29 13:13 | 2021-09-29 13:14 | 3316 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4700 | A21092900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 3316 | keep | 0 | Sep | 2021 | 0.0022585 | 0.0022585 | Momentary | FALSE | TRUE | Not_TMED_Event | 3316
UTUADO | 2021-09-29 13:13 | 2021-09-29 13:14 | 1241 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4700 | A21092900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1241 | keep | 0 | Sep | 2021 | 0.00084524 | 0.00084524 | Momentary | FALSE | TRUE | Not_TMED_Event | 1241
UTUADO | 2021-09-29 13:13 | 2021-09-29 13:14 | 650 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4700 | A21092900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 650 | keep | 0 | Sep | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | TRUE | Not_TMED_Event | 650
UTUADO | 2021-09-29 13:13 | 2021-09-29 13:14 | 1382 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4700 | A21092900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-09-29 13:13 | 2021-09-29 13:14 | 654 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4700 | A21092900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 654 | keep | 0 | Sep | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
BARRANQUITAS | 2021-09-29 13:13 | 2021-09-29 18:10 | 150 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21092900074 | New_Event | Wire Down | Include | Include | Equipment | 297 | 2021-09-29 | 44550 | keep | 0 | Sep | 2021 | 0.030343 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-29 13:13 | 2021-09-29 16:43 | 2 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21092900036 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-09-29 | 420 | keep | 0 | Sep | 2021 | 0.00028606 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
UTUADO | 2021-09-29 13:14 | 2021-09-29 13:17 | 10 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900079 | Partial_restoration | Bad Weather | Include | Include | Weather | 3 | 2021-09-29 | 30 | keep | 0 | Sep | 2021 | 2.0433e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-29 13:14 | 2021-09-30 09:35 | 2 | 020:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900055 | Partial_restoration | Bad Weather | Include | Include | Weather | 1221 | 2021-09-29 | 2442 | keep | 0 | Sep | 2021 | 0.0016632 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-29 13:14 | 2021-09-29 17:59 | 6 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900012 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2021-09-29 | 1710 | keep | 0 | Sep | 2021 | 0.0011647 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-09-29 13:14 | 2021-09-29 16:15 | 35 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CONVERTIDOR | A21092900101 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-09-29 | 6335 | keep | 0 | Sep | 2021 | 0.0043147 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2021-09-29 13:14 | 2021-09-29 14:53 | 2 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21092700000 | Partial_restoration | Bad Weather | Include | Include | Weather | 99 | 2021-09-29 | 198 | keep | 0 | Sep | 2021 | 0.00013486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-09-29 13:15 | 2021-09-29 19:30 | 50 | 006:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21092900104 | New_Event | Bad Weather | Include | Include | Weather | 375 | 2021-09-29 | 18750 | keep | 0 | Sep | 2021 | 0.012771 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-29 13:17 | 2021-09-29 17:39 | 80 | 004:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 30 EN CORTE DE LINEA REPARO LINEA ROTA | A21092800110 | New_Event | Wire Down | Include | Include | Equipment | 262 | 2021-09-29 | 20960 | keep | 0 | Sep | 2021 | 0.014276 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-29 13:18 | 2021-09-29 23:05 | 75 | 009:47 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21092900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 587 | 2021-09-29 | 44025 | keep | 0 | Sep | 2021 | 0.029985 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-29 13:22 | 2021-09-29 13:23 | 2858 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B21092900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-29 | 2858 | keep | 0 | Sep | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2021-09-29 13:23 | 2021-09-29 21:30 | 80 | 008:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21092900177 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 487 | 2021-09-29 | 38960 | keep | 0 | Sep | 2021 | 0.026535 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2021-09-29 13:25 | 2021-09-29 15:41 | 8 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE POR AVE | R21092900078 | New_Event |  |  | Include | Wildlife | 136 | 2021-09-29 | 1088 | keep | 0 | Sep | 2021 | 0.00074103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-29 13:30 | 2021-09-29 17:00 | 50 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900128 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-09-29 | 10500 | keep | 0 | Sep | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-29 13:32 | 2021-09-29 15:33 | 30 | 002:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21092900081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-09-29 | 3630 | keep | 0 | Sep | 2021 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-29 13:49 | 2021-09-29 14:10 | 1208 | 000:21 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE CAJA Y CRUCETAS PARTIDAS | S21092900112 | New_Event | Cutout Failure | Include | Include | Equipment | 21 | 2021-09-29 | 25368 | keep | 0 | Sep | 2021 | 0.017278 | 0.00082276 | Sustained | FALSE | FALSE | Not_TMED_Event | 1208
BAYAMON | 2021-09-29 13:51 | 2021-09-30 10:24 | 29 | 020:33 | P | NO SE REPORTO CAUSA | 1 X 25 SMU EN SU | B21092900136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1233 | 2021-09-29 | 35757 | keep | 0 | Sep | 2021 | 0.024354 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
UTUADO | 2021-09-29 13:51 | 2021-09-29 14:20 | 20 | 000:29 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA REMPLAZO PARARRAYO | A21092900108 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 29 | 2021-09-29 | 580 | keep | 0 | Sep | 2021 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-29 13:53 | 2021-09-29 17:37 | 75 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092900109 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-09-29 | 16800 | keep | 0 | Sep | 2021 | 0.011442 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1339 | keep | 0 | Sep | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 470 | keep | 0 | Sep | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | TRUE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 2483 | keep | 0 | Sep | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | TRUE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 2190 | keep | 0 | Sep | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | TRUE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 3006 | keep | 0 | Sep | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | TRUE | Not_TMED_Event | 179
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 107 | keep | 0 | Sep | 2021 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1666 | keep | 0 | Sep | 2021 | 0.0011347 | 0.0011347 | Momentary | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 4387 | keep | 0 | Sep | 2021 | 0.002988 | 0.002988 | Momentary | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 3147 | keep | 0 | Sep | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-09-29 13:54 | 2021-09-29 13:55 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 4304 | keep | 0 | Sep | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
BARRANQUITAS | 2021-09-29 13:57 | 2021-09-29 13:58 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
PONCE | 2021-09-29 14:00 | 2021-09-29 14:09 | 520 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RR EN OOF. SE CONSULTO CON EL PERSONAL EN EL AREA TRABAJANDO Y CERTIFICARON QUE NO HABIAN SIDO ELLOS. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21092900124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-09-29 | 4680 | keep | 0 | Sep | 2021 | 0.0031875 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
ARECIBO | 2021-09-29 14:00 | 2021-09-29 17:54 | 50 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21092900168 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2021-09-29 | 11700 | keep | 0 | Sep | 2021 | 0.0079688 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-29 14:00 | 2021-09-29 20:01 | 10 | 006:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092900089 | New_Event | Bad Weather | Include | Include | Weather | 361 | 2021-09-29 | 3610 | keep | 0 | Sep | 2021 | 0.0024588 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-29 14:06 | 2021-09-29 14:11 | 1153 | 000:05 | T | CABLE SOTERRADO AVERIADO | DISPARO | C21092900090 | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2021-09-29 | 5765 | keep | 0 | Sep | 2021 | 0.0039265 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 863 | keep | 0 | Sep | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 309 | keep | 0 | Sep | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 176 | keep | 0 | Sep | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-29 14:07 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRRE LINEA 2000 | M21092900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-29 | 974 | keep | 0 | Sep | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
MAYAGÃœEZ | 2021-09-29 14:06 | 2021-09-30 13:47 | 40 | 023:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21092900139 | New_Event | Wire Down | Include | Include | Equipment | 1421 | 2021-09-29 | 56840 | keep | 0 | Sep | 2021 | 0.038713 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-29 14:07 | 2021-09-29 18:00 | 50 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1X80 EN CORTE DE LINEA POR MAL TIEMPO | P21092900128 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-09-29 | 11650 | keep | 0 | Sep | 2021 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-29 14:09 | 2021-10-01 18:02 | 80 | 051:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900141 | New_Event | Bad Weather | Include | Include | Weather | 3113 | 2021-09-29 | 249040 | keep | 0 | Sep | 2021 | 0.16962 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-09-29 14:11 | 2021-09-29 20:28 | 34 | 006:17 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU - 13 REPARO TRAMO ENTRE EL SU - 13 Y EL T - 23 | C21092900003 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 377 | 2021-09-29 | 12818 | keep | 0 | Sep | 2021 | 0.0087303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-09-29 14:14 | 2021-09-29 18:04 | 653 | 003:50 | T | MAL TIEMPO/RAYOS/WET ASH | PERSONAL DE CAMPO PATRULLO ALIMENTADOR ENCONTRANDO DESGANCHE MASIVO Y EL MAL TIEMPO. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21092900131 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-09-29 | 150190 | keep | 0 | Sep | 2021 | 0.10229 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
MAYAGÃœEZ | 2021-09-29 14:14 | 2021-09-30 10:10 | 8 | 019:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092900143 | New_Event | Bad Weather | Include | Include | Weather | 1196 | 2021-09-29 | 9568 | keep | 0 | Sep | 2021 | 0.0065167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-29 14:14 | 2021-09-29 20:47 | 2791 | 006:33 | S | PROTECCION DEFECTUOSA | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR PORQUE INTERRUPTOR 8701-03 NO OPERO Y PASO AVERIA | A21092900000 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-09-29 | 1096863 | keep | 0 | Sep | 2021 | 0.74707 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-09-29 14:14 | 2021-09-29 20:47 | 1464 | 006:33 | S | PROTECCION DEFECTUOSA | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR PORQUE INTERRUPTOR 8701-03 NO OPERO Y PASO AVERIA | A21092900000 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-09-29 | 575352 | keep | 0 | Sep | 2021 | 0.39187 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-09-29 14:14 | 2021-09-29 20:47 | 759 | 006:33 | S | PROTECCION DEFECTUOSA | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR PORQUE INTERRUPTOR 8701-03 NO OPERO Y PASO AVERIA | A21092900000 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-09-29 | 298287 | keep | 0 | Sep | 2021 | 0.20316 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-09-29 14:14 | 2021-09-29 20:47 | 1500 | 006:33 | S | PROTECCION DEFECTUOSA | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR PORQUE INTERRUPTOR 8701-03 NO OPERO Y PASO AVERIA | A21092900000 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-09-29 | 589500 | keep | 0 | Sep | 2021 | 0.40151 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
BARRANQUITAS | 2021-09-29 14:17 | 2021-09-29 19:03 | 8 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21092900092 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2021-09-29 | 2288 | keep | 0 | Sep | 2021 | 0.0015583 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-29 14:18 | 2021-09-30 20:05 | 20 | 029:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21092900146 | New_Event | Wire Down | Include | Include | Equipment | 1787 | 2021-09-29 | 35740 | keep | 0 | Sep | 2021 | 0.024342 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-29 14:19 | 2021-09-29 14:22 | 80 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M21092900148 | Additional_clients | Bad Weather | Include | Include | Weather | 3 | 2021-09-29 | 240 | keep | 0 | Sep | 2021 | 0.00016346 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-29 14:21 | 2021-09-29 19:36 | 50 | 005:15 | P | HERRAJE ROTO O PODRIDO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | A21092900172 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 315 | 2021-09-29 | 15750 | keep | 0 | Sep | 2021 | 0.010727 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-29 14:21 | 2021-09-29 20:38 | 10 | 006:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REMPLAZO CAJA QUEMADA | A21092900117 | New_Event | Cutout Failure | Include | Include | Equipment | 377 | 2021-09-29 | 3770 | keep | 0 | Sep | 2021 | 0.0025677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-29 14:21 | 2021-09-29 18:00 | 30 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092900116 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-09-29 | 6570 | keep | 0 | Sep | 2021 | 0.0044748 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-29 14:22 | 2021-09-29 15:23 | 15 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21092800404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-09-29 | 915 | keep | 0 | Sep | 2021 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-29 14:22 | 2021-09-29 23:07 | 75 | 008:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | M21092900149 | New_Event | Wire Down | Include | Include | Equipment | 525 | 2021-09-29 | 39375 | keep | 0 | Sep | 2021 | 0.026818 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-29 14:22 | 2021-09-30 11:10 | 50 | 020:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900118 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1248 | 2021-09-29 | 62400 | keep | 0 | Sep | 2021 | 0.0425 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-09-29 14:22 | 2021-09-29 17:07 | 20 | 002:45 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR | A21092900119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-09-29 | 3300 | keep | 0 | Sep | 2021 | 0.0022476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-29 14:23 | 2021-09-29 17:41 | 1863 | 003:18 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 500 DESDE CANAS TC | P21092900138 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-09-29 | 368874 | keep | 0 | Sep | 2021 | 0.25124 | 0.0012689 | Sustained | FALSE | TRUE | Not_TMED_Event | 1863
PONCE | 2021-09-29 14:23 | 2021-09-29 17:41 | 708 | 003:18 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 500 DESDE CANAS TC | P21092900138 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-09-29 | 140184 | keep | 0 | Sep | 2021 | 0.095479 | 0.00048222 | Sustained | FALSE | TRUE | Not_TMED_Event | 708
YAUCO | 2021-09-29 14:23 | 2021-09-29 15:42 | 502 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500. SE PUSO EN SERVICIO DESDE COSTA SUR | P21092900146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-29 | 39658 | keep | 0 | Sep | 2021 | 0.027011 | 0.00034191 | Sustained | TRUE | TRUE | Not_TMED_Event | 502
YAUCO | 2021-09-29 14:23 | 2021-09-29 15:42 | 2747 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500. SE PUSO EN SERVICIO DESDE COSTA SUR | P21092900146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-29 | 217013 | keep | 0 | Sep | 2021 | 0.14781 | 0.001871 | Sustained | TRUE | TRUE | Not_TMED_Event | 2747
YAUCO | 2021-09-29 14:23 | 2021-09-29 15:42 | 1587 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500. SE PUSO EN SERVICIO DESDE COSTA SUR | P21092900146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-29 | 125373 | keep | 0 | Sep | 2021 | 0.085391 | 0.0010809 | Sustained | TRUE | TRUE | Not_TMED_Event | 1587
YAUCO | 2021-09-29 14:23 | 2021-09-29 15:42 | 2671 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500. SE PUSO EN SERVICIO DESDE COSTA SUR | P21092900146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-29 | 211009 | keep | 0 | Sep | 2021 | 0.14372 | 0.0018192 | Sustained | TRUE | TRUE | Not_TMED_Event | 2671
YAUCO | 2021-09-29 14:23 | 2021-09-29 15:42 | 508 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500. SE PUSO EN SERVICIO DESDE COSTA SUR | P21092900146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-29 | 40132 | keep | 0 | Sep | 2021 | 0.027334 | 0.000346 | Sustained | TRUE | TRUE | Not_TMED_Event | 508
YAUCO | 2021-09-29 14:23 | 2021-09-29 15:42 | 64 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500. SE PUSO EN SERVICIO DESDE COSTA SUR | P21092900146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-09-29 | 5056 | keep | 0 | Sep | 2021 | 0.0034436 | 4.359e-05 | Sustained | TRUE | TRUE | Not_TMED_Event | 64
UTUADO | 2021-09-29 14:24 | 2021-09-29 14:29 | 669 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21092900120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-29 | 3345 | keep | 0 | Sep | 2021 | 0.0022783 | 0.00045565 | Momentary | FALSE | FALSE | Not_TMED_Event | 669
ARECIBO | 2021-09-29 14:24 | 2021-09-29 17:36 | 15 | 003:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TOMAS | A21092900000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 192 | 2021-09-29 | 2880 | keep | 0 | Sep | 2021 | 0.0019616 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-09-29 14:33 | 2021-09-30 12:00 | 7 | 021:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21092900155 | New_Event | Bad Weather | Include | Include | Weather | 1287 | 2021-09-29 | 9009 | keep | 0 | Sep | 2021 | 0.006136 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-09-29 14:34 | 2021-09-29 16:07 | 60 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900156 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2021-09-29 | 5580 | keep | 0 | Sep | 2021 | 0.0038005 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-29 14:50 | 2021-09-30 12:15 | 12 | 021:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 50 KVA | M21093000087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1285 | 2021-09-29 | 15420 | keep | 0 | Sep | 2021 | 0.010502 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-29 14:52 | 2021-09-30 10:00 | 40 | 019:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900166 | New_Event | Bad Weather | Include | Include | Weather | 1148 | 2021-09-29 | 45920 | keep | 0 | Sep | 2021 | 0.031276 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-29 15:00 | 2021-09-30 11:16 | 6 | 020:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21092900151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1216 | 2021-09-29 | 7296 | keep | 0 | Sep | 2021 | 0.0049693 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-09-29 15:00 | 2021-09-29 21:02 | 120 | 006:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65, 2 X 40, 1 X 30 EN CORTE DE LINEA Y 4 X 15 EN TRANSFORMADOR | A21092900137 | New_Event | Bad Weather | Include | Include | Weather | 362 | 2021-09-29 | 43440 | keep | 0 | Sep | 2021 | 0.029587 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
YAUCO | 2021-09-29 15:07 | 2021-09-29 19:13 | 100 | 004:06 | P | DESGANCHE | 1X100 EN CORTE DE LINEA POR DESGANCHE Y MAL TIEMPO | P21092900166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-09-29 | 24600 | keep | 0 | Sep | 2021 | 0.016755 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-29 15:10 | 2021-09-29 17:00 | 5 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092900171 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-09-29 | 550 | keep | 0 | Sep | 2021 | 0.0003746 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-09-29 15:10 | 2021-09-29 18:00 | 75 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900172 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2021-09-29 | 12750 | keep | 0 | Sep | 2021 | 0.008684 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-09-29 15:16 | 2021-09-29 17:58 | 10 | 002:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SECUNDARIA ABIERTA | C21092900106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 162 | 2021-09-29 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-29 15:16 | 2021-09-29 17:41 | 40 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21092900107 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-09-29 | 5800 | keep | 0 | Sep | 2021 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 350 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 1400 | keep | 0 | Sep | 2021 | 0.00095353 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 215 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 860 | keep | 0 | Sep | 2021 | 0.00058574 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 262 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 1048 | keep | 0 | Sep | 2021 | 0.00071379 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 90 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 360 | keep | 0 | Sep | 2021 | 0.00024519 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:19 | 76 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-09-29 | 76 | keep | 0 | Sep | 2021 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:19 | 626 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-09-29 | 626 | keep | 0 | Sep | 2021 | 0.00042637 | 0.00042637 | Momentary | FALSE | FALSE | Not_TMED_Event | 626
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 3708 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 14832 | keep | 0 | Sep | 2021 | 0.010102 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 24 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 96 | keep | 0 | Sep | 2021 | 6.5385e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-09-29 15:18 | 2021-09-29 15:22 | 1 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VIADUCTO | S21092900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-09-29 | 4 | keep | 0 | Sep | 2021 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-09-29 15:22 | 2021-09-29 20:00 | 300 | 004:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 1 X 80 Y 1 X 65 EN CORTES DE LINEAS DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | M21092900180 | New_Event | Bad Weather | Include | Include | Weather | 278 | 2021-09-29 | 83400 | keep | 0 | Sep | 2021 | 0.056803 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-09-29 15:27 | 2021-09-30 12:18 | 75 | 020:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21092900183 | New_Event | Bad Weather | Include | Include | Weather | 1251 | 2021-09-29 | 93825 | keep | 0 | Sep | 2021 | 0.063904 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-29 15:30 | 2021-09-29 22:25 | 40 | 006:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A21092900146 | New_Event |  |  | Include | Wildlife | 415 | 2021-09-29 | 16600 | keep | 0 | Sep | 2021 | 0.011306 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-29 15:30 | 2021-09-29 17:57 | 5 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO CAUSA | C21092900109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-09-29 | 735 | keep | 0 | Sep | 2021 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-09-29 15:33 | 2021-09-29 15:34 | 2299 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092900112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 2299 | keep | 0 | Sep | 2021 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2021-09-29 15:34 | 2021-09-29 17:49 | 160 | 002:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21092900114 | New_Event |  |  | Include | Wildlife | 135 | 2021-09-29 | 21600 | keep | 0 | Sep | 2021 | 0.014712 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
SAN JUAN | 2021-09-29 15:35 | 2021-09-29 15:36 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-09-29 15:36 | 2021-09-29 17:56 | 50 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21092900136 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 140 | 2021-09-29 | 7000 | keep | 0 | Sep | 2021 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-29 15:40 | 2021-09-29 20:53 | 40 | 005:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 SMU 20 DE 80 AMP EN EL SU 4CA REEMPLAZO AISLADOR EN PROVICIONAL AEREO | R21092900095 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 313 | 2021-09-29 | 12520 | keep | 0 | Sep | 2021 | 0.0085273 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-09-29 15:41 | 2021-09-30 11:34 | 10 | 019:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900153 | New_Event | Bad Weather | Include | Include | Weather | 1193 | 2021-09-29 | 11930 | keep | 0 | Sep | 2021 | 0.0081255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-29 15:42 | 2021-09-29 16:06 | 3041 | 000:24 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS SE CERRO INTERRUPTOR | M21092900188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2021-09-29 | 72984 | keep | 0 | Sep | 2021 | 0.049709 | 0.0020712 | Sustained | FALSE | TRUE | Not_TMED_Event | 3041
HUMACAO | 2021-09-29 15:52 | 2021-09-29 17:49 | 6 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21092900115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2021-09-29 | 702 | keep | 0 | Sep | 2021 | 0.00047813 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-09-29 15:53 | 2021-09-29 21:01 | 80 | 005:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 40 EN RISER | C21092900116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2021-09-29 | 24640 | keep | 0 | Sep | 2021 | 0.016782 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-29 15:54 | 2021-09-29 17:38 | 1 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21092800157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-09-29 | 104 | keep | 0 | Sep | 2021 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-09-29 16:00 | 2021-09-30 09:20 | 10 | 017:20 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21092900158 | New_Event | Bad Weather | Include | Include | Weather | 1040 | 2021-09-29 | 10400 | keep | 0 | Sep | 2021 | 0.0070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-29 16:06 | 2021-09-29 18:19 | 40 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21092900118 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-09-29 | 5320 | keep | 0 | Sep | 2021 | 0.0036234 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-29 16:06 | 2021-09-29 22:11 | 15 | 006:05 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | C21092900118 | New_Event | Service Transformer Failure | Include | Include | Equipment | 365 | 2021-09-29 | 5475 | keep | 0 | Sep | 2021 | 0.003729 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-29 16:09 | 2021-09-29 16:10 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 2608 | keep | 0 | Sep | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BARRANQUITAS | 2021-09-29 16:18 | 2021-09-29 19:38 | 80 | 003:20 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21092900121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-09-29 | 16000 | keep | 0 | Sep | 2021 | 0.010898 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-29 16:20 | 2021-09-29 18:26 | 4 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR DIGGER EXCAVANDO AVERIO TOMA | R21092900100 | New_Event |  |  | Include | Wildlife | 126 | 2021-09-29 | 504 | keep | 0 | Sep | 2021 | 0.00034327 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-09-29 16:20 | 2021-09-29 17:00 | 50 | 000:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900160 | New_Event | Bad Weather | Include | Include | Weather | 40 | 2021-09-29 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-29 16:25 | 2021-09-29 16:26 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 95% DEL 1717-02 | B21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 5961 | keep | 0 | Sep | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-09-29 16:25 | 2021-09-29 16:26 | 850 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO 95% DEL 1717-02 | B21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 850 | keep | 0 | Sep | 2021 | 0.00057893 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
SAN JUAN | 2021-09-29 16:26 | 2021-09-29 16:30 | 20 | 000:04 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRANSFORMADOR | S21092900140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-29 | 80 | keep | 0 | Sep | 2021 | 5.4488e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-29 16:26 | 2021-09-30 13:00 | 60 | 020:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA CRUZADA | A21092900163 | New_Event | Wire Down | Include | Include | Equipment | 1234 | 2021-09-29 | 74040 | keep | 0 | Sep | 2021 | 0.050428 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-29 16:33 | 2021-09-29 21:24 | 80 | 004:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 50 EN CORTES DE LINEA LLUVIA | C21092900126 | New_Event | Bad Weather | Include | Include | Weather | 291 | 2021-09-29 | 23280 | keep | 0 | Sep | 2021 | 0.015856 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
FAJARDO | 2021-09-29 16:48 | 2021-09-30 14:08 | 30 | 021:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 25KVA | R21092900105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1280 | 2021-09-29 | 38400 | keep | 0 | Sep | 2021 | 0.026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-09-29 17:15 | 2021-09-29 22:18 | 50 | 005:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21092900174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2021-09-29 | 15150 | keep | 0 | Sep | 2021 | 0.010319 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-29 17:30 | 2021-09-29 17:34 | 5290 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR. PERSONAL DEL DESPACO REALIZANDO PRUEBA CON FUSIBLE EN EVENTO S21092800084 | S21092900000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2021-09-29 | 21160 | keep | 0 | Sep | 2021 | 0.014412 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-09-29 17:30 | 2021-09-29 17:34 | 207 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR. PERSONAL DEL DESPACO REALIZANDO PRUEBA CON FUSIBLE EN EVENTO S21092800084 | S21092900000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2021-09-29 | 828 | keep | 0 | Sep | 2021 | 0.00056395 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
MAYAGÃœEZ | 2021-09-29 17:33 | 2021-09-30 11:20 | 80 | 017:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900219 | New_Event | Bad Weather | Include | Include | Weather | 1067 | 2021-09-29 | 85360 | keep | 0 | Sep | 2021 | 0.058138 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-29 17:37 | 2021-09-29 18:35 | 100 | 000:58 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA L SE SACO RAMA SOBRE LINEA | P21092900197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-09-29 | 5800 | keep | 0 | Sep | 2021 | 0.0039504 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-29 17:40 | 2021-09-29 21:53 | 50 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21092900175 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-09-29 | 12650 | keep | 0 | Sep | 2021 | 0.0086159 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-29 17:52 | 2021-09-30 11:08 | 11 | 017:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO. | P21092900201 | New_Event | Bad Weather | Include | Include | Weather | 1036 | 2021-09-29 | 11396 | keep | 0 | Sep | 2021 | 0.0077618 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2021-09-29 17:56 | 2021-09-29 21:00 | 30 | 003:04 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR | A21092900153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-09-29 | 5520 | keep | 0 | Sep | 2021 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-09-29 18:08 | 2021-09-29 18:09 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092900204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 732 | keep | 0 | Sep | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
ARECIBO | 2021-09-29 18:22 | 2021-09-29 18:50 | 20 | 000:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092900186 | New_Event | Bad Weather | Include | Include | Weather | 28 | 2021-09-29 | 560 | keep | 0 | Sep | 2021 | 0.00038141 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-29 18:28 | 2021-09-30 17:35 | 50 | 023:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21092900229 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1387 | 2021-09-29 | 69350 | keep | 0 | Sep | 2021 | 0.047234 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-29 18:36 | 2021-09-29 18:37 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE PORTATIL #10 | P21092900207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 1979 | keep | 0 | Sep | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-09-29 18:36 | 2021-09-29 18:37 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE PORTATIL #10 | P21092900207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 5069 | keep | 0 | Sep | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-09-29 18:36 | 2021-09-29 18:37 | 5063 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE PORTATIL #10 | P21092900207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 5063 | keep | 0 | Sep | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
ARECIBO | 2021-09-29 18:39 | 2021-09-29 19:56 | 400 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | A21092900191 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-09-29 | 30800 | keep | 0 | Sep | 2021 | 0.020978 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
MAYAGÃœEZ | 2021-09-29 18:49 | 2021-09-30 12:10 | 100 | 017:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21092900236 | New_Event | Bad Weather | Include | Include | Weather | 1041 | 2021-09-29 | 104100 | keep | 0 | Sep | 2021 | 0.070902 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-29 18:51 | 2021-09-29 22:20 | 30 | 003:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21092900186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2021-09-29 | 6270 | keep | 0 | Sep | 2021 | 0.0042705 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-29 18:53 | 2021-09-29 20:03 | 15 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X15 EN TRANSFORMADOR POR AVE | P21092900209 | New_Event |  |  | Include | Wildlife | 70 | 2021-09-29 | 1050 | keep | 0 | Sep | 2021 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2021-09-29 19:05 | 2021-10-01 10:27 | 20 | 039:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P21092900215 | New_Event | Bad Weather | Include | Include | Weather | 2362 | 2021-09-29 | 47240 | keep | 0 | Sep | 2021 | 0.032175 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-29 19:05 | 2021-09-29 22:34 | 4664 | 003:29 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 6012-03 QUE ESTA LLEVANDO LA CARGA DEL 6012-02. SE REMPLAZO CAJA EN EL TRONCAL DEL ALIMENTADOR 6012-03 | M21092900323 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2021-09-29 | 974776 | keep | 0 | Sep | 2021 | 0.66392 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-09-29 19:05 | 2021-09-29 22:34 | 2067 | 003:29 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN EL TRONCAL DEL ALIMENTADOR EN EL FID:23555536 MARCA: CHNT 100AMP Y SE LE INSTALO FUSIBLE DE 20AMP EN LA MISMA. LUEGO DE ESTO SE CERRO EL INTERRUPTOR | M21092900323 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2021-09-29 | 432003 | keep | 0 | Sep | 2021 | 0.29424 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-09-29 19:05 | 2021-09-30 10:05 | 25 | 015:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900247 | New_Event | Bad Weather | Include | Include | Weather | 900 | 2021-09-29 | 22500 | keep | 0 | Sep | 2021 | 0.015325 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-09-29 19:28 | 2021-09-30 11:01 | 50 | 015:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21092900147 | New_Event | Wire Down | Include | Include | Equipment | 933 | 2021-09-29 | 46650 | keep | 0 | Sep | 2021 | 0.031773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-09-29 19:39 | 2021-09-29 21:29 | 10 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21092900117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-09-29 | 1100 | keep | 0 | Sep | 2021 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-29 19:45 | 2021-09-29 20:02 | 20 | 000:17 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE ELIMINO PARARRAYO | B21092900195 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 17 | 2021-09-29 | 340 | keep | 0 | Sep | 2021 | 0.00023157 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-29 19:59 | 2021-09-30 16:54 | 4 | 020:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21092900201 | New_Event | Bad Weather | Include | Include | Weather | 1255 | 2021-09-29 | 5020 | keep | 0 | Sep | 2021 | 0.0034191 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2021-09-29 20:18 | 2021-09-30 18:21 | 40 | 022:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21092900255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1323 | 2021-09-29 | 52920 | keep | 0 | Sep | 2021 | 0.036044 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-29 20:19 | 2021-09-30 22:06 | 30 | 025:47 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-7 CONSTRUYO PROVISIONAL T-48 @ T-49 | C21092900154 | New_Event | UG Cable Fault | Include | Include | Equipment | 1547 | 2021-09-29 | 46410 | keep | 0 | Sep | 2021 | 0.03161 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-09-29 20:23 | 2021-09-29 20:24 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21092900119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 2722 | keep | 0 | Sep | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
CAGUAS | 2021-09-29 20:24 | 2021-09-30 13:07 | 40 | 016:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21092900156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1003 | 2021-09-29 | 40120 | keep | 0 | Sep | 2021 | 0.027326 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-09-29 20:34 | 2021-09-30 10:30 | 20 | 013:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21092900204 | New_Event | Bad Weather | Include | Include | Weather | 836 | 2021-09-29 | 16720 | keep | 0 | Sep | 2021 | 0.011388 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-09-29 20:39 | 2021-09-29 22:46 | 280 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21092900124 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2021-09-29 | 35560 | keep | 0 | Sep | 2021 | 0.02422 | 0.00019071 | Sustained | FALSE | TRUE | Not_TMED_Event | 280
ARECIBO | 2021-09-29 20:47 | 2021-09-29 22:16 | 1200 | 001:29 | P | DESGANCHE | 3 PUENTES ABIERTOS EN EL TRONCAL DEL ALIMENTADOR SE VA A ABRIR EL INTERRUPTOR PARA REPARAR | A21092900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-09-29 | 106800 | keep | 0 | Sep | 2021 | 0.072741 | 0.00081731 | Sustained | FALSE | FALSE | Not_TMED_Event | 1200
HUMACAO | 2021-09-29 20:48 | 2021-09-30 11:00 | 10 | 014:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | C21092900158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 852 | 2021-09-29 | 8520 | keep | 0 | Sep | 2021 | 0.0058029 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-29 21:05 | 2021-09-30 15:00 | 70 | 017:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21093000105 | New_Event | Bad Weather | Include | Include | Weather | 1075 | 2021-09-29 | 75250 | keep | 0 | Sep | 2021 | 0.051252 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-09-29 21:32 | 2021-09-30 10:22 | 10 | 012:50 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R21092900129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 770 | 2021-09-29 | 7700 | keep | 0 | Sep | 2021 | 0.0052444 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-29 21:33 | 2021-09-30 21:50 | 50 | 024:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21093000317 | New_Event | Bad Weather | Include | Include | Weather | 1457 | 2021-09-29 | 72850 | keep | 0 | Sep | 2021 | 0.049618 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-29 21:39 | 2021-09-30 14:20 | 60 | 016:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21092900213 | New_Event | Bad Weather | Include | Include | Weather | 1001 | 2021-09-29 | 60060 | keep | 0 | Sep | 2021 | 0.040907 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-29 21:44 | 2021-09-30 11:44 | 6 | 014:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | R21092900130 | New_Event | Secondary Wire Down | Include | Include | Equipment | 840 | 2021-09-29 | 5040 | keep | 0 | Sep | 2021 | 0.0034327 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-09-29 21:55 | 2021-09-30 10:19 | 300 | 012:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER DE ENTRADA Y 3 X 100 EN RISER DE SALIDA POR MAL TIEMPO | P21092900224 | New_Event | Bad Weather | Include | Include | Weather | 744 | 2021-09-29 | 223200 | keep | 0 | Sep | 2021 | 0.15202 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-09-29 22:16 | 2021-09-29 23:44 | 1464 | 001:28 | T | DESGANCHE | SE ABRIO EL INTERRUPTOR 8701-03 QUE ESTA LLEVANDO LA CARGA DEL 8701-02 PARA REALIZAR DESGANCHE DE BAMBUAS CAIDAS SOBRE EL TRONCAL DEL ALIMENTADOR Y CERRAR 3 PUENTES PRIMARIOS ABIERTOS. EN EL LUGAR DE LA AVERIA PASAN JUNTOS LOS DOS ALIMENTADORES. | A21092900218 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-09-29 | 128832 | keep | 0 | Sep | 2021 | 0.087747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-29 22:16 | 2021-09-29 23:44 | 759 | 001:28 | T | DESGANCHE | SE ABRIO EL INTERRUPTOR 8701-03 QUE ESTA LLEVANDO LA CARGA DEL 8701-02 PARA REPARAR PUENTES PRIMARIOS ABIERTOS EN EL TRONCAL DEL ALIMENTADOR 8701-02. | A21092900218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-09-29 | 66792 | keep | 0 | Sep | 2021 | 0.045492 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2021-09-29 22:39 | 2021-09-30 01:52 | 100 | 003:13 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTE DE LINEAS | B21092900220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2021-09-29 | 19300 | keep | 0 | Sep | 2021 | 0.013145 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-29 22:47 | 2021-09-30 15:38 | 40 | 016:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21092900163 | New_Event | Bad Weather | Include | Include | Weather | 1011 | 2021-09-29 | 40440 | keep | 0 | Sep | 2021 | 0.027543 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-09-29 23:05 | 2021-09-30 13:13 | 30 | 014:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P21092900231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 848 | 2021-09-29 | 25440 | keep | 0 | Sep | 2021 | 0.017327 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-29 23:57 | 2021-09-29 23:58 | 900 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21092900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-29 | 900 | keep | 0 | Sep | 2021 | 0.00061299 | 0.00061299 | Momentary | FALSE | FALSE | Not_TMED_Event | 900
BAYAMON | 2021-09-30 00:33 | 2021-09-30 10:13 | 50 | 009:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21093000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 580 | 2021-09-30 | 29000 | keep | 0 | Sep | 2021 | 0.019752 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-30 00:52 | 2021-09-30 11:44 | 80 | 010:52 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21093000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 652 | 2021-09-30 | 52160 | keep | 0 | Sep | 2021 | 0.035526 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-09-30 00:53 | 2021-09-30 15:38 | 50 | 014:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C21093000016 | New_Event | Bad Weather | Include | Include | Weather | 885 | 2021-09-30 | 44250 | keep | 0 | Sep | 2021 | 0.030138 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-30 01:04 | 2021-09-30 01:05 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 5252 | keep | 0 | Sep | 2021 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
VEGA BAJA | 2021-09-30 01:43 | 2021-09-30 09:49 | 12 | 008:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21093000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 486 | 2021-09-30 | 5832 | keep | 0 | Sep | 2021 | 0.0039721 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-09-30 03:02 | 2021-09-30 10:04 | 26 | 007:02 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 20 EN PROVISIONAL SE REMPLAZO TERMINACION EN PM | B21093000008 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 422 | 2021-09-30 | 10972 | keep | 0 | Sep | 2021 | 0.007473 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
FAJARDO | 2021-09-30 03:09 | 2021-09-30 03:10 | 240 | 000:01 | T | OTRAS CAUSAS | RECIERRE | R21093000001 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-30 | 240 | keep | 0 | Sep | 2021 | 0.00016346 | 0.00016346 | Momentary | FALSE | FALSE | Not_TMED_Event | 240
FAJARDO | 2021-09-30 03:10 | 2021-09-30 16:34 | 1 | 013:24 | P | OTRAS CAUSAS | 3 X 50 Y 3 X 20 EN CORTE DE LINEA Y RISER PROBLEMA DEL CLIENTE | R21093000040 | 1st_after_momentary | Other Causes | Include | Include | Other | 804 | 2021-09-30 | 804 | keep | 0 | Sep | 2021 | 0.0005476 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-30 03:51 | 2021-09-30 03:52 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21093000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 1287 | keep | 0 | Sep | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
ARECIBO | 2021-09-30 04:52 | 2021-09-30 14:59 | 9 | 010:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21093000001 | New_Event | Bad Weather | Include | Include | Weather | 607 | 2021-09-30 | 5463 | keep | 0 | Sep | 2021 | 0.0037208 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-09-30 05:07 | 2021-09-30 05:08 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21093000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 2324 | keep | 0 | Sep | 2021 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
SAN JUAN | 2021-09-30 05:41 | 2021-09-30 18:52 | 15 | 013:11 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21093000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 791 | 2021-09-30 | 11865 | keep | 0 | Sep | 2021 | 0.0080812 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-30 06:16 | 2021-09-30 12:07 | 100 | 005:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN RISER CONTAMINACION | C21093000010 | New_Event |  |  | Include | Wildlife | 351 | 2021-09-30 | 35100 | keep | 0 | Sep | 2021 | 0.023906 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-09-30 06:35 | 2021-09-30 10:19 | 7 | 003:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21093000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2021-09-30 | 1568 | keep | 0 | Sep | 2021 | 0.001068 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-09-30 06:37 | 2021-09-30 13:28 | 50 | 006:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21092100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 411 | 2021-09-30 | 20550 | keep | 0 | Sep | 2021 | 0.013997 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-30 06:44 | 2021-09-30 16:20 | 25 | 009:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO VACUUM SWITCH AVERIADO EN MH-50 | P21092900228 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 576 | 2021-09-30 | 14400 | keep | 0 | Sep | 2021 | 0.0098078 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-09-30 06:59 | 2021-10-01 18:37 | 40 | 035:38 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y 2 X 20 EN RISER SE REEMPLAZO PARARRAYO | S21093000017 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2138 | 2021-09-30 | 85520 | keep | 0 | Sep | 2021 | 0.058247 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-09-30 07:17 | 2021-09-30 11:49 | 100 | 004:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21093000005 | New_Event |  |  | Include | Wildlife | 272 | 2021-09-30 | 27200 | keep | 0 | Sep | 2021 | 0.018526 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-30 07:22 | 2021-09-30 20:07 | 50 | 012:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21093000018 | New_Event | Bad Weather | Include | Include | Weather | 765 | 2021-09-30 | 38250 | keep | 0 | Sep | 2021 | 0.026052 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-09-30 07:22 | 2021-09-30 21:23 | 100 | 014:01 | P | DESGANCHE | 2X50 EN CORTE DE LINEA POR DESGANCHE | P21093000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 841 | 2021-09-30 | 84100 | keep | 0 | Sep | 2021 | 0.05728 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-30 07:44 | 2021-09-30 15:50 | 100 | 008:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21090000024 | New_Event | Bad Weather | Include | Include | Weather | 486 | 2021-09-30 | 48600 | keep | 0 | Sep | 2021 | 0.033101 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-30 07:46 | 2021-09-30 15:41 | 50 | 007:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21093000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2021-09-30 | 23750 | keep | 0 | Sep | 2021 | 0.016176 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-30 07:54 | 2021-09-30 12:50 | 65 | 004:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21093000022 | New_Event |  |  | Include | Wildlife | 296 | 2021-09-30 | 19240 | keep | 0 | Sep | 2021 | 0.013104 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-09-30 07:55 | 2021-09-30 11:48 | 50 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21093000034 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-09-30 | 11650 | keep | 0 | Sep | 2021 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-30 07:57 | 2021-09-30 09:43 | 10 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21093000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-09-30 | 1060 | keep | 0 | Sep | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-30 08:14 | 2021-09-30 11:05 | 80 | 002:51 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21093000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-09-30 | 13680 | keep | 0 | Sep | 2021 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-30 08:33 | 2021-09-30 15:00 | 50 | 006:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN SU-1 Y SE REPORTA AVERIA POR CHANGO | S21093000006 | New_Event |  |  | Include | Wildlife | 387 | 2021-09-30 | 19350 | keep | 0 | Sep | 2021 | 0.013179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-09-30 08:43 | 2021-09-30 09:55 | 30 | 001:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | R21093000013 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2021-09-30 | 2160 | keep | 0 | Sep | 2021 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-30 08:46 | 2021-09-30 11:17 | 1 | 002:31 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21093000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-09-30 | 151 | keep | 0 | Sep | 2021 | 0.00010285 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-30 08:53 | 2021-09-30 09:15 | 1 | 000:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN RISER REPARO NEUTRAL | C21093000033 | New_Event | Wire Down | Include | Include | Equipment | 22 | 2021-09-30 | 22 | keep | 0 | Sep | 2021 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-30 08:57 | 2021-09-30 08:58 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21093000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 1894 | keep | 0 | Sep | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
UTUADO | 2021-09-30 09:06 | 2021-09-30 13:30 | 150 | 004:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA Y 2 X 30 EN OTRO CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21093000018 | New_Event | Bad Weather | Include | Include | Weather | 264 | 2021-09-30 | 39600 | keep | 0 | Sep | 2021 | 0.026971 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-09-30 09:09 | 2021-09-30 14:45 | 30 | 005:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21093000035 | New_Event | Bad Weather | Include | Include | Weather | 336 | 2021-09-30 | 10080 | keep | 0 | Sep | 2021 | 0.0068654 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-30 09:19 | 2021-09-30 13:56 | 200 | 004:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE CON GATO | R21093000021 | New_Event |  |  | Include | Wildlife | 277 | 2021-09-30 | 55400 | keep | 0 | Sep | 2021 | 0.037733 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-30 09:37 | 2021-09-30 16:28 | 10 | 006:51 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21093000039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 411 | 2021-09-30 | 4110 | keep | 0 | Sep | 2021 | 0.0027993 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-30 09:38 | 2021-09-30 09:39 | 3316 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA | A21093000020 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-30 | 3316 | keep | 0 | Sep | 2021 | 0.0022585 | 0.0022585 | Momentary | FALSE | FALSE | Not_TMED_Event | 3316
SAN JUAN | 2021-09-30 09:39 | 2021-09-30 16:12 | 20 | 006:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21093000015 | New_Event | Wire Down | Include | Include | Equipment | 393 | 2021-09-30 | 7860 | keep | 0 | Sep | 2021 | 0.0053534 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-09-30 09:40 | 2021-09-30 15:04 | 79 | 005:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETORNO NEUTRAL ZAFADO | R21093000024 | New_Event | Wire Down | Include | Include | Equipment | 324 | 2021-09-30 | 25596 | keep | 0 | Sep | 2021 | 0.017433 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
BAYAMON | 2021-09-30 09:42 | 2021-10-01 19:30 | 15 | 033:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 X 25 KVA FID 8330378 | B21093000038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2028 | 2021-09-30 | 30420 | keep | 0 | Sep | 2021 | 0.020719 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-30 09:46 | 2021-10-01 11:04 | 15 | 025:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR Y SE REMPLAZO CAJA | S21093000017 | New_Event | Cutout Failure | Include | Include | Equipment | 1518 | 2021-09-30 | 22770 | keep | 0 | Sep | 2021 | 0.015509 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-30 10:24 | 2021-09-30 12:16 | 1 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21093000025 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2021-09-30 | 112 | keep | 0 | Sep | 2021 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-09-30 10:27 | 2021-09-30 10:39 | 3316 | 000:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA PRIMARIA ENERGIZADA EN EL PISO | A21093000027 | New_Event | Wire Down | Include | Include | Equipment | 12 | 2021-09-30 | 39792 | keep | 0 | Sep | 2021 | 0.027102 | 0.0022585 | Sustained | FALSE | TRUE | Not_TMED_Event | 3316
UTUADO | 2021-09-30 10:30 | 2021-09-30 16:20 | 6 | 005:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21093000028 | New_Event | Bad Weather | Include | Include | Weather | 350 | 2021-09-30 | 2100 | keep | 0 | Sep | 2021 | 0.0014303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-09-30 10:33 | 2021-09-30 15:25 | 50 | 004:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | P21093000038 | New_Event |  |  | Include | Wildlife | 292 | 2021-09-30 | 14600 | keep | 0 | Sep | 2021 | 0.009944 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-09-30 10:39 | 2021-09-30 11:59 | 160 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEAS PRIMARIAS ROTAS Y TRANSFORMADOR QUEMADO SE ABRIO PUENTES PARA SECCIONALIZAR | A21093000035 | Partial_restoration | Wire Down | Include | Include | Equipment | 80 | 2021-09-30 | 12800 | keep | 0 | Sep | 2021 | 0.008718 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-30 10:45 | 2021-09-30 12:26 | 13 | 001:41 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE DE LINEA A CAJA | S21092900173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-09-30 | 1313 | keep | 0 | Sep | 2021 | 0.00089428 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
HUMACAO | 2021-09-30 10:48 | 2021-09-30 13:14 | 10 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21093000058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-09-30 | 1460 | keep | 0 | Sep | 2021 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-09-30 11:03 | 2021-09-30 16:20 | 65 | 005:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21093000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2021-09-30 | 20605 | keep | 0 | Sep | 2021 | 0.014034 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-09-30 11:16 | 2021-09-30 15:53 | 100 | 004:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZARON DISCOS QUEMADOS | R21093000031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 277 | 2021-09-30 | 27700 | keep | 0 | Sep | 2021 | 0.018866 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-30 11:17 | 2021-09-30 16:00 | 50 | 004:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21093000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-09-30 | 14150 | keep | 0 | Sep | 2021 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-30 11:22 | 2021-09-30 17:59 | 40 | 006:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | B21093000049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 397 | 2021-09-30 | 15880 | keep | 0 | Sep | 2021 | 0.010816 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-30 11:25 | 2021-09-30 13:04 | 80 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21093000078 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-09-30 | 7920 | keep | 0 | Sep | 2021 | 0.0053943 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-09-30 11:30 | 2021-09-30 13:36 | 1 | 002:06 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETAS PARTIDAS Y CAJAS PRIMARIAS | A21093000011 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 126 | 2021-09-30 | 126 | keep | 0 | Sep | 2021 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-30 11:51 | 2021-09-30 12:38 | 7 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21093000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-09-30 | 329 | keep | 0 | Sep | 2021 | 0.00022408 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-09-30 11:56 | 2021-09-30 12:52 | 3 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | S21093000014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-09-30 | 168 | keep | 0 | Sep | 2021 | 0.00011442 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-09-30 11:57 | 2021-09-30 19:36 | 45 | 007:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA Y BAJANTE | C21093000077 | New_Event | Cutout Failure | Include | Include | Equipment | 459 | 2021-09-30 | 20655 | keep | 0 | Sep | 2021 | 0.014068 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-09-30 11:59 | 2021-09-30 14:45 | 10 | 002:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA 8320V 120/240V SER:91A370763 FID:33806997 | A21093000043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 166 | 2021-09-30 | 1660 | keep | 0 | Sep | 2021 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-30 12:07 | 2021-09-30 19:00 | 4 | 006:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | R21093000035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 413 | 2021-09-30 | 1652 | keep | 0 | Sep | 2021 | 0.0011252 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-09-30 12:16 | 2021-10-01 16:20 | 40 | 028:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21093000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1684 | 2021-09-30 | 67360 | keep | 0 | Sep | 2021 | 0.045879 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-30 12:25 | 2021-09-30 14:28 | 50 | 002:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21093000042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-09-30 | 6150 | keep | 0 | Sep | 2021 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-30 12:30 | 2021-09-30 13:55 | 10 | 001:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA A 2.4KV AVERIADO POR UNO DE IGUAL CAPACIDAD | P21093000066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2021-09-30 | 850 | keep | 0 | Sep | 2021 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-30 12:32 | 2021-09-30 12:33 | 50 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21093000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 50 | keep | 0 | Sep | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-30 12:37 | 2021-09-30 22:04 | 45 | 009:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO PUENTE HACIA CAJA PRIMARIA | R21093000037 | New_Event | Wire Down | Include | Include | Equipment | 567 | 2021-09-30 | 25515 | keep | 0 | Sep | 2021 | 0.017378 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-09-30 12:54 | 2021-09-30 16:54 | 60 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M21093000103 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-09-30 | 14400 | keep | 0 | Sep | 2021 | 0.0098078 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-30 13:04 | 2021-09-30 14:28 | 10 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21093000046 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-09-30 | 840 | keep | 0 | Sep | 2021 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-30 13:14 | 2021-09-30 17:49 | 25 | 004:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA POR IGUAL CAPACIDAD | S21092900108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 275 | 2021-09-30 | 6875 | keep | 0 | Sep | 2021 | 0.0046825 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-09-30 13:14 | 2021-09-30 15:26 | 10 | 002:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 50KVA POR 50KVA | B21093000064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 132 | 2021-09-30 | 1320 | keep | 0 | Sep | 2021 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-30 13:30 | 2021-09-30 15:08 | 25 | 001:38 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21092500208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-09-30 | 2450 | keep | 0 | Sep | 2021 | 0.0016687 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-30 13:37 | 2021-09-30 14:35 | 3 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21093000088 | New_Event |  |  | Include | Wildlife | 58 | 2021-09-30 | 174 | keep | 0 | Sep | 2021 | 0.00011851 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-09-30 13:38 | 2021-09-30 18:21 | 1 | 004:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | R21093000045 | New_Event | Wire Down | Include | Include | Equipment | 283 | 2021-09-30 | 283 | keep | 0 | Sep | 2021 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-09-30 13:49 | 2021-09-30 17:04 | 33 | 003:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR LQUEMADO DE 37.5 X 37.5KVA | R21093000047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2021-09-30 | 6435 | keep | 0 | Sep | 2021 | 0.0043828 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2021-09-30 13:54 | 2021-09-30 17:13 | 65 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA PRIMARIA | S21093000055 | New_Event | Wire Down | Include | Include | Equipment | 199 | 2021-09-30 | 12935 | keep | 0 | Sep | 2021 | 0.00881 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-09-30 13:54 | 2021-09-30 21:17 | 3006 | 007:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 443 | 2021-09-30 | 1331658 | keep | 0 | Sep | 2021 | 0.90699 | 0.0020474 | Sustained | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-09-30 13:54 | 2021-09-30 21:17 | 179 | 007:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 443 | 2021-09-30 | 79297 | keep | 0 | Sep | 2021 | 0.054009 | 0.00012192 | Sustained | FALSE | TRUE | Not_TMED_Event | 179
VEGA BAJA | 2021-09-30 13:59 | 2021-09-30 14:04 | 4027 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-30 | 20135 | keep | 0 | Sep | 2021 | 0.013714 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2021-09-30 13:59 | 2021-09-30 14:04 | 2468 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-30 | 12340 | keep | 0 | Sep | 2021 | 0.0084047 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2021-09-30 13:59 | 2021-09-30 14:04 | 1494 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-30 | 7470 | keep | 0 | Sep | 2021 | 0.0050878 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-09-30 13:59 | 2021-09-30 14:04 | 1310 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-30 | 6550 | keep | 0 | Sep | 2021 | 0.0044612 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2021-09-30 13:59 | 2021-09-30 14:04 | 215 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-30 | 1075 | keep | 0 | Sep | 2021 | 0.00073218 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-09-30 13:59 | 2021-09-30 14:04 | 1 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-09-30 | 5 | keep | 0 | Sep | 2021 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-30 14:05 | 2021-09-30 14:06 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21093000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 3871 | keep | 0 | Sep | 2021 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2021-09-30 14:25 | 2021-10-01 17:09 | 10 | 026:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21093000072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1604 | 2021-09-30 | 16040 | keep | 0 | Sep | 2021 | 0.010925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-30 14:29 | 2021-09-30 20:13 | 1 | 005:44 | P | PARARRAYOS DEFECTUOSO | REMPLAZO 3 PARARRAYOS HIZO BY PASS A LA MEDICION Y CERRO PUENTE | C21093000098 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 344 | 2021-09-30 | 344 | keep | 0 | Sep | 2021 | 0.0002343 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-30 14:34 | 2021-09-30 22:25 | 40 | 007:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21093000087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2021-09-30 | 18840 | keep | 0 | Sep | 2021 | 0.012832 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-09-30 14:34 | 2021-09-30 21:08 | 30 | 006:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | A21093000053 | New_Event | Wire Down | Include | Include | Equipment | 394 | 2021-09-30 | 11820 | keep | 0 | Sep | 2021 | 0.0080505 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-30 14:35 | 2021-09-30 14:36 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21093000205 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-09-30 | 1702 | keep | 0 | Sep | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-30 14:36 | 2021-09-30 15:48 | 3 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21093000088 | 1st_after_momentary |  |  | Include | Wildlife | 72 | 2021-09-30 | 216 | keep | 0 | Sep | 2021 | 0.00014712 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2021-09-30 14:41 | 2021-09-30 17:45 | 400 | 003:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PARTIDO | M21093000131 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2021-09-30 | 73600 | keep | 0 | Sep | 2021 | 0.050129 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2021-09-30 14:55 | 2021-09-30 17:10 | 4 | 002:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21093000135 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2021-09-30 | 540 | keep | 0 | Sep | 2021 | 0.00036779 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-09-30 14:55 | 2021-09-30 17:08 | 50 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21093000061 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-09-30 | 6650 | keep | 0 | Sep | 2021 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-30 15:03 | 2021-09-30 15:04 | 6197 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21093000220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 6197 | keep | 0 | Sep | 2021 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
AGUADILLA | 2021-09-30 15:05 | 2021-09-30 18:45 | 100 | 003:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | M21093000139 | New_Event | Wire Down | Include | Include | Equipment | 220 | 2021-09-30 | 22000 | keep | 0 | Sep | 2021 | 0.014984 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-30 15:14 | 2021-09-30 16:45 | 10 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO NEUTRAL | S21092900132 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-09-30 | 910 | keep | 0 | Sep | 2021 | 0.0006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-30 15:16 | 2021-09-30 17:42 | 40 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21093000114 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-09-30 | 5840 | keep | 0 | Sep | 2021 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-09-30 15:16 | 2021-09-30 17:07 | 100 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIAS | C21093000115 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2021-09-30 | 11100 | keep | 0 | Sep | 2021 | 0.0075602 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-30 15:19 | 2021-09-30 17:34 | 65 | 002:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA 1 X 50 EN OTRO CORTE DE LINEA SE REEMPLAZO CAJA Y SE LEVANTO CONDUCTOR | B21092900072 | Partial_restoration | Wire Down | Include | Include | Equipment | 135 | 2021-09-30 | 8775 | keep | 0 | Sep | 2021 | 0.0059766 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-30 15:24 | 2021-10-01 15:01 | 65 | 023:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 65 EN CORTE DE LINEA DISTINTO | B21093000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1417 | 2021-09-30 | 92105 | keep | 0 | Sep | 2021 | 0.062732 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-09-30 15:27 | 2021-09-30 15:28 | 2770 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21093000223 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-30 | 2770 | keep | 0 | Sep | 2021 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
CAGUAS | 2021-09-30 15:28 | 2021-09-30 16:21 | 100 | 000:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | A PETICION DEL SUPERVISOR JOSE COLON SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | C21092900118 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 53 | 2021-09-30 | 5300 | keep | 0 | Sep | 2021 | 0.0036098 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-30 15:29 | 2021-09-30 15:30 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21093000177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
VEGA BAJA | 2021-09-30 15:31 | 2021-09-30 16:04 | 50 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21093000098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-09-30 | 1650 | keep | 0 | Sep | 2021 | 0.0011238 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-09-30 15:32 | 2021-09-30 15:50 | 20 | 000:18 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21093000135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2021-09-30 | 360 | keep | 0 | Sep | 2021 | 0.00024519 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-30 15:38 | 2021-09-30 15:39 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C21093000177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-30 | 2635 | keep | 0 | Sep | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-30 15:38 | 2021-09-30 15:39 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C21093000177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-30 | 2280 | keep | 0 | Sep | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-09-30 15:38 | 2021-09-30 15:39 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C21093000177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-30 | 1617 | keep | 0 | Sep | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
BARRANQUITAS | 2021-09-30 15:39 | 2021-09-30 16:14 | 50 | 000:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C21093000016 | Partial_restoration | Bad Weather | Include | Include | Weather | 35 | 2021-09-30 | 1750 | keep | 0 | Sep | 2021 | 0.0011919 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-30 15:39 | 2021-09-30 16:14 | 10 | 000:35 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21092900015 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 35 | 2021-09-30 | 350 | keep | 0 | Sep | 2021 | 0.00023838 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-30 15:47 | 2021-09-30 16:46 | 1 | 000:59 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 30 EN SWITCH UNIT | C21093000156 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 59 | 2021-09-30 | 59 | keep | 0 | Sep | 2021 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-30 15:55 | 2021-09-30 16:22 | 1 | 000:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21093000080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-09-30 | 27 | keep | 0 | Sep | 2021 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-09-30 15:55 | 2021-09-30 17:16 | 650 | 001:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PRIMARIA SAFADA | A21093000082 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2021-09-30 | 52650 | keep | 0 | Sep | 2021 | 0.03586 | 0.00044271 | Sustained | FALSE | TRUE | Not_TMED_Event | 650
BARRANQUITAS | 2021-09-30 15:56 | 2021-09-30 16:14 | 20 | 000:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA LLUVIAS | C21093000164 | New_Event | Bad Weather | Include | Include | Weather | 18 | 2021-09-30 | 360 | keep | 0 | Sep | 2021 | 0.00024519 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-30 15:58 | 2021-10-01 12:01 | 60 | 020:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21093000165 | New_Event | Bad Weather | Include | Include | Weather | 1203 | 2021-09-30 | 72180 | keep | 0 | Sep | 2021 | 0.049161 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-30 15:59 | 2021-09-30 18:24 | 100 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 1 X 50 EN CORTES DE LINEA Y 1 X 10 Y 2 X 15 EN TRANSFORMADORES MAL TIEMPO | C21093000166 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-09-30 | 14500 | keep | 0 | Sep | 2021 | 0.0098759 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-09-30 16:13 | 2021-09-30 22:12 | 60 | 005:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21093000175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2021-09-30 | 21540 | keep | 0 | Sep | 2021 | 0.014671 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-09-30 16:14 | 2021-09-30 17:51 | 2635 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21093000177 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-09-30 | 255595 | keep | 0 | Sep | 2021 | 0.17408 | 0.0017947 | Sustained | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-30 16:14 | 2021-09-30 19:43 | 40 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21092900163 | Additional_clients | Bad Weather | Include | Include | Weather | 209 | 2021-09-30 | 8360 | keep | 0 | Sep | 2021 | 0.005694 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-09-30 16:14 | 2021-09-30 17:51 | 2280 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21093000177 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-09-30 | 221160 | keep | 0 | Sep | 2021 | 0.15063 | 0.0015529 | Sustained | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-09-30 16:14 | 2021-09-30 17:51 | 1617 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21093000177 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-09-30 | 156849 | keep | 0 | Sep | 2021 | 0.10683 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
CAGUAS | 2021-09-30 16:19 | 2021-09-30 20:40 | 40 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21093000179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2021-09-30 | 10440 | keep | 0 | Sep | 2021 | 0.0071106 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-30 16:21 | 2021-09-30 16:22 | 1017 | 000:01 | T | ERROR HUMANO | ABIERTO ERRONEAMENTE | C21093000249 | New_Event | Human Error | Include | Include | Other | 1 | 2021-09-30 | 1017 | keep | 0 | Sep | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2021-09-30 16:21 | 2021-09-30 17:11 | 2770 | 000:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | A PETICION DEL SUPERVISOR JOSE COLON SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | C21093000181 | Additional_clients | Wire Down | Include | Include | Equipment | 50 | 2021-09-30 | 138500 | keep | 0 | Sep | 2021 | 0.094332 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-30 16:33 | 2021-09-30 16:34 | 1983 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA CARGA POR EL 1801-02 | B21093000123 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-30 | 1983 | keep | 0 | Sep | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-09-30 16:33 | 2021-09-30 16:34 | 186 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA LLEVA EL 1711-04 | B21093000123 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-30 | 186 | keep | 0 | Sep | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
PONCE | 2021-09-30 16:36 | 2021-09-30 16:37 | 253 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21093000111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 253 | keep | 0 | Sep | 2021 | 0.00017232 | 0.00017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 253
BAYAMON | 2021-09-30 16:45 | 2021-09-30 19:15 | 345 | 002:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | S21093000119 | New_Event | Cutout Failure | Include | Include | Equipment | 150 | 2021-09-30 | 51750 | keep | 0 | Sep | 2021 | 0.035247 | 0.00023498 | Sustained | FALSE | TRUE | Not_TMED_Event | 345
MAYAGÃœEZ | 2021-09-30 16:49 | 2021-09-30 17:55 | 281 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2021-09-30 | 18546 | keep | 0 | Sep | 2021 | 0.012632 | 0.00019139 | Sustained | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-09-30 16:49 | 2021-09-30 17:55 | 1252 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2021-09-30 | 82632 | keep | 0 | Sep | 2021 | 0.05628 | 0.00085273 | Sustained | FALSE | TRUE | Not_TMED_Event | 1252
PONCE | 2021-09-30 16:50 | 2021-09-30 18:40 | 3744 | 001:50 | T | LINEA DE TRANSMISION 38KV | SE DESPEGO LINEA PRIMARIA DE LINEA DE TRANSMISION 4500 LA CUAL ESTA FUERA DE SERVICIO | P21093000103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2021-09-30 | 411840 | keep | 0 | Sep | 2021 | 0.2805 | 0.00255 | Sustained | FALSE | TRUE | Not_TMED_Event | 3744
PONCE | 2021-09-30 16:50 | 2021-09-30 18:44 | 3114 | 001:54 | T | LINEA DE TRANSMISION 38KV | SE DESPEGO LINEA, DE LINEA DE TRANSMISION 4500 LA CUAL ESTA FUERA DE SERVICIO CARGA 5004-06 | P21093000103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-09-30 | 354996 | keep | 0 | Sep | 2021 | 0.24179 | 0.0021209 | Sustained | FALSE | TRUE | Not_TMED_Event | 3114
ARECIBO | 2021-09-30 16:51 | 2021-10-03 11:56 | 150 | 067:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21093000072 | New_Event | Bad Weather | Include | Include | Weather | 4025 | 2021-09-30 | 603750 | keep | 0 | Sep | 2021 | 0.41121 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-30 16:51 | 2021-10-01 11:19 | 100 | 018:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21093000076 | New_Event | Bad Weather | Include | Include | Weather | 1108 | 2021-09-30 | 110800 | keep | 0 | Sep | 2021 | 0.075465 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 21:17 | 1339 | 004:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 263 | 2021-09-30 | 352157 | keep | 0 | Sep | 2021 | 0.23985 | 0.00091199 | Sustained | FALSE | TRUE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 21:17 | 470 | 004:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 263 | 2021-09-30 | 123610 | keep | 0 | Sep | 2021 | 0.08419 | 0.00032011 | Sustained | FALSE | TRUE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 21:17 | 2483 | 004:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 263 | 2021-09-30 | 653029 | keep | 0 | Sep | 2021 | 0.44478 | 0.0016912 | Sustained | FALSE | TRUE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 21:17 | 2190 | 004:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 263 | 2021-09-30 | 575970 | keep | 0 | Sep | 2021 | 0.39229 | 0.0014916 | Sustained | FALSE | TRUE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 18:32 | 107 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-09-30 | 10486 | keep | 0 | Sep | 2021 | 0.007142 | 7.2877e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 18:32 | 1666 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-09-30 | 163268 | keep | 0 | Sep | 2021 | 0.1112 | 0.0011347 | Sustained | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 18:32 | 4387 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-09-30 | 429926 | keep | 0 | Sep | 2021 | 0.29282 | 0.002988 | Sustained | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 18:32 | 3147 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-09-30 | 308406 | keep | 0 | Sep | 2021 | 0.21005 | 0.0021434 | Sustained | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-09-30 16:54 | 2021-09-30 18:32 | 4304 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21093000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-09-30 | 421792 | keep | 0 | Sep | 2021 | 0.28728 | 0.0029314 | Sustained | FALSE | TRUE | Not_TMED_Event | 4304
BAYAMON | 2021-09-30 16:59 | 2021-10-01 09:26 | 6 | 016:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21093000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 987 | 2021-09-30 | 5922 | keep | 0 | Sep | 2021 | 0.0040334 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-09-30 17:00 | 2021-09-30 17:01 | 4132 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P21093000128 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-30 | 4132 | keep | 0 | Sep | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-09-30 17:01 | 2021-09-30 21:56 | 75 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CORTE DE LINEA | P21093000130 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 295 | 2021-09-30 | 22125 | keep | 0 | Sep | 2021 | 0.015069 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-09-30 17:06 | 2021-09-30 20:18 | 20 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21093000015 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2021-09-30 | 3840 | keep | 0 | Sep | 2021 | 0.0026154 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-30 17:06 | 2021-09-30 18:15 | 100 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40 Y 1 X 65 EN CORTES DE LINEA MAL TIEMPO | C21093000216 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2021-09-30 | 6900 | keep | 0 | Sep | 2021 | 0.0046996 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-30 17:07 | 2021-09-30 21:30 | 150 | 004:23 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA | M21093000176 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 263 | 2021-09-30 | 39450 | keep | 0 | Sep | 2021 | 0.026869 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-09-30 17:07 | 2021-09-30 17:10 | 4381 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF CERRADO POR SCADA | M21093000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-30 | 13143 | keep | 0 | Sep | 2021 | 0.0089516 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2021-09-30 17:11 | 2021-09-30 19:28 | 770 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR | C21093000181 | Partial_restoration | Wire Down | Include | Include | Equipment | 137 | 2021-09-30 | 105490 | keep | 0 | Sep | 2021 | 0.071849 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-30 17:13 | 2021-09-30 20:28 | 1983 | 003:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN MACHETES DEL TRONCAL DEL 1801-02 QUE LLEVA LA CARGA DEL 1711-04 | B21093000128 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 195 | 2021-09-30 | 386685 | keep | 0 | Sep | 2021 | 0.26337 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-09-30 17:13 | 2021-09-30 20:28 | 186 | 003:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN MACHETES DEL TRONCAL LLEVANDO LA CARGA DEL 1711-04 | B21093000128 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 195 | 2021-09-30 | 36270 | keep | 0 | Sep | 2021 | 0.024703 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
UTUADO | 2021-09-30 17:17 | 2021-09-30 20:05 | 650 | 002:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PRIMARIA SAFADA | A21093000132 | Partial_restoration | Wire Down | Include | Include | Equipment | 168 | 2021-09-30 | 109200 | keep | 0 | Sep | 2021 | 0.074376 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-09-30 17:22 | 2021-10-01 12:17 | 15 | 018:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21093000105 | New_Event | Bad Weather | Include | Include | Weather | 1135 | 2021-09-30 | 17025 | keep | 0 | Sep | 2021 | 0.011596 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-09-30 17:27 | 2021-09-30 20:26 | 10 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | C21093000225 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-09-30 | 1790 | keep | 0 | Sep | 2021 | 0.0012192 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BARRANQUITAS | 2021-09-30 17:30 | 2021-09-30 19:28 | 100 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C21093000168 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-09-30 | 11800 | keep | 0 | Sep | 2021 | 0.0080369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-30 17:35 | 2021-10-01 10:02 | 62 | 016:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21093000227 | New_Event | Bad Weather | Include | Include | Weather | 987 | 2021-09-30 | 61194 | keep | 0 | Sep | 2021 | 0.041679 | 4.2228e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 62
UTUADO | 2021-09-30 17:45 | 2021-09-30 19:33 | 15 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21093000110 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-09-30 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-30 17:50 | 2021-10-01 13:40 | 80 | 019:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21093000122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1190 | 2021-09-30 | 95200 | keep | 0 | Sep | 2021 | 0.06484 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-09-30 17:51 | 2021-10-01 18:48 | 4 | 024:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21093000216 | New_Event | Bad Weather | Include | Include | Weather | 1497 | 2021-09-30 | 5988 | keep | 0 | Sep | 2021 | 0.0040784 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-09-30 17:51 | 2021-10-01 17:38 | 20 | 023:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA LLUVIAS | C21093000164 | New_Event | Bad Weather | Include | Include | Weather | 1427 | 2021-09-30 | 28540 | keep | 0 | Sep | 2021 | 0.019438 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-09-30 17:51 | 2021-10-01 14:39 | 50 | 020:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C21093000016 | New_Event | Bad Weather | Include | Include | Weather | 1248 | 2021-09-30 | 62400 | keep | 0 | Sep | 2021 | 0.0425 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-09-30 17:51 | 2021-09-30 18:53 | 10 | 001:02 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21092900015 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 62 | 2021-09-30 | 620 | keep | 0 | Sep | 2021 | 0.00042228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-09-30 17:53 | 2021-09-30 22:17 | 90 | 004:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | C21093000232 | New_Event | Bad Weather | Include | Include | Weather | 264 | 2021-09-30 | 23760 | keep | 0 | Sep | 2021 | 0.016183 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-09-30 17:55 | 2021-09-30 18:50 | 70 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21093000221 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2021-09-30 | 3850 | keep | 0 | Sep | 2021 | 0.0026222 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-09-30 17:57 | 2021-10-01 11:50 | 15 | 017:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21093000111 | New_Event | Bad Weather | Include | Include | Weather | 1073 | 2021-09-30 | 16095 | keep | 0 | Sep | 2021 | 0.010962 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-09-30 17:57 | 2021-10-01 16:00 | 5 | 022:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5 KVA | A21093000111 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1323 | 2021-09-30 | 6615 | keep | 0 | Sep | 2021 | 0.0045054 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-09-30 18:01 | 2021-09-30 19:37 | 50 | 001:36 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE SECCIONALIZO POSTE EN EL SUELO | R21093000090 | New_Event | Defective Pole | Include | Include | Equipment | 96 | 2021-09-30 | 4800 | keep | 0 | Sep | 2021 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-30 18:04 | 2021-10-01 09:22 | 69 | 015:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21093000234 | New_Event | Bad Weather | Include | Include | Weather | 918 | 2021-09-30 | 63342 | keep | 0 | Sep | 2021 | 0.043142 | 4.6996e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 69
UTUADO | 2021-09-30 18:11 | 2021-10-01 10:01 | 8 | 015:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21093000115 | New_Event | Bad Weather | Include | Include | Weather | 950 | 2021-09-30 | 7600 | keep | 0 | Sep | 2021 | 0.0051763 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-09-30 18:12 | 2021-10-01 11:00 | 45 | 016:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21093000232 | New_Event | Bad Weather | Include | Include | Weather | 1008 | 2021-09-30 | 45360 | keep | 0 | Sep | 2021 | 0.030894 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-09-30 18:22 | 2021-10-01 17:19 | 20 | 022:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21093000035 | New_Event | Bad Weather | Include | Include | Weather | 1377 | 2021-09-30 | 27540 | keep | 0 | Sep | 2021 | 0.018757 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-30 18:28 | 2021-10-02 14:49 | 40 | 044:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | M21093000243 | New_Event | Bad Weather | Include | Include | Weather | 2661 | 2021-09-30 | 106440 | keep | 0 | Sep | 2021 | 0.072496 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-30 18:29 | 2021-09-30 18:32 | 225 | 000:03 | T | ERROR HUMANO | PRESONAL REALIZANDO OPERACIONES DE CAMPO PARA ENERGIZAR VIA LIBRE D2021-00309 INDICA CAUSO AVERIA AL ENERGIZAR | S21093000000 | New_Event | Human Error | Include | Include | Other | 3 | 2021-09-30 | 675 | keep | 0 | Sep | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
UTUADO | 2021-09-30 18:32 | 2021-09-30 19:51 | 80 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21093000121 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2021-09-30 | 6320 | keep | 0 | Sep | 2021 | 0.0043045 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-09-30 18:35 | 2021-09-30 22:10 | 62 | 003:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | P21093000118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-09-30 | 13330 | keep | 0 | Sep | 2021 | 0.009079 | 4.2228e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 62
BAYAMON | 2021-09-30 18:38 | 2021-09-30 21:39 | 40 | 003:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21093000144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-09-30 | 7240 | keep | 0 | Sep | 2021 | 0.0049311 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-30 18:44 | 2021-10-01 19:53 | 40 | 025:09 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE RETIRO PARARRAYO | B21093000146 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1509 | 2021-09-30 | 60360 | keep | 0 | Sep | 2021 | 0.041111 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-30 18:47 | 2021-10-01 13:55 | 45 | 019:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON AISLADORES | B21093000147 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1148 | 2021-09-30 | 51660 | keep | 0 | Sep | 2021 | 0.035185 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
YAUCO | 2021-09-30 18:50 | 2021-10-02 12:00 | 15 | 041:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA A 2.4KV POR UNO DE IGUAL CAPACIDAD | P21093000138 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2470 | 2021-09-30 | 37050 | keep | 0 | Sep | 2021 | 0.025235 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-30 18:51 | 2021-10-01 14:25 | 40 | 019:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21093000128 | New_Event | Bad Weather | Include | Include | Weather | 1174 | 2021-09-30 | 46960 | keep | 0 | Sep | 2021 | 0.031984 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-30 18:52 | 2021-09-30 20:53 | 3 | 002:01 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21093000097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-09-30 | 363 | keep | 0 | Sep | 2021 | 0.00024724 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-09-30 19:00 | 2021-09-30 20:00 | 100 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 65 EN CORTE DE LINEA MAL TIEMPO | C21093000258 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-09-30 | 6000 | keep | 0 | Sep | 2021 | 0.0040866 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-30 19:09 | 2021-10-01 10:22 | 14 | 015:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21093000137 | New_Event | Cutout Failure | Include | Include | Equipment | 913 | 2021-09-30 | 12782 | keep | 0 | Sep | 2021 | 0.0087058 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
BAYAMON | 2021-09-30 19:27 | 2021-10-03 17:16 | 10 | 069:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | B21093000160 | New_Event | Cutout Failure | Include | Include | Equipment | 4189 | 2021-09-30 | 41890 | keep | 0 | Sep | 2021 | 0.028531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-30 19:38 | 2021-09-30 21:11 | 2000 | 001:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR | C21093000181 | New_Event | Wire Down | Include | Include | Equipment | 93 | 2021-09-30 | 186000 | keep | 0 | Sep | 2021 | 0.12668 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2021-09-30 19:40 | 2021-10-02 17:30 | 20 | 045:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA DESGANCHE | S21093000165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2750 | 2021-09-30 | 55000 | keep | 0 | Sep | 2021 | 0.03746 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-30 19:44 | 2021-10-01 11:00 | 80 | 015:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M21093000289 | New_Event | Wire Down | Include | Include | Equipment | 916 | 2021-09-30 | 73280 | keep | 0 | Sep | 2021 | 0.049911 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-09-30 19:55 | 2021-10-01 11:25 | 11 | 015:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE PRIMARIO | R21093000100 | New_Event | Wire Down | Include | Include | Equipment | 930 | 2021-09-30 | 10230 | keep | 0 | Sep | 2021 | 0.0069676 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-09-30 20:04 | 2021-09-30 20:05 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21093000147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-30 | 2163 | keep | 0 | Sep | 2021 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
BAYAMON | 2021-09-30 20:10 | 2021-10-01 10:45 | 40 | 014:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-7 | S21093000166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 875 | 2021-09-30 | 35000 | keep | 0 | Sep | 2021 | 0.023838 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-30 20:19 | 2021-10-01 12:40 | 30 | 016:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100100034 | New_Event | Bad Weather | Include | Include | Weather | 981 | 2021-09-30 | 29430 | keep | 0 | Sep | 2021 | 0.020045 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-09-30 20:40 | 2021-10-01 12:12 | 13 | 015:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75KVA A 2.4KV POR UNO DE IGUAL CAPACIDAD | P21093000153 | New_Event | Service Transformer Failure | Include | Include | Equipment | 932 | 2021-09-30 | 12116 | keep | 0 | Sep | 2021 | 0.0082522 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2021-09-30 20:45 | 2021-10-01 10:48 | 5 | 014:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21093000147 | New_Event | Bad Weather | Include | Include | Weather | 843 | 2021-09-30 | 4215 | keep | 0 | Sep | 2021 | 0.0028708 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-09-30 20:47 | 2021-09-30 22:30 | 38 | 001:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | P21096300155 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2021-09-30 | 3914 | keep | 0 | Sep | 2021 | 0.0026658 | 2.5882e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 38
ARECIBO | 2021-09-30 21:04 | 2021-09-30 22:33 | 5 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21093000154 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-09-30 | 445 | keep | 0 | Sep | 2021 | 0.00030309 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-30 21:07 | 2021-10-01 10:39 | 40 | 013:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21093000155 | New_Event | Bad Weather | Include | Include | Weather | 812 | 2021-09-30 | 32480 | keep | 0 | Sep | 2021 | 0.022122 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-09-30 21:16 | 2021-10-01 11:00 | 70 | 013:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO Y SE RAPARO BAJANTE PRIMARIO | C21093000292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 824 | 2021-09-30 | 57680 | keep | 0 | Sep | 2021 | 0.039286 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-09-30 21:20 | 2021-10-01 10:50 | 25 | 013:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21093000159 | New_Event | Wire Down | Include | Include | Equipment | 810 | 2021-09-30 | 20250 | keep | 0 | Sep | 2021 | 0.013792 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-09-30 21:21 | 2021-09-30 22:56 | 10 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21093000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2021-09-30 | 950 | keep | 0 | Sep | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-30 21:33 | 2021-10-01 16:17 | 50 | 018:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C21093000294 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1124 | 2021-09-30 | 56200 | keep | 0 | Sep | 2021 | 0.038278 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-09-30 21:40 | 2021-10-01 13:53 | 45 | 016:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21093000295 | New_Event | Bad Weather | Include | Include | Weather | 973 | 2021-09-30 | 43785 | keep | 0 | Sep | 2021 | 0.029822 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-09-30 21:48 | 2021-10-01 16:22 | 4 | 018:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA LLUVIAS | C21093000298 | New_Event | Bad Weather | Include | Include | Weather | 1114 | 2021-09-30 | 4456 | keep | 0 | Sep | 2021 | 0.003035 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-09-30 23:45 | 2021-10-01 14:54 | 40 | 015:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA CHINT DE 200 AMP | M21093000326 | New_Event | Cutout Failure | Include | Include | Equipment | 909 | 2021-09-30 | 36360 | keep | 0 | Sep | 2021 | 0.024765 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-30 23:52 | 2021-10-01 10:15 | 50 | 010:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21093000327 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2021-09-30 | 31150 | keep | 0 | Sep | 2021 | 0.021216 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-01 00:15 | 2021-10-01 01:24 | 7621 | 001:09 | T | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO MACHETES EN CARR 874 BO. HOYO MULA PARA SECCIONALIZAR CONDUCTORES CRUZADOS Y RIGIDOS QUEMADOS POR IMPACTO DE AUTO A POSTE | R21100100004 | New_Event |  |  | Include | Wildlife | 69 | 2021-10-01 | 525849 | keep | 0 | Oct | 2021 | 0.35815 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
BAYAMON | 2021-10-01 01:05 | 2021-10-01 12:25 | 25 | 011:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21100100004 | New_Event | Cutout Failure | Include | Include | Equipment | 680 | 2021-10-01 | 17000 | keep | 0 | Oct | 2021 | 0.011579 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-10-01 01:24 | 2021-10-01 02:51 | 3810 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | CERRO MACHETES EN CARR 874 HOYO MULA. REEMPLAZARON TRES RIGIDOS QUEMADOS Y SE REPARO CONDUCTOR CRUZADO POR IMPACTO DE AUTO A POSTE | R21100100004 | Partial_restoration |  |  | Include | Wildlife | 87 | 2021-10-01 | 331470 | keep | 0 | Oct | 2021 | 0.22576 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-01 01:54 | 2021-10-01 14:50 | 3 | 012:56 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR EN ADICION SE REEMPLAZO CAJA | C21100100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 776 | 2021-10-01 | 2328 | keep | 0 | Oct | 2021 | 0.0015856 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-01 02:38 | 2021-10-01 11:31 | 1297 | 008:53 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZA CONDUCTOR ENREDADO Y SE CIERRA AMARRE CONTRA 1901-03 QUE AMBOS ESTAN ATRAVES DEL PROVISIONAL 1904-06 | S21100100015 | New_Event | Wire Down | Include | Include | Equipment | 533 | 2021-10-01 | 691301 | keep | 0 | Oct | 2021 | 0.47084 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-10-01 02:38 | 2021-10-01 03:39 | 451 | 001:01 | T | NO SE REPORTO CAUSA | SE CERO INTERRUPTOR ABRIENDO MACHETES DE AMARRE ENTRE 1901 03 Y 1901 02 EN MARGINAL MARTINEZ NADAL ESQUINA BANCO POPULAR | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-10-01 | 27511 | keep | 0 | Oct | 2021 | 0.018738 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
VEGA BAJA | 2021-10-01 02:52 | 2021-10-01 02:54 | 4702 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21100200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-01 | 9404 | keep | 0 | Oct | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2021-10-01 03:53 | 2021-10-01 17:55 | 15 | 014:02 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN T-180 PROBO MALO DE T-179 @ T -180. T-179 FUERA DE SERVICIO E INFORMO EL SUPERVISOR JOSE R. SANTIAGO QUE POSTERIORMENTE SE CONSTRUYO PROVISIONAL AEREO DEL T-179 @ T-180 | B21100100010 | New_Event | UG Cable Fault | Include | Include | Equipment | 842 | 2021-10-01 | 12630 | keep | 0 | Oct | 2021 | 0.0086022 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-10-01 05:59 | 2021-10-01 06:53 | 2106 | 000:54 | T | PARARRAYOS DEFECTUOSO | DISPARO INTERRUPTOR SE SECCIONALIZO PARARRAYO AVERIADO | R21100100058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 54 | 2021-10-01 | 113724 | keep | 0 | Oct | 2021 | 0.077457 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CAGUAS | 2021-10-01 06:09 | 2021-10-01 11:34 | 70 | 005:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO Y REEMPLAZARON CAJA PRIMARIA | C21100100006 | New_Event | Wire Down | Include | Include | Equipment | 325 | 2021-10-01 | 22750 | keep | 0 | Oct | 2021 | 0.015495 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-10-01 06:24 | 2021-10-01 09:59 | 25 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100011 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-10-01 | 5375 | keep | 0 | Oct | 2021 | 0.0036609 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-01 06:45 | 2021-10-01 11:50 | 70 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100013 | New_Event | Bad Weather | Include | Include | Weather | 305 | 2021-10-01 | 21350 | keep | 0 | Oct | 2021 | 0.014541 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-10-01 06:53 | 2021-10-01 09:02 | 1157 | 002:09 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADOR SE CERRO MACHETE | R21100100081 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 129 | 2021-10-01 | 149253 | keep | 0 | Oct | 2021 | 0.10166 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-01 06:54 | 2021-10-01 14:20 | 30 | 007:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21100100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2021-10-01 | 13380 | keep | 0 | Oct | 2021 | 0.0091131 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-01 07:02 | 2021-10-01 07:03 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CAGUAS | 2021-10-01 07:03 | 2021-10-01 18:27 | 90 | 011:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21100100010 | New_Event | Bad Weather | Include | Include | Weather | 684 | 2021-10-01 | 61560 | keep | 0 | Oct | 2021 | 0.041928 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2021-10-01 07:03 | 2021-10-01 15:49 | 99 | 008:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21100100011 | New_Event | Bad Weather | Include | Include | Weather | 526 | 2021-10-01 | 52074 | keep | 0 | Oct | 2021 | 0.035467 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
VEGA BAJA | 2021-10-01 07:16 | 2021-10-01 12:50 | 100 | 005:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE LLEVO LINEA ZAFADA A SU SITIO | B21100100023 | New_Event | Wire Down | Include | Include | Equipment | 334 | 2021-10-01 | 33400 | keep | 0 | Oct | 2021 | 0.022749 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-10-01 07:21 | 2021-10-01 15:10 | 5 | 007:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100100019 | New_Event | Bad Weather | Include | Include | Weather | 469 | 2021-10-01 | 2345 | keep | 0 | Oct | 2021 | 0.0015972 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-01 07:25 | 2021-10-01 13:01 | 100 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO MACHETES | B21100100026 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2021-10-01 | 33600 | keep | 0 | Oct | 2021 | 0.022885 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-10-01 07:26 | 2021-10-01 14:44 | 64 | 007:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 10 EN CORTE DE LINEA LLUVIAS NO CERRO ORDENES | C21100100017 | New_Event | Bad Weather | Include | Include | Weather | 438 | 2021-10-01 | 28032 | keep | 0 | Oct | 2021 | 0.019092 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
ARECIBO | 2021-10-01 07:33 | 2021-10-01 11:02 | 80 | 003:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21100100020 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2021-10-01 | 16720 | keep | 0 | Oct | 2021 | 0.011388 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-01 07:36 | 2021-10-01 22:05 | 35 | 014:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21100100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 869 | 2021-10-01 | 30415 | keep | 0 | Oct | 2021 | 0.020716 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-10-01 07:37 | 2021-10-01 15:14 | 10 | 007:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P21100100011 | New_Event | Cutout Failure | Include | Include | Equipment | 457 | 2021-10-01 | 4570 | keep | 0 | Oct | 2021 | 0.0031126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-01 07:39 | 2021-10-01 19:50 | 60 | 012:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21100100023 | New_Event | Bad Weather | Include | Include | Weather | 731 | 2021-10-01 | 43860 | keep | 0 | Oct | 2021 | 0.029873 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-10-01 07:41 | 2021-10-01 07:42 | 2379 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | P21100100012 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-01 | 2379 | keep | 0 | Oct | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-10-01 07:42 | 2021-10-01 10:53 | 300 | 003:11 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 Y 3 X 80 EN DISTINTOS CORTES DE LINEA POR MAL TIEMPO | P21093000156 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 191 | 2021-10-01 | 57300 | keep | 0 | Oct | 2021 | 0.039027 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BARRANQUITAS | 2021-10-01 08:06 | 2021-10-03 16:39 | 200 | 056:33 | P | ESTRUCTURA AVERIADA | RELOCALIZO TRANSFORMADOR Y LEVANTO LINEAS, NO SE REMPLAZO EL POSTE | C21100100029 | New_Event | Defective Pole | Include | Include | Equipment | 3393 | 2021-10-01 | 678600 | keep | 0 | Oct | 2021 | 0.46219 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-10-01 08:06 | 2021-10-01 11:52 | 300 | 003:46 | P | FUEGO | 1 X 65 EN CORTE DE LINEA FUEGO EN POSTE PRIMARIO | C21100100029 | New_Event | Fire | Include | Include | Public | 226 | 2021-10-01 | 67800 | keep | 0 | Oct | 2021 | 0.046178 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
VEGA BAJA | 2021-10-01 08:08 | 2021-10-01 08:52 | 10 | 000:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2021-10-01 | 440 | keep | 0 | Oct | 2021 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-01 08:13 | 2021-10-01 16:00 | 4 | 007:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100100030 | New_Event | Bad Weather | Include | Include | Weather | 467 | 2021-10-01 | 1868 | keep | 0 | Oct | 2021 | 0.0012723 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-10-01 08:14 | 2021-10-01 08:15 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211001000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1945 | keep | 0 | Oct | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
PONCE | 2021-10-01 08:15 | 2021-10-01 11:55 | 87 | 003:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA, AVE CRUZO FASE | P21100100016 | New_Event |  |  | Include | Wildlife | 220 | 2021-10-01 | 19140 | keep | 0 | Oct | 2021 | 0.013036 | 5.9255e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 87
UTUADO | 2021-10-01 08:19 | 2021-10-01 10:13 | 4 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21100100031 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2021-10-01 | 456 | keep | 0 | Oct | 2021 | 0.00031058 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-10-01 08:37 | 2021-10-01 12:15 | 150 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21100100038 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-10-01 | 32700 | keep | 0 | Oct | 2021 | 0.022272 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
GUAYAMA | 2021-10-01 08:39 | 2021-10-01 14:47 | 150 | 006:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA | P21100100020 | New_Event | Cutout Failure | Include | Include | Equipment | 368 | 2021-10-01 | 55200 | keep | 0 | Oct | 2021 | 0.037596 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-10-01 08:39 | 2021-10-01 14:03 | 8 | 005:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21093000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 324 | 2021-10-01 | 2592 | keep | 0 | Oct | 2021 | 0.0017654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-01 08:43 | 2021-10-01 17:15 | 10 | 008:32 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | M21100100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 512 | 2021-10-01 | 5120 | keep | 0 | Oct | 2021 | 0.0034872 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-01 08:50 | 2021-10-01 22:20 | 75 | 013:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21100100090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 810 | 2021-10-01 | 60750 | keep | 0 | Oct | 2021 | 0.041377 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-10-01 08:58 | 2021-10-01 09:29 | 25 | 000:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100041 | New_Event | Bad Weather | Include | Include | Weather | 31 | 2021-10-01 | 775 | keep | 0 | Oct | 2021 | 0.00052785 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-01 09:03 | 2021-10-01 12:00 | 1 | 002:57 | P | OTRAS CAUSAS | 1 X 65 EN CORTE DE LINEA PROBLEMA INTERNO | M21100100052 | New_Event | Other Causes | Include | Include | Other | 177 | 2021-10-01 | 177 | keep | 0 | Oct | 2021 | 0.00012055 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-10-01 09:05 | 2021-10-01 16:24 | 3 | 007:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21092900079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 439 | 2021-10-01 | 1317 | keep | 0 | Oct | 2021 | 0.000897 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-10-01 09:12 | 2021-10-01 10:00 | 15 | 000:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100046 | New_Event | Bad Weather | Include | Include | Weather | 48 | 2021-10-01 | 720 | keep | 0 | Oct | 2021 | 0.00049039 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-10-01 09:19 | 2021-10-01 13:36 | 93 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO | R21100100086 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-10-01 | 23901 | keep | 0 | Oct | 2021 | 0.016279 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2021-10-01 09:21 | 2021-10-01 15:17 | 35 | 005:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE LINEA CRUCE POR AVE | S21100100038 | New_Event |  |  | Include | Wildlife | 356 | 2021-10-01 | 12460 | keep | 0 | Oct | 2021 | 0.0084864 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-10-01 09:22 | 2021-10-01 18:30 | 6 | 009:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER POR MAL TIEMPO | P21100100026 | New_Event | Bad Weather | Include | Include | Weather | 548 | 2021-10-01 | 3288 | keep | 0 | Oct | 2021 | 0.0022394 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-01 09:25 | 2021-10-01 10:16 | 1802 | 000:51 | T | DESGANCHE | DISPARO SE VERIFICO Y SE ABRIO MACHETE EN CARR 21 FRENTE A SUBESTACION LAS LOMAS ENREDADERA CRUZANDO FASE Y SE CERRO INTERRUPTOR 80% EN SERVICIO QUEDO FUERA 30% DEL 1346-02 | S21100100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2021-10-01 | 91902 | keep | 0 | Oct | 2021 | 0.062594 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
UTUADO | 2021-10-01 09:31 | 2021-10-02 18:29 | 40 | 032:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21100100054 | New_Event | Bad Weather | Include | Include | Weather | 1978 | 2021-10-01 | 79120 | keep | 0 | Oct | 2021 | 0.053888 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-01 09:34 | 2021-10-02 09:36 | 3 | 024:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REMPLAZO AISLADORES | C21100100055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1442 | 2021-10-01 | 4326 | keep | 0 | Oct | 2021 | 0.0029464 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CAGUAS | 2021-10-01 09:40 | 2021-10-01 17:50 | 6 | 008:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO BARRA EN PEDESTAL | C21100100059 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 490 | 2021-10-01 | 2940 | keep | 0 | Oct | 2021 | 0.0020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-01 09:46 | 2021-10-01 15:15 | 50 | 005:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETIRO SECUNDARIA FUERA DE USO CRUZANDO FASES | A21100100060 | New_Event | Wire Down | Include | Include | Equipment | 329 | 2021-10-01 | 16450 | keep | 0 | Oct | 2021 | 0.011204 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-01 09:59 | 2021-10-02 11:33 | 55 | 025:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO. | P21100100030 | New_Event | Bad Weather | Include | Include | Weather | 1534 | 2021-10-01 | 84370 | keep | 0 | Oct | 2021 | 0.057464 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
FAJARDO | 2021-10-01 10:00 | 2021-10-01 14:16 | 34 | 004:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | R21100100088 | New_Event |  |  | Include | Wildlife | 256 | 2021-10-01 | 8704 | keep | 0 | Oct | 2021 | 0.0059283 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
BAYAMON | 2021-10-01 10:16 | 2021-10-01 10:46 | 1844 | 000:30 | P | DESGANCHE | SE RETIRO ENREDADERA Y SE CERRO MACHETE 100% EN SERVICIO Y 30% EN SERVICIO 1346-02 | S21100100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2021-10-01 | 55320 | keep | 0 | Oct | 2021 | 0.037678 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
BAYAMON | 2021-10-01 10:16 | 2021-10-01 10:46 | 1100 | 000:30 | P | DESGANCHE | SE RETIRO ENREDADERA Y SE CERRO MACHETE 100% EN SERVICIO Y 30% EN SERVICIO 1346-02 | S21100100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2021-10-01 | 33000 | keep | 0 | Oct | 2021 | 0.022476 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
ARECIBO | 2021-10-01 10:18 | 2021-10-01 11:01 | 75 | 000:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PROTA FUSIBLE AVERIADO | A21100100067 | New_Event | Cutout Failure | Include | Include | Equipment | 43 | 2021-10-01 | 3225 | keep | 0 | Oct | 2021 | 0.0021965 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
FAJARDO | 2021-10-01 10:24 | 2021-10-01 11:40 | 12 | 001:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 75 KVA X 75 KVA | R21100100090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 76 | 2021-10-01 | 912 | keep | 0 | Oct | 2021 | 0.00062116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-10-01 10:30 | 2021-10-02 01:36 | 100 | 015:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN SU-1 POR MAL TIEMPO | P21100100035 | New_Event | Bad Weather | Include | Include | Weather | 906 | 2021-10-01 | 90600 | keep | 0 | Oct | 2021 | 0.061707 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-10-01 10:34 | 2021-10-01 12:32 | 7 | 001:58 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ACOMODO PISTOLA EN BUSHING PRIMARIO | C21100100074 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 118 | 2021-10-01 | 826 | keep | 0 | Oct | 2021 | 0.00056258 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-10-01 10:40 | 2021-10-02 12:32 | 100 | 025:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REALIZARON EMPALMES EN CABLE SOTERRADO AVERIADO POR EXCAVASION DE PERSONAL DE AAA SE CERRO DEL SU-5 AL PM-60 | P21100100092 | New_Event |  |  | Include | Wildlife | 1552 | 2021-10-01 | 155200 | keep | 0 | Oct | 2021 | 0.10571 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-10-01 11:00 | 2021-10-02 09:44 | 10 | 022:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21100100079 | New_Event |  |  | Include | Wildlife | 1364 | 2021-10-01 | 13640 | keep | 0 | Oct | 2021 | 0.0092901 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-01 11:09 | 2021-10-02 11:10 | 60 | 024:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100100288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1441 | 2021-10-01 | 86460 | keep | 0 | Oct | 2021 | 0.058888 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-01 11:12 | 2021-10-01 11:13 | 74 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1529-11 | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 74 | keep | 0 | Oct | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2021-10-01 11:12 | 2021-10-01 11:13 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1521-2 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1370 | keep | 0 | Oct | 2021 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
CANOVANAS | 2021-10-01 11:19 | 2021-10-01 14:15 | 14 | 002:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | R21100100091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 176 | 2021-10-01 | 2464 | keep | 0 | Oct | 2021 | 0.0016782 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
SAN JUAN | 2021-10-01 11:21 | 2021-10-01 11:23 | 10211 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 1204-5 SE VERIFICO CON PERSONAL DRC Y ME INDICAN QUE ELLOS NO HAN TENIDO CONTACTO CON LA LINEA Y QUE PUEDO PROCEDER A CERRAR INTERRUPTOR | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-01 | 20422 | keep | 0 | Oct | 2021 | 0.013909 | 0.0069547 | Momentary | FALSE | TRUE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-01 11:21 | 2021-10-01 11:23 | 4133 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 1204-5 SE VERIFICO CON PERSONAL DRC Y ME INDICAN QUE ELLOS NO HAN TENIDO CONTACTO CON LA LINEA Y QUE PUEDO PROCEDER A CERRAR INTERRUPTOR | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-01 | 8266 | keep | 0 | Oct | 2021 | 0.0056299 | 0.002815 | Momentary | FALSE | TRUE | Not_TMED_Event | 4133
PONCE | 2021-10-01 11:24 | 2021-10-01 17:11 | 50 | 005:47 | P | DESGANCHE | 1X50 EN CORTE DE LINEA POR DESGANCHE | P21100100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2021-10-01 | 17350 | keep | 0 | Oct | 2021 | 0.011817 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-01 11:29 | 2021-10-01 14:16 | 40 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21100100080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-10-01 | 6680 | keep | 0 | Oct | 2021 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-01 11:31 | 2021-10-01 15:49 | 400 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESENREDARON LINEAS, SE CERRO PUENTE Y SE CERRARON MACHETES | S21100100015 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2021-10-01 | 103200 | keep | 0 | Oct | 2021 | 0.070289 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
BAYAMON | 2021-10-01 11:37 | 2021-10-01 11:43 | 34 | 000:06 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21093000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-01 | 204 | keep | 0 | Oct | 2021 | 0.00013894 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
HUMACAO | 2021-10-01 11:37 | 2021-10-01 17:49 | 34 | 006:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 25KVA | C21100100093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 372 | 2021-10-01 | 12648 | keep | 0 | Oct | 2021 | 0.0086145 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
HUMACAO | 2021-10-01 11:57 | 2021-10-02 19:08 | 20 | 031:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y RETEZO LINEA | C21100100173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1871 | 2021-10-01 | 37420 | keep | 0 | Oct | 2021 | 0.025487 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-01 11:57 | 2021-10-01 16:59 | 200 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A21100100083 | New_Event | Wire Down | Include | Include | Equipment | 302 | 2021-10-01 | 60400 | keep | 0 | Oct | 2021 | 0.041138 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-10-01 11:59 | 2021-10-02 15:13 | 40 | 027:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21100100084 | New_Event | Wire Down | Include | Include | Equipment | 1634 | 2021-10-01 | 65360 | keep | 0 | Oct | 2021 | 0.044516 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-01 12:03 | 2021-10-01 12:56 | 5 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | C21100100101 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-10-01 | 265 | keep | 0 | Oct | 2021 | 0.00018049 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-10-01 12:19 | 2021-10-01 16:25 | 60 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21100100087 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2021-10-01 | 14760 | keep | 0 | Oct | 2021 | 0.010053 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-01 12:29 | 2021-10-01 17:27 | 8 | 004:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR Y SE DESENREDO SECUNDARIA | B21100100080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 298 | 2021-10-01 | 2384 | keep | 0 | Oct | 2021 | 0.0016237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-10-01 12:35 | 2021-10-01 12:58 | 8 | 000:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21100100066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 23 | 2021-10-01 | 184 | keep | 0 | Oct | 2021 | 0.00012532 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2021-10-01 12:36 | 2021-10-01 20:01 | 2 | 007:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1X8 EN TRANSFORMADOR POR MAL TIEMPO | P21100100050 | New_Event | Bad Weather | Include | Include | Weather | 445 | 2021-10-01 | 890 | keep | 0 | Oct | 2021 | 0.00060617 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-01 12:45 | 2021-10-01 13:15 | 4 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21093000114 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-10-01 | 120 | keep | 0 | Oct | 2021 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
HUMACAO | 2021-10-01 12:52 | 2021-10-02 13:03 | 10 | 024:11 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 75 KVA X 75 KVA | C21100100106 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1451 | 2021-10-01 | 14510 | keep | 0 | Oct | 2021 | 0.0098827 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-01 12:57 | 2021-10-01 14:11 | 100 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 Y 1 X 65 EN CORTE DE LINEA LLUVIAS | C21100100101 | Additional_clients | Bad Weather | Include | Include | Weather | 74 | 2021-10-01 | 7400 | keep | 0 | Oct | 2021 | 0.0050401 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-10-01 12:59 | 2021-10-02 09:15 | 15 | 020:16 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21100100092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1216 | 2021-10-01 | 18240 | keep | 0 | Oct | 2021 | 0.012423 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-01 13:02 | 2021-10-01 13:03 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21100100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 2999 | keep | 0 | Oct | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
HUMACAO | 2021-10-01 13:09 | 2021-10-01 13:10 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21100100113 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-01 | 2450 | keep | 0 | Oct | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-10-01 13:10 | 2021-10-01 17:40 | 130 | 004:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON ANIMAL | C21100100116 | 1st_after_momentary |  |  | Include | Wildlife | 270 | 2021-10-01 | 35100 | keep | 0 | Oct | 2021 | 0.023906 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
YAUCO | 2021-10-01 13:11 | 2021-10-01 13:43 | 11 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | P21100100054 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2021-10-01 | 352 | keep | 0 | Oct | 2021 | 0.00023975 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-10-01 13:24 | 2021-10-02 16:54 | 5 | 027:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO | M20100100106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1650 | 2021-10-01 | 8250 | keep | 0 | Oct | 2021 | 0.005619 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-01 13:28 | 2021-10-01 17:12 | 133 | 003:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21100100120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-10-01 | 29792 | keep | 0 | Oct | 2021 | 0.020291 | 9.0586e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 133
SAN JUAN | 2021-10-01 13:44 | 2021-10-01 14:04 | 4040 | 000:20 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-01 | 80800 | keep | 0 | Oct | 2021 | 0.055033 | 0.0027516 | Sustained | FALSE | FALSE | Not_TMED_Event | 4040
SAN JUAN | 2021-10-01 13:44 | 2021-10-01 14:04 | 207 | 000:20 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-01 | 4140 | keep | 0 | Oct | 2021 | 0.0028197 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
MAYAGÃœEZ | 2021-10-01 13:48 | 2021-10-01 16:09 | 10 | 002:21 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | M21100100116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-10-01 | 1410 | keep | 0 | Oct | 2021 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-01 13:48 | 2021-10-01 16:24 | 10 | 002:36 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | M21100100115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-10-01 | 1560 | keep | 0 | Oct | 2021 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-01 13:52 | 2021-10-01 19:32 | 54 | 005:40 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE ENDEREZO POSTE | R21100100099 | New_Event | Defective Pole | Include | Include | Equipment | 340 | 2021-10-01 | 18360 | keep | 0 | Oct | 2021 | 0.012505 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
ARECIBO | 2021-10-01 14:01 | 2021-10-01 20:35 | 7 | 006:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100100042 | New_Event | Bad Weather | Include | Include | Weather | 394 | 2021-10-01 | 2758 | keep | 0 | Oct | 2021 | 0.0018785 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-10-01 14:10 | 2021-10-01 15:39 | 12 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21100100062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2021-10-01 | 1068 | keep | 0 | Oct | 2021 | 0.00072741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-01 14:16 | 2021-10-01 14:21 | 1681 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LLEVA LA CARGA DEL 1303-1 Y 1346-5 | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-01 | 8405 | keep | 0 | Oct | 2021 | 0.0057246 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-01 14:16 | 2021-10-01 14:21 | 225 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LLEVA LA CARGA DEL 1303-1 Y 1346-5 | S21100100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-01 | 1125 | keep | 0 | Oct | 2021 | 0.00076623 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-01 14:16 | 2021-10-01 14:21 | 922 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LLEVA LA CARGA DEL 1303-1 Y 1346-5 | S21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-01 | 4610 | keep | 0 | Oct | 2021 | 0.0031399 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
ARECIBO | 2021-10-01 14:19 | 2021-10-02 10:21 | 15 | 020:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA ROEDOR CRUZO LINEAS SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21100100109 | New_Event |  |  | Include | Wildlife | 1202 | 2021-10-01 | 18030 | keep | 0 | Oct | 2021 | 0.01228 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-01 14:21 | 2021-10-01 16:27 | 40 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21100100080 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-10-01 | 5040 | keep | 0 | Oct | 2021 | 0.0034327 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-01 14:25 | 2021-10-02 13:11 | 20 | 022:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100111 | New_Event | Bad Weather | Include | Include | Weather | 1366 | 2021-10-01 | 27320 | keep | 0 | Oct | 2021 | 0.018608 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-01 14:35 | 2021-10-01 14:48 | 4 | 000:13 | P | OTRAS CAUSAS | 1 X 15 EN CORTE DE LINEA CONTAMINACION EN EL TRANSFORMADOR | R21100100102 | New_Event | Other Causes | Include | Include | Other | 13 | 2021-10-01 | 52 | keep | 0 | Oct | 2021 | 3.5417e-05 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-10-01 14:36 | 2021-10-01 14:37 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO EL 1706-03 | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1382 | keep | 0 | Oct | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-10-01 14:36 | 2021-10-01 14:37 | 663 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1706-02 LLEVANDO EL 1706-03 | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 663 | keep | 0 | Oct | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
CANOVANAS | 2021-10-01 14:43 | 2021-10-01 16:54 | 100 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21100100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-10-01 | 13100 | keep | 0 | Oct | 2021 | 0.0089224 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-01 14:49 | 2021-10-01 17:56 | 16 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | C21093000130 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-10-01 | 2992 | keep | 0 | Oct | 2021 | 0.0020378 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2021-10-01 14:57 | 2021-10-01 19:33 | 8 | 004:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR PUENTE SECUNDARIO | P21100100066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 276 | 2021-10-01 | 2208 | keep | 0 | Oct | 2021 | 0.0015039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-01 15:03 | 2021-10-02 15:33 | 9 | 024:30 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR PROLEC 50 KVA 120/240 SERIE M20J10009 X 50KVA | M21100100136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1470 | 2021-10-01 | 13230 | keep | 0 | Oct | 2021 | 0.0090109 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2021-10-01 15:08 | 2021-10-01 18:23 | 10 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN SU SE INSPECCIONO MAL TIEMPO | R21100100104 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2021-10-01 | 1950 | keep | 0 | Oct | 2021 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-01 15:12 | 2021-10-01 16:40 | 60 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO LINEAS | A21100100118 | New_Event |  |  | Include | Wildlife | 88 | 2021-10-01 | 5280 | keep | 0 | Oct | 2021 | 0.0035962 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-01 15:17 | 2021-10-01 16:50 | 1615 | 001:33 | T | DESGANCHE | DISPARO DE INERRUPTOR SE CERRO POR SCADA | R21100100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2021-10-01 | 150195 | keep | 0 | Oct | 2021 | 0.1023 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
MAYAGÃœEZ | 2021-10-01 15:20 | 2021-10-02 17:52 | 6 | 026:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21010100140 | New_Event | Bad Weather | Include | Include | Weather | 1592 | 2021-10-01 | 9552 | keep | 0 | Oct | 2021 | 0.0065058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-01 15:31 | 2021-10-01 17:33 | 60 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN MACHETES | B21100100128 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2021-10-01 | 7320 | keep | 0 | Oct | 2021 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-10-01 15:45 | 2021-10-01 20:04 | 80 | 004:19 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | B21100100132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2021-10-01 | 20720 | keep | 0 | Oct | 2021 | 0.014112 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-10-01 15:51 | 2021-10-01 16:30 | 10 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100100126 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-10-01 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-01 16:03 | 2021-10-01 16:04 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO INTERRUPTOR | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
AGUADILLA | 2021-10-01 16:31 | 2021-10-01 21:40 | 100 | 005:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA SAFADA DEL AISLADOR | M21100100147 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 309 | 2021-10-01 | 30900 | keep | 0 | Oct | 2021 | 0.021046 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-01 16:34 | 2021-10-01 16:35 | 5630 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21100100144 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-01 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2021-10-01 16:34 | 2021-10-02 11:34 | 15 | 019:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75KVA POR UNO DE 75KVA CAJA PRIMARIA Y PARARRAYO | B21100100147 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1140 | 2021-10-01 | 17100 | keep | 0 | Oct | 2021 | 0.011647 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-10-01 16:35 | 2021-10-02 14:12 | 40 | 021:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 Y 1 X 65 EN CORTES DE LINEA REMPLAZO CAJA QUEMADA | C21100100179 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1297 | 2021-10-01 | 51880 | keep | 0 | Oct | 2021 | 0.035335 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-10-01 16:38 | 2021-10-02 16:03 | 40 | 023:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21100100146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1405 | 2021-10-01 | 56200 | keep | 0 | Oct | 2021 | 0.038278 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-01 16:42 | 2021-10-01 16:54 | 1250 | 000:12 | P | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PORTATIL SECUNDARIO PARA REALIZAR CONEXION DE TRANSFORMADOR DE MEDICION REMOTA | S21100100000 | New_Event | Other Causes | Include | Include | Other | 12 | 2021-10-01 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
SAN JUAN | 2021-10-01 16:42 | 2021-10-01 16:54 | 320 | 000:12 | P | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PORTATIL SECUNDARIO PARA REALIZAR CONEXION DE TRANSFORMADOR DE MEDICION REMOTA | S21100100000 | New_Event | Other Causes | Include | Include | Other | 12 | 2021-10-01 | 3840 | keep | 0 | Oct | 2021 | 0.0026154 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2021-10-01 16:42 | 2021-10-01 16:54 | 630 | 000:12 | P | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PORTATIL SECUNDARIO PARA REALIZAR CONEXION DE TRANSFORMADOR DE MEDICION REMOTA | S21100100000 | New_Event | Other Causes | Include | Include | Other | 12 | 2021-10-01 | 7560 | keep | 0 | Oct | 2021 | 0.0051491 | 0.00042909 | Sustained | FALSE | FALSE | Not_TMED_Event | 630
VEGA BAJA | 2021-10-01 16:42 | 2021-10-01 16:43 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1310 | keep | 0 | Oct | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2021-10-01 16:46 | 2021-10-01 16:47 | 35 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21100100147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 35 | keep | 0 | Oct | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 35
VEGA BAJA | 2021-10-01 16:49 | 2021-10-02 12:15 | 120 | 019:26 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | B21100100157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1166 | 2021-10-01 | 139920 | keep | 0 | Oct | 2021 | 0.095299 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
SAN JUAN | 2021-10-01 16:50 | 2021-10-01 18:20 | 700 | 001:30 | P | DESGANCHE | PERSONAL LOCALIZANDO AVERIA | R21100100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-10-01 | 63000 | keep | 0 | Oct | 2021 | 0.042909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-01 16:50 | 2021-10-01 18:44 | 723 | 001:54 | T | DESGANCHE | SE ABRIO MACHETES N/O CONTRA EL 1711-05 Y SE CERRO INTERRUPTOR | B21100100159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-10-01 | 82422 | keep | 0 | Oct | 2021 | 0.056137 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-10-01 16:50 | 2021-10-01 20:17 | 1976 | 003:27 | T | DESGANCHE | SE REALIZO DESGANCHE EN EL 1711-05 Y SE CERRO AMARRE CONTRA EL 1711-02 | B21100100159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-10-01 | 409032 | keep | 0 | Oct | 2021 | 0.27859 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-10-01 16:51 | 2021-10-01 16:52 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100100158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 959 | keep | 0 | Oct | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
VEGA BAJA | 2021-10-01 16:52 | 2021-10-01 16:53 | 3076 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21100100158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 3076 | keep | 0 | Oct | 2021 | 0.002095 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
UTUADO | 2021-10-01 16:59 | 2021-10-01 17:15 | 1382 | 000:16 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A SUBESTACION PARA REPARAR PUENTE ABIERTO EN LINEA 8100 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-01 | 22112 | keep | 0 | Oct | 2021 | 0.01506 | 0.00094127 | Sustained | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-10-01 16:59 | 2021-10-01 17:15 | 654 | 000:16 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A SUBESTACION PARA REPARAR PUENTE ABIERTO EN LINEA 8100 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-01 | 10464 | keep | 0 | Oct | 2021 | 0.007127 | 0.00044544 | Sustained | FALSE | TRUE | Not_TMED_Event | 654
ARECIBO | 2021-10-01 17:03 | 2021-10-01 17:40 | 45 | 000:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCRAGAS ELECTRICAS | A21100100153 | New_Event | Bad Weather | Include | Include | Weather | 37 | 2021-10-01 | 1665 | keep | 0 | Oct | 2021 | 0.001134 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-01 17:06 | 2021-10-03 17:55 | 12 | 048:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO | A21100100156 | New_Event | Bad Weather | Include | Include | Weather | 2929 | 2021-10-01 | 35148 | keep | 0 | Oct | 2021 | 0.023939 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-10-01 17:06 | 2021-10-01 19:05 | 45 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES LLUVIAS | B21100100176 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2021-10-01 | 5355 | keep | 0 | Oct | 2021 | 0.0036473 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-10-01 17:07 | 2021-10-01 17:08 | 200 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO 50% DEL 9201-04 | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 200 | keep | 0 | Oct | 2021 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2021-10-01 17:08 | 2021-10-01 19:30 | 70 | 002:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZARON DISCOS | C21100100155 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 142 | 2021-10-01 | 9940 | keep | 0 | Oct | 2021 | 0.0067701 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-10-01 17:15 | 2021-10-02 12:15 | 200 | 019:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A21100100083 | Partial_restoration | Wire Down | Include | Include | Equipment | 1140 | 2021-10-01 | 228000 | keep | 0 | Oct | 2021 | 0.15529 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-01 17:29 | 2021-10-01 23:55 | 150 | 006:26 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21100100165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2021-10-01 | 57900 | keep | 0 | Oct | 2021 | 0.039435 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-10-01 17:33 | 2021-10-01 19:51 | 175 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE CERRO PUENTE ABIERTO EN TRONCAL | B21100100128 | Additional_clients | Wire Down | Include | Include | Equipment | 138 | 2021-10-01 | 24150 | keep | 0 | Oct | 2021 | 0.016448 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-01 17:36 | 2021-10-01 17:46 | 2791 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR DE EMERGENCIA PARA SECCIONALIZAR ALAMBRE PARTIDO | A21100100169 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2021-10-01 | 27910 | keep | 0 | Oct | 2021 | 0.019009 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
PONCE | 2021-10-01 17:37 | 2021-10-02 11:05 | 13 | 017:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA POR MAL TIEMPO | P21100100080 | New_Event | Bad Weather | Include | Include | Weather | 1048 | 2021-10-01 | 13624 | keep | 0 | Oct | 2021 | 0.0092792 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
ARECIBO | 2021-10-01 17:41 | 2021-10-01 19:20 | 150 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21100100170 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-10-01 | 14850 | keep | 0 | Oct | 2021 | 0.010114 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-10-01 17:45 | 2021-10-01 17:47 | 3387 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO Y SE CERRO POR SCADA | B21100100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-10-01 | 6774 | keep | 0 | Oct | 2021 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2021-10-01 17:46 | 2021-10-01 20:50 | 250 | 003:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR DE EMERGENCIA PARA SECCIONALIZAR ALAMBRE PARTIDO | A21100100169 | Partial_restoration | Wire Down | Include | Include | Equipment | 184 | 2021-10-01 | 46000 | keep | 0 | Oct | 2021 | 0.03133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-01 17:47 | 2021-10-01 18:03 | 1841 | 000:16 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A21100100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-01 | 29456 | keep | 0 | Oct | 2021 | 0.020062 | 0.0012539 | Sustained | FALSE | TRUE | Not_TMED_Event | 1841
UTUADO | 2021-10-01 17:47 | 2021-10-01 18:03 | 1950 | 000:16 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A21100100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-01 | 31200 | keep | 0 | Oct | 2021 | 0.02125 | 0.0013281 | Sustained | FALSE | TRUE | Not_TMED_Event | 1950
VEGA BAJA | 2021-10-01 17:47 | 2021-10-01 21:54 | 30 | 004:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 50 EN CORTE DE LINEA SE REMPLAZARON AISLADORES PARTIDOS | B21100100175 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 247 | 2021-10-01 | 7410 | keep | 0 | Oct | 2021 | 0.0050469 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-01 17:50 | 2021-10-01 17:51 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1843 | keep | 0 | Oct | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2021-10-01 17:51 | 2021-10-01 20:25 | 300 | 002:34 | P | NO SE REPORTO CAUSA | 3 X 65 EN CORTES DE LINEA SE PATRULLO | C21100100165 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 154 | 2021-10-01 | 46200 | keep | 0 | Oct | 2021 | 0.031467 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-01 18:00 | 2021-10-05 12:57 | 1 | 090:57 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE RELACIONADO WR5323000 | M21100500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5457 | 2021-10-01 | 5457 | keep | 0 | Oct | 2021 | 0.0037167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 1617 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 100254 | keep | 0 | Oct | 2021 | 0.068283 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 1017 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 63054 | keep | 0 | Oct | 2021 | 0.042946 | 0.00069267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 828 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21010010000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 51336 | keep | 0 | Oct | 2021 | 0.034965 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 863 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 53506 | keep | 0 | Oct | 2021 | 0.036443 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 309 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 19158 | keep | 0 | Oct | 2021 | 0.013048 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 176 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 10912 | keep | 0 | Oct | 2021 | 0.0074321 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-10-01 18:02 | 2021-10-01 19:04 | 974 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-10-01 | 60388 | keep | 0 | Oct | 2021 | 0.04113 | 0.00066339 | Sustained | FALSE | TRUE | Not_TMED_Event | 974
ARECIBO | 2021-10-01 18:14 | 2021-10-02 15:00 | 60 | 020:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A21100100187 | New_Event | Bad Weather | Include | Include | Weather | 1246 | 2021-10-01 | 74760 | keep | 0 | Oct | 2021 | 0.050919 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-10-01 18:15 | 2021-10-02 10:50 | 10 | 016:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21100100166 | New_Event | Bad Weather | Include | Include | Weather | 995 | 2021-10-01 | 9950 | keep | 0 | Oct | 2021 | 0.0067769 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-01 18:20 | 2021-10-01 18:22 | 1615 | 000:02 | T | DESGANCHE | DISPARO PERSONAL LOCALIZANDO AVERIA | R21100100000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-01 | 3230 | keep | 0 | Oct | 2021 | 0.0021999 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-01 18:22 | 2021-10-01 19:42 | 300 | 001:20 | P | DESGANCHE | SE RETIRARON ARBOLES SOBRE LINEA | R21100100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-10-01 | 24000 | keep | 0 | Oct | 2021 | 0.016346 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:31 | 1 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-01 | 2 | keep | 0 | Oct | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:31 | 2266 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-01 | 4532 | keep | 0 | Oct | 2021 | 0.0030867 | 0.0015434 | Momentary | FALSE | TRUE | Not_TMED_Event | 2266
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:31 | 1399 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-01 | 2798 | keep | 0 | Oct | 2021 | 0.0019057 | 0.00095285 | Momentary | FALSE | TRUE | Not_TMED_Event | 1399
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:30 | 1222 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 1222 | keep | 0 | Oct | 2021 | 0.0008323 | 0.0008323 | Momentary | FALSE | TRUE | Not_TMED_Event | 1222
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:30 | 2756 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 2756 | keep | 0 | Oct | 2021 | 0.0018771 | 0.0018771 | Momentary | FALSE | TRUE | Not_TMED_Event | 2756
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:30 | 2833 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 2833 | keep | 0 | Oct | 2021 | 0.0019295 | 0.0019295 | Momentary | FALSE | TRUE | Not_TMED_Event | 2833
ARECIBO | 2021-10-01 18:29 | 2021-10-01 18:30 | 1218 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 1218 | keep | 0 | Oct | 2021 | 0.00082957 | 0.00082957 | Momentary | FALSE | TRUE | Not_TMED_Event | 1218
ARECIBO | 2021-10-01 18:35 | 2021-10-01 21:30 | 60 | 002:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21100100198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-10-01 | 10500 | keep | 0 | Oct | 2021 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-01 18:39 | 2021-10-01 23:10 | 10 | 004:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100100225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2021-10-01 | 2710 | keep | 0 | Oct | 2021 | 0.0018458 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-01 18:40 | 2021-10-01 20:10 | 30 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100200 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-10-01 | 2700 | keep | 0 | Oct | 2021 | 0.001839 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-01 18:45 | 2021-10-02 11:20 | 30 | 016:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21100100204 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 995 | 2021-10-01 | 29850 | keep | 0 | Oct | 2021 | 0.020331 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-01 18:48 | 2021-10-01 18:50 | 1718 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21100100198 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-10-01 | 3436 | keep | 0 | Oct | 2021 | 0.0023402 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
ARECIBO | 2021-10-01 18:49 | 2021-10-02 12:10 | 200 | 017:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA LINEA ROTA POR ARBOL SOBRE LINEAS SE ABRIO PUENTES PARA SECCIONALIZAR LA AVERIA | A21100100206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1041 | 2021-10-01 | 208200 | keep | 0 | Oct | 2021 | 0.1418 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-01 18:56 | 2021-10-01 22:53 | 7 | 003:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100100211 | New_Event | Bad Weather | Include | Include | Weather | 237 | 2021-10-01 | 1659 | keep | 0 | Oct | 2021 | 0.0011299 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-01 18:57 | 2021-10-02 10:44 | 90 | 015:47 | P | TRANSFORMADOR AVERIADO | BOOSTER AVERIADO SE CERRO BY-PASS | M21100100205 | New_Event | Service Transformer Failure | Include | Include | Equipment | 947 | 2021-10-01 | 85230 | keep | 0 | Oct | 2021 | 0.05805 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2021-10-01 19:02 | 2021-10-02 19:43 | 100 | 024:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100216 | New_Event | Bad Weather | Include | Include | Weather | 1481 | 2021-10-01 | 148100 | keep | 0 | Oct | 2021 | 0.10087 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 4390 | keep | 0 | Oct | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | TRUE | Not_TMED_Event | 4390
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 2092 | keep | 0 | Oct | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | TRUE | Not_TMED_Event | 2092
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 540 | keep | 0 | Oct | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | TRUE | Not_TMED_Event | 540
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 131 | keep | 0 | Oct | 2021 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 131
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 2281 | keep | 0 | Oct | 2021 | 0.0015536 | 0.0015536 | Momentary | FALSE | TRUE | Not_TMED_Event | 2281
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 1569 | keep | 0 | Oct | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
CAGUAS | 2021-10-01 19:04 | 2021-10-01 19:05 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C21100100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-01 | 2417 | keep | 0 | Oct | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | TRUE | Not_TMED_Event | 2417
MAYAGÃœEZ | 2021-10-01 19:04 | 2021-10-02 11:40 | 80 | 016:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21092900141 | New_Event | Bad Weather | Include | Include | Weather | 996 | 2021-10-01 | 79680 | keep | 0 | Oct | 2021 | 0.05427 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-01 19:05 | 2021-10-01 20:20 | 2234 | 001:15 | T | NO SE REPORTO CAUSA | DISPARO CON RTU DOWN, SE SUBIO RTU Y SE CERRO POR CONTROL | B21100100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-10-01 | 167550 | keep | 0 | Oct | 2021 | 0.11412 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
UTUADO | 2021-10-01 19:08 | 2021-10-01 19:40 | 15 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN TRANSFORMADOR MAL TIEMPO | A21100100224 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2021-10-01 | 480 | keep | 0 | Oct | 2021 | 0.00032693 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-10-01 19:11 | 2021-10-02 10:05 | 120 | 014:54 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 Y 1 X 65 EN CORTES DE LINEA DESCARGAS ELECTRICAS | B21100100237 | New_Event | Bad Weather | Include | Include | Weather | 894 | 2021-10-01 | 107280 | keep | 0 | Oct | 2021 | 0.073068 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
HUMACAO | 2021-10-01 19:12 | 2021-10-02 11:26 | 100 | 016:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 Y 2 X 40 EN CORTES DE LINEA REMPLAZO DISCO | C21100100174 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 974 | 2021-10-01 | 97400 | keep | 0 | Oct | 2021 | 0.066339 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-01 19:12 | 2021-10-01 19:13 | 1153 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100100175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1153 | keep | 0 | Oct | 2021 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
ARECIBO | 2021-10-01 19:12 | 2021-10-01 20:15 | 50 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100226 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-10-01 | 3150 | keep | 0 | Oct | 2021 | 0.0021455 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-01 19:21 | 2021-10-01 20:10 | 30 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100231 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-10-01 | 1470 | keep | 0 | Oct | 2021 | 0.0010012 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-01 19:27 | 2021-10-02 09:52 | 50 | 014:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100280 | New_Event | Bad Weather | Include | Include | Weather | 865 | 2021-10-01 | 43250 | keep | 0 | Oct | 2021 | 0.029457 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-10-01 19:28 | 2021-10-02 16:58 | 40 | 021:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21100200270 | New_Event | Bad Weather | Include | Include | Weather | 1290 | 2021-10-01 | 51600 | keep | 0 | Oct | 2021 | 0.035145 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-01 19:29 | 2021-10-02 14:19 | 16 | 018:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | R21100100013 | New_Event | Bad Weather | Include | Include | Weather | 1130 | 2021-10-01 | 18080 | keep | 0 | Oct | 2021 | 0.012314 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
ARECIBO | 2021-10-01 19:34 | 2021-10-01 21:25 | 40 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100238 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2021-10-01 | 4440 | keep | 0 | Oct | 2021 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-10-01 19:38 | 2021-10-01 20:22 | 100 | 000:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C21093000168 | New_Event | Bad Weather | Include | Include | Weather | 44 | 2021-10-01 | 4400 | keep | 0 | Oct | 2021 | 0.0029968 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-01 19:39 | 2021-10-01 22:01 | 1935 | 002:22 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21100100276 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 142 | 2021-10-01 | 274770 | keep | 0 | Oct | 2021 | 0.18714 | 0.0013179 | Sustained | FALSE | TRUE | Not_TMED_Event | 1935
BAYAMON | 2021-10-01 19:39 | 2021-10-01 22:01 | 3 | 002:22 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21100100276 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 142 | 2021-10-01 | 426 | keep | 0 | Oct | 2021 | 0.00029015 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-01 19:39 | 2021-10-01 22:01 | 61 | 002:22 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21100100276 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 142 | 2021-10-01 | 8662 | keep | 0 | Oct | 2021 | 0.0058996 | 4.1547e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 61
BAYAMON | 2021-10-01 19:39 | 2021-10-01 22:01 | 1501 | 002:22 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21100100276 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 142 | 2021-10-01 | 213142 | keep | 0 | Oct | 2021 | 0.14517 | 0.0010223 | Sustained | FALSE | TRUE | Not_TMED_Event | 1501
BAYAMON | 2021-10-01 19:39 | 2021-10-01 22:01 | 546 | 002:22 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21100100276 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 142 | 2021-10-01 | 77532 | keep | 0 | Oct | 2021 | 0.052807 | 0.00037188 | Sustained | FALSE | TRUE | Not_TMED_Event | 546
BAYAMON | 2021-10-01 19:39 | 2021-10-01 23:46 | 959 | 004:07 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 CARGA POR SUBESTACION PORTATIL 1904 | S21100100208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2021-10-01 | 236873 | keep | 0 | Oct | 2021 | 0.16133 | 0.00065317 | Sustained | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-10-01 19:39 | 2021-10-01 23:46 | 1297 | 004:07 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 CARGA POR SUBESTACION PORTATIL 1904 | S21100100208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2021-10-01 | 320359 | keep | 0 | Oct | 2021 | 0.2182 | 0.00088338 | Sustained | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-10-01 19:39 | 2021-10-01 23:46 | 451 | 004:07 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 CARGA POR SUBESTACION PORTATIL 1904 | S21100100208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2021-10-01 | 111397 | keep | 0 | Oct | 2021 | 0.075872 | 0.00030717 | Sustained | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-10-01 19:39 | 2021-10-01 23:46 | 1264 | 004:07 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 CARGA POR SUBESTACION PORTATIL 1904 | S21100100208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2021-10-01 | 312208 | keep | 0 | Oct | 2021 | 0.21264 | 0.0008609 | Sustained | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-10-01 19:39 | 2021-10-01 23:46 | 620 | 004:07 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 CARGA POR SUBESTACION PORTATIL 1904 | S21100100208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2021-10-01 | 153140 | keep | 0 | Oct | 2021 | 0.1043 | 0.00042228 | Sustained | FALSE | TRUE | Not_TMED_Event | 620
SAN JUAN | 2021-10-01 19:40 | 2021-10-03 10:20 | 15 | 038:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA SE REPARO SECUNDARIA | S21100100202 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2320 | 2021-10-01 | 34800 | keep | 0 | Oct | 2021 | 0.023702 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-01 19:53 | 2021-10-02 16:05 | 50 | 020:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21100100223 | New_Event | Bad Weather | Include | Include | Weather | 1212 | 2021-10-01 | 60600 | keep | 0 | Oct | 2021 | 0.041274 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-01 19:55 | 2021-10-01 20:59 | 60 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | R21100100141 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-10-01 | 3840 | keep | 0 | Oct | 2021 | 0.0026154 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-01 20:02 | 2021-10-03 09:22 | 40 | 037:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100100227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2240 | 2021-10-01 | 89600 | keep | 0 | Oct | 2021 | 0.061026 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-01 20:25 | 2021-10-02 01:00 | 144 | 004:35 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE. | P21100100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-10-01 | 39600 | keep | 0 | Oct | 2021 | 0.026971 | 9.8078e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 144
BARRANQUITAS | 2021-10-01 20:29 | 2021-10-02 12:29 | 150 | 016:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA REMPLAZO AISLADOR | C21100100184 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 960 | 2021-10-01 | 144000 | keep | 0 | Oct | 2021 | 0.098078 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-01 20:33 | 2021-10-01 22:28 | 653 | 001:55 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR RAMA SOBRE LA LINEA. SE ABREN MACHETES PARA SECCIONALIZAR AVERIA. | P21100100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-10-01 | 75095 | keep | 0 | Oct | 2021 | 0.051147 | 0.00044476 | Sustained | FALSE | TRUE | Not_TMED_Event | 653
PONCE | 2021-10-01 20:44 | 2021-10-01 20:45 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100102 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-01 20:44 | 2021-10-01 20:45 | 1746 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100102 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-10-01 20:44 | 2021-10-01 20:45 | 113 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100102 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
ARECIBO | 2021-10-01 20:46 | 2021-10-02 11:00 | 7 | 014:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 37.5 KVA | A21100100254 | New_Event | Service Transformer Failure | Include | Include | Equipment | 854 | 2021-10-01 | 5978 | keep | 0 | Oct | 2021 | 0.0040716 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-01 20:50 | 2021-10-01 20:51 | 2791 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES | A21100100000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-10-01 | 2791 | keep | 0 | Oct | 2021 | 0.0019009 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-01 20:59 | 2021-10-02 19:09 | 8 | 022:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | C21100100189 | New_Event | Wire Down | Include | Include | Equipment | 1330 | 2021-10-01 | 10640 | keep | 0 | Oct | 2021 | 0.0072469 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
PONCE | 2021-10-01 21:01 | 2021-10-01 21:02 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE INTERRUPTOR | P21100100111 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-01 21:01 | 2021-10-01 21:02 | 1746 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE INTERRUPTOR | P21100100011 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-10-01 21:01 | 2021-10-01 21:02 | 113 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE INTERRUPTOR | P21100100111 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
PONCE | 2021-10-01 21:04 | 2021-10-01 21:05 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21100100112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-01 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-10-01 21:04 | 2021-10-01 21:05 | 113 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE INTERRUPTOR | P21100100112 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
BARRANQUITAS | 2021-10-01 21:36 | 2021-10-02 11:38 | 8 | 014:02 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21100100191 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 842 | 2021-10-01 | 6736 | keep | 0 | Oct | 2021 | 0.0045879 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-10-01 21:45 | 2021-10-02 17:19 | 6 | 019:34 | P | ESTRUCTURA AVERIADA | SE RELOCALIZO TRANSFORMADOR DE POSTE PARTIDO | C21100100029 | New_Event | Defective Pole | Include | Include | Equipment | 1174 | 2021-10-01 | 7044 | keep | 0 | Oct | 2021 | 0.0047976 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-01 22:05 | 2021-10-01 22:06 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100123 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-01 22:05 | 2021-10-01 22:06 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100123 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-01 22:05 | 2021-10-01 22:06 | 113 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100123 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
ARECIBO | 2021-10-01 22:07 | 2021-10-02 19:30 | 150 | 021:23 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100275 | New_Event | Bad Weather | Include | Include | Weather | 1283 | 2021-10-01 | 192450 | keep | 0 | Oct | 2021 | 0.13108 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-01 22:09 | 2021-10-01 22:10 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100125 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-01 22:09 | 2021-10-01 22:10 | 1746 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100125 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-10-01 22:09 | 2021-10-01 22:10 | 113 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | P21100100125 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-01 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
PONCE | 2021-10-01 22:12 | 2021-10-01 23:28 | 778 | 001:16 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR POR AVERIA SOTETERRADA EN EL MH-406. SE SECCIONALIZO AVERIA Y SE CERRO INTERRUPTOR | P21100100127 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 76 | 2021-10-01 | 59128 | keep | 0 | Oct | 2021 | 0.040272 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-01 22:12 | 2021-10-01 23:28 | 1746 | 001:16 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR POR AVERIA SOTETERRADA EN EL MH-406. SE SECCIONALIZO AVERIA Y SE CERRO INTERRUPTOR. | P21100100127 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 76 | 2021-10-01 | 132696 | keep | 0 | Oct | 2021 | 0.090379 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-10-01 22:12 | 2021-10-01 23:28 | 113 | 001:16 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR POR AVERIA SOTETERRADA EN EL MH-406. SE SECCIONALIZO AVERIA Y SE CERRO INTERRUPTOR | P21100100127 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 76 | 2021-10-01 | 8588 | keep | 0 | Oct | 2021 | 0.0058492 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BARRANQUITAS | 2021-10-01 22:25 | 2021-10-03 16:01 | 4 | 041:36 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO 25 KVA X 25 LVA | C21100100135 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2496 | 2021-10-01 | 9984 | keep | 0 | Oct | 2021 | 0.0068001 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-10-01 22:28 | 2021-10-01 23:35 | 444 | 001:07 | P | DESGANCHE | SE RETIRO RAMA DE LA LINEA Y SE CERRARON MACHETES | P21100100140 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-10-01 | 29748 | keep | 0 | Oct | 2021 | 0.020261 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
GUAYAMA | 2021-10-01 22:29 | 2021-10-01 23:51 | 35 | 001:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21100100137 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2021-10-01 | 2870 | keep | 0 | Oct | 2021 | 0.0019547 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-10-01 22:38 | 2021-10-02 10:41 | 40 | 012:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE DE LINEA A CAJA | R21100100145 | New_Event | Wire Down | Include | Include | Equipment | 723 | 2021-10-01 | 28920 | keep | 0 | Oct | 2021 | 0.019697 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-01 22:51 | 2021-10-02 12:39 | 50 | 013:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100282 | Partial_restoration | Bad Weather | Include | Include | Weather | 828 | 2021-10-01 | 41400 | keep | 0 | Oct | 2021 | 0.028197 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-10-01 23:22 | 2021-10-02 19:10 | 6 | 019:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100100288 | New_Event | Bad Weather | Include | Include | Weather | 1188 | 2021-10-01 | 7128 | keep | 0 | Oct | 2021 | 0.0048548 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
PONCE | 2021-10-02 00:05 | 2021-10-05 13:23 | 2 | 085:18 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | PERSONAL DE SOTERRADO CAMBIO CABLE Y TERMINACION EN VACUUM SWITCH | P21100200001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 5118 | 2021-10-02 | 10236 | keep | 0 | Oct | 2021 | 0.0069717 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
UTUADO | 2021-10-02 00:40 | 2021-10-04 16:10 | 50 | 063:30 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE DE 45 PIES METAL FID-33678504 Y TRANSFORMADOR HOWARD 37.5 KVA 4160/120-240V SERIE 179541318 X 37.5KVA | A21100200002 | New_Event | Defective Pole | Include | Include | Equipment | 3810 | 2021-10-02 | 190500 | keep | 0 | Oct | 2021 | 0.12975 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2021-10-02 01:04 | 2021-10-02 09:53 | 10 | 008:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 529 | 2021-10-02 | 5290 | keep | 0 | Oct | 2021 | 0.003603 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
SAN JUAN | 2021-10-02 01:09 | 2021-10-02 01:10 | 2891 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO | R21100200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-02 | 2891 | keep | 0 | Oct | 2021 | 0.001969 | 0.001969 | Momentary | FALSE | FALSE | TMED_Event | 2891
SAN JUAN | 2021-10-02 01:10 | 2021-10-04 11:34 | 40 | 058:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA ELIMINO CAJA QUEMADA VACANTE | R21100200077 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 3504 | 2021-10-02 | 140160 | keep | 0 | Oct | 2021 | 0.095462 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 01:24 | 2021-10-02 14:45 | 40 | 013:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21100200004 | New_Event | Wire Down | Include | Include | Equipment | 801 | 2021-10-02 | 32040 | keep | 0 | Oct | 2021 | 0.021822 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
VEGA BAJA | 2021-10-02 01:40 | 2021-10-02 01:41 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1526 | keep | 0 | Oct | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | TMED_Event | 1526
SAN JUAN | 2021-10-02 01:48 | 2021-10-02 01:49 | 351 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 351 | keep | 0 | Oct | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | TMED_Event | 351
ARECIBO | 2021-10-02 04:29 | 2021-10-02 12:10 | 200 | 007:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100200007 | New_Event | Bad Weather | Include | Include | Weather | 461 | 2021-10-02 | 92200 | keep | 0 | Oct | 2021 | 0.062797 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CAGUAS | 2021-10-02 05:20 | 2021-10-02 14:31 | 50 | 009:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21100200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 551 | 2021-10-02 | 27550 | keep | 0 | Oct | 2021 | 0.018764 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-10-02 05:30 | 2021-10-02 13:19 | 1935 | 007:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | B21100200015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 469 | 2021-10-02 | 907515 | keep | 0 | Oct | 2021 | 0.6181 | 0.0013179 | Sustained | FALSE | TRUE | TMED_Event | 1935
BAYAMON | 2021-10-02 05:30 | 2021-10-02 13:19 | 3 | 007:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | B21100200015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 469 | 2021-10-02 | 1407 | keep | 0 | Oct | 2021 | 0.0009583 | 2.0433e-06 | Sustained | FALSE | TRUE | TMED_Event | 3
BAYAMON | 2021-10-02 05:30 | 2021-10-02 13:19 | 61 | 007:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | B21100200015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 469 | 2021-10-02 | 28609 | keep | 0 | Oct | 2021 | 0.019485 | 4.1547e-05 | Sustained | FALSE | TRUE | TMED_Event | 61
BAYAMON | 2021-10-02 05:30 | 2021-10-02 13:19 | 1501 | 007:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | B21100200015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 469 | 2021-10-02 | 703969 | keep | 0 | Oct | 2021 | 0.47947 | 0.0010223 | Sustained | FALSE | TRUE | TMED_Event | 1501
BAYAMON | 2021-10-02 05:30 | 2021-10-02 13:19 | 546 | 007:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | B21100200015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 469 | 2021-10-02 | 256074 | keep | 0 | Oct | 2021 | 0.17441 | 0.00037188 | Sustained | FALSE | TRUE | TMED_Event | 546
FAJARDO | 2021-10-02 05:30 | 2021-10-02 08:09 | 3003 | 002:39 | T | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZO AISLADOR QUEMADO | R21100200076 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 159 | 2021-10-02 | 477477 | keep | 0 | Oct | 2021 | 0.32521 | 0.0020453 | Sustained | FALSE | FALSE | TMED_Event | 3003
VEGA BAJA | 2021-10-02 05:37 | 2021-10-02 05:38 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | TMED_Event | 3000
FAJARDO | 2021-10-02 06:05 | 2021-10-02 08:53 | 1234 | 002:48 | T | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZO AISLADOR QUEMADO | R21100200033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 168 | 2021-10-02 | 207312 | keep | 0 | Oct | 2021 | 0.1412 | 0.00084047 | Sustained | FALSE | FALSE | TMED_Event | 1234
GUAYAMA | 2021-10-02 06:11 | 2021-10-02 06:12 | 1833 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P21100200006 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-02 | 1833 | keep | 0 | Oct | 2021 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | TMED_Event | 1833
GUAYAMA | 2021-10-02 06:12 | 2021-10-02 18:40 | 125 | 012:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y CORTE DE LINEA | P21100200161 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 748 | 2021-10-02 | 93500 | keep | 0 | Oct | 2021 | 0.063682 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
CAGUAS | 2021-10-02 06:15 | 2021-10-02 06:16 | 473 | 000:01 | T | DESGANCHE | RECIERRE | C21100200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 473 | keep | 0 | Oct | 2021 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | TMED_Event | 473
CAGUAS | 2021-10-02 06:16 | 2021-10-02 11:23 | 158 | 005:07 | P | DESGANCHE | DESGANCHE Y PUENTE ABIERTO | C21100200009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-10-02 | 48506 | keep | 0 | Oct | 2021 | 0.033037 | 0.00010761 | Sustained | FALSE | FALSE | TMED_Event | 158
BAYAMON | 2021-10-02 06:33 | 2021-10-02 14:08 | 80 | 007:35 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21100200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 455 | 2021-10-02 | 36400 | keep | 0 | Oct | 2021 | 0.024792 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
CANOVANAS | 2021-10-02 06:43 | 2021-10-02 09:47 | 80 | 003:04 | P | SOBRECARGA | 1 X 80 EN CORTE DE LINEA FUSIBLE FUNDIDO POR SOBRE CARGA DE LA LINEA | R21100200043 | New_Event | Trip Due To Overload | Include | Include | Other | 184 | 2021-10-02 | 14720 | keep | 0 | Oct | 2021 | 0.010026 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-10-02 06:50 | 2021-10-02 06:51 | 3744 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21100200009 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-02 | 3744 | keep | 0 | Oct | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | TMED_Event | 3744
PONCE | 2021-10-02 06:50 | 2021-10-02 06:51 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 3114 | keep | 0 | Oct | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | TMED_Event | 3114
MAYAGÃœEZ | 2021-10-02 07:06 | 2021-10-02 11:38 | 7 | 004:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-10-02 | 1904 | keep | 0 | Oct | 2021 | 0.0012968 | 4.7677e-06 | Sustained | FALSE | TRUE | TMED_Event | 7
CANOVANAS | 2021-10-02 07:09 | 2021-10-02 07:10 | 4188 | 000:01 | T | DESGANCHE | RECIERRE | R21100200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | TMED_Event | 4188
CANOVANAS | 2021-10-02 07:10 | 2021-10-02 13:04 | 100 | 005:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21100200111 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-10-02 | 35400 | keep | 0 | Oct | 2021 | 0.024111 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-10-02 07:25 | 2021-10-03 10:42 | 50 | 027:17 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1637 | 2021-10-02 | 81850 | keep | 0 | Oct | 2021 | 0.055748 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
VEGA BAJA | 2021-10-02 07:34 | 2021-10-02 13:22 | 8 | 005:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100200042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 348 | 2021-10-02 | 2784 | keep | 0 | Oct | 2021 | 0.0018962 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2021-10-02 07:38 | 2021-10-02 11:14 | 10 | 003:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100200022 | New_Event | Bad Weather | Include | Include | Weather | 216 | 2021-10-02 | 2160 | keep | 0 | Oct | 2021 | 0.0014712 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2021-10-02 07:42 | 2021-10-02 09:24 | 1565 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-02 | 159630 | keep | 0 | Oct | 2021 | 0.10872 | 0.0010659 | Sustained | FALSE | TRUE | TMED_Event | 1565
CAGUAS | 2021-10-02 07:42 | 2021-10-02 09:24 | 976 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-02 | 99552 | keep | 0 | Oct | 2021 | 0.067804 | 0.00066475 | Sustained | FALSE | TRUE | TMED_Event | 976
CAGUAS | 2021-10-02 07:42 | 2021-10-02 09:24 | 548 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-02 | 55896 | keep | 0 | Oct | 2021 | 0.038071 | 0.00037324 | Sustained | FALSE | TRUE | TMED_Event | 548
CAGUAS | 2021-10-02 07:42 | 2021-10-02 12:04 | 315 | 004:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 262 | 2021-10-02 | 82530 | keep | 0 | Oct | 2021 | 0.056211 | 0.00021455 | Sustained | FALSE | TRUE | TMED_Event | 315
CAGUAS | 2021-10-02 07:42 | 2021-10-02 12:04 | 870 | 004:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 262 | 2021-10-02 | 227940 | keep | 0 | Oct | 2021 | 0.15525 | 0.00059255 | Sustained | FALSE | TRUE | TMED_Event | 870
CAGUAS | 2021-10-02 07:42 | 2021-10-02 12:04 | 2906 | 004:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 262 | 2021-10-02 | 761372 | keep | 0 | Oct | 2021 | 0.51857 | 0.0019793 | Sustained | FALSE | TRUE | TMED_Event | 2906
CAGUAS | 2021-10-02 07:42 | 2021-10-02 12:04 | 2343 | 004:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 262 | 2021-10-02 | 613866 | keep | 0 | Oct | 2021 | 0.4181 | 0.0015958 | Sustained | FALSE | TRUE | TMED_Event | 2343
FAJARDO | 2021-10-02 07:54 | 2021-10-02 14:14 | 100 | 006:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA CRUCE CON TENSOR | R21100200071 | New_Event | Wire Down | Include | Include | Equipment | 380 | 2021-10-02 | 38000 | keep | 0 | Oct | 2021 | 0.025882 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
FAJARDO | 2021-10-02 08:09 | 2021-10-02 12:50 | 1750 | 004:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZO AISLADOR QUEMADO | R21100200076 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 281 | 2021-10-02 | 491750 | keep | 0 | Oct | 2021 | 0.33493 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
MAYAGÃœEZ | 2021-10-02 08:10 | 2021-10-03 09:31 | 100 | 025:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 Y 1 X 100 EN CORTES DE LINEA SE REMPLAZO PORTAFUSIBLES AVERIADO | M21100200027 | New_Event | Cutout Failure | Include | Include | Equipment | 1521 | 2021-10-02 | 152100 | keep | 0 | Oct | 2021 | 0.10359 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BARRANQUITAS | 2021-10-02 08:13 | 2021-10-02 12:07 | 5 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21100100033 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2021-10-02 | 1170 | keep | 0 | Oct | 2021 | 0.00079688 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
HUMACAO | 2021-10-02 08:22 | 2021-10-02 17:13 | 300 | 008:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN RISER 2 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21100200064 | New_Event | Bad Weather | Include | Include | Weather | 531 | 2021-10-02 | 159300 | keep | 0 | Oct | 2021 | 0.1085 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
BAYAMON | 2021-10-02 08:52 | 2021-10-02 12:06 | 30 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21100200066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2021-10-02 | 5820 | keep | 0 | Oct | 2021 | 0.003964 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
FAJARDO | 2021-10-02 08:53 | 2021-10-02 11:24 | 634 | 002:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZO AISLADOR QUEMADO | R21100200033 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2021-10-02 | 95734 | keep | 0 | Oct | 2021 | 0.065204 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
PONCE | 2021-10-02 08:59 | 2021-10-02 18:53 | 20 | 009:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21100200019 | New_Event | Bad Weather | Include | Include | Weather | 594 | 2021-10-02 | 11880 | keep | 0 | Oct | 2021 | 0.0080914 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
PONCE | 2021-10-02 09:03 | 2021-10-02 12:49 | 100 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P21100200020 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2021-10-02 | 22600 | keep | 0 | Oct | 2021 | 0.015393 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
PONCE | 2021-10-02 09:13 | 2021-10-03 11:57 | 4 | 026:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | P21092800083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1604 | 2021-10-02 | 6416 | keep | 0 | Oct | 2021 | 0.0043699 | 2.7244e-06 | Sustained | FALSE | TRUE | TMED_Event | 4
MAYAGÃœEZ | 2021-10-02 09:30 | 2021-10-03 14:05 | 8 | 028:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21100200056 | New_Event | Bad Weather | Include | Include | Weather | 1715 | 2021-10-02 | 13720 | keep | 0 | Oct | 2021 | 0.0093446 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
UTUADO | 2021-10-02 09:31 | 2021-10-03 10:19 | 5 | 024:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21100200034 | New_Event | Bad Weather | Include | Include | Weather | 1488 | 2021-10-02 | 7440 | keep | 0 | Oct | 2021 | 0.0050674 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2021-10-02 09:47 | 2021-10-02 11:05 | 12 | 001:18 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | B21100200091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-02 | 936 | keep | 0 | Oct | 2021 | 0.00063751 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
MAYAGÃœEZ | 2021-10-02 09:52 | 2021-10-02 11:39 | 50 | 001:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21100200058 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2021-10-02 | 5350 | keep | 0 | Oct | 2021 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
FAJARDO | 2021-10-02 10:02 | 2021-10-02 15:14 | 60 | 005:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21100200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2021-10-02 | 18720 | keep | 0 | Oct | 2021 | 0.01275 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
MAYAGÃœEZ | 2021-10-02 10:03 | 2021-10-02 20:15 | 80 | 010:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21100100067 | New_Event | Bad Weather | Include | Include | Weather | 612 | 2021-10-02 | 48960 | keep | 0 | Oct | 2021 | 0.033346 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-10-02 10:04 | 2021-10-02 12:18 | 87 | 002:14 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA POR PARARRAYO CRUZADO | P21100200030 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 134 | 2021-10-02 | 11658 | keep | 0 | Oct | 2021 | 0.0079402 | 5.9255e-05 | Sustained | FALSE | TRUE | TMED_Event | 87
CANOVANAS | 2021-10-02 10:08 | 2021-10-02 12:16 | 40 | 002:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21100200103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-10-02 | 5120 | keep | 0 | Oct | 2021 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 10:14 | 2021-10-02 10:15 | 2231 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS DE ARBOL SOBRE LAS LINEAS | A21100200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | TMED_Event | 2231
SAN JUAN | 2021-10-02 10:20 | 2021-10-02 10:21 | 10211 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO CARGA POR EL 1206-03 | S21100200031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-02 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | TMED_Event | 10211
SAN JUAN | 2021-10-02 10:20 | 2021-10-02 10:21 | 4133 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO LLEVA 1204-05 | S21100200031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-02 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2021-10-02 10:22 | 2021-10-02 11:09 | 4133 | 000:47 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO CON RECIERRE EN OFF SE PATRULLO SE RETIRO PALMA CRUZANDO FASE Y SE REMPLAZO AISLADOR CARR. 846 KM 0.4 COVADONGA LLEVA 1204-05 | S21100200031 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 47 | 2021-10-02 | 194251 | keep | 0 | Oct | 2021 | 0.1323 | 0.002815 | Sustained | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2021-10-02 10:23 | 2021-10-02 11:09 | 10211 | 000:46 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO CON RECIERRE EN OFF SE PATRULLO SE RETIRO PALMA CRUZANDO FASE Y SE REMPLAZO AISLADOR CARR 846 KM 0.4 COVADONGA CARGA POR EL 1206-03 | S21100200031 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 46 | 2021-10-02 | 469706 | keep | 0 | Oct | 2021 | 0.31991 | 0.0069547 | Sustained | FALSE | FALSE | TMED_Event | 10211
MAYAGÃœEZ | 2021-10-02 10:29 | 2021-10-03 12:23 | 300 | 025:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR AVERIA DE LINEA PRIMARIA ROTA | M21100200066 | New_Event | Wire Down | Include | Include | Equipment | 1554 | 2021-10-02 | 466200 | keep | 0 | Oct | 2021 | 0.31753 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
ARECIBO | 2021-10-02 10:34 | 2021-10-02 10:35 | 2231 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS DE ARBOL SOBRE LAS LINEAS | A21100200043 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | TMED_Event | 2231
ARECIBO | 2021-10-02 10:35 | 2021-10-03 10:18 | 40 | 023:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100200046 | New_Event | Bad Weather | Include | Include | Weather | 1423 | 2021-10-02 | 56920 | keep | 0 | Oct | 2021 | 0.038768 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 10:38 | 2021-10-02 10:39 | 2231 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS DE ARBOL SOBRE LAS LINEAS | A21100200043 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | TMED_Event | 2231
BAYAMON | 2021-10-02 10:40 | 2021-10-02 10:41 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1720-08 | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 2402 | keep | 0 | Oct | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | TMED_Event | 2402
BAYAMON | 2021-10-02 10:40 | 2021-10-02 10:41 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1709-02 | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1 | keep | 0 | Oct | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | TMED_Event | 1
FAJARDO | 2021-10-02 10:40 | 2021-10-02 13:14 | 200 | 002:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO | R21100200111 | New_Event | Bad Weather | Include | Include | Weather | 154 | 2021-10-02 | 30800 | keep | 0 | Oct | 2021 | 0.020978 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
ARECIBO | 2021-10-02 10:41 | 2021-10-02 10:42 | 2231 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS DE ARBOL SOBRE LAS LINEAS | A21100200043 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | TMED_Event | 2231
ARECIBO | 2021-10-02 10:45 | 2021-10-02 10:46 | 2231 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS DE ARBOL SOBRE LAS LINEAS | A21100200043 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | TMED_Event | 2231
ARECIBO | 2021-10-02 10:47 | 2021-10-02 12:24 | 2231 | 001:37 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE RETIRO RAMAS DE ARBOL SOBRE LAS LINEAS | A21100200053 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-10-02 | 216407 | keep | 0 | Oct | 2021 | 0.14739 | 0.0015195 | Sustained | FALSE | TRUE | TMED_Event | 2231
SAN JUAN | 2021-10-02 10:48 | 2021-10-02 12:26 | 87 | 001:38 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21100200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2021-10-02 | 8526 | keep | 0 | Oct | 2021 | 0.005807 | 5.9255e-05 | Sustained | FALSE | TRUE | TMED_Event | 87
PONCE | 2021-10-02 10:48 | 2021-10-02 10:49 | 1979 | 000:01 | S | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE PORTATIL 10 | P211002000XX | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-02 | 1979 | keep | 0 | Oct | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | TMED_Event | 1979
PONCE | 2021-10-02 10:48 | 2021-10-02 10:49 | 5069 | 000:01 | S | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE PORTATIL 10 | P211002000XX | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-02 | 5069 | keep | 0 | Oct | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | TMED_Event | 5069
PONCE | 2021-10-02 10:48 | 2021-10-02 10:49 | 5063 | 000:01 | S | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE PORTATIL 10 | P211002000XX | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-02 | 5063 | keep | 0 | Oct | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | TMED_Event | 5063
BAYAMON | 2021-10-02 10:52 | 2021-10-02 14:59 | 50 | 004:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | B21100200115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2021-10-02 | 12350 | keep | 0 | Oct | 2021 | 0.0084115 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-10-02 10:52 | 2021-10-02 12:26 | 69 | 001:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100200115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-10-02 | 6486 | keep | 0 | Oct | 2021 | 0.0044176 | 4.6996e-05 | Sustained | FALSE | TRUE | TMED_Event | 69
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 108 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 1368 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 1368 | keep | 0 | Oct | 2021 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | TMED_Event | 1368
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 2064 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 2064 | keep | 0 | Oct | 2021 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | TMED_Event | 2064
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 1681 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 1681 | keep | 0 | Oct | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | TMED_Event | 1681
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 2435 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 2435 | keep | 0 | Oct | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | TMED_Event | 2435
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 726 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 LLEVA EL 1346-04 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 726 | keep | 0 | Oct | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | TMED_Event | 726
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 225 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 225 | keep | 0 | Oct | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 870 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECERRO L-36200 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 870 | keep | 0 | Oct | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | TMED_Event | 870
SAN JUAN | 2021-10-02 10:53 | 2021-10-02 10:54 | 3932 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECERRO L-36200 CARGA POR EL 1303-03 | S21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 3932 | keep | 0 | Oct | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | TMED_Event | 3932
FAJARDO | 2021-10-02 10:58 | 2021-10-02 11:52 | 60 | 000:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTES DE LINEA SE REEMPLAZO CAJA | R21100200114 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2021-10-02 | 3240 | keep | 0 | Oct | 2021 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
GUAYAMA | 2021-10-02 11:09 | 2021-10-02 13:32 | 12 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | P21100200035 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2021-10-02 | 1716 | keep | 0 | Oct | 2021 | 0.0011688 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
MAYAGÃœEZ | 2021-10-02 11:16 | 2021-10-02 14:00 | 300 | 002:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21100200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-10-02 | 49200 | keep | 0 | Oct | 2021 | 0.03351 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
HUMACAO | 2021-10-02 11:22 | 2021-10-02 20:36 | 40 | 009:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21100200134 | New_Event | Bad Weather | Include | Include | Weather | 554 | 2021-10-02 | 22160 | keep | 0 | Oct | 2021 | 0.015093 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-10-02 11:22 | 2021-10-02 18:10 | 150 | 006:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | B21100200125 | New_Event | Wire Down | Include | Include | Equipment | 408 | 2021-10-02 | 61200 | keep | 0 | Oct | 2021 | 0.041683 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CAGUAS | 2021-10-02 11:23 | 2021-10-02 14:18 | 1271 | 002:55 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA DESGANCHAR REMPLAZAR 2 PIN Y LEVANTAR NEUTRAL PRIMARIO EN LA SALIDA DEL INTERRUPTOR | C21100200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-10-02 | 222425 | keep | 0 | Oct | 2021 | 0.15149 | 0.00086567 | Sustained | FALSE | FALSE | TMED_Event | 1271
CAGUAS | 2021-10-02 11:23 | 2021-10-02 14:18 | 473 | 002:55 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA DESGANCHAR Y CERRAR PUENTE | C21100200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-10-02 | 82775 | keep | 0 | Oct | 2021 | 0.056378 | 0.00032216 | Sustained | FALSE | FALSE | TMED_Event | 473
BAYAMON | 2021-10-02 11:35 | 2021-10-02 11:36 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 2605 | keep | 0 | Oct | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | TMED_Event | 2605
CANOVANAS | 2021-10-02 11:35 | 2021-10-02 11:36 | 1648 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R21100200130 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-02 | 1648 | keep | 0 | Oct | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | TMED_Event | 1648
CANOVANAS | 2021-10-02 11:36 | 2021-10-02 15:33 | 166 | 003:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21100200141 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 237 | 2021-10-02 | 39342 | keep | 0 | Oct | 2021 | 0.026796 | 0.00011306 | Sustained | FALSE | TRUE | TMED_Event | 166
CAGUAS | 2021-10-02 11:43 | 2021-10-02 12:58 | 1228 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14400 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2021-10-02 | 92100 | keep | 0 | Oct | 2021 | 0.062729 | 0.00083639 | Sustained | FALSE | TRUE | TMED_Event | 1228
CAGUAS | 2021-10-02 11:43 | 2021-10-02 12:58 | 1893 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14400 | C21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2021-10-02 | 141975 | keep | 0 | Oct | 2021 | 0.096699 | 0.0012893 | Sustained | FALSE | TRUE | TMED_Event | 1893
CAGUAS | 2021-10-02 11:46 | 2021-10-02 11:49 | 1879 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO | C21100200158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-02 | 5637 | keep | 0 | Oct | 2021 | 0.0038393 | 0.0012798 | Momentary | FALSE | FALSE | TMED_Event | 1879
FAJARDO | 2021-10-02 11:52 | 2021-10-02 11:53 | 1234 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R21100200000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-02 | 1234 | keep | 0 | Oct | 2021 | 0.00084047 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
FAJARDO | 2021-10-02 11:53 | 2021-10-02 15:38 | 60 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTES DE LINEA SE REEMPLAZO CAJA | R21100200114 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 225 | 2021-10-02 | 13500 | keep | 0 | Oct | 2021 | 0.0091948 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
FAJARDO | 2021-10-02 11:53 | 2021-10-02 16:26 | 50 | 004:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21100200176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-10-02 | 13650 | keep | 0 | Oct | 2021 | 0.009297 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-10-02 11:54 | 2021-10-03 13:55 | 250 | 026:01 | P | DESGANCHE | 2 X 65 Y 1 X 140 EN CORTES DE LINEA | C21100200166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1561 | 2021-10-02 | 390250 | keep | 0 | Oct | 2021 | 0.2658 | 0.00017027 | Sustained | FALSE | TRUE | TMED_Event | 250
HUMACAO | 2021-10-02 11:57 | 2021-10-02 19:27 | 100 | 007:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | C21100200173 | New_Event | Bad Weather | Include | Include | Weather | 450 | 2021-10-02 | 45000 | keep | 0 | Oct | 2021 | 0.030649 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
HUMACAO | 2021-10-02 11:59 | 2021-10-02 15:42 | 100 | 003:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA REMPLAZO AISLADOR | C21100200177 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 223 | 2021-10-02 | 22300 | keep | 0 | Oct | 2021 | 0.015188 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
PONCE | 2021-10-02 12:00 | 2021-10-02 13:57 | 70 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21100100077 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-10-02 | 8190 | keep | 0 | Oct | 2021 | 0.0055782 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
BAYAMON | 2021-10-02 12:00 | 2021-10-02 13:11 | 25 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21100200129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2021-10-02 | 1775 | keep | 0 | Oct | 2021 | 0.0012089 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
BAYAMON | 2021-10-02 12:11 | 2021-10-02 15:27 | 10 | 003:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADO AVERIADO 37.5 X 37.5KVA | S21100200067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 196 | 2021-10-02 | 1960 | keep | 0 | Oct | 2021 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2021-10-02 12:18 | 2021-10-02 15:37 | 1382 | 003:19 | T | NO SE REPORTO CAUSA | DISPARO LLEVANDO LA CARGA DEL 1706-03 SE ABRIO AMARRE Y SE CERRO EL 1706-02 | B21100200152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2021-10-02 | 275018 | keep | 0 | Oct | 2021 | 0.18731 | 0.00094127 | Sustained | FALSE | FALSE | TMED_Event | 1382
BAYAMON | 2021-10-02 12:18 | 2021-10-02 16:50 | 663 | 004:32 | T | NO SE REPORTO CAUSA | NO SE ENCONTRO CAUSA APARENTE Y SE CERRO AMARRE ENTRE 1706-02 Y 1706-03 | B21100200152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2021-10-02 | 180336 | keep | 0 | Oct | 2021 | 0.12283 | 0.00045157 | Sustained | FALSE | FALSE | TMED_Event | 663
PONCE | 2021-10-02 12:19 | 2021-10-03 12:00 | 40 | 023:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21100200045 | New_Event |  |  | Include | Wildlife | 1421 | 2021-10-02 | 56840 | keep | 0 | Oct | 2021 | 0.038713 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 12:20 | 2021-10-02 14:44 | 75 | 002:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100200077 | New_Event | Bad Weather | Include | Include | Weather | 144 | 2021-10-02 | 10800 | keep | 0 | Oct | 2021 | 0.0073558 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
CAGUAS | 2021-10-02 12:21 | 2021-10-02 16:11 | 1087 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 ENTRADA DE CONVERTIDOR CERRO PUENTE | C21100200203 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2021-10-02 | 250010 | keep | 0 | Oct | 2021 | 0.17028 | 0.00074035 | Sustained | FALSE | FALSE | TMED_Event | 1087
BAYAMON | 2021-10-02 12:22 | 2021-10-02 12:23 | 74 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF CARGA POR EL 1529-11 | S21100200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 74 | keep | 0 | Oct | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2021-10-02 12:22 | 2021-10-02 12:23 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF LLEVA EL 1521-02 | S21100200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1370 | keep | 0 | Oct | 2021 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | TMED_Event | 1370
BAYAMON | 2021-10-02 12:23 | 2021-10-02 14:02 | 1 | 001:39 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO COORDINADO CON ING. BERMUDEZ A.A.A | B21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-10-02 | 99 | keep | 0 | Oct | 2021 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2021-10-02 12:30 | 2021-10-03 10:51 | 25 | 022:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21100200078 | New_Event | Bad Weather | Include | Include | Weather | 1341 | 2021-10-02 | 33525 | keep | 0 | Oct | 2021 | 0.022834 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
BAYAMON | 2021-10-02 12:32 | 2021-10-02 12:33 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1085 | keep | 0 | Oct | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | TMED_Event | 1085
BAYAMON | 2021-10-02 12:32 | 2021-10-03 16:15 | 60 | 027:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21100200166 | New_Event | Wire Down | Include | Include | Equipment | 1663 | 2021-10-02 | 99780 | keep | 0 | Oct | 2021 | 0.06796 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
PONCE | 2021-10-02 12:32 | 2021-10-02 12:33 | 2113 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21100200046 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-02 | 2113 | keep | 0 | Oct | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | TMED_Event | 2113
PONCE | 2021-10-02 12:33 | 2021-10-03 01:30 | 100 | 012:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REALIZARON EMPALMES EN CABLE SOTERRADO AVERIADO POR EXCAVASION DE PERSONAL DE AAA SE CERRO DEL SU-5 AL PM-60 | P21100100092 | 1st_after_momentary |  |  | Include | Wildlife | 777 | 2021-10-02 | 77700 | keep | 0 | Oct | 2021 | 0.052921 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
VEGA BAJA | 2021-10-02 12:39 | 2021-10-02 13:32 | 30 | 000:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | B21100200171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-10-02 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-10-02 12:39 | 2021-10-03 11:11 | 50 | 022:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100200169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1352 | 2021-10-02 | 67600 | keep | 0 | Oct | 2021 | 0.046042 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-10-02 12:44 | 2021-10-02 17:00 | 25 | 004:16 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | A21100200089 | New_Event | Defective Pole | Include | Include | Equipment | 256 | 2021-10-02 | 6400 | keep | 0 | Oct | 2021 | 0.004359 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BAYAMON | 2021-10-02 12:51 | 2021-10-02 14:23 | 40 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | B21100200178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-10-02 | 3680 | keep | 0 | Oct | 2021 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-10-02 12:56 | 2021-10-02 14:36 | 150 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | P21100200048 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-10-02 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
SAN JUAN | 2021-10-02 13:08 | 2021-10-03 13:31 | 12 | 024:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE Y SE HIZO DESGANCHE | S21100200081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1463 | 2021-10-02 | 17556 | keep | 0 | Oct | 2021 | 0.011957 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BAYAMON | 2021-10-02 13:11 | 2021-10-02 22:25 | 40 | 009:14 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTE DE LINEAS | B21100200186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 554 | 2021-10-02 | 22160 | keep | 0 | Oct | 2021 | 0.015093 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 2791 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 11164 | keep | 0 | Oct | 2021 | 0.0076037 | 0.0019009 | Momentary | FALSE | TRUE | TMED_Event | 2791
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 1464 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 5856 | keep | 0 | Oct | 2021 | 0.0039885 | 0.00099712 | Momentary | FALSE | TRUE | TMED_Event | 1464
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 759 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 3036 | keep | 0 | Oct | 2021 | 0.0020678 | 0.00051695 | Momentary | FALSE | TRUE | TMED_Event | 759
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 1500 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 6000 | keep | 0 | Oct | 2021 | 0.0040866 | 0.0010216 | Momentary | FALSE | TRUE | TMED_Event | 1500
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 2132 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 8528 | keep | 0 | Oct | 2021 | 0.0058084 | 0.0014521 | Momentary | FALSE | TRUE | TMED_Event | 2132
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 2366 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 9464 | keep | 0 | Oct | 2021 | 0.0064459 | 0.0016115 | Momentary | FALSE | TRUE | TMED_Event | 2366
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 1976 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 7904 | keep | 0 | Oct | 2021 | 0.0053834 | 0.0013458 | Momentary | FALSE | TRUE | TMED_Event | 1976
ARECIBO | 2021-10-02 13:11 | 2021-10-02 13:15 | 3688 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 14752 | keep | 0 | Oct | 2021 | 0.010048 | 0.0025119 | Momentary | FALSE | TRUE | TMED_Event | 3688
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 3070 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 12280 | keep | 0 | Oct | 2021 | 0.0083639 | 0.002091 | Momentary | FALSE | TRUE | TMED_Event | 3070
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 2735 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 10940 | keep | 0 | Oct | 2021 | 0.0074512 | 0.0018628 | Momentary | FALSE | TRUE | TMED_Event | 2735
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 1070 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 4280 | keep | 0 | Oct | 2021 | 0.0029151 | 0.00072877 | Momentary | FALSE | TRUE | TMED_Event | 1070
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 1647 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 6588 | keep | 0 | Oct | 2021 | 0.0044871 | 0.0011218 | Momentary | FALSE | TRUE | TMED_Event | 1647
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 3295 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 13180 | keep | 0 | Oct | 2021 | 0.0089768 | 0.0022442 | Momentary | FALSE | TRUE | TMED_Event | 3295
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 1180 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 4720 | keep | 0 | Oct | 2021 | 0.0032148 | 0.00080369 | Momentary | FALSE | TRUE | TMED_Event | 1180
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 320 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 1280 | keep | 0 | Oct | 2021 | 0.0008718 | 0.00021795 | Momentary | FALSE | TRUE | TMED_Event | 320
BAYAMON | 2021-10-02 13:11 | 2021-10-02 13:15 | 2234 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21100200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-02 | 8936 | keep | 0 | Oct | 2021 | 0.0060863 | 0.0015216 | Momentary | FALSE | TRUE | TMED_Event | 2234
ARECIBO | 2021-10-02 13:15 | 2021-10-02 13:37 | 20 | 000:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100100111 | New_Event | Bad Weather | Include | Include | Weather | 22 | 2021-10-02 | 440 | keep | 0 | Oct | 2021 | 0.00029968 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
BAYAMON | 2021-10-02 13:15 | 2021-10-02 14:20 | 25 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21100200129 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 65 | 2021-10-02 | 1625 | keep | 0 | Oct | 2021 | 0.0011068 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:00 | 591 | 003:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21100200211 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 224 | 2021-10-02 | 132384 | keep | 0 | Oct | 2021 | 0.090166 | 0.00040253 | Sustained | FALSE | TRUE | TMED_Event | 591
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 1924 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 230880 | keep | 0 | Oct | 2021 | 0.15725 | 0.0013104 | Sustained | FALSE | TRUE | TMED_Event | 1924
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 968 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 116160 | keep | 0 | Oct | 2021 | 0.079116 | 0.0006593 | Sustained | FALSE | TRUE | TMED_Event | 968
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 680 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 81600 | keep | 0 | Oct | 2021 | 0.055577 | 0.00046314 | Sustained | FALSE | TRUE | TMED_Event | 680
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 2246 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 269520 | keep | 0 | Oct | 2021 | 0.18357 | 0.0015297 | Sustained | FALSE | TRUE | TMED_Event | 2246
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:30 | 2470 | 004:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 254 | 2021-10-02 | 627380 | keep | 0 | Oct | 2021 | 0.42731 | 0.0016823 | Sustained | FALSE | TRUE | TMED_Event | 2470
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:30 | 1182 | 004:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 254 | 2021-10-02 | 300228 | keep | 0 | Oct | 2021 | 0.20448 | 0.00080505 | Sustained | FALSE | TRUE | TMED_Event | 1182
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:30 | 2340 | 004:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 254 | 2021-10-02 | 594360 | keep | 0 | Oct | 2021 | 0.40482 | 0.0015938 | Sustained | FALSE | TRUE | TMED_Event | 2340
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:30 | 1637 | 004:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200208 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 254 | 2021-10-02 | 415798 | keep | 0 | Oct | 2021 | 0.2832 | 0.001115 | Sustained | FALSE | TRUE | TMED_Event | 1637
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:00 | 1475 | 003:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 224 | 2021-10-02 | 330400 | keep | 0 | Oct | 2021 | 0.22503 | 0.0010046 | Sustained | FALSE | TRUE | TMED_Event | 1475
YAUCO | 2021-10-02 13:16 | 2021-10-02 17:00 | 661 | 003:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 224 | 2021-10-02 | 148064 | keep | 0 | Oct | 2021 | 0.10085 | 0.0004502 | Sustained | FALSE | TRUE | TMED_Event | 661
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 1569 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200192 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 188280 | keep | 0 | Oct | 2021 | 0.12824 | 0.0010686 | Sustained | FALSE | TRUE | TMED_Event | 1569
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 2309 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200192 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 277080 | keep | 0 | Oct | 2021 | 0.18872 | 0.0015726 | Sustained | FALSE | TRUE | TMED_Event | 2309
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 2179 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200192 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 261480 | keep | 0 | Oct | 2021 | 0.17809 | 0.0014841 | Sustained | FALSE | TRUE | TMED_Event | 2179
YAUCO | 2021-10-02 13:16 | 2021-10-02 15:16 | 2440 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200192 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-10-02 | 292800 | keep | 0 | Oct | 2021 | 0.19942 | 0.0016619 | Sustained | FALSE | TRUE | TMED_Event | 2440
YAUCO | 2021-10-02 13:16 | 2021-10-02 23:48 | 1352 | 010:32 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 632 | 2021-10-02 | 854464 | keep | 0 | Oct | 2021 | 0.58197 | 0.00092084 | Sustained | FALSE | TRUE | TMED_Event | 1352
YAUCO | 2021-10-02 13:16 | 2021-10-02 23:48 | 3973 | 010:32 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 632 | 2021-10-02 | 2510936 | keep | 0 | Oct | 2021 | 1.7102 | 0.002706 | Sustained | FALSE | TRUE | TMED_Event | 3973
YAUCO | 2021-10-02 13:16 | 2021-10-02 23:48 | 2484 | 010:32 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21100200210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 632 | 2021-10-02 | 1569888 | keep | 0 | Oct | 2021 | 1.0692 | 0.0016918 | Sustained | FALSE | TRUE | TMED_Event | 2484
BARRANQUITAS | 2021-10-02 13:16 | 2021-10-02 15:52 | 150 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO | C21100200232 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-10-02 | 23400 | keep | 0 | Oct | 2021 | 0.015938 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
MAYAGÃœEZ | 2021-10-02 13:22 | 2021-10-02 17:50 | 281 | 004:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 268 | 2021-10-02 | 75308 | keep | 0 | Oct | 2021 | 0.051292 | 0.00019139 | Sustained | FALSE | TRUE | TMED_Event | 281
MAYAGÃœEZ | 2021-10-02 13:22 | 2021-10-02 17:50 | 1252 | 004:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 268 | 2021-10-02 | 335536 | keep | 0 | Oct | 2021 | 0.22853 | 0.00085273 | Sustained | FALSE | TRUE | TMED_Event | 1252
MAYAGÃœEZ | 2021-10-02 13:22 | 2021-10-02 17:50 | 595 | 004:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 268 | 2021-10-02 | 159460 | keep | 0 | Oct | 2021 | 0.10861 | 0.00040525 | Sustained | FALSE | TRUE | TMED_Event | 595
MAYAGÃœEZ | 2021-10-02 13:22 | 2021-10-02 17:50 | 51 | 004:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 268 | 2021-10-02 | 13668 | keep | 0 | Oct | 2021 | 0.0093092 | 3.4736e-05 | Sustained | FALSE | TRUE | TMED_Event | 51
MAYAGÃœEZ | 2021-10-02 13:22 | 2021-10-02 17:50 | 721 | 004:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 268 | 2021-10-02 | 193228 | keep | 0 | Oct | 2021 | 0.13161 | 0.00049107 | Sustained | FALSE | TRUE | TMED_Event | 721
PONCE | 2021-10-02 13:24 | 2021-10-02 18:23 | 100 | 004:59 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | P21100200183 | New_Event | Bad Weather | Include | Include | Weather | 299 | 2021-10-02 | 29900 | keep | 0 | Oct | 2021 | 0.020365 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-10-02 13:29 | 2021-10-04 09:48 | 1 | 044:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100200096 | New_Event | Bad Weather | Include | Include | Weather | 2659 | 2021-10-02 | 2659 | keep | 0 | Oct | 2021 | 0.001811 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
GUAYAMA | 2021-10-02 13:32 | 2021-10-02 13:33 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100200078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 4132 | keep | 0 | Oct | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | TMED_Event | 4132
ARECIBO | 2021-10-02 13:32 | 2021-10-02 14:57 | 15 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100200098 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-10-02 | 1275 | keep | 0 | Oct | 2021 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
GUAYAMA | 2021-10-02 13:33 | 2021-10-02 15:20 | 12 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | P21100200035 | Partial_restoration | Bad Weather | Include | Include | Weather | 107 | 2021-10-02 | 1284 | keep | 0 | Oct | 2021 | 0.00087453 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
MAYAGÃœEZ | 2021-10-02 13:33 | 2021-10-02 13:34 | 1671 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21100200107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 1671 | keep | 0 | Oct | 2021 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | TMED_Event | 1671
MAYAGÃœEZ | 2021-10-02 13:33 | 2021-10-02 13:34 | 3036 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR | M21100200109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-10-02 | 3036 | keep | 0 | Oct | 2021 | 0.0020678 | 0.0020678 | Momentary | FALSE | FALSE | TMED_Event | 3036
VEGA BAJA | 2021-10-02 13:33 | 2021-10-02 22:36 | 10 | 009:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100200197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 543 | 2021-10-02 | 5430 | keep | 0 | Oct | 2021 | 0.0036983 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CANOVANAS | 2021-10-02 13:34 | 2021-10-02 17:01 | 325 | 003:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21100200153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-10-02 | 67275 | keep | 0 | Oct | 2021 | 0.045821 | 0.00022136 | Sustained | FALSE | TRUE | TMED_Event | 325
MAYAGÃœEZ | 2021-10-02 13:34 | 2021-10-02 18:20 | 100 | 004:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21100200189 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-10-02 | 28600 | keep | 0 | Oct | 2021 | 0.019479 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CANOVANAS | 2021-10-02 13:37 | 2021-10-02 16:54 | 325 | 003:17 | P | DESGANCHE | 2 X 140 Y 1 X 80 EN CORTES DE LINEA | R21100200155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-10-02 | 64025 | keep | 0 | Oct | 2021 | 0.043607 | 0.00022136 | Sustained | FALSE | TRUE | TMED_Event | 325
BARRANQUITAS | 2021-10-02 13:38 | 2021-10-03 10:04 | 10 | 020:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO CAJA AVERIADA | C21100200247 | New_Event | Cutout Failure | Include | Include | Equipment | 1226 | 2021-10-02 | 12260 | keep | 0 | Oct | 2021 | 0.0083502 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
MAYAGÃœEZ | 2021-10-02 13:41 | 2021-10-03 12:38 | 140 | 022:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21100200112 | New_Event | Bad Weather | Include | Include | Weather | 1377 | 2021-10-02 | 192780 | keep | 0 | Oct | 2021 | 0.1313 | 9.5353e-05 | Sustained | FALSE | TRUE | TMED_Event | 140
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 13:44 | 2999 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21100200116 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-02 | 2999 | keep | 0 | Oct | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | TMED_Event | 2999
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 1339 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 29458 | keep | 0 | Oct | 2021 | 0.020064 | 0.00091199 | Sustained | FALSE | TRUE | TMED_Event | 1339
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 470 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 10340 | keep | 0 | Oct | 2021 | 0.0070425 | 0.00032011 | Sustained | FALSE | TRUE | TMED_Event | 470
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 2483 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 54626 | keep | 0 | Oct | 2021 | 0.037206 | 0.0016912 | Sustained | FALSE | TRUE | TMED_Event | 2483
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 2190 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 48180 | keep | 0 | Oct | 2021 | 0.032815 | 0.0014916 | Sustained | FALSE | TRUE | TMED_Event | 2190
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 3006 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 66132 | keep | 0 | Oct | 2021 | 0.045042 | 0.0020474 | Sustained | FALSE | TRUE | TMED_Event | 3006
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 179 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 3938 | keep | 0 | Oct | 2021 | 0.0026822 | 0.00012192 | Sustained | FALSE | TRUE | TMED_Event | 179
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 107 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 7.2877e-05 | Sustained | FALSE | TRUE | TMED_Event | 107
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 1666 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 36652 | keep | 0 | Oct | 2021 | 0.024964 | 0.0011347 | Sustained | FALSE | TRUE | TMED_Event | 1666
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 4387 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 96514 | keep | 0 | Oct | 2021 | 0.065735 | 0.002988 | Sustained | FALSE | TRUE | TMED_Event | 4387
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 13:44 | 637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100200114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 637 | keep | 0 | Oct | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | TMED_Event | 637
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 3147 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 69234 | keep | 0 | Oct | 2021 | 0.047155 | 0.0021434 | Sustained | FALSE | TRUE | TMED_Event | 3147
MAYAGÃœEZ | 2021-10-02 13:43 | 2021-10-02 14:05 | 4304 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-02 | 94688 | keep | 0 | Oct | 2021 | 0.064492 | 0.0029314 | Sustained | FALSE | TRUE | TMED_Event | 4304
MAYAGÃœEZ | 2021-10-02 13:44 | 2021-10-03 13:32 | 80 | 023:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21100200303 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1428 | 2021-10-02 | 114240 | keep | 0 | Oct | 2021 | 0.077808 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
FAJARDO | 2021-10-02 13:51 | 2021-10-02 14:47 | 1 | 000:56 | P | DESGANCHE | 2 X 20 EN TRANSFORMADOR | R21100200158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-10-02 | 56 | keep | 0 | Oct | 2021 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CANOVANAS | 2021-10-02 13:51 | 2021-10-02 20:47 | 200 | 006:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN SU LLUVIAS | R21100200139 | New_Event | Bad Weather | Include | Include | Weather | 416 | 2021-10-02 | 83200 | keep | 0 | Oct | 2021 | 0.056667 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
CAGUAS | 2021-10-02 13:52 | 2021-10-03 07:18 | 40 | 017:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21100200251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1046 | 2021-10-02 | 41840 | keep | 0 | Oct | 2021 | 0.028497 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-10-02 13:52 | 2021-10-02 13:53 | 411 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 411 | keep | 0 | Oct | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | TMED_Event | 411
MAYAGÃœEZ | 2021-10-02 13:54 | 2021-10-02 21:06 | 75 | 007:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21100200139 | New_Event | Bad Weather | Include | Include | Weather | 432 | 2021-10-02 | 32400 | keep | 0 | Oct | 2021 | 0.022067 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
ARECIBO | 2021-10-02 13:54 | 2021-10-02 13:55 | 1548 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1548 | keep | 0 | Oct | 2021 | 0.0010543 | 0.0010543 | Momentary | FALSE | FALSE | TMED_Event | 1548
MAYAGÃœEZ | 2021-10-02 13:57 | 2021-10-02 13:58 | 411 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 411 | keep | 0 | Oct | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | TMED_Event | 411
ARECIBO | 2021-10-02 13:59 | 2021-10-02 14:00 | 1883 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A21100200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-02 | 1883 | keep | 0 | Oct | 2021 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | TMED_Event | 1883
ARECIBO | 2021-10-02 14:00 | 2021-10-02 14:01 | 1548 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR MAL TIEMPO | A21100200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1548 | keep | 0 | Oct | 2021 | 0.0010543 | 0.0010543 | Momentary | FALSE | FALSE | TMED_Event | 1548
ARECIBO | 2021-10-02 14:00 | 2021-10-02 19:00 | 60 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21100200294 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 300 | 2021-10-02 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
GUAYAMA | 2021-10-02 14:07 | 2021-10-02 14:08 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100200109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1945 | keep | 0 | Oct | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | TMED_Event | 1945
CAGUAS | 2021-10-02 14:12 | 2021-10-02 14:13 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21100200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1879 | keep | 0 | Oct | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | TMED_Event | 1879
GUAYAMA | 2021-10-02 14:14 | 2021-10-02 14:15 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21100200142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1173 | keep | 0 | Oct | 2021 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | TMED_Event | 1173
ARECIBO | 2021-10-02 14:17 | 2021-10-02 14:49 | 308 | 000:32 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF CERRADO POR SCADA | A21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2021-10-02 | 9856 | keep | 0 | Oct | 2021 | 0.0067129 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
VEGA BAJA | 2021-10-02 14:19 | 2021-10-02 19:00 | 80 | 004:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B21100200165 | New_Event | Cutout Failure | Include | Include | Equipment | 281 | 2021-10-02 | 22480 | keep | 0 | Oct | 2021 | 0.015311 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-10-02 14:21 | 2021-10-02 16:19 | 70 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21100200121 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-10-02 | 8260 | keep | 0 | Oct | 2021 | 0.0056258 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
ARECIBO | 2021-10-02 14:24 | 2021-10-02 14:25 | 1222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1222 | keep | 0 | Oct | 2021 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | TMED_Event | 1222
BAYAMON | 2021-10-02 14:24 | 2021-10-02 16:34 | 100 | 002:10 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA | B21100200207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-10-02 | 13000 | keep | 0 | Oct | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-10-02 14:28 | 2021-10-02 20:17 | 53 | 005:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE DESCRUZARON CONDUCTORES | R21100200172 | New_Event | Wire Down | Include | Include | Equipment | 349 | 2021-10-02 | 18497 | keep | 0 | Oct | 2021 | 0.012598 | 3.6098e-05 | Sustained | FALSE | TRUE | TMED_Event | 53
CAGUAS | 2021-10-02 14:28 | 2021-10-03 10:09 | 100 | 019:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | C21100200263 | New_Event | Cutout Failure | Include | Include | Equipment | 1181 | 2021-10-02 | 118100 | keep | 0 | Oct | 2021 | 0.080437 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-10-02 14:29 | 2021-10-02 14:30 | 2756 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21100200131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 2756 | keep | 0 | Oct | 2021 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | TMED_Event | 2756
GUAYAMA | 2021-10-02 14:30 | 2021-10-02 15:19 | 150 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | P21100200129 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-10-02 | 7350 | keep | 0 | Oct | 2021 | 0.0050061 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CANOVANAS | 2021-10-02 14:32 | 2021-10-02 16:24 | 33 | 001:52 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21100200173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-10-02 | 3696 | keep | 0 | Oct | 2021 | 0.0025173 | 2.2476e-05 | Sustained | FALSE | TRUE | TMED_Event | 33
SAN JUAN | 2021-10-02 14:37 | 2021-10-02 14:38 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 726 | keep | 0 | Oct | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | TMED_Event | 726
SAN JUAN | 2021-10-02 14:37 | 2021-10-02 14:38 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 3932 | keep | 0 | Oct | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | TMED_Event | 3932
BARRANQUITAS | 2021-10-02 14:38 | 2021-10-02 18:14 | 40 | 003:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21100200266 | New_Event | Bad Weather | Include | Include | Weather | 216 | 2021-10-02 | 8640 | keep | 0 | Oct | 2021 | 0.0058847 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-10-02 14:42 | 2021-10-02 14:43 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21100200143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 2379 | keep | 0 | Oct | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | TMED_Event | 2379
HUMACAO | 2021-10-02 14:44 | 2021-10-02 14:45 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 3420 | keep | 0 | Oct | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | TMED_Event | 3420
MAYAGÃœEZ | 2021-10-02 14:44 | 2021-10-02 16:30 | 20 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M20100200216 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-10-02 | 2120 | keep | 0 | Oct | 2021 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
ARECIBO | 2021-10-02 14:47 | 2021-10-02 15:06 | 1541 | 000:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-02 | 29279 | keep | 0 | Oct | 2021 | 0.019942 | 0.0010496 | Sustained | FALSE | TRUE | TMED_Event | 1541
ARECIBO | 2021-10-02 14:47 | 2021-10-02 15:06 | 307 | 000:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-02 | 5833 | keep | 0 | Oct | 2021 | 0.0039728 | 0.0002091 | Sustained | FALSE | TRUE | TMED_Event | 307
ARECIBO | 2021-10-02 14:47 | 2021-10-02 15:06 | 1277 | 000:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-02 | 24263 | keep | 0 | Oct | 2021 | 0.016525 | 0.00086976 | Sustained | FALSE | TRUE | TMED_Event | 1277
ARECIBO | 2021-10-02 14:47 | 2021-10-02 15:06 | 1644 | 000:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-02 | 31236 | keep | 0 | Oct | 2021 | 0.021275 | 0.0011197 | Sustained | FALSE | TRUE | TMED_Event | 1644
ARECIBO | 2021-10-02 14:47 | 2021-10-02 15:06 | 1831 | 000:19 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-02 | 34789 | keep | 0 | Oct | 2021 | 0.023695 | 0.0012471 | Sustained | FALSE | TRUE | TMED_Event | 1831
CAGUAS | 2021-10-02 14:49 | 2021-10-02 16:54 | 45 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C21100100129 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2021-10-02 | 5625 | keep | 0 | Oct | 2021 | 0.0038312 | 3.0649e-05 | Sustained | FALSE | TRUE | TMED_Event | 45
ARECIBO | 2021-10-02 14:49 | 2021-10-03 14:25 | 420 | 023:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN EL TRONCAL DEL ALIMENTADOR | A21100200147 | New_Event | Wire Down | Include | Include | Equipment | 1416 | 2021-10-02 | 594720 | keep | 0 | Oct | 2021 | 0.40506 | 0.00028606 | Sustained | FALSE | FALSE | TMED_Event | 420
ARECIBO | 2021-10-02 14:49 | 2021-10-03 09:47 | 200 | 018:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 20 EN CORTE DE LINEA MAL TIEMPO | A21100200146 | New_Event | Bad Weather | Include | Include | Weather | 1138 | 2021-10-02 | 227600 | keep | 0 | Oct | 2021 | 0.15502 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
BAYAMON | 2021-10-02 14:50 | 2021-10-03 11:13 | 40 | 020:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100200211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1223 | 2021-10-02 | 48920 | keep | 0 | Oct | 2021 | 0.033319 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-10-02 14:51 | 2021-10-03 15:08 | 5 | 024:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21100200212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1457 | 2021-10-02 | 7285 | keep | 0 | Oct | 2021 | 0.0049618 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
PONCE | 2021-10-02 14:53 | 2021-10-02 19:29 | 1340 | 004:36 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR SE PATRULLO Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO NO SE ENCONTRO CAUSA | P21100200145 | New_Event | Bad Weather | Include | Include | Weather | 276 | 2021-10-02 | 369840 | keep | 0 | Oct | 2021 | 0.2519 | 0.00091267 | Sustained | FALSE | FALSE | TMED_Event | 1340
PONCE | 2021-10-02 14:55 | 2021-10-02 14:56 | 595 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21100200154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 595 | keep | 0 | Oct | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | TMED_Event | 595
UTUADO | 2021-10-02 14:59 | 2021-10-03 18:15 | 5 | 027:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21100200159 | New_Event | Bad Weather | Include | Include | Weather | 1636 | 2021-10-02 | 8180 | keep | 0 | Oct | 2021 | 0.0055714 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
PONCE | 2021-10-02 15:01 | 2021-10-02 20:01 | 50 | 005:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21100200149 | New_Event | Bad Weather | Include | Include | Weather | 300 | 2021-10-02 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
PONCE | 2021-10-02 15:05 | 2021-10-02 15:06 | 2379 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | P21100200151 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-02 | 2379 | keep | 0 | Oct | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | TMED_Event | 2379
PONCE | 2021-10-02 15:06 | 2021-10-02 19:20 | 150 | 004:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21100200183 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 254 | 2021-10-02 | 38100 | keep | 0 | Oct | 2021 | 0.02595 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
HUMACAO | 2021-10-02 15:11 | 2021-10-02 20:37 | 200 | 005:26 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | C21100200274 | New_Event | Bad Weather | Include | Include | Weather | 326 | 2021-10-02 | 65200 | keep | 0 | Oct | 2021 | 0.044407 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
ARECIBO | 2021-10-02 15:13 | 2021-10-03 03:08 | 1628 | 011:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO LINEA PRIMARIA PARTIDA | A21100200181 | New_Event | Wire Down | Include | Include | Equipment | 715 | 2021-10-02 | 1164020 | keep | 0 | Oct | 2021 | 0.79281 | 0.0011088 | Sustained | FALSE | TRUE | TMED_Event | 1628
AGUADILLA | 2021-10-02 15:16 | 2021-10-02 15:17 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 1047 | keep | 0 | Oct | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | TMED_Event | 1047
GUAYAMA | 2021-10-02 15:24 | 2021-10-02 16:43 | 200 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21100200164 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2021-10-02 | 15800 | keep | 0 | Oct | 2021 | 0.010761 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
SAN JUAN | 2021-10-02 15:28 | 2021-10-02 15:30 | 1026 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE VERIFICO PERSONAL FUERA MAL TIEMPO | R21100200000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-10-02 | 2052 | keep | 0 | Oct | 2021 | 0.0013976 | 0.0006988 | Momentary | FALSE | FALSE | TMED_Event | 1026
BAYAMON | 2021-10-02 15:30 | 2021-10-02 15:36 | 1 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO COORDINADO CON ING. BERMUDEZ A.A.A | B21100200000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-02 | 6 | keep | 0 | Oct | 2021 | 4.0866e-06 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
MAYAGÃœEZ | 2021-10-02 15:37 | 2021-10-02 20:24 | 150 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | M21100100252 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2021-10-02 | 43050 | keep | 0 | Oct | 2021 | 0.029321 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
FAJARDO | 2021-10-02 15:39 | 2021-10-02 17:45 | 50 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE DESCRUZARON LINEAS | R21100200180 | New_Event | Wire Down | Include | Include | Equipment | 126 | 2021-10-02 | 6300 | keep | 0 | Oct | 2021 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
PONCE | 2021-10-02 15:39 | 2021-10-02 18:30 | 14 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P21100200170 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2021-10-02 | 2394 | keep | 0 | Oct | 2021 | 0.0016305 | 9.5353e-06 | Sustained | FALSE | TRUE | TMED_Event | 14
PONCE | 2021-10-02 15:39 | 2021-10-03 10:26 | 200 | 018:47 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100200169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1127 | 2021-10-02 | 225400 | keep | 0 | Oct | 2021 | 0.15352 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
AGUADILLA | 2021-10-02 15:39 | 2021-10-03 14:25 | 60 | 022:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21100200253 | New_Event | Bad Weather | Include | Include | Weather | 1366 | 2021-10-02 | 81960 | keep | 0 | Oct | 2021 | 0.055823 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CAGUAS | 2021-10-02 15:40 | 2021-10-02 19:10 | 50 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21100200289 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-10-02 | 10500 | keep | 0 | Oct | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-10-02 15:41 | 2021-10-02 19:19 | 125 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100200201 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-10-02 | 27250 | keep | 0 | Oct | 2021 | 0.01856 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
BARRANQUITAS | 2021-10-02 15:45 | 2021-10-02 17:21 | 65 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21100200290 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2021-10-02 | 6240 | keep | 0 | Oct | 2021 | 0.00425 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
ARECIBO | 2021-10-02 15:46 | 2021-10-03 10:34 | 100 | 018:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100200209 | New_Event | Bad Weather | Include | Include | Weather | 1128 | 2021-10-02 | 112800 | keep | 0 | Oct | 2021 | 0.076828 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-10-02 15:47 | 2021-10-03 09:52 | 68 | 018:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21100200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1085 | 2021-10-02 | 73780 | keep | 0 | Oct | 2021 | 0.050251 | 4.6314e-05 | Sustained | FALSE | TRUE | TMED_Event | 68
VEGA BAJA | 2021-10-02 15:47 | 2021-10-05 11:59 | 30 | 068:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21100200220 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4092 | 2021-10-02 | 122760 | keep | 0 | Oct | 2021 | 0.083611 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
HUMACAO | 2021-10-02 15:51 | 2021-10-02 20:38 | 80 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21100200296 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2021-10-02 | 22960 | keep | 0 | Oct | 2021 | 0.015638 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
HUMACAO | 2021-10-02 15:52 | 2021-10-02 21:25 | 65 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21100200297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2021-10-02 | 21645 | keep | 0 | Oct | 2021 | 0.014742 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
MAYAGÃœEZ | 2021-10-02 16:00 | 2021-10-02 17:02 | 2825 | 001:02 | T | MAL TIEMPO/RAYOS/WET ASH | INTERRUPTOR ABIERTO NO RTU CERRADO MANUAL | M21100200000 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2021-10-02 | 175150 | keep | 0 | Oct | 2021 | 0.11929 | 0.0019241 | Sustained | FALSE | FALSE | TMED_Event | 2825
MAYAGÃœEZ | 2021-10-02 16:06 | 2021-10-02 18:33 | 80 | 002:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 C/L MAL TIEMPO | M21100200262 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2021-10-02 | 11760 | keep | 0 | Oct | 2021 | 0.0080097 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
SAN JUAN | 2021-10-02 16:07 | 2021-10-02 19:44 | 4 | 003:37 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL SECUNDARIO | R21100200183 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 217 | 2021-10-02 | 868 | keep | 0 | Oct | 2021 | 0.00059119 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
ARECIBO | 2021-10-02 16:18 | 2021-10-02 18:25 | 50 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100200224 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2021-10-02 | 6350 | keep | 0 | Oct | 2021 | 0.004325 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-10-02 16:29 | 2021-10-02 21:23 | 60 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA, 1 X 40 EN OTRO CORTE DE LINEA SE LEVANTO CONDUCTOR | B21100200226 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-10-02 | 17640 | keep | 0 | Oct | 2021 | 0.012015 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-10-02 16:41 | 2021-10-03 17:24 | 1 | 024:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B21100200229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1483 | 2021-10-02 | 1483 | keep | 0 | Oct | 2021 | 0.0010101 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
UTUADO | 2021-10-02 16:41 | 2021-10-02 20:11 | 60 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100200239 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-10-02 | 12600 | keep | 0 | Oct | 2021 | 0.0085818 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CANOVANAS | 2021-10-02 16:44 | 2021-10-02 17:26 | 30 | 000:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21100200186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-10-02 | 1260 | keep | 0 | Oct | 2021 | 0.00085818 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
UTUADO | 2021-10-02 16:44 | 2021-10-03 12:51 | 5 | 020:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21100200241 | New_Event | Bad Weather | Include | Include | Weather | 1207 | 2021-10-02 | 6035 | keep | 0 | Oct | 2021 | 0.0041104 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CAGUAS | 2021-10-02 16:46 | 2021-10-02 20:30 | 1 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21100200309 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-10-02 | 224 | keep | 0 | Oct | 2021 | 0.00015257 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
ARECIBO | 2021-10-02 16:46 | 2021-10-02 18:22 | 14 | 001:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 50KVA MARCA PROLEC 7620/13700V 120/240V SER:20I10322 FID:29542213 X 25 KVA | A21100200198 | New_Event | Service Transformer Failure | Include | Include | Equipment | 96 | 2021-10-02 | 1344 | keep | 0 | Oct | 2021 | 0.00091539 | 9.5353e-06 | Sustained | FALSE | FALSE | TMED_Event | 14
CANOVANAS | 2021-10-02 16:54 | 2021-10-02 16:55 | 4154 | 000:01 | T | DESGANCHE | RECIERRE | R21100200187 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-02 | 4154 | keep | 0 | Oct | 2021 | 0.0028293 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2021-10-02 16:55 | 2021-10-02 17:41 | 325 | 000:46 | P | DESGANCHE | 2 X 140 Y 1 X 80 EN CORTES DE LINEA | R21100200155 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-10-02 | 14950 | keep | 0 | Oct | 2021 | 0.010182 | 0.00022136 | Sustained | FALSE | TRUE | TMED_Event | 325
CANOVANAS | 2021-10-02 17:07 | 2021-10-02 18:43 | 23 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | R21100200188 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2021-10-02 | 2208 | keep | 0 | Oct | 2021 | 0.0015039 | 1.5665e-05 | Sustained | FALSE | TRUE | TMED_Event | 23
CAGUAS | 2021-10-02 17:07 | 2021-10-03 12:19 | 20 | 019:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21100200316 | New_Event | Wire Down | Include | Include | Equipment | 1152 | 2021-10-02 | 23040 | keep | 0 | Oct | 2021 | 0.015692 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
PONCE | 2021-10-02 17:14 | 2021-10-03 13:40 | 170 | 020:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA LINEA PRIMARIA CRUZADA CON CABLE MENSAJERO DE CABLE TV | P21100200223 | New_Event |  |  | Include | Wildlife | 1226 | 2021-10-02 | 208420 | keep | 0 | Oct | 2021 | 0.14195 | 0.00011579 | Sustained | FALSE | TRUE | TMED_Event | 170
MAYAGÃœEZ | 2021-10-02 17:18 | 2021-10-02 19:15 | 150 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21100200300 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-10-02 | 17550 | keep | 0 | Oct | 2021 | 0.011953 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
ARECIBO | 2021-10-02 17:21 | 2021-10-02 20:05 | 40 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21100200261 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2021-10-02 | 6560 | keep | 0 | Oct | 2021 | 0.004468 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 17:21 | 2021-10-03 21:46 | 15 | 028:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21100200261 | New_Event | Bad Weather | Include | Include | Weather | 1705 | 2021-10-02 | 25575 | keep | 0 | Oct | 2021 | 0.017419 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2021-10-02 17:23 | 2021-10-03 10:05 | 180 | 016:42 | P | DESGANCHE | SE ABRE CORTE DE LINEA PARA RETIRAR RAMA CRUZANDO LINEA | S21100200098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1002 | 2021-10-02 | 180360 | keep | 0 | Oct | 2021 | 0.12284 | 0.0001226 | Sustained | FALSE | TRUE | TMED_Event | 180
SAN JUAN | 2021-10-02 17:27 | 2021-10-03 13:28 | 50 | 020:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21100200099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1201 | 2021-10-02 | 60050 | keep | 0 | Oct | 2021 | 0.0409 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-10-02 17:29 | 2021-10-02 20:13 | 2000 | 002:44 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R21100200000 | New_Event | UG Cable Fault | Include | Include | Equipment | 164 | 2021-10-02 | 328000 | keep | 0 | Oct | 2021 | 0.2234 | 0.0013622 | Sustained | FALSE | FALSE | TMED_Event | 2000
MAYAGÃœEZ | 2021-10-02 17:33 | 2021-10-03 12:05 | 600 | 018:32 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21100200309 | New_Event | Bad Weather | Include | Include | Weather | 1112 | 2021-10-02 | 667200 | keep | 0 | Oct | 2021 | 0.45443 | 0.00040866 | Sustained | FALSE | TRUE | TMED_Event | 600
ARECIBO | 2021-10-02 17:34 | 2021-10-03 17:50 | 25 | 024:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO ERMCO 50KVA 2400/4160 #82011973292 FID-33593246 X 50KVA | A21100200268 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1456 | 2021-10-02 | 36400 | keep | 0 | Oct | 2021 | 0.024792 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
FAJARDO | 2021-10-02 17:44 | 2021-10-03 08:28 | 970 | 014:44 | T | NO SE REPORTO CAUSA | INTERRUPTOR CERRADO EN EL CAMPO NO RTU | R21100200204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 884 | 2021-10-02 | 857480 | keep | 0 | Oct | 2021 | 0.58403 | 0.00066066 | Sustained | FALSE | FALSE | TMED_Event | 970
ARECIBO | 2021-10-02 17:48 | 2021-10-03 11:27 | 200 | 017:39 | P | DESGANCHE | 3 X 50 Y 1 X 65 EN CORTE DE LINEA | A21100200280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1059 | 2021-10-02 | 211800 | keep | 0 | Oct | 2021 | 0.14426 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CANOVANAS | 2021-10-02 17:54 | 2021-10-02 17:55 | 1894 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | R21100200211 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-02 | 1894 | keep | 0 | Oct | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | TMED_Event | 1894
VEGA BAJA | 2021-10-02 17:56 | 2021-10-03 17:24 | 50 | 023:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100200229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1408 | 2021-10-02 | 70400 | keep | 0 | Oct | 2021 | 0.047949 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-10-02 18:00 | 2021-10-04 09:24 | 6 | 039:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | A21100200016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2364 | 2021-10-02 | 14184 | keep | 0 | Oct | 2021 | 0.0096607 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
PONCE | 2021-10-02 18:10 | 2021-10-02 21:02 | 978 | 002:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE REPARO TRES FASES EN TRONCAL PRIMARIO | P21100200274 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2021-10-02 | 168216 | keep | 0 | Oct | 2021 | 0.11457 | 0.00066611 | Sustained | FALSE | FALSE | TMED_Event | 978
MAYAGÃœEZ | 2021-10-02 18:13 | 2021-10-04 18:18 | 5 | 048:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15KVA 2400/4160V 120/240V SER:82011973164 MARCA:RMCO 15 KVA | M21100200327 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2885 | 2021-10-02 | 14425 | keep | 0 | Oct | 2021 | 0.0098248 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
MAYAGÃœEZ | 2021-10-02 18:18 | 2021-10-02 22:45 | 30 | 004:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CORTE DE LINEA | M21100200329 | New_Event | Wire Down | Include | Include | Equipment | 267 | 2021-10-02 | 8010 | keep | 0 | Oct | 2021 | 0.0054556 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-10-02 18:19 | 2021-10-04 12:50 | 100 | 042:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21100200429 | New_Event | Bad Weather | Include | Include | Weather | 2551 | 2021-10-02 | 255100 | keep | 0 | Oct | 2021 | 0.17375 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
YAUCO | 2021-10-02 18:20 | 2021-10-03 17:25 | 150 | 023:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100200242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1385 | 2021-10-02 | 207750 | keep | 0 | Oct | 2021 | 0.1415 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
MAYAGÃœEZ | 2021-10-02 18:21 | 2021-10-03 15:04 | 125 | 020:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21100200330 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1243 | 2021-10-02 | 155375 | keep | 0 | Oct | 2021 | 0.10583 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
CAGUAS | 2021-10-02 18:36 | 2021-10-02 19:33 | 50 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21100200334 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-10-02 | 2850 | keep | 0 | Oct | 2021 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-10-02 18:37 | 2021-10-03 15:14 | 50 | 020:37 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100200243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1237 | 2021-10-02 | 61850 | keep | 0 | Oct | 2021 | 0.042126 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-10-02 18:42 | 2021-10-03 18:46 | 15 | 024:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100200245 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1444 | 2021-10-02 | 21660 | keep | 0 | Oct | 2021 | 0.014753 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
ARECIBO | 2021-10-02 18:46 | 2021-10-03 09:27 | 100 | 014:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | A21100200298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2021-10-02 | 88100 | keep | 0 | Oct | 2021 | 0.060005 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-10-02 18:48 | 2021-10-03 11:50 | 100 | 017:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21100200300 | New_Event | Bad Weather | Include | Include | Weather | 1022 | 2021-10-02 | 102200 | keep | 0 | Oct | 2021 | 0.069608 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-10-02 18:49 | 2021-10-02 22:37 | 12 | 003:48 | P | DESGANCHE | SE REPARO PUENTE ABIERTO EN CORTE DE LINEA | A21100100206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-10-02 | 2736 | keep | 0 | Oct | 2021 | 0.0018635 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
YAUCO | 2021-10-02 18:50 | 2021-10-03 18:37 | 15 | 023:47 | P | ESTRUCTURA AVERIADA | 3 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE DE MADERA 40 PIES PARTIDO POR POSTE METAL 45 PIES | P21100200250 | New_Event | Defective Pole | Include | Include | Equipment | 1427 | 2021-10-02 | 21405 | keep | 0 | Oct | 2021 | 0.014579 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
SAN JUAN | 2021-10-02 18:54 | 2021-10-03 18:49 | 180 | 023:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21100200230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1435 | 2021-10-02 | 258300 | keep | 0 | Oct | 2021 | 0.17593 | 0.0001226 | Sustained | FALSE | TRUE | TMED_Event | 180
MAYAGÃœEZ | 2021-10-02 19:00 | 2021-10-03 13:45 | 50 | 018:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21100200050 | New_Event | Wire Down | Include | Include | Equipment | 1125 | 2021-10-02 | 56250 | keep | 0 | Oct | 2021 | 0.038312 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
ARECIBO | 2021-10-02 19:03 | 2021-10-03 13:40 | 50 | 018:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21100200307 | New_Event | Bad Weather | Include | Include | Weather | 1117 | 2021-10-02 | 55850 | keep | 0 | Oct | 2021 | 0.038039 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-10-02 19:11 | 2021-10-03 10:23 | 30 | 015:12 | P | DESGANCHE | 1 X 30 EN CIRTE DE LINEA | C21100200338 | New_Event | Vegetation Contact | Include | Include | Vegetation | 912 | 2021-10-02 | 27360 | keep | 0 | Oct | 2021 | 0.018635 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
SAN JUAN | 2021-10-02 19:25 | 2021-10-03 11:06 | 12 | 015:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y SE RETIRO RAMA | S21100200100 | New_Event | Cutout Failure | Include | Include | Equipment | 941 | 2021-10-02 | 11292 | keep | 0 | Oct | 2021 | 0.0076909 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
PONCE | 2021-10-02 19:29 | 2021-10-03 16:42 | 10 | 021:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 NX EN SU DESCARGAS ELECTRICAS | P21100200267 | Partial_restoration | Bad Weather | Include | Include | Weather | 1273 | 2021-10-02 | 12730 | keep | 0 | Oct | 2021 | 0.0086703 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
ARECIBO | 2021-10-02 19:32 | 2021-10-02 21:29 | 30 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21100200219 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-10-02 | 3510 | keep | 0 | Oct | 2021 | 0.0023906 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
GUAYAMA | 2021-10-02 19:33 | 2021-10-02 19:34 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21100200276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 215 | keep | 0 | Oct | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | TMED_Event | 215
CAGUAS | 2021-10-02 20:04 | 2021-10-02 20:17 | 1 | 000:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REMPLAZO HOT CLAMP | C21100200343 | New_Event | Wire Down | Include | Include | Equipment | 13 | 2021-10-02 | 13 | keep | 0 | Oct | 2021 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CANOVANAS | 2021-10-02 20:10 | 2021-10-02 22:05 | 25 | 001:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21100200245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-10-02 | 2875 | keep | 0 | Oct | 2021 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
ARECIBO | 2021-10-02 20:11 | 2021-10-03 18:59 | 30 | 022:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21100200330 | New_Event | Bad Weather | Include | Include | Weather | 1368 | 2021-10-02 | 41040 | keep | 0 | Oct | 2021 | 0.027952 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
SAN JUAN | 2021-10-02 20:13 | 2021-10-02 22:29 | 800 | 002:16 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU7 AL SU8 | R21100300015 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 136 | 2021-10-02 | 108800 | keep | 0 | Oct | 2021 | 0.074103 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-10-02 20:16 | 2021-10-03 11:28 | 60 | 015:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21100200211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 912 | 2021-10-02 | 54720 | keep | 0 | Oct | 2021 | 0.03727 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
CANOVANAS | 2021-10-02 20:19 | 2021-10-02 23:18 | 81 | 002:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21100200248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2021-10-02 | 14499 | keep | 0 | Oct | 2021 | 0.0098752 | 5.5169e-05 | Sustained | FALSE | TRUE | TMED_Event | 81
BAYAMON | 2021-10-02 20:31 | 2021-10-02 21:23 | 25 | 000:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REPARO AISLADOR | B21100200268 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2021-10-02 | 1300 | keep | 0 | Oct | 2021 | 0.00088542 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
UTUADO | 2021-10-02 20:38 | 2021-10-03 09:08 | 100 | 012:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21100200338 | New_Event | Bad Weather | Include | Include | Weather | 750 | 2021-10-02 | 75000 | keep | 0 | Oct | 2021 | 0.051082 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-10-02 20:41 | 2021-10-02 20:42 | 5191 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 5191 | keep | 0 | Oct | 2021 | 0.0035356 | 0.0035356 | Momentary | FALSE | FALSE | TMED_Event | 5191
CANOVANAS | 2021-10-02 21:01 | 2021-10-03 09:56 | 40 | 012:55 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO BAJANTE DE CAJA A LINEA | R21100200256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 775 | 2021-10-02 | 31000 | keep | 0 | Oct | 2021 | 0.021114 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-10-02 21:06 | 2021-10-02 21:07 | 1541 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPA;RO DE LINEA 2700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 1541 | keep | 0 | Oct | 2021 | 0.0010496 | 0.0010496 | Momentary | FALSE | TRUE | TMED_Event | 1541
ARECIBO | 2021-10-02 21:06 | 2021-10-02 21:07 | 307 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPA;RO DE LINEA 2700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 307 | keep | 0 | Oct | 2021 | 0.0002091 | 0.0002091 | Momentary | FALSE | TRUE | TMED_Event | 307
ARECIBO | 2021-10-02 21:06 | 2021-10-02 21:07 | 1277 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPA;RO DE LINEA 2700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 1277 | keep | 0 | Oct | 2021 | 0.00086976 | 0.00086976 | Momentary | FALSE | TRUE | TMED_Event | 1277
ARECIBO | 2021-10-02 21:06 | 2021-10-02 21:07 | 1644 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPA;RO DE LINEA 2700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 1644 | keep | 0 | Oct | 2021 | 0.0011197 | 0.0011197 | Momentary | FALSE | TRUE | TMED_Event | 1644
ARECIBO | 2021-10-02 21:06 | 2021-10-02 21:07 | 1831 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPA;RO DE LINEA 2700 | A21100200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-02 | 1831 | keep | 0 | Oct | 2021 | 0.0012471 | 0.0012471 | Momentary | FALSE | TRUE | TMED_Event | 1831
ARECIBO | 2021-10-02 21:11 | 2021-10-03 14:25 | 20 | 017:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100200347 | New_Event | Bad Weather | Include | Include | Weather | 1034 | 2021-10-02 | 20680 | keep | 0 | Oct | 2021 | 0.014085 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
HUMACAO | 2021-10-02 21:15 | 2021-10-03 13:02 | 25 | 015:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21100200346 | New_Event | Bad Weather | Include | Include | Weather | 947 | 2021-10-02 | 23675 | keep | 0 | Oct | 2021 | 0.016125 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
BAYAMON | 2021-10-02 21:20 | 2021-10-02 21:21 | 418 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21100200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-02 | 418 | keep | 0 | Oct | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | TMED_Event | 418
FAJARDO | 2021-10-02 21:21 | 2021-10-03 14:57 | 60 | 017:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | R21100200285 | New_Event | Bad Weather | Include | Include | Weather | 1056 | 2021-10-02 | 63360 | keep | 0 | Oct | 2021 | 0.043154 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
HUMACAO | 2021-10-02 21:26 | 2021-10-03 11:21 | 40 | 013:55 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21100200347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 835 | 2021-10-02 | 33400 | keep | 0 | Oct | 2021 | 0.022749 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
YAUCO | 2021-10-02 21:32 | 2021-10-03 10:35 | 70 | 013:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21100200299 | New_Event | Bad Weather | Include | Include | Weather | 783 | 2021-10-02 | 54810 | keep | 0 | Oct | 2021 | 0.037331 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
ARECIBO | 2021-10-02 21:37 | 2021-10-03 18:08 | 80 | 020:31 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA DESGANCHE | A21100300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1231 | 2021-10-02 | 98480 | keep | 0 | Oct | 2021 | 0.067074 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BAYAMON | 2021-10-02 21:49 | 2021-10-03 14:13 | 15 | 016:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21100200274 | New_Event | Secondary Wire Down | Include | Include | Equipment | 984 | 2021-10-02 | 14760 | keep | 0 | Oct | 2021 | 0.010053 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
HUMACAO | 2021-10-02 21:55 | 2021-10-03 09:45 | 80 | 011:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21100200349 | New_Event | Vegetation Contact | Include | Include | Vegetation | 710 | 2021-10-02 | 56800 | keep | 0 | Oct | 2021 | 0.038686 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
CANOVANAS | 2021-10-02 21:59 | 2021-10-03 09:29 | 4 | 011:30 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR DESGANCHE | R21100200296 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 690 | 2021-10-02 | 2760 | keep | 0 | Oct | 2021 | 0.0018798 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
MAYAGÃœEZ | 2021-10-02 22:02 | 2021-10-03 10:54 | 50 | 012:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21100200417 | New_Event | Bad Weather | Include | Include | Weather | 772 | 2021-10-02 | 38600 | keep | 0 | Oct | 2021 | 0.02629 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-10-02 22:11 | 2021-10-03 18:58 | 60 | 020:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21100200421 | New_Event | Bad Weather | Include | Include | Weather | 1247 | 2021-10-02 | 74820 | keep | 0 | Oct | 2021 | 0.05096 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CANOVANAS | 2021-10-02 22:26 | 2021-10-03 09:44 | 4 | 011:18 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA | R21100200302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 678 | 2021-10-02 | 2712 | keep | 0 | Oct | 2021 | 0.0018471 | 2.7244e-06 | Sustained | FALSE | TRUE | TMED_Event | 4
SAN JUAN | 2021-10-02 22:29 | 2021-10-02 22:36 | 2000 | 000:07 | P | CABLE SOTERRADO AVERIADO | DISPARO INTERRUPTOR PERSONAL REALIZANDO OPERACIONES CERRADO POR CONTROL | R21100200000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 7 | 2021-10-02 | 14000 | keep | 0 | Oct | 2021 | 0.0095353 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2021-10-02 22:36 | 2021-10-03 00:15 | 800 | 001:39 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU7 AL SU8 | R21100300015 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 99 | 2021-10-02 | 79200 | keep | 0 | Oct | 2021 | 0.053943 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
PONCE | 2021-10-02 22:50 | 2021-10-03 12:52 | 100 | 014:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100200307 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2021-10-02 | 84200 | keep | 0 | Oct | 2021 | 0.057348 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-10-02 22:55 | 2021-10-03 01:30 | 12 | 002:35 | T | CABLE SOTERRADO AVERIADO | SE CERRO INTERRUPTOR ABRIENDO EN SU 26B HACIA RISER EN CALLE BETANCES EN HATO REY POR APARENTE CABLE SOTERRADO AVERIADO | S21100200110 | New_Event | UG Cable Fault | Include | Include | Equipment | 155 | 2021-10-02 | 1860 | keep | 0 | Oct | 2021 | 0.0012668 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2021-10-02 23:28 | 2021-10-04 10:36 | 6 | 035:08 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO Y REPARO SECUNDARIA | C21100200354 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2108 | 2021-10-02 | 12648 | keep | 0 | Oct | 2021 | 0.0086145 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
VEGA BAJA | 2021-10-02 23:38 | 2021-10-03 11:11 | 75 | 011:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21100200204 | New_Event | Wire Down | Include | Include | Equipment | 693 | 2021-10-02 | 51975 | keep | 0 | Oct | 2021 | 0.0354 | 5.1082e-05 | Sustained | FALSE | FALSE | TMED_Event | 75
GUAYAMA | 2021-10-02 23:49 | 2021-10-03 09:55 | 70 | 010:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA DE 100 AMP | P21100200312 | New_Event | Cutout Failure | Include | Include | Equipment | 606 | 2021-10-02 | 42420 | keep | 0 | Oct | 2021 | 0.028892 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
ARECIBO | 2021-10-03 | 2021-10-03 07:45 | 40 | 007:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA REPARO LINEA PRIMARIA PARTIDA | A21100300000 | New_Event | Wire Down | Include | Include | Equipment | 465 | 2021-10-03 | 18600 | keep | 0 | Oct | 2021 | 0.012668 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-03 00:15 | 2021-10-03 00:24 | 2000 | 000:09 | P | CABLE SOTERRADO AVERIADO | DISPARO INTERRUPTOR PERSONAL REALIZANDO OPERACIONES CERRADO POR CONTROL | R21100200000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 9 | 2021-10-03 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-03 00:15 | 2021-10-03 09:30 | 80 | 009:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21100300002 | New_Event | Bad Weather | Include | Include | Weather | 555 | 2021-10-03 | 44400 | keep | 0 | Oct | 2021 | 0.030241 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-03 00:24 | 2021-10-03 11:26 | 1200 | 011:02 | P | CABLE SOTERRADO AVERIADO | PERSONAL LOCALIZANDO AVERIA | R21100300015 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 662 | 2021-10-03 | 794400 | keep | 0 | Oct | 2021 | 0.54106 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-03 00:28 | 2021-10-03 12:12 | 50 | 011:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21100300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 704 | 2021-10-03 | 35200 | keep | 0 | Oct | 2021 | 0.023975 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-03 01:30 | 2021-10-04 13:57 | 7 | 036:27 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | AVERIA DE SU-26C A RISER, SE CERRO DE SU-26B A RISER N/O SU CARGA X 1424-6 | S21100300012 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2187 | 2021-10-03 | 15309 | keep | 0 | Oct | 2021 | 0.010427 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-03 01:37 | 2021-10-03 14:15 | 25 | 012:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | A21100300005 | New_Event | Wire Down | Include | Include | Equipment | 758 | 2021-10-03 | 18950 | keep | 0 | Oct | 2021 | 0.012907 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-10-03 01:41 | 2021-10-03 20:28 | 80 | 018:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21100300114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1127 | 2021-10-03 | 90160 | keep | 0 | Oct | 2021 | 0.061408 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
FAJARDO | 2021-10-03 01:45 | 2021-10-03 12:10 | 20 | 010:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA RETIRO POSTE DEL TELEFONO PARTIDO Y RETEZO LINEAS | R21100300006 | New_Event |  |  | Include | Wildlife | 625 | 2021-10-03 | 12500 | keep | 0 | Oct | 2021 | 0.0085137 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-03 04:52 | 2021-10-03 17:00 | 600 | 012:08 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | M21100300013 | New_Event | Switch Failure | Include | Include | Equipment | 728 | 2021-10-03 | 436800 | keep | 0 | Oct | 2021 | 0.2975 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 107 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 428 | keep | 0 | Oct | 2021 | 0.00029151 | 7.2877e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 1666 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 6664 | keep | 0 | Oct | 2021 | 0.0045388 | 0.0011347 | Momentary | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 4387 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 17548 | keep | 0 | Oct | 2021 | 0.011952 | 0.002988 | Momentary | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 2073 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 8292 | keep | 0 | Oct | 2021 | 0.0056476 | 0.0014119 | Momentary | FALSE | TRUE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 637 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 2548 | keep | 0 | Oct | 2021 | 0.0017354 | 0.00043386 | Momentary | FALSE | TRUE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 1491 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 5964 | keep | 0 | Oct | 2021 | 0.0040621 | 0.0010155 | Momentary | FALSE | TRUE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 3147 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 12588 | keep | 0 | Oct | 2021 | 0.0085736 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-10-03 05:37 | 2021-10-03 05:41 | 4304 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 | M21100300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-03 | 17216 | keep | 0 | Oct | 2021 | 0.011726 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
ARECIBO | 2021-10-03 05:52 | 2021-10-03 20:35 | 200 | 014:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA ABB 100 AMP | A21100300014 | New_Event | Cutout Failure | Include | Include | Equipment | 883 | 2021-10-03 | 176600 | keep | 0 | Oct | 2021 | 0.12028 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-10-03 06:00 | 2021-10-03 12:24 | 8 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21100300112 | New_Event | Bad Weather | Include | Include | Weather | 384 | 2021-10-03 | 3072 | keep | 0 | Oct | 2021 | 0.0020923 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-03 06:21 | 2021-10-03 10:22 | 50 | 004:01 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21100300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2021-10-03 | 12050 | keep | 0 | Oct | 2021 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-03 06:40 | 2021-10-04 12:16 | 30 | 029:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | M21100300014 | New_Event | Bad Weather | Include | Include | Weather | 1776 | 2021-10-03 | 53280 | keep | 0 | Oct | 2021 | 0.036289 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-03 06:40 | 2021-10-03 13:26 | 30 | 006:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21100300021 | New_Event | Bad Weather | Include | Include | Weather | 406 | 2021-10-03 | 12180 | keep | 0 | Oct | 2021 | 0.0082957 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-03 06:42 | 2021-10-03 15:10 | 40 | 008:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21100300019 | New_Event | Bad Weather | Include | Include | Weather | 508 | 2021-10-03 | 20320 | keep | 0 | Oct | 2021 | 0.01384 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-10-03 06:45 | 2021-10-04 12:04 | 5 | 029:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | C21100300004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1759 | 2021-10-03 | 8795 | keep | 0 | Oct | 2021 | 0.0059902 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-03 06:50 | 2021-10-03 12:50 | 6 | 006:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIA | C21100300005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 360 | 2021-10-03 | 2160 | keep | 0 | Oct | 2021 | 0.0014712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-03 07:02 | 2021-10-03 07:04 | 3718 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21100300004 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-10-03 | 7436 | keep | 0 | Oct | 2021 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2021-10-03 07:03 | 2021-10-03 09:21 | 75 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-10-03 | 10350 | keep | 0 | Oct | 2021 | 0.0070493 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-10-03 07:04 | 2021-10-03 12:03 | 40 | 004:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA | S21100300005 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 299 | 2021-10-03 | 11960 | keep | 0 | Oct | 2021 | 0.0081459 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-03 07:06 | 2021-10-03 09:46 | 20 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21100300010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-10-03 | 3200 | keep | 0 | Oct | 2021 | 0.0021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-10-03 07:12 | 2021-10-03 14:20 | 60 | 007:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100300024 | New_Event | Bad Weather | Include | Include | Weather | 428 | 2021-10-03 | 25680 | keep | 0 | Oct | 2021 | 0.017491 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-03 07:18 | 2021-10-03 07:19 | 4369 | 000:01 | T | SECUNDARIA/DESGANCHE | RECIERRE | C21100300010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1 | 2021-10-03 | 4369 | keep | 0 | Oct | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-10-03 07:19 | 2021-10-03 14:52 | 40 | 007:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21100200251 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 453 | 2021-10-03 | 18120 | keep | 0 | Oct | 2021 | 0.012341 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-03 07:19 | 2021-10-03 15:28 | 10 | 008:09 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21100300029 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 489 | 2021-10-03 | 4890 | keep | 0 | Oct | 2021 | 0.0033306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-10-03 07:20 | 2021-10-03 10:42 | 50 | 003:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-10-03 | 10100 | keep | 0 | Oct | 2021 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-03 07:22 | 2021-10-03 17:15 | 50 | 009:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21100300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 593 | 2021-10-03 | 29650 | keep | 0 | Oct | 2021 | 0.020194 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-03 07:26 | 2021-10-03 19:35 | 60 | 012:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21100300033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 729 | 2021-10-03 | 43740 | keep | 0 | Oct | 2021 | 0.029791 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-10-03 07:37 | 2021-10-03 15:40 | 125 | 008:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21100300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2021-10-03 | 60375 | keep | 0 | Oct | 2021 | 0.041121 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-10-03 07:47 | 2021-10-03 16:56 | 20 | 009:09 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21100300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2021-10-03 | 10980 | keep | 0 | Oct | 2021 | 0.0074784 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-03 07:47 | 2021-10-03 09:40 | 100 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 NX EN SU -5 AVERIA SOTERRADA CAUSADA POR PESONAL AAA | P21100300015 | New_Event |  |  | Include | Wildlife | 113 | 2021-10-03 | 11300 | keep | 0 | Oct | 2021 | 0.0076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-03 07:49 | 2021-10-03 14:35 | 80 | 006:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21100300041 | New_Event | Bad Weather | Include | Include | Weather | 406 | 2021-10-03 | 32480 | keep | 0 | Oct | 2021 | 0.022122 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-03 07:49 | 2021-10-03 13:22 | 70 | 005:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21100300032 | New_Event | Bad Weather | Include | Include | Weather | 333 | 2021-10-03 | 23310 | keep | 0 | Oct | 2021 | 0.015876 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BARRANQUITAS | 2021-10-03 07:52 | 2021-10-03 17:22 | 100 | 009:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA | C21100300013 | New_Event | Wire Down | Include | Include | Equipment | 570 | 2021-10-03 | 57000 | keep | 0 | Oct | 2021 | 0.038822 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-03 08:03 | 2021-10-05 17:22 | 200 | 057:19 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO LINEA AEREA PROVISIONAL | M21100300048 | New_Event | UG Cable Fault | Include | Include | Equipment | 3439 | 2021-10-03 | 687800 | keep | 0 | Oct | 2021 | 0.46846 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-03 08:06 | 2021-10-03 08:39 | 7 | 000:33 | P | OTRAS CAUSAS | 1 X 15 EN BANCO DE TRANSFORMADORES SE DEJO FUERA LA TIENDA WONDERS POR PROA | R21100300017 | New_Event | Other Causes | Include | Include | Other | 33 | 2021-10-03 | 231 | keep | 0 | Oct | 2021 | 0.00015733 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-03 08:16 | 2021-10-04 15:29 | 50 | 031:13 | P | HERRAJE ROTO O PODRIDO | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO CRUCETA PARTIDA | M21100300062 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1873 | 2021-10-03 | 93650 | keep | 0 | Oct | 2021 | 0.063785 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-03 08:18 | 2021-10-04 13:04 | 60 | 028:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1726 | 2021-10-03 | 103560 | keep | 0 | Oct | 2021 | 0.070534 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-03 08:27 | 2021-10-03 16:45 | 6 | 008:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | A21100300040 | New_Event | Bad Weather | Include | Include | Weather | 498 | 2021-10-03 | 2988 | keep | 0 | Oct | 2021 | 0.0020351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-03 08:29 | 2021-10-03 18:44 | 25 | 010:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR PAJARO QUE CRUZO LINEAS | M21100300067 | New_Event |  |  | Include | Wildlife | 615 | 2021-10-03 | 15375 | keep | 0 | Oct | 2021 | 0.010472 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-03 08:29 | 2021-10-03 12:01 | 12 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | A21100300041 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-10-03 | 2544 | keep | 0 | Oct | 2021 | 0.0017327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-03 08:32 | 2021-10-04 11:35 | 15 | 027:03 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | B21100300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1623 | 2021-10-03 | 24345 | keep | 0 | Oct | 2021 | 0.016581 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-03 08:36 | 2021-10-03 18:40 | 2 | 010:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE PRIMARIO ABIERTO | A21100300043 | New_Event | Wire Down | Include | Include | Equipment | 604 | 2021-10-03 | 1208 | keep | 0 | Oct | 2021 | 0.00082276 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-03 08:41 | 2021-10-03 18:30 | 60 | 009:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | A21100300046 | New_Event | Bad Weather | Include | Include | Weather | 589 | 2021-10-03 | 35340 | keep | 0 | Oct | 2021 | 0.02407 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-03 08:41 | 2021-10-03 16:32 | 50 | 007:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21100300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2021-10-03 | 23550 | keep | 0 | Oct | 2021 | 0.01604 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-03 08:43 | 2021-10-03 08:44 | 1403 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21100300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 1403 | keep | 0 | Oct | 2021 | 0.00095558 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
BAYAMON | 2021-10-03 08:52 | 2021-10-03 16:05 | 40 | 007:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21100300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 433 | 2021-10-03 | 17320 | keep | 0 | Oct | 2021 | 0.011797 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-03 08:53 | 2021-10-03 08:54 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1705-03 | B21100300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 478 | keep | 0 | Oct | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-10-03 08:53 | 2021-10-03 08:54 | 949 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1705-01 | B21100300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 949 | keep | 0 | Oct | 2021 | 0.00064636 | 0.00064636 | Momentary | FALSE | FALSE | Not_TMED_Event | 949
SAN JUAN | 2021-10-03 08:59 | 2021-10-03 09:00 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-03 | S21100300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-03 08:59 | 2021-10-03 09:00 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-05 | S21100300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-03 09:00 | 2021-10-03 16:04 | 38 | 007:04 | P | NO SE REPORTO CAUSA | 2 X 20 EN CORTE DE LINEA | S21100300102 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 424 | 2021-10-03 | 16112 | keep | 0 | Oct | 2021 | 0.010974 | 2.5882e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 38
ARECIBO | 2021-10-03 09:18 | 2021-10-03 10:21 | 50 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | A21100300062 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-10-03 | 3150 | keep | 0 | Oct | 2021 | 0.0021455 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-03 09:22 | 2021-10-03 16:26 | 40 | 007:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21100300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2021-10-03 | 16960 | keep | 0 | Oct | 2021 | 0.011551 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-03 09:26 | 2021-10-03 09:27 | 1922 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21100300031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-03 | 1922 | keep | 0 | Oct | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2021-10-03 09:27 | 2021-10-03 15:38 | 4 | 006:11 | P | PARARRAYOS DEFECTUOSO | 1 X 8 EN TRANSFORMADOR ELIMINO PARARRAYO | C21100300038 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 371 | 2021-10-03 | 1484 | keep | 0 | Oct | 2021 | 0.0010107 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-03 09:29 | 2021-10-03 10:30 | 30 | 001:01 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-10-03 | 1830 | keep | 0 | Oct | 2021 | 0.0012464 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-03 09:40 | 2021-10-03 09:41 | 2113 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | P21100300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-03 | 2113 | keep | 0 | Oct | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2021-10-03 09:41 | 2021-10-03 09:49 | 100 | 000:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 NX EN SU -5 AVERIA SOTERRADA CAUSADA POR PESONAL AAA | P21100300015 | Partial_restoration |  |  | Include | Wildlife | 8 | 2021-10-03 | 800 | keep | 0 | Oct | 2021 | 0.00054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-03 09:47 | 2021-10-03 09:54 | 1 | 000:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21100300073 | New_Event | Bad Weather | Include | Include | Weather | 7 | 2021-10-03 | 7 | keep | 0 | Oct | 2021 | 4.7677e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-03 09:49 | 2021-10-03 09:50 | 2113 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | P21100300028 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-03 | 2113 | keep | 0 | Oct | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2021-10-03 09:50 | 2021-10-03 10:08 | 100 | 000:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 NX EN SU -5 AVERIA SOTERRADA CAUSADA POR PESONAL AAA | P21100300015 | Partial_restoration |  |  | Include | Wildlife | 18 | 2021-10-03 | 1800 | keep | 0 | Oct | 2021 | 0.001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-03 09:53 | 2021-10-03 09:54 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100300033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
CAGUAS | 2021-10-03 10:04 | 2021-10-04 11:49 | 8 | 025:45 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADO RQUEMADO 37.5 KVA X 37.5 KVA | C21100300032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1545 | 2021-10-03 | 12360 | keep | 0 | Oct | 2021 | 0.0084183 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-10-03 10:05 | 2021-10-03 11:24 | 250 | 001:19 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21100200098 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-10-03 | 19750 | keep | 0 | Oct | 2021 | 0.013452 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-10-03 10:08 | 2021-10-03 10:09 | 2113 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | P21100300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-03 | 2113 | keep | 0 | Oct | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2021-10-03 10:09 | 2021-10-03 10:10 | 100 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 NX EN SU -5 AVERIA SOTERRADA CAUSADA POR PESONAL AAA | P21100300015 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-03 | 100 | keep | 0 | Oct | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-10-03 10:09 | 2021-10-03 13:31 | 8 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21100300083 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2021-10-03 | 1616 | keep | 0 | Oct | 2021 | 0.0011007 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
PONCE | 2021-10-03 10:10 | 2021-10-03 10:11 | 2113 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | P21100300032 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-03 | 2113 | keep | 0 | Oct | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:21 | 108 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-03 | 1080 | keep | 0 | Oct | 2021 | 0.00073558 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:21 | 1368 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-03 | 13680 | keep | 0 | Oct | 2021 | 0.0093174 | 0.00093174 | Sustained | FALSE | TRUE | Not_TMED_Event | 1368
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:21 | 2064 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-03 | 20640 | keep | 0 | Oct | 2021 | 0.014058 | 0.0014058 | Sustained | FALSE | TRUE | Not_TMED_Event | 2064
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 1681 | 000:08 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 13448 | keep | 0 | Oct | 2021 | 0.0091594 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 2435 | 000:08 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 19480 | keep | 0 | Oct | 2021 | 0.013268 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 726 | 000:08 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 5808 | keep | 0 | Oct | 2021 | 0.0039558 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 225 | 000:08 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 1800 | keep | 0 | Oct | 2021 | 0.001226 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 870 | 000:08 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 6960 | keep | 0 | Oct | 2021 | 0.0047404 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 726 | 000:08 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 5808 | keep | 0 | Oct | 2021 | 0.0039558 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-10-03 10:11 | 2021-10-03 10:19 | 1598 | 000:08 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21100300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-03 | 12784 | keep | 0 | Oct | 2021 | 0.0087071 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
PONCE | 2021-10-03 10:11 | 2021-10-03 10:16 | 100 | 000:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 NX EN SU -5 AVERIA SOTERRADA CAUSADA POR PESONAL AAA | P21100300015 | 1st_after_momentary |  |  | Include | Wildlife | 5 | 2021-10-03 | 500 | keep | 0 | Oct | 2021 | 0.00034055 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-10-03 10:11 | 2021-10-03 22:00 | 250 | 011:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21100200352 | New_Event | Bad Weather | Include | Include | Weather | 709 | 2021-10-03 | 177250 | keep | 0 | Oct | 2021 | 0.12072 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
PONCE | 2021-10-03 10:16 | 2021-10-03 12:02 | 2113 | 001:46 | T | DESGANCHE | DISPARO INTERRUPTOR CON RR EN OFF SE RETIRO RAMA EN COMPLEJO FERIAL DE PONCE | P21100300033 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-10-03 | 223978 | keep | 0 | Oct | 2021 | 0.15255 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2021-10-03 10:17 | 2021-10-03 20:10 | 200 | 009:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | M21100300123 | New_Event | Wire Down | Include | Include | Equipment | 593 | 2021-10-03 | 118600 | keep | 0 | Oct | 2021 | 0.080778 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-10-03 10:28 | 2021-10-03 11:17 | 35 | 000:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21100300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2021-10-03 | 1715 | keep | 0 | Oct | 2021 | 0.0011681 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-03 10:34 | 2021-10-03 10:35 | 3438 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B21100300042 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-03 | 3438 | keep | 0 | Oct | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
MAYAGÃœEZ | 2021-10-03 10:34 | 2021-10-03 18:10 | 100 | 007:36 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA POR DESGANCHE | M21100300129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 456 | 2021-10-03 | 45600 | keep | 0 | Oct | 2021 | 0.031058 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-03 10:35 | 2021-10-03 11:51 | 100 | 001:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | B21100300047 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 76 | 2021-10-03 | 7600 | keep | 0 | Oct | 2021 | 0.0051763 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-03 10:38 | 2021-10-03 18:04 | 10 | 007:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2021-10-03 | 4460 | keep | 0 | Oct | 2021 | 0.0030377 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-10-03 10:38 | 2021-10-04 12:59 | 150 | 026:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100300090 | New_Event | Bad Weather | Include | Include | Weather | 1581 | 2021-10-03 | 237150 | keep | 0 | Oct | 2021 | 0.16152 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-03 10:49 | 2021-10-03 17:55 | 40 | 007:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | M21100300138 | New_Event | Bad Weather | Include | Include | Weather | 426 | 2021-10-03 | 17040 | keep | 0 | Oct | 2021 | 0.011606 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-03 10:49 | 2021-10-03 11:33 | 12 | 000:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2021-10-03 | 528 | keep | 0 | Oct | 2021 | 0.00035962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-10-03 11:02 | 2021-10-03 14:30 | 1 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21100300044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-10-03 | 208 | keep | 0 | Oct | 2021 | 0.00014167 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-03 11:09 | 2021-10-04 13:20 | 30 | 026:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN PROVISIONAL AEREO | B21100300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1571 | 2021-10-03 | 47130 | keep | 0 | Oct | 2021 | 0.0321 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-03 11:19 | 2021-10-04 15:59 | 100 | 028:40 | P | DESGANCHE | 1 X 65 Y 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1720 | 2021-10-03 | 172000 | keep | 0 | Oct | 2021 | 0.11715 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-03 11:22 | 2021-10-04 10:57 | 3 | 023:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE | M21100300161 | New_Event | Wire Down | Include | Include | Equipment | 1415 | 2021-10-03 | 4245 | keep | 0 | Oct | 2021 | 0.0028913 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-10-03 11:26 | 2021-10-03 11:30 | 2000 | 000:04 | P | CABLE SOTERRADO AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA | R21100300015 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 4 | 2021-10-03 | 8000 | keep | 0 | Oct | 2021 | 0.0054488 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-03 11:27 | 2021-10-03 13:50 | 8 | 002:23 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | A21100300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-10-03 | 1144 | keep | 0 | Oct | 2021 | 0.00077917 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-10-03 11:28 | 2021-10-04 18:56 | 50 | 031:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1888 | 2021-10-03 | 94400 | keep | 0 | Oct | 2021 | 0.064295 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-03 11:30 | 2021-10-03 13:50 | 800 | 002:20 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU7 AL SU8 | R21100300015 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 140 | 2021-10-03 | 112000 | keep | 0 | Oct | 2021 | 0.076283 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2021-10-03 11:32 | 2021-10-03 13:27 | 20 | 001:55 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21100300049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 115 | 2021-10-03 | 2300 | keep | 0 | Oct | 2021 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-03 11:43 | 2021-10-04 15:26 | 15 | 027:43 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | M21100300173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1663 | 2021-10-03 | 24945 | keep | 0 | Oct | 2021 | 0.01699 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-03 11:43 | 2021-10-03 14:40 | 12 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21100300104 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-10-03 | 2124 | keep | 0 | Oct | 2021 | 0.0014466 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-10-03 11:46 | 2021-10-03 15:15 | 100 | 003:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21100300176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-10-03 | 20900 | keep | 0 | Oct | 2021 | 0.014235 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-03 11:46 | 2021-10-03 17:30 | 150 | 005:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21100300105 | New_Event | Bad Weather | Include | Include | Weather | 344 | 2021-10-03 | 51600 | keep | 0 | Oct | 2021 | 0.035145 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
GUAYAMA | 2021-10-03 11:47 | 2021-10-03 11:48 | 1173 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE INTERRUPTOR | P21100300045 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-03 | 1173 | keep | 0 | Oct | 2021 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2021-10-03 11:48 | 2021-10-03 13:01 | 80 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21100300046 | 1st_after_momentary |  |  | Include | Wildlife | 73 | 2021-10-03 | 5840 | keep | 0 | Oct | 2021 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-10-03 11:50 | 2021-10-03 13:38 | 100 | 001:48 | P | NO SE REPORTO CAUSA | 3 X 65 EN CORTE DE LINEA | B21100300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2021-10-03 | 10800 | keep | 0 | Oct | 2021 | 0.0073558 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-03 11:56 | 2021-10-03 11:57 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100300061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 1382 | keep | 0 | Oct | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-10-03 11:56 | 2021-10-03 11:57 | 663 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100300061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 663 | keep | 0 | Oct | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
PONCE | 2021-10-03 12:02 | 2021-10-03 15:22 | 100 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 NX EN SU -5 AVERIA SOTERRADA CAUSADA POR PESONAL AAA | P21100300015 | Partial_restoration |  |  | Include | Wildlife | 200 | 2021-10-03 | 20000 | keep | 0 | Oct | 2021 | 0.013622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-03 12:13 | 2021-10-03 18:00 | 10 | 005:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21100300114 | New_Event | Bad Weather | Include | Include | Weather | 347 | 2021-10-03 | 3470 | keep | 0 | Oct | 2021 | 0.0023634 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-10-03 12:18 | 2021-10-03 12:43 | 1 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21100300051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2021-10-03 | 25 | keep | 0 | Oct | 2021 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-03 12:19 | 2021-10-03 22:38 | 30 | 010:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21100200195 | New_Event | Bad Weather | Include | Include | Weather | 619 | 2021-10-03 | 18570 | keep | 0 | Oct | 2021 | 0.012648 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-10-03 12:22 | 2021-10-03 13:23 | 20 | 001:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21100300049 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2021-10-03 | 1220 | keep | 0 | Oct | 2021 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-10-03 12:54 | 2021-10-04 12:45 | 200 | 023:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1431 | 2021-10-03 | 286200 | keep | 0 | Oct | 2021 | 0.19493 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-10-03 13:03 | 2021-10-03 17:29 | 10 | 004:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21100300054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-10-03 | 2660 | keep | 0 | Oct | 2021 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-03 13:08 | 2021-10-03 14:57 | 60 | 001:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-10-03 | 6540 | keep | 0 | Oct | 2021 | 0.0044544 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-03 13:24 | 2021-10-03 16:15 | 50 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100300132 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2021-10-03 | 8550 | keep | 0 | Oct | 2021 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-03 13:36 | 2021-10-03 13:37 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 2858 | keep | 0 | Oct | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
SAN JUAN | 2021-10-03 13:50 | 2021-10-03 13:52 | 2000 | 000:02 | P | CABLE SOTERRADO AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA AVERIA DEL SU7 AL SU8 | R21100300015 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2021-10-03 | 4000 | keep | 0 | Oct | 2021 | 0.0027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-03 13:52 | 2021-10-03 14:20 | 800 | 000:28 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU7 AL SU8 | R21100300015 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 28 | 2021-10-03 | 22400 | keep | 0 | Oct | 2021 | 0.015257 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
ARECIBO | 2021-10-03 14:00 | 2021-10-03 14:45 | 11 | 000:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO MOLONY 25 KVA #SRE000281346 FID-31502683 POR 25 KVA | A21100300141 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2021-10-03 | 495 | keep | 0 | Oct | 2021 | 0.00033714 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-10-03 14:20 | 2021-10-03 14:22 | 2000 | 000:02 | P | CABLE SOTERRADO AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA AVERIA DEL SU7 AL SU8 | R21100300000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2021-10-03 | 4000 | keep | 0 | Oct | 2021 | 0.0027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-03 14:22 | 2021-10-03 16:02 | 800 | 001:40 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU 7 AL SU 8 | R21100300015 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 100 | 2021-10-03 | 80000 | keep | 0 | Oct | 2021 | 0.054488 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
ARECIBO | 2021-10-03 14:25 | 2021-10-03 14:55 | 1265 | 000:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE PRIMARIO EN EL TRONCAL | A21100300143 | Additional_clients | Wire Down | Include | Include | Equipment | 30 | 2021-10-03 | 37950 | keep | 0 | Oct | 2021 | 0.025848 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-03 14:26 | 2021-10-04 21:00 | 150 | 030:34 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRARON BAMBUAS SOBRE LAS LINEAS | M21100300265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1834 | 2021-10-03 | 275100 | keep | 0 | Oct | 2021 | 0.18737 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-10-03 14:33 | 2021-10-03 15:40 | 40 | 001:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21100300146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-10-03 | 2680 | keep | 0 | Oct | 2021 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-03 14:38 | 2021-10-04 11:18 | 70 | 020:40 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | M21100300271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1240 | 2021-10-03 | 86800 | keep | 0 | Oct | 2021 | 0.059119 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-10-03 14:49 | 2021-10-03 15:50 | 20 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100300088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-10-03 | 1220 | keep | 0 | Oct | 2021 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-10-03 14:55 | 2021-10-04 11:26 | 80 | 020:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100300073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1231 | 2021-10-03 | 98480 | keep | 0 | Oct | 2021 | 0.067074 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-03 14:55 | 2021-10-03 19:00 | 20 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100200347 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-10-03 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-03 15:07 | 2021-10-03 18:35 | 50 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21100300151 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2021-10-03 | 10400 | keep | 0 | Oct | 2021 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-10-03 15:10 | 2021-10-04 10:04 | 150 | 018:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100300111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1134 | 2021-10-03 | 170100 | keep | 0 | Oct | 2021 | 0.11585 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-03 15:18 | 2021-10-03 17:30 | 50 | 002:12 | P | CABLE SOTERRADO AVERIADO | SE REPARO PROVISIONAL AEREO | P21100300078 | New_Event | UG Cable Fault | Include | Include | Equipment | 132 | 2021-10-03 | 6600 | keep | 0 | Oct | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-03 15:19 | 2021-10-03 18:00 | 5 | 002:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 25KVA MARCA ERMCO SER:# 82011973262 FID:18426973 4160/7200V 120/240V X 25 KVA | M21100300284 | New_Event | Service Transformer Failure | Include | Include | Equipment | 161 | 2021-10-03 | 805 | keep | 0 | Oct | 2021 | 0.00054828 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-03 15:20 | 2021-10-03 17:30 | 30 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100200187 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-10-03 | 3900 | keep | 0 | Oct | 2021 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-03 15:22 | 2021-10-03 22:33 | 100 | 007:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21100200153 | New_Event | Bad Weather | Include | Include | Weather | 431 | 2021-10-03 | 43100 | keep | 0 | Oct | 2021 | 0.029355 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-03 15:26 | 2021-10-04 09:40 | 15 | 018:14 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100300094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1094 | 2021-10-03 | 16410 | keep | 0 | Oct | 2021 | 0.011177 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-10-03 15:41 | 2021-10-04 19:43 | 80 | 028:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21100300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1682 | 2021-10-03 | 134560 | keep | 0 | Oct | 2021 | 0.091648 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-10-03 15:50 | 2021-10-03 17:16 | 19 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21100300061 | New_Event |  |  | Include | Wildlife | 86 | 2021-10-03 | 1634 | keep | 0 | Oct | 2021 | 0.0011129 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
CAGUAS | 2021-10-03 15:56 | 2021-10-03 17:15 | 10 | 001:19 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | C21100300062 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 79 | 2021-10-03 | 790 | keep | 0 | Oct | 2021 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-03 16:01 | 2021-10-03 18:17 | 130 | 002:16 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | R21100300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-10-03 | 17680 | keep | 0 | Oct | 2021 | 0.012042 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
SAN JUAN | 2021-10-03 16:02 | 2021-10-03 16:07 | 2000 | 000:05 | P | CABLE SOTERRADO AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA, AVERIA DEL SU7 AL SU8 | R21100300000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 5 | 2021-10-03 | 10000 | keep | 0 | Oct | 2021 | 0.006811 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-10-03 16:22 | 2021-10-03 17:50 | 5 | 001:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO | R21100300082 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2021-10-03 | 440 | keep | 0 | Oct | 2021 | 0.00029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-03 16:24 | 2021-10-03 18:35 | 1 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21100300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-10-03 | 131 | keep | 0 | Oct | 2021 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-03 16:24 | 2021-10-03 16:25 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21100300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 3699 | keep | 0 | Oct | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
VEGA BAJA | 2021-10-03 16:29 | 2021-10-03 16:51 | 50 | 000:22 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21100300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2021-10-03 | 1100 | keep | 0 | Oct | 2021 | 0.0007492 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-03 16:37 | 2021-10-04 13:04 | 10 | 020:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21100300161 | New_Event | Bad Weather | Include | Include | Weather | 1227 | 2021-10-03 | 12270 | keep | 0 | Oct | 2021 | 0.008357 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-03 16:42 | 2021-10-03 16:50 | 10 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR POR MAL TIEMPO | M21100300336 | New_Event | Bad Weather | Include | Include | Weather | 8 | 2021-10-03 | 80 | keep | 0 | Oct | 2021 | 5.4488e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-03 17:01 | 2021-10-03 18:05 | 50 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21100300089 | New_Event |  |  | Include | Wildlife | 64 | 2021-10-03 | 3200 | keep | 0 | Oct | 2021 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-03 17:12 | 2021-10-04 12:11 | 20 | 018:59 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100300091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1139 | 2021-10-03 | 22780 | keep | 0 | Oct | 2021 | 0.015515 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-03 17:13 | 2021-10-03 17:51 | 15 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | S21100300089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-10-03 | 570 | keep | 0 | Oct | 2021 | 0.00038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-03 17:26 | 2021-10-04 12:09 | 50 | 018:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO Y LEVANTO AEREO PROVICIONAL | R21100300090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1123 | 2021-10-03 | 56150 | keep | 0 | Oct | 2021 | 0.038244 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-03 17:45 | 2021-10-03 19:57 | 13 | 002:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM-6 100KVA A 13.2KV AVERIADO 100KVA | P21100300095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 132 | 2021-10-03 | 1716 | keep | 0 | Oct | 2021 | 0.0011688 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2021-10-03 17:49 | 2021-10-03 17:50 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 3041 | keep | 0 | Oct | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
FAJARDO | 2021-10-03 18:04 | 2021-10-03 19:34 | 7 | 001:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO | R21100300096 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2021-10-03 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-03 18:06 | 2021-10-04 11:06 | 40 | 017:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21100300374 | New_Event | Bad Weather | Include | Include | Weather | 1020 | 2021-10-03 | 40800 | keep | 0 | Oct | 2021 | 0.027789 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-10-03 18:13 | 2021-10-04 16:00 | 50 | 021:47 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA POR DESGANCHE | M21100300376 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1307 | 2021-10-03 | 65350 | keep | 0 | Oct | 2021 | 0.04451 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-03 18:19 | 2021-10-04 12:38 | 100 | 018:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA | M21100300380 | New_Event | Wire Down | Include | Include | Equipment | 1099 | 2021-10-03 | 109900 | keep | 0 | Oct | 2021 | 0.074852 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-03 18:21 | 2021-10-05 01:23 | 140 | 031:02 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA SU-4 | R21140300015 | New_Event | UG Cable Fault | Include | Include | Equipment | 1862 | 2021-10-03 | 260680 | keep | 0 | Oct | 2021 | 0.17755 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2021-10-03 18:28 | 2021-10-04 00:25 | 1408 | 005:57 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO MACHETES DE AMARRE EN MARGINAL CARRETERA 2 URBANIZACION SANTA ROSA SE REPARO TERMINACION AVERIADA EN RISER DE SALIDA ALIMENTADOR 1714-02 LLEVA LA CARGA DEL 1714-03 | B21100300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 357 | 2021-10-03 | 502656 | keep | 0 | Oct | 2021 | 0.34236 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-10-03 18:28 | 2021-10-03 23:58 | 1408 | 005:30 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA SE REPARO TERMINACION AVERIADA EN RISER DE SALIDA LLEVA CARGA 1714 03 | B21100300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 330 | 2021-10-03 | 464640 | keep | 0 | Oct | 2021 | 0.31646 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-10-03 18:28 | 2021-10-04 00:25 | 455 | 005:57 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO MACHETES DE AMARRE EN MARGINAL CARRETERA 2 URBANIZACION SANTA ROSA SE REPARO TERMINACION AVERIADA EN RISER DE SALIDA ALIMENTADOR 1714 02 | B21100300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 357 | 2021-10-03 | 162435 | keep | 0 | Oct | 2021 | 0.11063 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
MAYAGÃœEZ | 2021-10-03 18:30 | 2021-10-03 19:28 | 80 | 000:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21100300384 | New_Event | Bad Weather | Include | Include | Weather | 58 | 2021-10-03 | 4640 | keep | 0 | Oct | 2021 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-03 18:40 | 2021-10-03 18:43 | 135 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21100300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-03 | 405 | keep | 0 | Oct | 2021 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
ARECIBO | 2021-10-03 18:40 | 2021-10-03 19:24 | 2071 | 000:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR AUTORIZADO POR ANGEL SOTO PARA REPARAR BAJANTE EN CORTE DE LINEA | A21100300173 | New_Event | Wire Down | Include | Include | Equipment | 44 | 2021-10-03 | 91124 | keep | 0 | Oct | 2021 | 0.062064 | 0.0014105 | Sustained | FALSE | TRUE | Not_TMED_Event | 2071
MAYAGÃœEZ | 2021-10-03 19:16 | 2021-10-03 20:40 | 60 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21100300390 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-10-03 | 5040 | keep | 0 | Oct | 2021 | 0.0034327 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-03 19:52 | 2021-10-04 09:32 | 8 | 013:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100300178 | New_Event | Bad Weather | Include | Include | Weather | 820 | 2021-10-03 | 6560 | keep | 0 | Oct | 2021 | 0.004468 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-03 19:53 | 2021-10-03 20:00 | 1935 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV | B21100300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-10-03 | 13545 | keep | 0 | Oct | 2021 | 0.0092254 | 0.0013179 | Sustained | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-10-03 19:53 | 2021-10-03 20:00 | 3 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV | B21100300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-10-03 | 21 | keep | 0 | Oct | 2021 | 1.4303e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-03 19:53 | 2021-10-03 20:00 | 61 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV | B21100300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-10-03 | 427 | keep | 0 | Oct | 2021 | 0.00029083 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-10-03 19:53 | 2021-10-03 20:00 | 1501 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV | B21100300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-10-03 | 10507 | keep | 0 | Oct | 2021 | 0.0071563 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-10-03 19:53 | 2021-10-03 20:00 | 546 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV | B21100300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-10-03 | 3822 | keep | 0 | Oct | 2021 | 0.0026031 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
UTUADO | 2021-10-03 20:12 | 2021-10-04 11:14 | 4 | 015:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100300182 | New_Event | Bad Weather | Include | Include | Weather | 902 | 2021-10-03 | 3608 | keep | 0 | Oct | 2021 | 0.0024574 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-03 20:29 | 2021-10-04 10:05 | 150 | 013:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21100300408 | New_Event | Bad Weather | Include | Include | Weather | 816 | 2021-10-03 | 122400 | keep | 0 | Oct | 2021 | 0.083366 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-03 20:41 | 2021-10-04 16:19 | 17 | 019:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA | S21100300100 | New_Event | Wire Down | Include | Include | Equipment | 1178 | 2021-10-03 | 20026 | keep | 0 | Oct | 2021 | 0.01364 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
SAN JUAN | 2021-10-03 20:54 | 2021-10-04 13:21 | 7 | 016:27 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | R21100300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 987 | 2021-10-03 | 6909 | keep | 0 | Oct | 2021 | 0.0047057 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-10-03 20:55 | 2021-10-04 00:58 | 540 | 004:03 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE REMPLAZO | P21100400005 | New_Event | Switch Failure | Include | Include | Equipment | 243 | 2021-10-03 | 131220 | keep | 0 | Oct | 2021 | 0.089373 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
BAYAMON | 2021-10-03 20:57 | 2021-10-03 20:58 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21100300128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 3438 | keep | 0 | Oct | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
ARECIBO | 2021-10-03 21:00 | 2021-10-04 14:50 | 100 | 017:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21100300184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1070 | 2021-10-03 | 107000 | keep | 0 | Oct | 2021 | 0.072877 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-03 21:15 | 2021-10-03 21:16 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100300130 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 3438 | keep | 0 | Oct | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
CANOVANAS | 2021-10-03 21:26 | 2021-10-03 22:34 | 7 | 001:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R21100300113 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2021-10-03 | 476 | keep | 0 | Oct | 2021 | 0.0003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-03 21:28 | 2021-10-03 22:26 | 200 | 000:58 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100200352 | New_Event | Bad Weather | Include | Include | Weather | 58 | 2021-10-03 | 11600 | keep | 0 | Oct | 2021 | 0.0079007 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
GUAYAMA | 2021-10-03 21:30 | 2021-10-04 12:16 | 13 | 014:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CONECTO BAJANTE DE LINEA PRIMARIA A CAJA DE TRANSFORMADOR | P21100300107 | New_Event | Wire Down | Include | Include | Equipment | 886 | 2021-10-03 | 11518 | keep | 0 | Oct | 2021 | 0.0078449 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-10-03 21:42 | 2021-10-04 11:51 | 300 | 014:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40, 1 X 65, 1 X 80 Y 2 X 100 EN CORTE DE LINEA MAL TIEMPO | M21100300422 | New_Event | Bad Weather | Include | Include | Weather | 849 | 2021-10-03 | 254700 | keep | 0 | Oct | 2021 | 0.17348 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-03 21:47 | 2021-10-04 14:51 | 105 | 017:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21100300423 | New_Event | Bad Weather | Include | Include | Weather | 1024 | 2021-10-03 | 107520 | keep | 0 | Oct | 2021 | 0.073231 | 7.1515e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 105
CANOVANAS | 2021-10-03 22:25 | 2021-10-03 22:26 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21100300118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-03 | 3699 | keep | 0 | Oct | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
AGUADILLA | 2021-10-03 23:06 | 2021-10-04 14:36 | 2946 | 015:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARARON LINEAS PRIMARIAS PARTIDAS | M21100300428 | New_Event | Wire Down | Include | Include | Equipment | 930 | 2021-10-03 | 2739780 | keep | 0 | Oct | 2021 | 1.8661 | 0.0020065 | Sustained | FALSE | TRUE | Not_TMED_Event | 2946
ARECIBO | 2021-10-03 23:21 | 2021-10-04 12:42 | 125 | 013:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100300189 | New_Event | Bad Weather | Include | Include | Weather | 801 | 2021-10-03 | 100125 | keep | 0 | Oct | 2021 | 0.068195 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
HUMACAO | 2021-10-03 23:34 | 2021-10-04 12:20 | 40 | 012:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21100300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 766 | 2021-10-03 | 30640 | keep | 0 | Oct | 2021 | 0.020869 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-10-03 23:45 | 2021-10-04 12:22 | 40 | 012:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21100300076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 757 | 2021-10-03 | 30280 | keep | 0 | Oct | 2021 | 0.020624 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-04 00:01 | 2021-10-04 09:06 | 1 | 009:05 | P | DESGANCHE | 1 X 25 EN RISER | C21100400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 545 | 2021-10-04 | 545 | keep | 0 | Oct | 2021 | 0.0003712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-10-04 00:19 | 2021-10-04 00:20 | 1648 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | R21100400001 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-04 | 1648 | keep | 0 | Oct | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-10-04 00:20 | 2021-10-04 10:48 | 40 | 010:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 40 EN CORTES DE LINEA | R21100400009 | 1st_after_momentary |  |  | Include | Wildlife | 628 | 2021-10-04 | 25120 | keep | 0 | Oct | 2021 | 0.017109 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-04 00:53 | 2021-10-04 11:22 | 35 | 010:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA | S21100400001 | New_Event | Wire Down | Include | Include | Equipment | 629 | 2021-10-04 | 22015 | keep | 0 | Oct | 2021 | 0.014994 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-10-04 00:58 | 2021-10-04 01:16 | 2751 | 000:18 | T | MAL TIEMPO/RAYOS/WET ASH | REMPLAZO DE MACHETE QUEMADO | P21100400006 | New_Event | Bad Weather | Include | Include | Weather | 18 | 2021-10-04 | 49518 | keep | 0 | Oct | 2021 | 0.033726 | 0.0018737 | Sustained | FALSE | FALSE | Not_TMED_Event | 2751
SAN JUAN | 2021-10-04 01:25 | 2021-10-04 01:26 | 99 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 1647-07 CERRADO POR CONTROL | R21100400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 99 | keep | 0 | Oct | 2021 | 6.7428e-05 | 6.7428e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 99
SAN JUAN | 2021-10-04 01:25 | 2021-10-04 01:26 | 31 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1647-06 CERRADO POR CONTROL | R21100400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 31 | keep | 0 | Oct | 2021 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
PONCE | 2021-10-04 03:19 | 2021-10-04 03:20 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100400012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 3744 | keep | 0 | Oct | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-10-04 03:19 | 2021-10-04 03:20 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 3114 | keep | 0 | Oct | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
CANOVANAS | 2021-10-04 03:46 | 2021-10-04 12:16 | 7 | 008:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21100400004 | New_Event |  |  | Include | Wildlife | 510 | 2021-10-04 | 3570 | keep | 0 | Oct | 2021 | 0.0024315 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-04 03:58 | 2021-10-04 04:01 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303 05 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-04 | 675 | keep | 0 | Oct | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-04 03:58 | 2021-10-04 04:01 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1303 04 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-04 | 2610 | keep | 0 | Oct | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-10-04 04:13 | 2021-10-04 04:14 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 1526 | keep | 0 | Oct | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-10-04 04:14 | 2021-10-04 20:31 | 20 | 016:17 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21100400041 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 977 | 2021-10-04 | 19540 | keep | 0 | Oct | 2021 | 0.013309 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-04 04:29 | 2021-10-04 04:30 | 2435 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR CARGA POR 1909-08 | S21100400000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-04 | 2435 | keep | 0 | Oct | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-10-04 04:29 | 2021-10-04 04:30 | 2956 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR LLEVA CARGA 1907-05 | S21100400000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-04 | 2956 | keep | 0 | Oct | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-10-04 04:30 | 2021-10-04 23:05 | 30 | 018:35 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE RETIRARON 3 PARARRAYOS DEFECTUOSOS | S21100400013 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1115 | 2021-10-04 | 33450 | keep | 0 | Oct | 2021 | 0.022783 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-04 05:06 | 2021-10-04 05:07 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 2113 | keep | 0 | Oct | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BARRANQUITAS | 2021-10-04 05:16 | 2021-10-04 12:49 | 20 | 007:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21100400002 | New_Event | Wire Down | Include | Include | Equipment | 453 | 2021-10-04 | 9060 | keep | 0 | Oct | 2021 | 0.0061707 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-04 05:25 | 2021-10-04 10:46 | 150 | 005:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100400003 | New_Event | Bad Weather | Include | Include | Weather | 321 | 2021-10-04 | 48150 | keep | 0 | Oct | 2021 | 0.032795 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
GUAYAMA | 2021-10-04 06:00 | 2021-10-04 11:42 | 5 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P21100400051 | New_Event | Bad Weather | Include | Include | Weather | 342 | 2021-10-04 | 1710 | keep | 0 | Oct | 2021 | 0.0011647 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-10-04 06:25 | 2021-10-04 10:23 | 65 | 003:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21100400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-10-04 | 15470 | keep | 0 | Oct | 2021 | 0.010537 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-10-04 06:31 | 2021-10-04 10:59 | 30 | 004:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | B21100400015 | New_Event |  |  | Include | Wildlife | 268 | 2021-10-04 | 8040 | keep | 0 | Oct | 2021 | 0.005476 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-04 06:35 | 2021-10-05 12:07 | 80 | 029:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21100400012 | New_Event | Wire Down | Include | Include | Equipment | 1772 | 2021-10-04 | 141760 | keep | 0 | Oct | 2021 | 0.096552 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-04 06:36 | 2021-10-04 06:37 | 449 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | P21100400017 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-04 | 449 | keep | 0 | Oct | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2021-10-04 06:37 | 2021-10-04 14:27 | 100 | 007:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | P21100400033 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 470 | 2021-10-04 | 47000 | keep | 0 | Oct | 2021 | 0.032011 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-04 06:47 | 2021-10-04 12:03 | 6 | 005:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21100400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-10-04 | 1896 | keep | 0 | Oct | 2021 | 0.0012914 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-10-04 06:49 | 2021-10-04 20:11 | 1 | 013:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 802 | 2021-10-04 | 802 | keep | 0 | Oct | 2021 | 0.00054624 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-04 06:52 | 2021-10-04 11:05 | 80 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 2 X 50 EN CORTE DE LINEA MAL TIEMPO | M21100400019 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-10-04 | 20240 | keep | 0 | Oct | 2021 | 0.013785 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-04 06:54 | 2021-10-04 10:24 | 50 | 003:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21100300008 | New_Event |  |  | Include | Wildlife | 210 | 2021-10-04 | 10500 | keep | 0 | Oct | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-04 07:07 | 2021-10-04 23:46 | 30 | 016:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21100400019 | New_Event | Cutout Failure | Include | Include | Equipment | 999 | 2021-10-04 | 29970 | keep | 0 | Oct | 2021 | 0.020412 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-04 07:11 | 2021-10-04 10:20 | 50 | 003:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-10-04 | 9450 | keep | 0 | Oct | 2021 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-04 07:29 | 2021-10-04 15:10 | 5 | 007:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21100400009 | New_Event | Bad Weather | Include | Include | Weather | 461 | 2021-10-04 | 2305 | keep | 0 | Oct | 2021 | 0.0015699 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-10-04 07:36 | 2021-10-04 11:13 | 2 | 003:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-10-04 | 434 | keep | 0 | Oct | 2021 | 0.0002956 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CAGUAS | 2021-10-04 07:42 | 2021-10-04 15:35 | 30 | 007:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21100400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2021-10-04 | 14190 | keep | 0 | Oct | 2021 | 0.0096647 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-10-04 07:44 | 2021-10-04 07:45 | 1593 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21100400000 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-04 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-10-04 07:45 | 2021-10-04 09:14 | 81 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21100400022 | 1st_after_momentary |  |  | Include | Wildlife | 89 | 2021-10-04 | 7209 | keep | 0 | Oct | 2021 | 0.00491 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
MAYAGÃœEZ | 2021-10-04 07:48 | 2021-10-04 11:00 | 8 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | M21100400036 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-10-04 | 1536 | keep | 0 | Oct | 2021 | 0.0010462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-04 08:01 | 2021-10-05 13:16 | 1 | 029:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21100400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1755 | 2021-10-04 | 1755 | keep | 0 | Oct | 2021 | 0.0011953 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-04 08:05 | 2021-10-04 17:10 | 100 | 009:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21100400014 | New_Event | Wire Down | Include | Include | Equipment | 545 | 2021-10-04 | 54500 | keep | 0 | Oct | 2021 | 0.03712 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-10-04 08:15 | 2021-10-05 11:34 | 12 | 027:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21100400014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1639 | 2021-10-04 | 19668 | keep | 0 | Oct | 2021 | 0.013396 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-04 08:16 | 2021-10-04 14:43 | 1 | 006:27 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR SE INSPECCIONO | R21100400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 387 | 2021-10-04 | 387 | keep | 0 | Oct | 2021 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-04 08:21 | 2021-10-04 21:27 | 20 | 013:06 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU7 AL SU8 TRAMO SE CONSTRUYO AEREO PROVISIONAL DEL AEREO EXISTENTE AL T5 | R21100400015 | New_Event | UG Cable Fault | Include | Include | Equipment | 786 | 2021-10-04 | 15720 | keep | 0 | Oct | 2021 | 0.010707 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-10-04 08:22 | 2021-10-04 16:50 | 20 | 008:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | R21100400016 | New_Event | Wire Down | Include | Include | Equipment | 508 | 2021-10-04 | 10160 | keep | 0 | Oct | 2021 | 0.0069199 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-04 08:24 | 2021-10-04 14:40 | 15 | 006:16 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | A21100400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2021-10-04 | 5640 | keep | 0 | Oct | 2021 | 0.0038414 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-04 08:31 | 2021-10-05 09:16 | 10 | 024:45 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN RISER | S21100400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1485 | 2021-10-04 | 14850 | keep | 0 | Oct | 2021 | 0.010114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-04 08:39 | 2021-10-04 08:41 | 2782 | 000:02 | T | PARARRAYOS DEFECTUOSO | DISPARO NO RECERRO LLEVA 20% DEL 1111-1 SE PROBO QUEDO EN SERVICIO | S21100400024 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2021-10-04 | 5564 | keep | 0 | Oct | 2021 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2021-10-04 08:48 | 2021-10-04 10:56 | 12 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE | S21100400016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2021-10-04 | 1536 | keep | 0 | Oct | 2021 | 0.0010462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-10-04 08:49 | 2021-10-04 16:30 | 100 | 007:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2021-10-04 | 46100 | keep | 0 | Oct | 2021 | 0.031399 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-10-04 08:52 | 2021-10-04 10:43 | 200 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | P21100400041 | New_Event |  |  | Include | Wildlife | 111 | 2021-10-04 | 22200 | keep | 0 | Oct | 2021 | 0.01512 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-04 08:56 | 2021-10-04 09:45 | 400 | 000:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO 20% DE LA CARGA ESTA POR EL 1118-01 SE PATRULLO NO SE REPORTO CAUSA | S21100400024 | New_Event | Wire Down | Include | Include | Equipment | 49 | 2021-10-04 | 19600 | keep | 0 | Oct | 2021 | 0.013349 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-10-04 08:56 | 2021-10-04 09:45 | 2782 | 000:49 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO LLEVA 20% DEL 1111-01 SE PATRULLO NO SE REPORTO CAUSA | S21100400024 | New_Event | Wire Down | Include | Include | Equipment | 49 | 2021-10-04 | 136318 | keep | 0 | Oct | 2021 | 0.092846 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
BARRANQUITAS | 2021-10-04 09:09 | 2021-10-04 09:10 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 18400 | C21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2410 | keep | 0 | Oct | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | TRUE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-10-04 09:09 | 2021-10-04 09:10 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 18400 | C21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2826 | keep | 0 | Oct | 2021 | 0.0019248 | 0.0019248 | Momentary | FALSE | TRUE | Not_TMED_Event | 2826
CANOVANAS | 2021-10-04 09:11 | 2021-10-04 15:09 | 10 | 005:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R21100400027 | New_Event |  |  | Include | Wildlife | 358 | 2021-10-04 | 3580 | keep | 0 | Oct | 2021 | 0.0024383 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-04 09:12 | 2021-10-04 11:48 | 100 | 002:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21100400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-10-04 | 15600 | keep | 0 | Oct | 2021 | 0.010625 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-04 09:12 | 2021-10-04 10:30 | 15 | 001:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA POR 37.5KVA | B21100400038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 78 | 2021-10-04 | 1170 | keep | 0 | Oct | 2021 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-10-04 09:14 | 2021-10-04 09:15 | 1593 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21100400000 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-10-04 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-04 09:15 | 2021-10-04 15:54 | 81 | 006:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21100400022 | 1st_after_momentary |  |  | Include | Wildlife | 399 | 2021-10-04 | 32319 | keep | 0 | Oct | 2021 | 0.022012 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
BARRANQUITAS | 2021-10-04 09:18 | 2021-10-04 09:33 | 2635 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-10-04 | 39525 | keep | 0 | Oct | 2021 | 0.02692 | 0.0017947 | Sustained | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-10-04 09:18 | 2021-10-04 09:33 | 2280 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-10-04 | 34200 | keep | 0 | Oct | 2021 | 0.023293 | 0.0015529 | Sustained | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-10-04 09:18 | 2021-10-04 09:33 | 1617 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 | C21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-10-04 | 24255 | keep | 0 | Oct | 2021 | 0.01652 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 2791 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2791 | keep | 0 | Oct | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | TRUE | Not_TMED_Event | 2791
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 1464 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1464 | keep | 0 | Oct | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 759 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 759 | keep | 0 | Oct | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | TRUE | Not_TMED_Event | 759
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 1500 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1500 | keep | 0 | Oct | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 1500
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 2132 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2132 | keep | 0 | Oct | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | TRUE | Not_TMED_Event | 2132
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 2366 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2366 | keep | 0 | Oct | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | TRUE | Not_TMED_Event | 2366
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 1976 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1976 | keep | 0 | Oct | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | TRUE | Not_TMED_Event | 1976
ARECIBO | 2021-10-04 09:24 | 2021-10-04 09:25 | 3688 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 3688 | keep | 0 | Oct | 2021 | 0.0025119 | 0.0025119 | Momentary | FALSE | TRUE | Not_TMED_Event | 3688
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 3070 | keep | 0 | Oct | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | TRUE | Not_TMED_Event | 3070
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2735 | keep | 0 | Oct | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | TRUE | Not_TMED_Event | 2735
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1070 | keep | 0 | Oct | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | TRUE | Not_TMED_Event | 1070
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1647 | keep | 0 | Oct | 2021 | 0.0011218 | 0.0011218 | Momentary | FALSE | TRUE | Not_TMED_Event | 1647
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 3295 | keep | 0 | Oct | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | TRUE | Not_TMED_Event | 3295
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1180 | keep | 0 | Oct | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | TRUE | Not_TMED_Event | 1180
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | TRUE | Not_TMED_Event | 320
BAYAMON | 2021-10-04 09:24 | 2021-10-04 09:25 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B21100400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | TRUE | Not_TMED_Event | 2234
ARECIBO | 2021-10-04 09:25 | 2021-10-04 15:40 | 6 | 006:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | A21100200016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 375 | 2021-10-04 | 2250 | keep | 0 | Oct | 2021 | 0.0015325 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-04 09:27 | 2021-10-05 10:23 | 1 | 024:56 | P | DESGANCHE | 2 X 10 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1496 | 2021-10-04 | 1496 | keep | 0 | Oct | 2021 | 0.0010189 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-04 09:28 | 2021-10-04 14:49 | 15 | 005:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100400036 | New_Event | Bad Weather | Include | Include | Weather | 321 | 2021-10-04 | 4815 | keep | 0 | Oct | 2021 | 0.0032795 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-04 09:30 | 2021-10-04 13:39 | 40 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21100400037 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-10-04 | 9960 | keep | 0 | Oct | 2021 | 0.0067837 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-10-04 09:35 | 2021-10-04 18:39 | 30 | 009:04 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21100400039 | New_Event | Defective Pole | Include | Include | Equipment | 544 | 2021-10-04 | 16320 | keep | 0 | Oct | 2021 | 0.011115 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-04 09:36 | 2021-10-04 14:58 | 40 | 005:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21100400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-10-04 | 12880 | keep | 0 | Oct | 2021 | 0.0087725 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-04 09:36 | 2021-10-05 18:27 | 8 | 032:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | M21100400054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1971 | 2021-10-04 | 15768 | keep | 0 | Oct | 2021 | 0.01074 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-04 09:36 | 2021-10-04 17:19 | 20 | 007:43 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA POR 50KVA | B21100300034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 463 | 2021-10-04 | 9260 | keep | 0 | Oct | 2021 | 0.0063069 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-04 09:36 | 2021-10-04 14:01 | 100 | 004:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21100400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 265 | 2021-10-04 | 26500 | keep | 0 | Oct | 2021 | 0.018049 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-04 09:40 | 2021-10-04 18:54 | 20 | 009:14 | P | DESGANCHE | 1 X 100 Y 2 X 65 EN CORTES DE LINEA POR DESGANCHE | M21100400056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 554 | 2021-10-04 | 11080 | keep | 0 | Oct | 2021 | 0.0075465 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
GUAYAMA | 2021-10-04 09:51 | 2021-10-04 11:56 | 15 | 002:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 13.2 KV CON LIQUEO DE ACEITE X 50 KVA | P21100400037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-10-04 | 1875 | keep | 0 | Oct | 2021 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-04 09:51 | 2021-10-04 16:50 | 200 | 006:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 30 Y 1 X 80 EN CORTES DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PARTIDO | A21100400041 | New_Event | Wire Down | Include | Include | Equipment | 419 | 2021-10-04 | 83800 | keep | 0 | Oct | 2021 | 0.057076 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-04 09:53 | 2021-10-04 15:20 | 1 | 005:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21100400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2021-10-04 | 327 | keep | 0 | Oct | 2021 | 0.00022272 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-10-04 09:55 | 2021-10-05 11:50 | 1 | 025:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONEXIONES EN PEDESTAL | P21100400039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1555 | 2021-10-04 | 1555 | keep | 0 | Oct | 2021 | 0.0010591 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-04 09:58 | 2021-10-05 12:59 | 80 | 027:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1621 | 2021-10-04 | 129680 | keep | 0 | Oct | 2021 | 0.088324 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-04 10:05 | 2021-10-04 10:06 | 1548 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A21100400048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-04 | 1548 | keep | 0 | Oct | 2021 | 0.0010543 | 0.0010543 | Momentary | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2021-10-04 10:05 | 2021-10-04 10:06 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21100400049 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-04 | 3431 | keep | 0 | Oct | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-10-04 10:05 | 2021-10-04 11:40 | 40 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21100400045 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-10-04 | 3800 | keep | 0 | Oct | 2021 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-04 10:06 | 2021-10-04 22:31 | 70 | 012:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21100400150 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 745 | 2021-10-04 | 52150 | keep | 0 | Oct | 2021 | 0.035519 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-10-04 10:06 | 2021-10-04 17:55 | 9 | 007:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100400127 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 469 | 2021-10-04 | 4221 | keep | 0 | Oct | 2021 | 0.0028749 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-10-04 10:10 | 2021-10-04 20:15 | 3 | 010:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 30 EN CORTE DE LINEA LINEAS ANREDADAS | A21100400063 | New_Event | Wire Down | Include | Include | Equipment | 605 | 2021-10-04 | 1815 | keep | 0 | Oct | 2021 | 0.0012362 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
ARECIBO | 2021-10-04 10:10 | 2021-10-04 10:11 | 438 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A21100400053 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-04 | 438 | keep | 0 | Oct | 2021 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
SAN JUAN | 2021-10-04 10:14 | 2021-10-04 11:06 | 400 | 000:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO LLEVA 20% DEL 1111-01 SE ABRE N/O SAGRADO CORAZON ESQUINA PONCE DE LEON Y SE CERRO 1118-10 QUEDO FUERA CARGA 1111-01 SE ENCONTRO PUENTE COLGANDO DEL PARQUE ESQUINA FERNANDEZ JUNCOS | S21100400024 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2021-10-04 | 20800 | keep | 0 | Oct | 2021 | 0.014167 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-10-04 10:14 | 2021-10-04 10:37 | 2782 | 000:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO LLEVA 20% DEL 1111-1 SE ABRE N/O SAGRADO CORAZON ESQ. PONCE DE LEON Y SE CERRO 1118-10 QUEO FUERA CARGA 1111-1 SE ENCONTRO PUENTE COLGANDO DEL PARQUET ESQ. FERNANDEZ JUNCOS | S21100400024 | New_Event | Wire Down | Include | Include | Equipment | 23 | 2021-10-04 | 63986 | keep | 0 | Oct | 2021 | 0.043581 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
HUMACAO | 2021-10-04 10:16 | 2021-10-04 14:18 | 65 | 004:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21100400053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-10-04 | 15730 | keep | 0 | Oct | 2021 | 0.010714 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-10-04 10:16 | 2021-10-04 15:28 | 20 | 005:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21100400106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2021-10-04 | 6240 | keep | 0 | Oct | 2021 | 0.00425 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-10-04 10:17 | 2021-10-05 11:10 | 100 | 024:53 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P21100400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1493 | 2021-10-04 | 149300 | keep | 0 | Oct | 2021 | 0.10169 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-04 10:22 | 2021-10-04 16:50 | 50 | 006:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21100400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2021-10-04 | 19400 | keep | 0 | Oct | 2021 | 0.013213 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-04 10:26 | 2021-10-11 18:38 | 50 | 176:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SEPARARON LINEAS CRUZADAS | A21100400061 | New_Event | Wire Down | Include | Include | Equipment | 10572 | 2021-10-04 | 528600 | keep | 0 | Oct | 2021 | 0.36003 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-04 10:35 | 2021-10-04 19:59 | 2 | 009:24 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL SECUNDARIO | R21100400036 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 564 | 2021-10-04 | 1128 | keep | 0 | Oct | 2021 | 0.00076828 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-10-04 10:42 | 2021-10-04 18:10 | 80 | 007:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M21100400082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-10-04 | 35840 | keep | 0 | Oct | 2021 | 0.02441 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-04 10:45 | 2021-10-04 14:13 | 60 | 003:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21100400066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-10-04 | 12480 | keep | 0 | Oct | 2021 | 0.0085001 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-04 10:47 | 2021-10-04 18:16 | 50 | 007:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHO ENDEREZO POSTE Y LEVANTO CONDUCTOR | C21100400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2021-10-04 | 22450 | keep | 0 | Oct | 2021 | 0.015291 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-04 10:48 | 2021-10-04 17:02 | 50 | 006:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21100400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2021-10-04 | 18700 | keep | 0 | Oct | 2021 | 0.012736 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-04 10:50 | 2021-10-04 14:27 | 1 | 003:37 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHO Y REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21100400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-10-04 | 217 | keep | 0 | Oct | 2021 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-04 10:53 | 2021-10-04 10:54 | 1093 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21100400052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 1093 | keep | 0 | Oct | 2021 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
SAN JUAN | 2021-10-04 10:59 | 2021-10-05 17:49 | 10 | 030:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CONSTRUYO PROVISIONAL AEREO SECUNDARIO | R21100400041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1850 | 2021-10-04 | 18500 | keep | 0 | Oct | 2021 | 0.0126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-04 11:09 | 2021-10-04 11:57 | 400 | 000:48 | P | PARARRAYOS DEFECTUOSO | DISPARO NO RECERRO 20% DE LA CARGA ESTA POR EL 1118-01 SE ABRIO N/O PARA RETIRAR PARARAYO #1880 LOS ROSALES | S21100400024 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 48 | 2021-10-04 | 19200 | keep | 0 | Oct | 2021 | 0.013077 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-10-04 11:09 | 2021-10-04 11:35 | 2782 | 000:26 | T | PARARRAYOS DEFECTUOSO | DISPARO NO RECERRO LLEVA 20% 1111-1 SE ABRIO N/O PARA RETIRAR PARARAYO #1880 LOS ROSALES | S21100400024 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 26 | 2021-10-04 | 72332 | keep | 0 | Oct | 2021 | 0.049265 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
ARECIBO | 2021-10-04 11:10 | 2021-10-04 20:20 | 300 | 009:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100400071 | New_Event | Bad Weather | Include | Include | Weather | 550 | 2021-10-04 | 165000 | keep | 0 | Oct | 2021 | 0.11238 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
GUAYAMA | 2021-10-04 11:12 | 2021-10-04 14:30 | 3 | 003:18 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA EN TRANSFORMADOR PARA REMPLAZO PEDESTAL SECUNDARIO | P21100400050 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 198 | 2021-10-04 | 594 | keep | 0 | Oct | 2021 | 0.00040457 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-04 11:21 | 2021-10-04 11:30 | 959 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-04 | 8631 | keep | 0 | Oct | 2021 | 0.0058785 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-10-04 11:21 | 2021-10-04 11:30 | 1297 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-04 | 11673 | keep | 0 | Oct | 2021 | 0.0079504 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-10-04 11:21 | 2021-10-04 11:30 | 451 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-04 | 4059 | keep | 0 | Oct | 2021 | 0.0027646 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-10-04 11:21 | 2021-10-04 11:30 | 1264 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-04 | 11376 | keep | 0 | Oct | 2021 | 0.0077481 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2021-10-04 11:21 | 2021-10-04 11:30 | 620 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-04 | 5580 | keep | 0 | Oct | 2021 | 0.0038005 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2021-10-04 11:22 | 2021-10-04 11:29 | 1935 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-04 | 13545 | keep | 0 | Oct | 2021 | 0.0092254 | 0.0013179 | Sustained | FALSE | TRUE | Not_TMED_Event | 1935
BAYAMON | 2021-10-04 11:22 | 2021-10-04 11:29 | 3 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-04 | 21 | keep | 0 | Oct | 2021 | 1.4303e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-04 11:22 | 2021-10-04 11:29 | 61 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-04 | 427 | keep | 0 | Oct | 2021 | 0.00029083 | 4.1547e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 61
BAYAMON | 2021-10-04 11:22 | 2021-10-04 11:29 | 1501 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-04 | 10507 | keep | 0 | Oct | 2021 | 0.0071563 | 0.0010223 | Sustained | FALSE | TRUE | Not_TMED_Event | 1501
BAYAMON | 2021-10-04 11:22 | 2021-10-04 11:29 | 546 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-04 | 3822 | keep | 0 | Oct | 2021 | 0.0026031 | 0.00037188 | Sustained | FALSE | TRUE | Not_TMED_Event | 546
ARECIBO | 2021-10-04 11:26 | 2021-10-04 14:40 | 50 | 003:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21100400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-10-04 | 9700 | keep | 0 | Oct | 2021 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-04 11:30 | 2021-10-04 12:24 | 10 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21100300068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-10-04 | 540 | keep | 0 | Oct | 2021 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-04 11:31 | 2021-10-04 15:11 | 35 | 003:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 X 75KVA | R21100400043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 220 | 2021-10-04 | 7700 | keep | 0 | Oct | 2021 | 0.0052444 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2021-10-04 11:31 | 2021-10-04 11:32 | 669 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21100400082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 669 | keep | 0 | Oct | 2021 | 0.00045565 | 0.00045565 | Momentary | FALSE | TRUE | Not_TMED_Event | 669
SAN JUAN | 2021-10-04 11:40 | 2021-10-04 16:21 | 3 | 004:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SECUNDARIOS | R21100400046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 281 | 2021-10-04 | 843 | keep | 0 | Oct | 2021 | 0.00057416 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-10-04 11:40 | 2021-10-04 15:10 | 1 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | A21100400087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2021-10-04 | 210 | keep | 0 | Oct | 2021 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-04 11:41 | 2021-10-04 18:47 | 60 | 007:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M21100400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 426 | 2021-10-04 | 25560 | keep | 0 | Oct | 2021 | 0.017409 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-04 11:41 | 2021-10-04 13:38 | 10 | 001:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA POR 37.5KVA | B21100200142 | New_Event | Service Transformer Failure | Include | Include | Equipment | 117 | 2021-10-04 | 1170 | keep | 0 | Oct | 2021 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-04 11:50 | 2021-10-04 19:03 | 27 | 007:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21100400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 433 | 2021-10-04 | 11691 | keep | 0 | Oct | 2021 | 0.0079627 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
HUMACAO | 2021-10-04 11:59 | 2021-10-05 17:37 | 6 | 029:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21100400077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1778 | 2021-10-04 | 10668 | keep | 0 | Oct | 2021 | 0.0072659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-04 12:01 | 2021-10-04 14:44 | 35 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21100400065 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-10-04 | 5705 | keep | 0 | Oct | 2021 | 0.0038856 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-10-04 12:05 | 2021-10-04 20:55 | 6 | 008:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | A21100400093 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 530 | 2021-10-04 | 3180 | keep | 0 | Oct | 2021 | 0.0021659 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-04 12:06 | 2021-10-04 16:12 | 80 | 004:06 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21100400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-10-04 | 19680 | keep | 0 | Oct | 2021 | 0.013404 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-04 12:07 | 2021-10-04 19:30 | 1 | 007:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR GLOBO DE HELIO | P21100400053 | New_Event |  |  | Include | Wildlife | 443 | 2021-10-04 | 443 | keep | 0 | Oct | 2021 | 0.00030173 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-10-04 12:16 | 2021-10-04 17:50 | 6 | 005:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21100400109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 334 | 2021-10-04 | 2004 | keep | 0 | Oct | 2021 | 0.0013649 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-04 12:18 | 2021-10-04 13:45 | 20 | 001:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR REPARAR CONEXIONES | M21100400110 | New_Event | Secondary Wire Down | Include | Include | Equipment | 87 | 2021-10-04 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-10-04 12:21 | 2021-10-04 13:31 | 470 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR ALAMBRE PARTIDO | M21100400000 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-10-04 | 32900 | keep | 0 | Oct | 2021 | 0.022408 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
AGUADILLA | 2021-10-04 12:21 | 2021-10-04 13:31 | 1345 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR ALAMBRE PARTIDO | M21100400000 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-10-04 | 94150 | keep | 0 | Oct | 2021 | 0.064125 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
SAN JUAN | 2021-10-04 12:24 | 2021-10-04 12:25 | 400 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO 20% DE LA CARGA ESTA POR EL 1118-10 SE PROBO QUEDO EN SERVICIO | S21100400024 | Partial_restoration | Wire Down | Include | Include | Equipment | 1 | 2021-10-04 | 400 | keep | 0 | Oct | 2021 | 0.00027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-04 12:25 | 2021-10-04 16:00 | 22 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA | S21100400088 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2021-10-04 | 4730 | keep | 0 | Oct | 2021 | 0.0032216 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
CAGUAS | 2021-10-04 12:30 | 2021-10-04 12:43 | 4 | 000:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR DESPEGO BAJANTE | C21100400087 | New_Event | Wire Down | Include | Include | Equipment | 13 | 2021-10-04 | 52 | keep | 0 | Oct | 2021 | 3.5417e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-04 12:31 | 2021-10-04 12:34 | 2203 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR SU-26 A RISER CONTRA 1424-6 | S21100400062 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-10-04 | 6609 | keep | 0 | Oct | 2021 | 0.0045014 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
VEGA BAJA | 2021-10-04 12:38 | 2021-10-04 14:45 | 27 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21100400071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-10-04 | 3429 | keep | 0 | Oct | 2021 | 0.0023355 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
CAGUAS | 2021-10-04 12:43 | 2021-10-04 12:44 | 3005 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | C21100400091 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-10-04 | 3005 | keep | 0 | Oct | 2021 | 0.0020467 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-04 12:44 | 2021-10-04 13:11 | 1605 | 000:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | CERRO EL IR 3006-5D CRUCE POR REPTIL | C21100400091 | New_Event |  |  | Include | Wildlife | 27 | 2021-10-04 | 43335 | keep | 0 | Oct | 2021 | 0.029515 | 0.0010932 | Sustained | FALSE | FALSE | Not_TMED_Event | 1605
CAGUAS | 2021-10-04 12:44 | 2021-10-05 13:46 | 10 | 025:02 | P | DESGANCHE | DESGANCHARON Y CERRO PUENTE | C21100400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1502 | 2021-10-04 | 15020 | keep | 0 | Oct | 2021 | 0.01023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-04 12:44 | 2021-10-04 16:36 | 20 | 003:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA ABRIO PUENTES PARA SECCIONALIZAR CONDUCTOR EN EL SUELO Y DESGANCHE | C21100400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2021-10-04 | 4640 | keep | 0 | Oct | 2021 | 0.0031603 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-04 12:44 | 2021-10-05 16:20 | 35 | 027:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21100400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1656 | 2021-10-04 | 57960 | keep | 0 | Oct | 2021 | 0.039476 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
YAUCO | 2021-10-04 12:45 | 2021-10-04 19:36 | 100 | 006:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21100400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2021-10-04 | 41100 | keep | 0 | Oct | 2021 | 0.027993 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-04 12:48 | 2021-10-04 17:56 | 100 | 005:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21100400082 | New_Event | Wire Down | Include | Include | Equipment | 308 | 2021-10-04 | 30800 | keep | 0 | Oct | 2021 | 0.020978 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-04 12:50 | 2021-10-04 12:52 | 959 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-04 | 1918 | keep | 0 | Oct | 2021 | 0.0013063 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:50 | 2021-10-04 12:52 | 1297 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-04 | 2594 | keep | 0 | Oct | 2021 | 0.0017668 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:50 | 2021-10-04 12:52 | 451 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-04 | 902 | keep | 0 | Oct | 2021 | 0.00061435 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:50 | 2021-10-04 12:52 | 1264 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-04 | 2528 | keep | 0 | Oct | 2021 | 0.0017218 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:50 | 2021-10-04 12:52 | 620 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-9800 | S21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-04 | 1240 | keep | 0 | Oct | 2021 | 0.00084456 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:51 | 2021-10-04 12:52 | 1935 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1935 | keep | 0 | Oct | 2021 | 0.0013179 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:51 | 2021-10-04 12:52 | 3 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 3 | keep | 0 | Oct | 2021 | 2.0433e-06 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:51 | 2021-10-04 12:52 | 61 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 61 | keep | 0 | Oct | 2021 | 4.1547e-05 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:51 | 2021-10-04 12:52 | 1501 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 1501 | keep | 0 | Oct | 2021 | 0.0010223 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 12:51 | 2021-10-04 12:52 | 546 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21100400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-04 | 546 | keep | 0 | Oct | 2021 | 0.00037188 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-10-04 12:52 | 2021-10-04 14:39 | 1 | 001:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO | P21100400065 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2021-10-04 | 107 | keep | 0 | Oct | 2021 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-04 12:56 | 2021-10-04 19:15 | 27 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2021-10-04 | 10233 | keep | 0 | Oct | 2021 | 0.0069696 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
UTUADO | 2021-10-04 12:56 | 2021-10-04 15:08 | 10 | 002:12 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | A21100400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-10-04 | 1320 | keep | 0 | Oct | 2021 | 0.00089905 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-04 13:04 | 2021-10-04 14:51 | 50 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21100400104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-10-04 | 5350 | keep | 0 | Oct | 2021 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-04 13:11 | 2021-10-04 17:16 | 4 | 004:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR DESPEGO BAJANTE | C21100400087 | New_Event | Wire Down | Include | Include | Equipment | 245 | 2021-10-04 | 980 | keep | 0 | Oct | 2021 | 0.00066747 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-04 13:16 | 2021-10-04 16:36 | 100 | 003:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21100400128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-10-04 | 20000 | keep | 0 | Oct | 2021 | 0.013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-04 13:20 | 2021-10-04 16:32 | 16 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA | B21100400091 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2021-10-04 | 3072 | keep | 0 | Oct | 2021 | 0.0020923 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2021-10-04 13:22 | 2021-10-05 11:01 | 60 | 021:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21100400057 | New_Event | Bad Weather | Include | Include | Weather | 1299 | 2021-10-04 | 77940 | keep | 0 | Oct | 2021 | 0.053085 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-10-04 13:25 | 2021-10-04 16:28 | 13 | 003:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | NO FUNDIO SE REEMPLAZO | R21100400059 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2021-10-04 | 2379 | keep | 0 | Oct | 2021 | 0.0016203 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2021-10-04 13:26 | 2021-10-04 21:44 | 50 | 008:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 498 | 2021-10-04 | 24900 | keep | 0 | Oct | 2021 | 0.016959 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-10-04 13:33 | 2021-10-04 18:20 | 150 | 004:47 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-10-04 | 43050 | keep | 0 | Oct | 2021 | 0.029321 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-04 13:35 | 2021-10-04 15:30 | 1 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100400106 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-10-04 | 115 | keep | 0 | Oct | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-04 13:50 | 2021-10-05 17:02 | 2 | 027:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M21100400146 | New_Event | Wire Down | Include | Include | Equipment | 1632 | 2021-10-04 | 3264 | keep | 0 | Oct | 2021 | 0.0022231 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CAGUAS | 2021-10-04 13:52 | 2021-10-04 14:19 | 100 | 000:27 | P | DESGANCHE | ABRIO CORTE DE LINEA PARA DESGANCHAR Y LEVANTAR CONDUCTOR | C21100400120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-10-04 | 2700 | keep | 0 | Oct | 2021 | 0.001839 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-04 13:53 | 2021-10-04 14:15 | 40 | 000:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21100400147 | New_Event | Bad Weather | Include | Include | Weather | 22 | 2021-10-04 | 880 | keep | 0 | Oct | 2021 | 0.00059936 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-04 13:55 | 2021-10-04 14:48 | 20 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21100400149 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-10-04 | 1060 | keep | 0 | Oct | 2021 | 0.00072196 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-10-04 13:55 | 2021-10-04 17:45 | 80 | 003:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE INSTALO BRAZO PARA SEPARAR LINEA DE POSTE DE TELEFONO | A21100400109 | New_Event |  |  | Include | Wildlife | 230 | 2021-10-04 | 18400 | keep | 0 | Oct | 2021 | 0.012532 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-04 13:57 | 2021-10-04 16:45 | 65 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21100400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2021-10-04 | 10920 | keep | 0 | Oct | 2021 | 0.0074376 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-10-04 13:58 | 2021-10-04 14:33 | 150 | 000:35 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTE DE LINEA | R21100400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2021-10-04 | 5250 | keep | 0 | Oct | 2021 | 0.0035758 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-10-04 13:58 | 2021-10-04 18:58 | 50 | 005:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21100400110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2021-10-04 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-04 13:59 | 2021-10-04 21:19 | 80 | 007:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21100400074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2021-10-04 | 35200 | keep | 0 | Oct | 2021 | 0.023975 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 4027 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 20135 | keep | 0 | Oct | 2021 | 0.013714 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 2468 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 12340 | keep | 0 | Oct | 2021 | 0.0084047 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 1494 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 7470 | keep | 0 | Oct | 2021 | 0.0050878 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 2368 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 11840 | keep | 0 | Oct | 2021 | 0.0080642 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 538 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 2690 | keep | 0 | Oct | 2021 | 0.0018321 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 1284 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 6420 | keep | 0 | Oct | 2021 | 0.0043726 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 1310 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 6550 | keep | 0 | Oct | 2021 | 0.0044612 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 215 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 1075 | keep | 0 | Oct | 2021 | 0.00073218 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 1 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 5 | keep | 0 | Oct | 2021 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 652 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 3260 | keep | 0 | Oct | 2021 | 0.0022204 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-10-04 13:59 | 2021-10-04 14:04 | 2704 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE VEGA ALTA | B21100400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-04 | 13520 | keep | 0 | Oct | 2021 | 0.0092084 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
MAYAGÃœEZ | 2021-10-04 14:00 | 2021-10-04 17:17 | 80 | 003:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M21100400152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-10-04 | 15760 | keep | 0 | Oct | 2021 | 0.010734 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-04 14:05 | 2021-10-04 17:59 | 10 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21100400124 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-10-04 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-10-04 14:08 | 2021-10-04 18:36 | 4 | 004:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | R21100400063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 268 | 2021-10-04 | 1072 | keep | 0 | Oct | 2021 | 0.00073013 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-10-04 14:23 | 2021-10-04 20:26 | 30 | 006:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2021-10-04 | 10890 | keep | 0 | Oct | 2021 | 0.0074171 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-04 14:24 | 2021-10-04 16:48 | 10 | 002:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | M21100400162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-10-04 | 1440 | keep | 0 | Oct | 2021 | 0.00098078 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-04 14:26 | 2021-10-04 16:35 | 16 | 002:09 | P | TRANSFORMADOR AVERIADO | INSTALO TRANSFORMADOR DE 25 KVA | C21100400148 | New_Event | Service Transformer Failure | Include | Include | Equipment | 129 | 2021-10-04 | 2064 | keep | 0 | Oct | 2021 | 0.0014058 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2021-10-04 14:38 | 2021-10-04 17:30 | 30 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA 1 X 20 EN RISER Y 1 X 10 EN TRANSFORMADOR NO CAUSA | C21100400129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-10-04 | 5160 | keep | 0 | Oct | 2021 | 0.0035145 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-04 14:39 | 2021-10-05 11:13 | 1 | 020:34 | P | OTRAS CAUSAS | PROBLEMA INTERNO | P21100400089 | New_Event | Other Causes | Include | Include | Other | 1234 | 2021-10-04 | 1234 | keep | 0 | Oct | 2021 | 0.00084047 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-04 14:48 | 2021-10-04 21:20 | 4 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21100400119 | New_Event | Bad Weather | Include | Include | Weather | 392 | 2021-10-04 | 1568 | keep | 0 | Oct | 2021 | 0.001068 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
CAGUAS | 2021-10-04 14:51 | 2021-10-04 16:57 | 50 | 002:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100400132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-10-04 | 6300 | keep | 0 | Oct | 2021 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-04 15:00 | 2021-10-05 09:30 | 20 | 018:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21100400122 | New_Event | Bad Weather | Include | Include | Weather | 1110 | 2021-10-04 | 22200 | keep | 0 | Oct | 2021 | 0.01512 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-04 15:04 | 2021-10-04 18:41 | 40 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA | S21100400085 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2021-10-04 | 8680 | keep | 0 | Oct | 2021 | 0.0059119 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-04 15:05 | 2021-10-04 16:57 | 80 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21100400136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-10-04 | 8960 | keep | 0 | Oct | 2021 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-10-04 15:11 | 2021-10-05 00:16 | 200 | 009:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21100400131 | New_Event | Cutout Failure | Include | Include | Equipment | 545 | 2021-10-04 | 109000 | keep | 0 | Oct | 2021 | 0.074239 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-10-04 15:12 | 2021-10-04 15:55 | 140 | 000:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR DESCARGAS ELECTRICAS | A21100400124 | New_Event | Bad Weather | Include | Include | Weather | 43 | 2021-10-04 | 6020 | keep | 0 | Oct | 2021 | 0.0041002 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
GUAYAMA | 2021-10-04 15:15 | 2021-10-04 17:09 | 9 | 001:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 4.16KV POR LIQUEO DE ACEITE X 50KVA | P21100400138 | New_Event | Service Transformer Failure | Include | Include | Equipment | 114 | 2021-10-04 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2021-10-04 15:18 | 2021-10-04 16:32 | 50 | 001:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100400138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-10-04 | 3700 | keep | 0 | Oct | 2021 | 0.0025201 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-04 15:22 | 2021-10-04 16:31 | 6 | 001:09 | P | PROTECCION DEFECTUOSA | 1 X 15 EN TRANSFORMADOR TENIA FUSIBLE DE MENOR CAPACIDAD | C21100400140 | New_Event | Protection Miscoordination | Include | Include | Other | 69 | 2021-10-04 | 414 | keep | 0 | Oct | 2021 | 0.00028197 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-04 15:30 | 2021-10-04 18:28 | 63 | 002:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES | B21100400136 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-10-04 | 11214 | keep | 0 | Oct | 2021 | 0.0076378 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2021-10-04 15:40 | 2021-10-05 15:41 | 10 | 024:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | S21100400105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1441 | 2021-10-04 | 14410 | keep | 0 | Oct | 2021 | 0.0098146 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-04 15:40 | 2021-10-05 12:02 | 80 | 020:22 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21100400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1222 | 2021-10-04 | 97760 | keep | 0 | Oct | 2021 | 0.066584 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-04 15:40 | 2021-10-04 16:27 | 70 | 000:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO | R21100400069 | New_Event | Cutout Failure | Include | Include | Equipment | 47 | 2021-10-04 | 3290 | keep | 0 | Oct | 2021 | 0.0022408 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
YAUCO | 2021-10-04 15:46 | 2021-10-04 20:06 | 75 | 004:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100400107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2021-10-04 | 19500 | keep | 0 | Oct | 2021 | 0.013281 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-10-04 15:52 | 2021-10-04 15:53 | 1922 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100400151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 1922 | keep | 0 | Oct | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
PONCE | 2021-10-04 15:58 | 2021-10-04 15:59 | 2446 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | P21100400111 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-10-04 | 2446 | keep | 0 | Oct | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2021-10-04 15:59 | 2021-10-04 17:54 | 815 | 001:55 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE DE RISER DE SALIDA AVERIADO | P21100400127 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 115 | 2021-10-04 | 93725 | keep | 0 | Oct | 2021 | 0.063836 | 0.00055509 | Sustained | FALSE | FALSE | Not_TMED_Event | 815
BAYAMON | 2021-10-04 16:01 | 2021-10-04 16:03 | 514 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1520-1 Y 1520-4 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 1028 | keep | 0 | Oct | 2021 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-10-04 16:01 | 2021-10-04 16:03 | 752 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1520-1 Y 1520-4 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 1504 | keep | 0 | Oct | 2021 | 0.0010244 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-10-04 16:01 | 2021-10-04 16:03 | 68 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1520-1 Y 1520-4 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 136 | keep | 0 | Oct | 2021 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2021-10-04 16:02 | 2021-10-04 19:35 | 150 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21100400133 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-10-04 | 31950 | keep | 0 | Oct | 2021 | 0.021761 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-04 16:07 | 2021-10-04 17:35 | 25 | 001:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21100400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-10-04 | 2200 | keep | 0 | Oct | 2021 | 0.0014984 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-10-04 16:10 | 2021-10-04 16:11 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100400170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 181 | keep | 0 | Oct | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
BARRANQUITAS | 2021-10-04 16:11 | 2021-10-05 15:01 | 4 | 022:50 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21100400158 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1370 | 2021-10-04 | 5480 | keep | 0 | Oct | 2021 | 0.0037324 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-04 16:14 | 2021-10-04 18:46 | 30 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE 100 AMP. MARCA SHINT | M21100400189 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-10-04 | 4560 | keep | 0 | Oct | 2021 | 0.0031058 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-04 16:14 | 2021-10-04 17:35 | 16 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21100400153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-10-04 | 1296 | keep | 0 | Oct | 2021 | 0.0008827 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-10-04 16:15 | 2021-10-05 12:25 | 25 | 020:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100400191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1210 | 2021-10-04 | 30250 | keep | 0 | Oct | 2021 | 0.020603 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
YAUCO | 2021-10-04 16:16 | 2021-10-05 13:52 | 100 | 021:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | P21100400117 | New_Event | Bad Weather | Include | Include | Weather | 1296 | 2021-10-04 | 129600 | keep | 0 | Oct | 2021 | 0.08827 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-04 16:22 | 2021-10-04 17:53 | 150 | 001:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21100400163 | New_Event |  |  | Include | Wildlife | 91 | 2021-10-04 | 13650 | keep | 0 | Oct | 2021 | 0.009297 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
YAUCO | 2021-10-04 16:37 | 2021-10-04 16:38 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21100400123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 1475 | keep | 0 | Oct | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-10-04 16:38 | 2021-10-05 10:22 | 50 | 017:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR CONTACTO DE AVE | P21100400124 | New_Event |  |  | Include | Wildlife | 1064 | 2021-10-04 | 53200 | keep | 0 | Oct | 2021 | 0.036234 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-04 16:46 | 2021-10-05 14:14 | 30 | 021:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100400163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1288 | 2021-10-04 | 38640 | keep | 0 | Oct | 2021 | 0.026318 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-04 16:50 | 2021-10-05 20:45 | 20 | 027:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA SE CERRO PUENTE PRIMARIO | A21100400041 | New_Event | Wire Down | Include | Include | Equipment | 1675 | 2021-10-04 | 33500 | keep | 0 | Oct | 2021 | 0.022817 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-04 16:53 | 2021-10-04 19:09 | 16 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21100300167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2021-10-04 | 2176 | keep | 0 | Oct | 2021 | 0.0014821 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2021-10-04 16:53 | 2021-10-05 14:40 | 2 | 021:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21100400169 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1307 | 2021-10-04 | 2614 | keep | 0 | Oct | 2021 | 0.0017804 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-04 16:54 | 2021-10-04 16:55 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 1227 | keep | 0 | Oct | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
GUAYAMA | 2021-10-04 17:00 | 2021-10-04 21:24 | 100 | 004:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21100400128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2021-10-04 | 26400 | keep | 0 | Oct | 2021 | 0.017981 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-04 17:14 | 2021-10-04 20:42 | 100 | 003:28 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21100400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-10-04 | 20800 | keep | 0 | Oct | 2021 | 0.014167 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-04 17:19 | 2021-10-05 11:45 | 10 | 018:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA EN EL FID: 24094418 MARCA: CHANCE 100AMP | M21100400210 | New_Event | Cutout Failure | Include | Include | Equipment | 1106 | 2021-10-04 | 11060 | keep | 0 | Oct | 2021 | 0.0075329 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-04 17:25 | 2021-10-04 18:17 | 81 | 000:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21100400175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-10-04 | 4212 | keep | 0 | Oct | 2021 | 0.0028688 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
CAGUAS | 2021-10-04 17:30 | 2021-10-04 20:02 | 50 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21100400177 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2021-10-04 | 7600 | keep | 0 | Oct | 2021 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-04 17:32 | 2021-10-05 09:15 | 30 | 015:43 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA ELIMINO PARARRAYO | C21100400178 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 943 | 2021-10-04 | 28290 | keep | 0 | Oct | 2021 | 0.019268 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-04 17:33 | 2021-10-05 14:18 | 1 | 020:45 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER | B21100400180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1245 | 2021-10-04 | 1245 | keep | 0 | Oct | 2021 | 0.00084796 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-04 17:46 | 2021-10-06 12:16 | 20 | 042:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y SE CERRO CORTE DE LINEA | M21100400208 | New_Event | Wire Down | Include | Include | Equipment | 2550 | 2021-10-04 | 51000 | keep | 0 | Oct | 2021 | 0.034736 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-04 17:50 | 2021-10-04 21:09 | 16 | 003:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 POR 50 KVA HOJA DE CONSERVACION MON73355-1 | B21100400109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 199 | 2021-10-04 | 3184 | keep | 0 | Oct | 2021 | 0.0021686 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2021-10-04 17:54 | 2021-10-04 18:50 | 2446 | 000:56 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE EN RISER DE SALIDA Y SE COLOCO INTERRUPTOR EN SERVICIO | P21100400127 | Additional_clients | Switch Failure | Include | Include | Equipment | 56 | 2021-10-04 | 136976 | keep | 0 | Oct | 2021 | 0.093294 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-04 18:03 | 2021-10-05 16:08 | 8 | 022:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA PRIMARIA SECUNDARIA Y SE REALIZO DESGANCHE | M21100500216 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1325 | 2021-10-04 | 10600 | keep | 0 | Oct | 2021 | 0.0072196 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-04 18:09 | 2021-10-05 14:00 | 50 | 019:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M21100400217 | New_Event | Wire Down | Include | Include | Equipment | 1191 | 2021-10-04 | 59550 | keep | 0 | Oct | 2021 | 0.040559 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-04 18:28 | 2021-10-05 10:56 | 10 | 016:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | M21100400221 | New_Event | Secondary Wire Down | Include | Include | Equipment | 988 | 2021-10-04 | 9880 | keep | 0 | Oct | 2021 | 0.0067292 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-04 18:33 | 2021-10-04 19:05 | 12 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21100400148 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2021-10-04 | 384 | keep | 0 | Oct | 2021 | 0.00026154 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-10-04 18:40 | 2021-10-04 18:42 | 4381 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21100400222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 8762 | keep | 0 | Oct | 2021 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
GUAYAMA | 2021-10-04 18:41 | 2021-10-04 22:14 | 50 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEAS LINEAS ARRIADAS | P21100400137 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-10-04 | 10650 | keep | 0 | Oct | 2021 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-04 18:45 | 2021-10-05 10:39 | 50 | 015:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21100400151 | New_Event | Bad Weather | Include | Include | Weather | 954 | 2021-10-04 | 47700 | keep | 0 | Oct | 2021 | 0.032488 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-04 18:46 | 2021-10-04 19:25 | 20 | 000:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO AISLADOR PARTIDO | A21100400152 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 39 | 2021-10-04 | 780 | keep | 0 | Oct | 2021 | 0.00053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-10-04 19:03 | 2021-10-04 20:25 | 776 | 001:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE EN LA SALIDA DEL INTERRUPTOR | C21100400198 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2021-10-04 | 63632 | keep | 0 | Oct | 2021 | 0.043339 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
AGUADILLA | 2021-10-04 19:04 | 2021-10-05 13:42 | 400 | 018:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21100400231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1118 | 2021-10-04 | 447200 | keep | 0 | Oct | 2021 | 0.30459 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
BAYAMON | 2021-10-04 19:15 | 2021-10-05 15:53 | 5 | 020:38 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100400200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1238 | 2021-10-04 | 6190 | keep | 0 | Oct | 2021 | 0.004216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-04 20:09 | 2021-10-05 09:52 | 410 | 013:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA | C21100500110 | New_Event | Cutout Failure | Include | Include | Equipment | 823 | 2021-10-04 | 337430 | keep | 0 | Oct | 2021 | 0.22982 | 0.00027925 | Sustained | FALSE | FALSE | Not_TMED_Event | 410
ARECIBO | 2021-10-04 20:10 | 2021-10-04 21:03 | 6 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21100400313 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-10-04 | 318 | keep | 0 | Oct | 2021 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-04 21:02 | 2021-10-04 21:17 | 150 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21100400155 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2021-10-04 | 2250 | keep | 0 | Oct | 2021 | 0.0015325 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-10-04 21:04 | 2021-10-05 19:02 | 22 | 021:58 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO Y SE ENERGIZO PROVISIONAL HACIA T-180 | B21100100210 | New_Event | UG Cable Fault | Include | Include | Equipment | 1318 | 2021-10-04 | 28996 | keep | 0 | Oct | 2021 | 0.019749 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2021-10-04 21:12 | 2021-10-04 21:13 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1105-1 Y 1133-4 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2021-10-04 21:12 | 2021-10-04 21:13 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1105-1 Y 1133-4 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 308 | keep | 0 | Oct | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-10-04 21:12 | 2021-10-04 21:13 | 333 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1105-1 Y 1133-4 | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 333 | keep | 0 | Oct | 2021 | 0.0002268 | 0.0002268 | Momentary | FALSE | FALSE | Not_TMED_Event | 333
SAN JUAN | 2021-10-04 21:22 | 2021-10-05 11:31 | 50 | 014:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA AVERIADA | R21100400078 | New_Event | Cutout Failure | Include | Include | Equipment | 849 | 2021-10-04 | 42450 | keep | 0 | Oct | 2021 | 0.028913 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-04 21:36 | 2021-10-04 21:38 | 2402 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA LA CARGA DEL 1720-08 | B21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 4804 | keep | 0 | Oct | 2021 | 0.003272 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-10-04 21:36 | 2021-10-04 21:38 | 1 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA TRANSFERIDA AL 1709-02 | B21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 2 | keep | 0 | Oct | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-04 21:45 | 2021-10-04 21:46 | 351 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-04 | 351 | keep | 0 | Oct | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
BAYAMON | 2021-10-04 21:53 | 2021-10-04 21:55 | 1514 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | B21100400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-04 | 3028 | keep | 0 | Oct | 2021 | 0.0020624 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-10-04 22:06 | 2021-10-04 22:16 | 1514 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | B21100400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-10-04 | 15140 | keep | 0 | Oct | 2021 | 0.010312 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-10-04 22:16 | 2021-10-04 22:55 | 500 | 000:39 | P | NO SE REPORTO CAUSA | SE REPARO PUENTE ABIERTO Y SE REALIZO DESGANCHE | B21100400000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 39 | 2021-10-04 | 19500 | keep | 0 | Oct | 2021 | 0.013281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-04 22:46 | 2021-10-05 05:51 | 30 | 007:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRO POROVISIONAL | B21100400208 | New_Event | Wire Down | Include | Include | Equipment | 425 | 2021-10-04 | 12750 | keep | 0 | Oct | 2021 | 0.008684 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-10-04 22:55 | 2021-10-05 01:45 | 1514 | 002:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE CERRO POR SCADA SE REPARO PUENTE ABIERTO Y SE REALIZO DESGANCHE | B21100400000 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-10-04 | 257380 | keep | 0 | Oct | 2021 | 0.1753 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
FAJARDO | 2021-10-05 00:48 | 2021-10-05 02:40 | 5 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | R21100400079 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2021-10-05 | 560 | keep | 0 | Oct | 2021 | 0.00038141 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-05 01:10 | 2021-10-05 01:11 | 386 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 386 | keep | 0 | Oct | 2021 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
YAUCO | 2021-10-05 01:54 | 2021-10-05 01:55 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211005000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 3973 | keep | 0 | Oct | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
HUMACAO | 2021-10-05 02:02 | 2021-10-05 02:03 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21140500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1467 | keep | 0 | Oct | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2021-10-05 02:03 | 2021-10-05 02:04 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
MAYAGÃœEZ | 2021-10-05 02:39 | 2021-10-05 17:30 | 50 | 014:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21100500010 | New_Event | Bad Weather | Include | Include | Weather | 891 | 2021-10-05 | 44550 | keep | 0 | Oct | 2021 | 0.030343 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-05 02:49 | 2021-10-05 02:50 | 1730 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211005000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1730 | keep | 0 | Oct | 2021 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
MAYAGÃœEZ | 2021-10-05 03:28 | 2021-10-05 20:00 | 40 | 016:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100500020 | New_Event | Bad Weather | Include | Include | Weather | 992 | 2021-10-05 | 39680 | keep | 0 | Oct | 2021 | 0.027026 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-10-05 03:33 | 2021-10-05 03:34 | 3902 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR LLUVIA | C21100500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-05 | 3902 | keep | 0 | Oct | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2021-10-05 03:34 | 2021-10-05 17:15 | 65 | 013:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21100500052 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 821 | 2021-10-05 | 53365 | keep | 0 | Oct | 2021 | 0.036347 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-10-05 04:06 | 2021-10-05 04:07 | 1268 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR NO SE REPORTO LA CAUSA | M21100500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-05 | 1268 | keep | 0 | Oct | 2021 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2021-10-05 04:07 | 2021-10-05 10:50 | 200 | 006:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21100500024 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 403 | 2021-10-05 | 80600 | keep | 0 | Oct | 2021 | 0.054896 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-10-05 04:09 | 2021-10-05 04:10 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
SAN JUAN | 2021-10-05 05:59 | 2021-10-05 06:00 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1615 | keep | 0 | Oct | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
ARECIBO | 2021-10-05 06:00 | 2021-10-05 11:35 | 150 | 005:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21100500070 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2021-10-05 | 50250 | keep | 0 | Oct | 2021 | 0.034225 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-05 06:36 | 2021-10-05 06:38 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF CARGA POR EL 1620-04 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-05 | 72 | keep | 0 | Oct | 2021 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-05 06:36 | 2021-10-05 06:38 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1620-1 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-05 | 344 | keep | 0 | Oct | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-10-05 06:39 | 2021-10-05 06:40 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 638 | keep | 0 | Oct | 2021 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2021-10-05 06:40 | 2021-10-05 11:51 | 100 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21100500086 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-10-05 | 31100 | keep | 0 | Oct | 2021 | 0.021182 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 07:00 | 1894 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-05 | 3788 | keep | 0 | Oct | 2021 | 0.00258 | 0.00129 | Momentary | FALSE | TRUE | Not_TMED_Event | 1894
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 07:00 | 4154 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-05 | 8308 | keep | 0 | Oct | 2021 | 0.0056585 | 0.0028293 | Momentary | FALSE | TRUE | Not_TMED_Event | 4154
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 07:00 | 424 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-05 | 848 | keep | 0 | Oct | 2021 | 0.00057757 | 0.00028878 | Momentary | FALSE | TRUE | Not_TMED_Event | 424
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 07:00 | 2708 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-05 | 5416 | keep | 0 | Oct | 2021 | 0.0036888 | 0.0018444 | Momentary | FALSE | TRUE | Not_TMED_Event | 2708
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 07:00 | 2524 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-05 | 5048 | keep | 0 | Oct | 2021 | 0.0034382 | 0.0017191 | Momentary | FALSE | TRUE | Not_TMED_Event | 2524
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 07:00 | 1648 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-05 | 3296 | keep | 0 | Oct | 2021 | 0.0022449 | 0.0011224 | Momentary | FALSE | TRUE | Not_TMED_Event | 1648
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 06:59 | 2580 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-05 | 2580 | keep | 0 | Oct | 2021 | 0.0017572 | 0.0017572 | Momentary | FALSE | TRUE | Not_TMED_Event | 2580
CANOVANAS | 2021-10-05 06:58 | 2021-10-05 06:59 | 500 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21100500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-05 | 500 | keep | 0 | Oct | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | TRUE | Not_TMED_Event | 500
CANOVANAS | 2021-10-05 06:59 | 2021-10-05 07:02 | 1124 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO | R21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-05 | 3372 | keep | 0 | Oct | 2021 | 0.0022967 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
CANOVANAS | 2021-10-05 06:59 | 2021-10-05 07:00 | 2580 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 11100 | R21100500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-05 | 2580 | keep | 0 | Oct | 2021 | 0.0017572 | 0.0017572 | Momentary | FALSE | TRUE | Not_TMED_Event | 2580
CANOVANAS | 2021-10-05 06:59 | 2021-10-05 07:00 | 500 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 11100 | R21100500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-05 | 500 | keep | 0 | Oct | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | TRUE | Not_TMED_Event | 500
CAGUAS | 2021-10-05 07:02 | 2021-10-05 07:03 | 2448 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE | C21100500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-10-05 | 2448 | keep | 0 | Oct | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2021-10-05 07:03 | 2021-10-05 18:05 | 6 | 011:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO Y LEVANTO SECUNDARIA | C21100500169 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 662 | 2021-10-05 | 3972 | keep | 0 | Oct | 2021 | 0.0027053 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-05 07:35 | 2021-10-05 07:36 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211005000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-05 07:35 | 2021-10-05 07:36 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211005000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-10-05 07:35 | 2021-10-05 07:36 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE. LLEVA LA CARGA DEL 5004-08 Y 5004-09 | P211005000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
SAN JUAN | 2021-10-05 08:25 | 2021-10-06 18:17 | 25 | 033:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | S21100500002 | New_Event | Cutout Failure | Include | Include | Equipment | 2032 | 2021-10-05 | 50800 | keep | 0 | Oct | 2021 | 0.0346 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-10-05 08:28 | 2021-10-05 09:24 | 20 | 000:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21100400026 | New_Event | Bad Weather | Include | Include | Weather | 56 | 2021-10-05 | 1120 | keep | 0 | Oct | 2021 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-05 08:30 | 2021-10-05 10:56 | 50 | 002:26 | P | NO SE REPORTO CAUSA | SE REMPLAZO CAJA QUEMADA | S21100500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-10-05 | 7300 | keep | 0 | Oct | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-10-05 08:33 | 2021-10-05 11:08 | 50 | 002:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21100500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-10-05 | 7750 | keep | 0 | Oct | 2021 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-05 08:33 | 2021-10-05 09:56 | 50 | 001:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-10-05 | 4150 | keep | 0 | Oct | 2021 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-05 08:33 | 2021-10-05 13:17 | 150 | 004:44 | P | DESGANCHE | 1 X 80 EN CONVERTIDOR POR DESGANCHE | A21100500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-10-05 | 42600 | keep | 0 | Oct | 2021 | 0.029015 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-10-05 08:33 | 2021-10-05 12:11 | 30 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21100500012 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-10-05 | 6540 | keep | 0 | Oct | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-10-05 08:33 | 2021-10-05 10:20 | 1000 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR NO SE REPORTO CAUSA | A21100500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-10-05 | 107000 | keep | 0 | Oct | 2021 | 0.072877 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
VEGA BAJA | 2021-10-05 08:33 | 2021-10-05 18:33 | 7 | 010:00 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | B21100500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 600 | 2021-10-05 | 4200 | keep | 0 | Oct | 2021 | 0.0028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-10-05 08:33 | 2021-10-05 14:00 | 40 | 005:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A PARARRAYO | C21100500004 | New_Event | Wire Down | Include | Include | Equipment | 327 | 2021-10-05 | 13080 | keep | 0 | Oct | 2021 | 0.0089087 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-05 08:34 | 2021-10-05 15:05 | 110 | 006:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R21100500002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 391 | 2021-10-05 | 43010 | keep | 0 | Oct | 2021 | 0.029294 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
PONCE | 2021-10-05 08:34 | 2021-10-05 16:47 | 10 | 008:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21100500060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 493 | 2021-10-05 | 4930 | keep | 0 | Oct | 2021 | 0.0033578 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-05 08:34 | 2021-10-05 14:30 | 20 | 005:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21100500037 | New_Event | Cutout Failure | Include | Include | Equipment | 356 | 2021-10-05 | 7120 | keep | 0 | Oct | 2021 | 0.0048494 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-10-05 08:34 | 2021-10-05 13:42 | 200 | 005:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21100500022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2021-10-05 | 61600 | keep | 0 | Oct | 2021 | 0.041955 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-10-05 08:35 | 2021-10-05 10:45 | 100 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR REPTIL | R21100500013 | New_Event |  |  | Include | Wildlife | 130 | 2021-10-05 | 13000 | keep | 0 | Oct | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-05 08:35 | 2021-10-05 11:19 | 50 | 002:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-10-05 | 8200 | keep | 0 | Oct | 2021 | 0.005585 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-05 08:35 | 2021-10-05 15:20 | 7 | 006:45 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21100500057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 405 | 2021-10-05 | 2835 | keep | 0 | Oct | 2021 | 0.0019309 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-10-05 08:35 | 2021-10-05 16:41 | 40 | 008:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO AISLADOR | C21100500056 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 486 | 2021-10-05 | 19440 | keep | 0 | Oct | 2021 | 0.01324 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-05 08:35 | 2021-10-05 10:52 | 80 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21100500078 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-10-05 | 10960 | keep | 0 | Oct | 2021 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-05 08:35 | 2021-10-05 11:37 | 50 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | C21100500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2021-10-05 | 9100 | keep | 0 | Oct | 2021 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-10-05 08:35 | 2021-10-05 12:02 | 50 | 003:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR AVE CRUZAR FASE | P21100500044 | New_Event |  |  | Include | Wildlife | 207 | 2021-10-05 | 10350 | keep | 0 | Oct | 2021 | 0.0070493 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-05 08:35 | 2021-10-05 10:43 | 10 | 002:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA A 7620 VOLTIOS X 37.5KVA | P21100500050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 128 | 2021-10-05 | 1280 | keep | 0 | Oct | 2021 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-05 08:35 | 2021-10-05 12:18 | 100 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1X100 EN CORTE DE LINEA PO FUERTES BRISAS | P21100500046 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2021-10-05 | 22300 | keep | 0 | Oct | 2021 | 0.015188 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-05 08:35 | 2021-10-05 11:42 | 2 | 003:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21100500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-10-05 | 374 | keep | 0 | Oct | 2021 | 0.00025473 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
YAUCO | 2021-10-05 08:35 | 2021-10-05 15:21 | 100 | 006:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEAS AVE CRUZO LINEAS | P21100500144 | New_Event |  |  | Include | Wildlife | 406 | 2021-10-05 | 40600 | keep | 0 | Oct | 2021 | 0.027652 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-05 08:35 | 2021-10-05 09:55 | 20 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | A21100500029 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-10-05 | 1600 | keep | 0 | Oct | 2021 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-05 08:36 | 2021-10-05 16:21 | 10 | 007:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100500061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 465 | 2021-10-05 | 4650 | keep | 0 | Oct | 2021 | 0.0031671 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-05 08:36 | 2021-10-05 15:04 | 1 | 006:28 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA PARARRAYO AVERIADO EN SUBESTACION DEL CLIENTE | R21100500021 | New_Event | Other Causes | Include | Include | Other | 388 | 2021-10-05 | 388 | keep | 0 | Oct | 2021 | 0.00026427 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-05 08:36 | 2021-10-05 11:59 | 50 | 003:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21100500094 | New_Event |  |  | Include | Wildlife | 203 | 2021-10-05 | 10150 | keep | 0 | Oct | 2021 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-05 08:36 | 2021-10-05 09:18 | 50 | 000:42 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21100500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-10-05 | 2100 | keep | 0 | Oct | 2021 | 0.0014303 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-10-05 08:36 | 2021-10-05 15:50 | 100 | 007:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P21100500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2021-10-05 | 43400 | keep | 0 | Oct | 2021 | 0.02956 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-05 08:36 | 2021-10-05 15:20 | 1 | 006:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21100500044 | New_Event | Bad Weather | Include | Include | Weather | 404 | 2021-10-05 | 404 | keep | 0 | Oct | 2021 | 0.00027516 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-05 08:36 | 2021-10-06 10:36 | 1 | 025:60 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21100500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1560 | 2021-10-05 | 1560 | keep | 0 | Oct | 2021 | 0.0010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-05 08:36 | 2021-10-05 20:32 | 7 | 011:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100500052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 716 | 2021-10-05 | 5012 | keep | 0 | Oct | 2021 | 0.0034137 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2021-10-05 08:40 | 2021-10-05 17:49 | 100 | 009:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21100500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2021-10-05 | 54900 | keep | 0 | Oct | 2021 | 0.037392 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-05 08:42 | 2021-10-05 20:27 | 5 | 011:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100500064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 705 | 2021-10-05 | 3525 | keep | 0 | Oct | 2021 | 0.0024009 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-10-05 08:52 | 2021-10-05 17:40 | 60 | 008:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21100500091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 528 | 2021-10-05 | 31680 | keep | 0 | Oct | 2021 | 0.021577 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-10-05 08:52 | 2021-10-05 10:15 | 1 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE TRANSFORMADOR NO SE REPUSO FUSIBLE | P21100500092 | New_Event | Wire Down | Include | Include | Equipment | 83 | 2021-10-05 | 83 | keep | 0 | Oct | 2021 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-05 08:55 | 2021-10-05 19:20 | 7 | 010:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 625 | 2021-10-05 | 4375 | keep | 0 | Oct | 2021 | 0.0029798 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-10-05 08:55 | 2021-10-05 17:25 | 40 | 008:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21100500055 | New_Event | Cutout Failure | Include | Include | Equipment | 510 | 2021-10-05 | 20400 | keep | 0 | Oct | 2021 | 0.013894 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-05 08:56 | 2021-10-05 17:50 | 8 | 008:54 | P | NO SE REPORTO CAUSA | 1 X 20 EN PM | B21100500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 534 | 2021-10-05 | 4272 | keep | 0 | Oct | 2021 | 0.0029096 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-10-05 08:56 | 2021-10-05 12:36 | 65 | 003:40 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21100500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-10-05 | 14300 | keep | 0 | Oct | 2021 | 0.0097397 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
UTUADO | 2021-10-05 09:12 | 2021-10-05 12:36 | 5 | 003:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR RAYOS | A21100500066 | New_Event | Bad Weather | Include | Include | Weather | 204 | 2021-10-05 | 1020 | keep | 0 | Oct | 2021 | 0.00069472 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-05 09:19 | 2021-10-05 11:30 | 7 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21100500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2021-10-05 | 917 | keep | 0 | Oct | 2021 | 0.00062456 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-05 09:20 | 2021-10-07 20:23 | 25 | 059:03 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN RISER SE REALIZARON EMPALMES EN 2 PUNTOS | B21100500073 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 3543 | 2021-10-05 | 88575 | keep | 0 | Oct | 2021 | 0.060328 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2021-10-05 09:20 | 2021-10-05 15:50 | 50 | 006:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100400067 | New_Event | Bad Weather | Include | Include | Weather | 390 | 2021-10-05 | 19500 | keep | 0 | Oct | 2021 | 0.013281 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-05 09:26 | 2021-10-05 10:44 | 1 | 001:18 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | S21100500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-05 | 78 | keep | 0 | Oct | 2021 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-05 09:33 | 2021-10-05 10:21 | 5 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21100500111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-10-05 | 240 | keep | 0 | Oct | 2021 | 0.00016346 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-05 09:40 | 2021-10-05 09:41 | 1590 | 000:01 | T | DESGANCHE | RECIERRE | C21100500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-05 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2021-10-05 09:41 | 2021-10-05 17:43 | 120 | 008:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21100500115 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 482 | 2021-10-05 | 57840 | keep | 0 | Oct | 2021 | 0.039395 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
YAUCO | 2021-10-05 09:47 | 2021-10-05 19:48 | 10 | 010:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR POR CONTACTO DE AVE | P21100500096 | New_Event |  |  | Include | Wildlife | 601 | 2021-10-05 | 6010 | keep | 0 | Oct | 2021 | 0.0040934 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-05 09:47 | 2021-10-05 17:09 | 20 | 007:22 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA CAMBIAR 2 POSTES PARTIDOS | P21100500095 | New_Event | Defective Pole | Include | Include | Equipment | 442 | 2021-10-05 | 8840 | keep | 0 | Oct | 2021 | 0.0060209 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-05 09:51 | 2021-10-05 10:52 | 50 | 001:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21100500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-10-05 | 3050 | keep | 0 | Oct | 2021 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-05 09:58 | 2021-10-05 14:49 | 14 | 004:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | R21100500036 | New_Event | Wire Down | Include | Include | Equipment | 291 | 2021-10-05 | 4074 | keep | 0 | Oct | 2021 | 0.0027748 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
BAYAMON | 2021-10-05 10:04 | 2021-10-05 21:05 | 50 | 011:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100500084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 661 | 2021-10-05 | 33050 | keep | 0 | Oct | 2021 | 0.02251 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-05 10:11 | 2021-10-05 15:09 | 50 | 004:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REMPLAZO AISLADOR | C21100500119 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 298 | 2021-10-05 | 14900 | keep | 0 | Oct | 2021 | 0.010148 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-05 10:13 | 2021-10-06 16:49 | 3 | 030:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO 3 ALAMBRES PRIMARIOS | P21100500043 | New_Event | Wire Down | Include | Include | Equipment | 1836 | 2021-10-05 | 5508 | keep | 0 | Oct | 2021 | 0.0037515 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CANOVANAS | 2021-10-05 10:14 | 2021-10-05 14:03 | 50 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SAFADO HACIA CAJA PRIMARIA | R21100500039 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2021-10-05 | 11450 | keep | 0 | Oct | 2021 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-10-05 10:15 | 2021-10-05 11:44 | 1 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REEMPLAZO BAJANTE SECUNDARIO | R21100500032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2021-10-05 | 89 | keep | 0 | Oct | 2021 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-10-05 10:15 | 2021-10-05 16:12 | 10 | 005:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P21100500103 | New_Event | Wire Down | Include | Include | Equipment | 357 | 2021-10-05 | 3570 | keep | 0 | Oct | 2021 | 0.0024315 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-05 10:23 | 2021-10-05 17:44 | 30 | 007:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21100500122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2021-10-05 | 13230 | keep | 0 | Oct | 2021 | 0.0090109 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-05 10:28 | 2021-10-05 13:08 | 200 | 002:40 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21100500084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-10-05 | 32000 | keep | 0 | Oct | 2021 | 0.021795 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-05 10:29 | 2021-10-05 11:55 | 30 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR VIENTOS | A21100500077 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-10-05 | 2580 | keep | 0 | Oct | 2021 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-05 10:30 | 2021-10-05 11:23 | 90 | 000:53 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL CAIDO SOBRE LA LINEA PRIMARIA | M21100500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-10-05 | 4770 | keep | 0 | Oct | 2021 | 0.0032488 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-10-05 10:33 | 2021-10-05 11:45 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE SECUNDARIA | S21100500037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-10-05 | 720 | keep | 0 | Oct | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-05 10:35 | 2021-10-05 13:46 | 50 | 003:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | A21100500080 | New_Event | Bad Weather | Include | Include | Weather | 191 | 2021-10-05 | 9550 | keep | 0 | Oct | 2021 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-05 10:39 | 2021-10-05 15:38 | 60 | 004:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100400064 | New_Event | Bad Weather | Include | Include | Weather | 299 | 2021-10-05 | 17940 | keep | 0 | Oct | 2021 | 0.012219 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-10-05 10:46 | 2021-10-07 13:00 | 4 | 050:14 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO CORTE DE LINEA | A21100500083 | New_Event | Defective Pole | Include | Include | Equipment | 3014 | 2021-10-05 | 12056 | keep | 0 | Oct | 2021 | 0.0082113 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-10-05 11:00 | 2021-10-05 13:50 | 40 | 002:50 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS | A21100500086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-10-05 | 6800 | keep | 0 | Oct | 2021 | 0.0046314 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-05 11:23 | 2021-10-05 12:12 | 1 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21100500092 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-10-05 | 49 | keep | 0 | Oct | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-05 11:24 | 2021-10-05 16:55 | 5 | 005:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100500097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 331 | 2021-10-05 | 1655 | keep | 0 | Oct | 2021 | 0.0011272 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-05 11:24 | 2021-10-05 11:36 | 30 | 000:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | B21100500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2021-10-05 | 360 | keep | 0 | Oct | 2021 | 0.00024519 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-05 11:26 | 2021-10-05 17:48 | 10 | 006:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO | A21100500089 | New_Event | Bad Weather | Include | Include | Weather | 382 | 2021-10-05 | 3820 | keep | 0 | Oct | 2021 | 0.0026018 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-05 11:33 | 2021-10-06 18:17 | 42 | 030:44 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRANSFORMADOR | S21100500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1844 | 2021-10-05 | 77448 | keep | 0 | Oct | 2021 | 0.052749 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CAGUAS | 2021-10-05 11:38 | 2021-10-05 11:39 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 2608 | keep | 0 | Oct | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
ARECIBO | 2021-10-05 12:09 | 2021-10-05 19:40 | 10 | 007:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21100500093 | New_Event | Bad Weather | Include | Include | Weather | 451 | 2021-10-05 | 4510 | keep | 0 | Oct | 2021 | 0.0030717 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-10-05 12:09 | 2021-10-07 12:28 | 5 | 048:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO NEUTRAL | A21100500104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2899 | 2021-10-05 | 14495 | keep | 0 | Oct | 2021 | 0.0098725 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-05 12:10 | 2021-10-05 12:11 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 437 | keep | 0 | Oct | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2021-10-05 12:25 | 2021-10-05 13:07 | 1 | 000:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21100400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2021-10-05 | 42 | keep | 0 | Oct | 2021 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-10-05 12:28 | 2021-10-05 12:29 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100500106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2021-10-05 12:28 | 2021-10-06 16:10 | 300 | 027:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | A21100500099 | New_Event | Wire Down | Include | Include | Equipment | 1662 | 2021-10-05 | 498600 | keep | 0 | Oct | 2021 | 0.33959 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
PONCE | 2021-10-05 12:32 | 2021-10-05 13:13 | 1952 | 000:41 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO. SE CERRO EL PUENTE Y SE CERRO INTERRUPTOR | P21100500135 | New_Event | Wire Down | Include | Include | Equipment | 41 | 2021-10-05 | 80032 | keep | 0 | Oct | 2021 | 0.054509 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
SAN JUAN | 2021-10-05 12:36 | 2021-10-05 20:42 | 52 | 008:06 | P | DESGANCHE | 1 X 100 CORTE DE LINEA | S21100500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 486 | 2021-10-05 | 25272 | keep | 0 | Oct | 2021 | 0.017213 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
HUMACAO | 2021-10-05 12:40 | 2021-10-05 17:04 | 5 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A TRANSFORMADOR Y BAJANTE SECUNDARIO | C21100500148 | New_Event | Wire Down | Include | Include | Equipment | 264 | 2021-10-05 | 1320 | keep | 0 | Oct | 2021 | 0.00089905 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-05 12:40 | 2021-10-05 13:40 | 5 | 001:00 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA DESGANCHE EN SECUNDARIA | A21100500100 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 60 | 2021-10-05 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-05 12:59 | 2021-10-05 19:31 | 5 | 006:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | A21100500105 | New_Event | Wire Down | Include | Include | Equipment | 392 | 2021-10-05 | 1960 | keep | 0 | Oct | 2021 | 0.0013349 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-10-05 13:00 | 2021-10-05 18:49 | 100 | 005:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21100500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2021-10-05 | 34900 | keep | 0 | Oct | 2021 | 0.02377 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-05 13:05 | 2021-10-05 13:09 | 3360 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLAVA 80% Y 40% DEL 1204-3 SE VERIFICO CON COMPAÃ‘IA EXPERT ESTABA TOMANDO ALIMENTOS SE PROBO QUEDO EN SERVICIO | S21100500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-05 | 13440 | keep | 0 | Oct | 2021 | 0.0091539 | 0.0022885 | Momentary | FALSE | FALSE | Not_TMED_Event | 3360
SAN JUAN | 2021-10-05 13:05 | 2021-10-05 13:09 | 552 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLAVA 80% Y 40% DEL 1204-3 SE VERIFICO CON COMPAÃ‘IA EXPERT ESTABA TOMANDO ALIMENTOS SE PROBO QUEDO EN SERVICIO | S21100500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-05 | 2208 | keep | 0 | Oct | 2021 | 0.0015039 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
HUMACAO | 2021-10-05 13:06 | 2021-10-05 18:26 | 50 | 005:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100500153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2021-10-05 | 16000 | keep | 0 | Oct | 2021 | 0.010898 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-05 13:15 | 2021-10-05 15:41 | 100 | 002:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PRIMARIO | P21100500161 | New_Event | Wire Down | Include | Include | Equipment | 146 | 2021-10-05 | 14600 | keep | 0 | Oct | 2021 | 0.009944 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-05 13:17 | 2021-10-06 13:47 | 1 | 024:30 | P | TRANSFORMADOR AVERIADO | 1 X 5 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR QUEMADO DE 15KVA POR LA MISMA CAPACIDAD EN EL FID: 31437336 MARCA: EATON #SERIE 2055098938 VOLTAJES 4160/7200 120-240 | A21100500107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1470 | 2021-10-05 | 1470 | keep | 0 | Oct | 2021 | 0.0010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-05 13:19 | 2021-10-05 18:40 | 110 | 005:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100500115 | New_Event | Bad Weather | Include | Include | Weather | 321 | 2021-10-05 | 35310 | keep | 0 | Oct | 2021 | 0.024049 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
MAYAGÃœEZ | 2021-10-05 13:32 | 2021-10-05 13:33 | 2560 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21100500116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-05 | 2560 | keep | 0 | Oct | 2021 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
MAYAGÃœEZ | 2021-10-05 13:33 | 2021-10-05 19:30 | 500 | 005:57 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA, 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500119 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-10-05 | 178500 | keep | 0 | Oct | 2021 | 0.12158 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
PONCE | 2021-10-05 13:40 | 2021-10-05 18:13 | 10 | 004:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21100500150 | New_Event | Secondary Wire Down | Include | Include | Equipment | 273 | 2021-10-05 | 2730 | keep | 0 | Oct | 2021 | 0.0018594 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-05 13:42 | 2021-10-05 16:35 | 150 | 002:53 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21100500167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-10-05 | 25950 | keep | 0 | Oct | 2021 | 0.017674 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-05 13:50 | 2021-10-06 11:10 | 12 | 021:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE SUELTO EN CAJA PRIMARIA HACIA TRANSFORMADOR. | P21100500128 | New_Event | Wire Down | Include | Include | Equipment | 1280 | 2021-10-05 | 15360 | keep | 0 | Oct | 2021 | 0.010462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-05 13:56 | 2021-10-05 13:57 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 651 | keep | 0 | Oct | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
AGUADILLA | 2021-10-05 13:58 | 2021-10-05 13:59 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21100500127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2021-10-05 14:01 | 2021-10-05 15:46 | 30 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | C21100500168 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2021-10-05 | 3150 | keep | 0 | Oct | 2021 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-05 14:08 | 2021-10-05 16:53 | 50 | 002:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-10-05 | 8250 | keep | 0 | Oct | 2021 | 0.005619 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-05 14:18 | 2021-10-05 14:19 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA CARGA POR 6404-02 | M21100500135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1117 | keep | 0 | Oct | 2021 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2021-10-05 14:18 | 2021-10-05 14:19 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6404-01 | M21100500135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1671 | keep | 0 | Oct | 2021 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
BAYAMON | 2021-10-05 14:21 | 2021-10-05 16:13 | 23 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21100500123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-10-05 | 2576 | keep | 0 | Oct | 2021 | 0.0017545 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
SAN JUAN | 2021-10-05 14:27 | 2021-10-05 14:28 | 314 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S21100500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-05 | 314 | keep | 0 | Oct | 2021 | 0.00021386 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2021-10-05 14:33 | 2021-10-05 15:52 | 314 | 001:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO INTERRUPTOR Y SE CERRO POR SCADA | S21100500000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 79 | 2021-10-05 | 24806 | keep | 0 | Oct | 2021 | 0.016895 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
AGUADILLA | 2021-10-05 14:34 | 2021-10-05 14:35 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21100500142 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2021-10-05 14:37 | 2021-10-05 17:30 | 75 | 002:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21100500113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-10-05 | 12975 | keep | 0 | Oct | 2021 | 0.0088372 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-10-05 14:38 | 2021-10-05 14:39 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21100500144 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2021-10-05 14:39 | 2021-10-05 14:42 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL CARGA POR EL 1303-05 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-05 | 675 | keep | 0 | Oct | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-05 14:39 | 2021-10-05 14:42 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA EL 1303-04 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-05 | 2610 | keep | 0 | Oct | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-10-05 14:41 | 2021-10-05 16:56 | 6 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIO | B21100500128 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2021-10-05 | 810 | keep | 0 | Oct | 2021 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-05 14:42 | 2021-10-05 18:10 | 30 | 003:28 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA DESGANCHE | A21100500114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-10-05 | 6240 | keep | 0 | Oct | 2021 | 0.00425 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-05 14:48 | 2021-10-05 14:50 | 1827 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21100500146 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-05 | 3654 | keep | 0 | Oct | 2021 | 0.0024887 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2021-10-05 14:55 | 2021-10-05 17:12 | 40 | 002:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21100500116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-10-05 | 5480 | keep | 0 | Oct | 2021 | 0.0037324 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-05 15:00 | 2021-10-05 19:40 | 15 | 004:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN MONTURA AVE CRUZO LINEAS | P21100500125 | New_Event |  |  | Include | Wildlife | 280 | 2021-10-05 | 4200 | keep | 0 | Oct | 2021 | 0.0028606 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-05 15:00 | 2021-10-05 19:12 | 200 | 004:12 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500151 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-10-05 | 50400 | keep | 0 | Oct | 2021 | 0.034327 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-05 15:02 | 2021-10-05 16:45 | 150 | 001:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-10-05 | 15450 | keep | 0 | Oct | 2021 | 0.010523 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-05 15:12 | 2021-10-06 14:35 | 75 | 023:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21100500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1403 | 2021-10-05 | 105225 | keep | 0 | Oct | 2021 | 0.071668 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-10-05 15:15 | 2021-10-05 16:33 | 60 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21100500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-05 | 4680 | keep | 0 | Oct | 2021 | 0.0031875 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-10-05 15:19 | 2021-10-05 16:27 | 8 | 001:08 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO T-12 PARA REEMPLAZAR DOS BARRAS EN PEDESTAL Y REEMPLAZO PEDESTAL | R21100500058 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 68 | 2021-10-05 | 544 | keep | 0 | Oct | 2021 | 0.00037052 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-05 15:22 | 2021-10-05 16:20 | 80 | 000:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-10-05 | 4640 | keep | 0 | Oct | 2021 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-05 15:30 | 2021-10-05 15:31 | 1935 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21100500142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 1935 | keep | 0 | Oct | 2021 | 0.0013179 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-10-05 15:31 | 2021-10-05 18:57 | 655 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO DEL TRONCAL | B21100500144 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2021-10-05 | 134930 | keep | 0 | Oct | 2021 | 0.0919 | 0.00044612 | Sustained | FALSE | FALSE | Not_TMED_Event | 655
ARECIBO | 2021-10-05 15:31 | 2021-10-06 15:30 | 300 | 023:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21100500126 | New_Event | Wire Down | Include | Include | Equipment | 1439 | 2021-10-05 | 431700 | keep | 0 | Oct | 2021 | 0.29403 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-10-05 15:32 | 2021-10-05 18:05 | 250 | 002:33 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | A21100500128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-10-05 | 38250 | keep | 0 | Oct | 2021 | 0.026052 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
AGUADILLA | 2021-10-05 15:37 | 2021-10-06 15:57 | 60 | 024:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1460 | 2021-10-05 | 87600 | keep | 0 | Oct | 2021 | 0.059664 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-05 15:50 | 2021-10-06 15:15 | 1 | 023:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100500173 | New_Event | Bad Weather | Include | Include | Weather | 1405 | 2021-10-05 | 1405 | keep | 0 | Oct | 2021 | 0.00095694 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-05 15:52 | 2021-10-05 16:52 | 60 | 001:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO | S21100500000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2021-10-05 | 3600 | keep | 0 | Oct | 2021 | 0.0024519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-05 15:59 | 2021-10-05 19:22 | 50 | 003:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100500178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-10-05 | 10150 | keep | 0 | Oct | 2021 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-05 16:00 | 2021-10-05 18:50 | 100 | 002:50 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P21100500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-10-05 | 17000 | keep | 0 | Oct | 2021 | 0.011579 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-05 16:03 | 2021-10-05 20:05 | 88 | 004:02 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21100500193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-10-05 | 21296 | keep | 0 | Oct | 2021 | 0.014505 | 5.9936e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 88
AGUADILLA | 2021-10-05 16:03 | 2021-10-05 22:15 | 50 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE A CAJA PRIMARIA PARTIDO | M21100500180 | New_Event | Wire Down | Include | Include | Equipment | 372 | 2021-10-05 | 18600 | keep | 0 | Oct | 2021 | 0.012668 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-10-05 16:03 | 2021-10-06 11:34 | 35 | 019:31 | P | DESGANCHE | 2 X 20 EN CONVERTIDOR REQUIERE DESGANCHE | A21100500180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1171 | 2021-10-05 | 40985 | keep | 0 | Oct | 2021 | 0.027915 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-10-05 16:03 | 2021-10-06 17:08 | 30 | 025:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21100500135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1505 | 2021-10-05 | 45150 | keep | 0 | Oct | 2021 | 0.030751 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-05 16:10 | 2021-10-05 18:10 | 30 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100500184 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-10-05 | 3600 | keep | 0 | Oct | 2021 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-05 16:16 | 2021-10-06 14:15 | 40 | 021:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA DE TRANSFORMADOR QUEMADA | A21100500141 | New_Event | Cutout Failure | Include | Include | Equipment | 1319 | 2021-10-05 | 52760 | keep | 0 | Oct | 2021 | 0.035935 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-05 16:19 | 2021-10-05 18:10 | 130 | 001:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A21100500145 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2021-10-05 | 14430 | keep | 0 | Oct | 2021 | 0.0098282 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
PONCE | 2021-10-05 16:32 | 2021-10-05 16:40 | 25 | 000:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIAS | P21100500161 | New_Event | Cutout Failure | Include | Include | Equipment | 8 | 2021-10-05 | 200 | keep | 0 | Oct | 2021 | 0.00013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-10-05 16:41 | 2021-10-06 10:47 | 60 | 018:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A21100500152 | New_Event | Wire Down | Include | Include | Equipment | 1086 | 2021-10-05 | 65160 | keep | 0 | Oct | 2021 | 0.04438 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-10-05 16:44 | 2021-10-05 17:32 | 658 | 000:48 | T | DESGANCHE | DISPARO POR DESGANCHE SE REMOVIO ARBOL SOBRE LINEAS | P21100500163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-10-05 | 31584 | keep | 0 | Oct | 2021 | 0.021512 | 0.00044816 | Sustained | FALSE | TRUE | Not_TMED_Event | 658
PONCE | 2021-10-05 16:49 | 2021-10-06 11:55 | 75 | 019:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REPORTAN DESGANCHE | P21100500164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1146 | 2021-10-05 | 85950 | keep | 0 | Oct | 2021 | 0.05854 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-10-05 16:54 | 2021-10-05 18:08 | 6 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100500160 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-10-05 | 444 | keep | 0 | Oct | 2021 | 0.00030241 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-05 16:57 | 2021-10-05 18:43 | 55 | 001:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21100500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-10-05 | 5830 | keep | 0 | Oct | 2021 | 0.0039708 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-10-05 17:06 | 2021-10-05 19:17 | 300 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES QUEMADO | M21100500206 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2021-10-05 | 39300 | keep | 0 | Oct | 2021 | 0.026767 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-10-05 17:17 | 2021-10-06 16:14 | 15 | 022:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21100500208 | New_Event | Wire Down | Include | Include | Equipment | 1377 | 2021-10-05 | 20655 | keep | 0 | Oct | 2021 | 0.014068 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-05 17:33 | 2021-10-05 17:34 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 3941 | keep | 0 | Oct | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
SAN JUAN | 2021-10-05 17:44 | 2021-10-05 17:45 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-05 17:44 | 2021-10-05 17:45 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1204-05 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-05 17:45 | 2021-10-05 21:13 | 32 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21100500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-10-05 | 6656 | keep | 0 | Oct | 2021 | 0.0045334 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
AGUADILLA | 2021-10-05 17:45 | 2021-10-06 19:48 | 20 | 026:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | M21100500212 | New_Event | Wire Down | Include | Include | Equipment | 1563 | 2021-10-05 | 31260 | keep | 0 | Oct | 2021 | 0.021291 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-10-05 18:05 | 2021-10-05 20:00 | 50 | 001:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21100500176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-10-05 | 5750 | keep | 0 | Oct | 2021 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-05 18:06 | 2021-10-05 19:51 | 40 | 001:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21100500066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-10-05 | 4200 | keep | 0 | Oct | 2021 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-05 18:07 | 2021-10-05 22:57 | 500 | 004:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPORTA PUENTE ABIERTO A LA SALIDA DEL 1704-03 QUE LLEVA LA CARGA DEL 1706-02 | B21100500186 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2021-10-05 | 145000 | keep | 0 | Oct | 2021 | 0.098759 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2021-10-05 18:11 | 2021-10-05 18:50 | 60 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21100500162 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-10-05 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-05 18:27 | 2021-10-06 11:47 | 3 | 017:20 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21100500069 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1040 | 2021-10-05 | 3120 | keep | 0 | Oct | 2021 | 0.002125 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-10-05 18:47 | 2021-10-06 18:18 | 15 | 023:31 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 25KVA X 37.5KVA | S21100500112 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1411 | 2021-10-05 | 21165 | keep | 0 | Oct | 2021 | 0.014415 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-10-05 18:50 | 2021-10-06 10:54 | 40 | 016:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R21100500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 964 | 2021-10-05 | 38560 | keep | 0 | Oct | 2021 | 0.026263 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-10-05 18:56 | 2021-10-06 10:07 | 100 | 015:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | C21100500214 | New_Event | Cutout Failure | Include | Include | Equipment | 911 | 2021-10-05 | 91100 | keep | 0 | Oct | 2021 | 0.062048 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-05 18:57 | 2021-10-05 19:45 | 1935 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO DEL TRONCAL LLEVA PARTE DEL 1708-02 | B21100500210 | Additional_clients | Wire Down | Include | Include | Equipment | 48 | 2021-10-05 | 92880 | keep | 0 | Oct | 2021 | 0.06326 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-05 18:57 | 2021-10-05 19:45 | 500 | 000:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1707-01 PARA CERRAR PUENTE ABIERTO DEL TRONCAL LLEVA PARTE DEL 1708-02 | B21100500210 | New_Event | Wire Down | Include | Include | Equipment | 48 | 2021-10-05 | 24000 | keep | 0 | Oct | 2021 | 0.016346 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
YAUCO | 2021-10-05 19:07 | 2021-10-07 19:08 | 15 | 048:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANFORMADOR 300 KVA SOTERRADO AVERIADO X LO MISMO | P21100500089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2881 | 2021-10-05 | 43215 | keep | 0 | Oct | 2021 | 0.029434 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-10-05 19:22 | 2021-10-05 20:57 | 7 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21100500076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2021-10-05 | 665 | keep | 0 | Oct | 2021 | 0.00045293 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-10-05 19:23 | 2021-10-06 11:30 | 80 | 016:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHO REMPLAZO CAJA AVERIADA Y AISLADOR | C21100500219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 967 | 2021-10-05 | 77360 | keep | 0 | Oct | 2021 | 0.05269 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-05 19:32 | 2021-10-06 13:06 | 200 | 017:34 | P | DESGANCHE | 1 X 100 EN CONVERTIDOR Y 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21100500222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1054 | 2021-10-05 | 210800 | keep | 0 | Oct | 2021 | 0.14357 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-05 19:35 | 2021-10-06 10:40 | 10 | 015:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR, SE REALIZO DESGANCHE Y SE CERRO BAJANTE SECUNDARIO | S21100500016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 905 | 2021-10-05 | 9050 | keep | 0 | Oct | 2021 | 0.0061639 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-05 19:51 | 2021-10-05 22:37 | 65 | 002:46 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | B21100500224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-10-05 | 10790 | keep | 0 | Oct | 2021 | 0.007349 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
HUMACAO | 2021-10-05 19:58 | 2021-10-06 13:30 | 30 | 017:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REMPLAZO DISCO | C21100500222 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1052 | 2021-10-05 | 31560 | keep | 0 | Oct | 2021 | 0.021495 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-05 20:19 | 2021-10-06 11:02 | 50 | 014:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A21100500168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2021-10-05 | 44150 | keep | 0 | Oct | 2021 | 0.03007 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-05 20:23 | 2021-10-06 08:44 | 50 | 012:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100500226 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 741 | 2021-10-05 | 37050 | keep | 0 | Oct | 2021 | 0.025235 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-05 20:38 | 2021-10-05 21:48 | 91 | 001:10 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21100500129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-10-05 | 6370 | keep | 0 | Oct | 2021 | 0.0043386 | 6.198e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 91
SAN JUAN | 2021-10-05 20:39 | 2021-10-05 23:37 | 1862 | 002:58 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR SECUNDARIO DE LA PORTATIL SE CERRO PUENTE EN MACHETE DE SALIDA HACIA LA SUBESTACION | R21100500075 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-10-05 | 331436 | keep | 0 | Oct | 2021 | 0.22574 | 0.0012682 | Sustained | FALSE | FALSE | Not_TMED_Event | 1862
SAN JUAN | 2021-10-05 20:39 | 2021-10-05 23:37 | 1613 | 002:58 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR SECUNDARIO DE LA PORTATIL SE CERRO PUENTE EN MACHETE DE SALIDA HACIA LA SUBESTACION | R21100500075 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-10-05 | 287114 | keep | 0 | Oct | 2021 | 0.19555 | 0.0010986 | Sustained | FALSE | FALSE | Not_TMED_Event | 1613
SAN JUAN | 2021-10-05 20:39 | 2021-10-05 23:37 | 1448 | 002:58 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR SECUNDARIO DE LA PORTATIL SE CERRO PUENTE EN MACHETE DE SALIDA HACIA LA SUBESTACION | R21100500075 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-10-05 | 257744 | keep | 0 | Oct | 2021 | 0.17555 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
BAYAMON | 2021-10-05 20:51 | 2021-10-05 20:54 | 390 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-05 | 1170 | keep | 0 | Oct | 2021 | 0.00079688 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2021-10-05 21:04 | 2021-10-06 03:15 | 49 | 006:11 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21100500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2021-10-05 | 18179 | keep | 0 | Oct | 2021 | 0.012382 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
VEGA BAJA | 2021-10-05 21:25 | 2021-10-05 22:43 | 7 | 001:18 | P | NO SE REPORTO CAUSA | SE ABRIO TRANSFORMADOR Y SE SECCIONALIZO SECUNDARIA | B21100500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-05 | 546 | keep | 0 | Oct | 2021 | 0.00037188 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-05 21:32 | 2021-10-05 22:54 | 1681 | 001:22 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1303-01 Y 1346-06 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-10-05 | 137842 | keep | 0 | Oct | 2021 | 0.093884 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-05 21:32 | 2021-10-05 23:28 | 355 | 001:56 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 ADEMAS LLEVA LA CARGA PARCIAL DEL 1346-02 SE ABRIO AMARRE Y SE CERRO POR SCADA | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-10-05 | 41180 | keep | 0 | Oct | 2021 | 0.028048 | 0.00024179 | Sustained | FALSE | FALSE | Not_TMED_Event | 355
SAN JUAN | 2021-10-05 21:32 | 2021-10-05 22:54 | 1598 | 001:22 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 Y SE CERRO POR SCADA ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1303-01 Y 1346-06 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-10-05 | 131036 | keep | 0 | Oct | 2021 | 0.089248 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-10-05 21:32 | 2021-10-05 22:54 | 1802 | 001:22 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 ADEMAS LLEVA LA CARGA PARCIAL DEL 1346-02 SE ABRIO AMARRE Y SE CERRO POR SCADA | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-10-05 | 147764 | keep | 0 | Oct | 2021 | 0.10064 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-10-05 22:09 | 2021-10-05 22:10 | 2234 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR | B21100500000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-05 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-10-05 22:11 | 2021-10-06 16:35 | 50 | 018:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100500176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1104 | 2021-10-05 | 55200 | keep | 0 | Oct | 2021 | 0.037596 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-05 22:12 | 2021-10-05 22:13 | 2234 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR | B21100500000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-05 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-10-05 22:13 | 2021-10-06 05:00 | 35 | 006:47 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B21100500259 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 407 | 2021-10-05 | 14245 | keep | 0 | Oct | 2021 | 0.0097022 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-05 22:36 | 2021-10-06 15:43 | 50 | 017:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO PORTAFUSIBLES | S21100500253 | New_Event | Cutout Failure | Include | Include | Equipment | 1027 | 2021-10-05 | 51350 | keep | 0 | Oct | 2021 | 0.034974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-05 22:38 | 2021-10-05 22:39 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-05 | 4089 | keep | 0 | Oct | 2021 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2021-10-05 22:57 | 2021-10-05 23:22 | 1048 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPRTOR 1704-3 PARA CERRAR PUENTE ABIERTO EN MACHETE DE SALIDA. ADEMAS LLEVA LA CARGA DEL 1706-02 | B21100500186 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-10-05 | 26200 | keep | 0 | Oct | 2021 | 0.017845 | 0.00071379 | Sustained | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2021-10-05 22:57 | 2021-10-05 23:22 | 1382 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPRTOR 1704-3 PARA CERRAR PUENTE ABIERTO EN MACHETE DE SALIDA. ADEMAS LLEVA LA CARGA DEL 1706-02 | B21100500186 | Additional_clients | Wire Down | Include | Include | Equipment | 25 | 2021-10-05 | 34550 | keep | 0 | Oct | 2021 | 0.023532 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-05 22:58 | 2021-10-06 11:20 | 60 | 012:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21100500264 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 742 | 2021-10-05 | 44520 | keep | 0 | Oct | 2021 | 0.030322 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-05 23:21 | 2021-10-06 09:32 | 80 | 010:11 | P | HERRAJE ROTO O PODRIDO | 1 X 80 EN CORTE DE LINEA RETIRO PEDAZO DE CRUCETA SOBRE PUENTE | C21100500241 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 611 | 2021-10-05 | 48880 | keep | 0 | Oct | 2021 | 0.033292 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-05 23:22 | 2021-10-06 14:05 | 5 | 014:43 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21100500257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2021-10-05 | 4415 | keep | 0 | Oct | 2021 | 0.003007 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-05 23:24 | 2021-10-06 11:34 | 40 | 012:10 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21100500202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 730 | 2021-10-05 | 29200 | keep | 0 | Oct | 2021 | 0.019888 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-05 23:40 | 2021-10-06 13:00 | 50 | 013:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRL PARTIDO Y SE CERRO CORTE DE LINEA | M21100500238 | New_Event | Wire Down | Include | Include | Equipment | 800 | 2021-10-05 | 40000 | keep | 0 | Oct | 2021 | 0.027244 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-05 23:42 | 2021-10-06 10:59 | 65 | 011:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHO Y ENDEREZO POSTE | R21100500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 677 | 2021-10-05 | 44005 | keep | 0 | Oct | 2021 | 0.029972 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-10-05 23:46 | 2021-10-06 10:48 | 50 | 011:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100500272 | New_Event | Vegetation Contact | Include | Include | Vegetation | 662 | 2021-10-05 | 33100 | keep | 0 | Oct | 2021 | 0.022544 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-05 23:54 | 2021-10-06 03:57 | 10 | 004:03 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21100500162 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 243 | 2021-10-05 | 2430 | keep | 0 | Oct | 2021 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-06 | 2021-10-06 17:44 | 50 | 017:44 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | P21100600050 | New_Event | Defective Pole | Include | Include | Equipment | 1064 | 2021-10-06 | 53200 | keep | 0 | Oct | 2021 | 0.036234 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-06 00:14 | 2021-10-06 10:46 | 4 | 010:32 | P | OTRAS CAUSAS | 3 X 100 EN CORTE DE LINEA SE DEJO FUERA CLIENTE POR PROA | S21100600002 | New_Event | Other Causes | Include | Include | Other | 632 | 2021-10-06 | 2528 | keep | 0 | Oct | 2021 | 0.0017218 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-06 00:38 | 2021-10-06 18:00 | 60 | 017:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21100600001 | New_Event | Cutout Failure | Include | Include | Equipment | 1042 | 2021-10-06 | 62520 | keep | 0 | Oct | 2021 | 0.042582 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-10-06 01:26 | 2021-10-06 01:27 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1303-01 Y 1346-06 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1681 | keep | 0 | Oct | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-06 01:26 | 2021-10-06 01:27 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DE LOS ALIMENTADORES 1303-01 Y 1346-06 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1598 | keep | 0 | Oct | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-10-06 01:26 | 2021-10-06 01:27 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 Y SE CERRO POR SCADA ADEMAS LLEVA LA CARGA PARCIAL DEL 1346-02 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1802 | keep | 0 | Oct | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
FAJARDO | 2021-10-06 01:40 | 2021-10-06 08:03 | 40 | 006:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO PIN | R21100600002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 383 | 2021-10-06 | 15320 | keep | 0 | Oct | 2021 | 0.010434 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-06 01:44 | 2021-10-06 14:09 | 200 | 012:25 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE DESGANCHO Y SE REPARO LINEA ZAFADA DE AISLADOR | M21100600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 745 | 2021-10-06 | 149000 | keep | 0 | Oct | 2021 | 0.10148 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-10-06 02:04 | 2021-10-06 02:05 | 2343 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR CONDUCTOR PRIMARIO EN EL SUELO CERRADO POR CONTROL | R21100600003 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-06 | 2343 | keep | 0 | Oct | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2021-10-06 02:05 | 2021-10-06 06:06 | 200 | 004:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | R21100600006 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 241 | 2021-10-06 | 48200 | keep | 0 | Oct | 2021 | 0.032829 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-10-06 02:52 | 2021-10-06 11:33 | 150 | 008:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHO Y REMPLAZO PORTAFUSIBLE | C21100600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2021-10-06 | 78150 | keep | 0 | Oct | 2021 | 0.053228 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-10-06 03:05 | 2021-10-06 03:06 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21100600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2021-10-06 03:15 | 2021-10-06 05:34 | 390 | 002:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR. SE INSTALO TIGUERO EN LINEA TRONCAL Y SE CERRO POR SCADA | S21100600014 | New_Event | Wire Down | Include | Include | Equipment | 139 | 2021-10-06 | 54210 | keep | 0 | Oct | 2021 | 0.036922 | 0.00026563 | Sustained | FALSE | TRUE | Not_TMED_Event | 390
CANOVANAS | 2021-10-06 03:57 | 2021-10-06 03:59 | 2106 | 000:02 | T | SECUNDARIA/DESGANCHE | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21100600000 | Additional_clients | Secondary Vegetation | Include | Include | Vegetation | 2 | 2021-10-06 | 4212 | keep | 0 | Oct | 2021 | 0.0028688 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-10-06 03:59 | 2021-10-06 12:54 | 10 | 008:55 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21100500162 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 535 | 2021-10-06 | 5350 | keep | 0 | Oct | 2021 | 0.0036439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-06 04:00 | 2021-10-06 04:01 | 1894 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECERRO INTERRUPTOR | R21100600011 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-06 | 1894 | keep | 0 | Oct | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2021-10-06 04:01 | 2021-10-06 16:28 | 180 | 012:27 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN SU-10 REEMPLAZO TERMINACION EN PROVISONAL AEREO Y CAJA DE PROVISIONAL AEREO | R21100600066 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 747 | 2021-10-06 | 134460 | keep | 0 | Oct | 2021 | 0.09158 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2021-10-06 04:16 | 2021-10-06 07:00 | 4188 | 002:44 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO EL ALIMENTADOR | R21100600012 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2021-10-06 | 686832 | keep | 0 | Oct | 2021 | 0.4678 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
VEGA BAJA | 2021-10-06 04:31 | 2021-10-06 04:32 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 3332 | keep | 0 | Oct | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2021-10-06 04:32 | 2021-10-06 14:36 | 8 | 010:04 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100600059 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 604 | 2021-10-06 | 4832 | keep | 0 | Oct | 2021 | 0.0032911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-06 04:33 | 2021-10-06 10:42 | 30 | 006:09 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA | S21100600012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-10-06 | 11070 | keep | 0 | Oct | 2021 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-06 05:00 | 2021-10-06 05:03 | 2234 | 000:03 | T | PARARRAYOS DEFECTUOSO | DEISPARO DE INTRRUPTOR Y SE CERRO POR SCADA | B21100600000 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 3 | 2021-10-06 | 6702 | keep | 0 | Oct | 2021 | 0.0045647 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-06 05:03 | 2021-10-06 12:23 | 30 | 007:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21100500259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2021-10-06 | 13200 | keep | 0 | Oct | 2021 | 0.0089905 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-06 05:03 | 2021-10-06 19:21 | 35 | 014:18 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B21100500259 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 858 | 2021-10-06 | 30030 | keep | 0 | Oct | 2021 | 0.020453 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-06 05:13 | 2021-10-06 21:45 | 60 | 016:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SUBIO PRIMARIA Y SE LLEVO A SU SITIO Y SE CERRO INTERRUPTOR SCADA | B21100600018 | New_Event | Wire Down | Include | Include | Equipment | 992 | 2021-10-06 | 59520 | keep | 0 | Oct | 2021 | 0.040539 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-06 05:34 | 2021-10-06 18:03 | 49 | 012:29 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21100500134 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 749 | 2021-10-06 | 36701 | keep | 0 | Oct | 2021 | 0.024997 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-06 05:45 | 2021-10-06 17:51 | 140 | 012:06 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100600013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 726 | 2021-10-06 | 101640 | keep | 0 | Oct | 2021 | 0.069227 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
YAUCO | 2021-10-06 05:57 | 2021-10-06 15:04 | 100 | 009:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21100600010 | New_Event | Wire Down | Include | Include | Equipment | 547 | 2021-10-06 | 54700 | keep | 0 | Oct | 2021 | 0.037256 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-10-06 06:06 | 2021-10-06 10:20 | 112 | 004:14 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P21100600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2021-10-06 | 28448 | keep | 0 | Oct | 2021 | 0.019376 | 7.6283e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 112
PONCE | 2021-10-06 06:16 | 2021-10-06 10:36 | 165 | 004:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA | P21100600011 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2021-10-06 | 42900 | keep | 0 | Oct | 2021 | 0.029219 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
CAGUAS | 2021-10-06 06:29 | 2021-10-06 15:24 | 50 | 008:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REMPLAZO PIN POLE TOP Y LEVANTO CONDUCTOR | C21100600007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 535 | 2021-10-06 | 26750 | keep | 0 | Oct | 2021 | 0.018219 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-06 06:35 | 2021-10-06 09:42 | 100 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTE VIENTO | A21100600015 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-10-06 | 18700 | keep | 0 | Oct | 2021 | 0.012736 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-06 06:47 | 2021-10-06 10:32 | 65 | 003:45 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-10-06 | 14625 | keep | 0 | Oct | 2021 | 0.009961 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-10-06 06:48 | 2021-10-06 11:26 | 75 | 004:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2021-10-06 | 20850 | keep | 0 | Oct | 2021 | 0.014201 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-10-06 07:00 | 2021-10-06 10:56 | 2000 | 003:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA Y PARARRAYO | R21100600033 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 236 | 2021-10-06 | 472000 | keep | 0 | Oct | 2021 | 0.32148 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-06 07:18 | 2021-10-07 12:34 | 5 | 029:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO EN TRASFORMADOR NO FUNDIO FUSIBLE | P21100600019 | New_Event | Wire Down | Include | Include | Equipment | 1756 | 2021-10-06 | 8780 | keep | 0 | Oct | 2021 | 0.00598 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-10-06 07:21 | 2021-10-06 07:22 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1945 | keep | 0 | Oct | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
UTUADO | 2021-10-06 07:28 | 2021-10-06 12:18 | 30 | 004:50 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21100600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2021-10-06 | 8700 | keep | 0 | Oct | 2021 | 0.0059255 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-10-06 07:31 | 2021-10-06 16:30 | 55 | 008:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21100600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2021-10-06 | 29645 | keep | 0 | Oct | 2021 | 0.020191 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-10-06 07:41 | 2021-10-06 12:24 | 50 | 004:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21100600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2021-10-06 | 14150 | keep | 0 | Oct | 2021 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-06 07:45 | 2021-10-07 13:48 | 1 | 030:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A21100600022 | New_Event | Bad Weather | Include | Include | Weather | 1803 | 2021-10-06 | 1803 | keep | 0 | Oct | 2021 | 0.001228 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-10-06 07:50 | 2021-10-06 07:51 | 1648 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21100600041 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-06 | 1648 | keep | 0 | Oct | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-10-06 07:51 | 2021-10-06 13:56 | 40 | 006:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CAMION SACUDIO LINEA SECUNDARIA | R21100600058 | 1st_after_momentary |  |  | Include | Wildlife | 365 | 2021-10-06 | 14600 | keep | 0 | Oct | 2021 | 0.009944 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-06 07:51 | 2021-10-07 04:22 | 10 | 020:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN SU LLUVIAS | R21100600006 | New_Event | Bad Weather | Include | Include | Weather | 1231 | 2021-10-06 | 12310 | keep | 0 | Oct | 2021 | 0.0083843 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-10-06 07:55 | 2021-10-06 11:16 | 20 | 003:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | R21100600040 | New_Event | Wire Down | Include | Include | Equipment | 201 | 2021-10-06 | 4020 | keep | 0 | Oct | 2021 | 0.002738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-06 07:56 | 2021-10-06 20:24 | 36 | 012:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21100600045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 748 | 2021-10-06 | 26928 | keep | 0 | Oct | 2021 | 0.018341 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
ARECIBO | 2021-10-06 08:05 | 2021-10-06 19:44 | 100 | 011:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21100600026 | New_Event | Wire Down | Include | Include | Equipment | 699 | 2021-10-06 | 69900 | keep | 0 | Oct | 2021 | 0.047609 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-06 08:06 | 2021-10-06 15:00 | 4 | 006:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M21100600024 | New_Event | Wire Down | Include | Include | Equipment | 414 | 2021-10-06 | 1656 | keep | 0 | Oct | 2021 | 0.0011279 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-06 08:07 | 2021-10-06 11:11 | 40 | 003:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO ARBOL | M21100600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-10-06 | 7360 | keep | 0 | Oct | 2021 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-10-06 08:09 | 2021-10-06 12:35 | 32 | 004:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REPORTAN DESGANCHE | P21100600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-10-06 | 8512 | keep | 0 | Oct | 2021 | 0.0057975 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
CAGUAS | 2021-10-06 08:21 | 2021-10-06 16:24 | 1 | 008:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA RETEZO CONDUCTOR | C21100600011 | New_Event | Wire Down | Include | Include | Equipment | 483 | 2021-10-06 | 483 | keep | 0 | Oct | 2021 | 0.00032897 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-06 08:26 | 2021-10-06 14:18 | 50 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN PROVISIONAL AEREO SE RETIRO SECUNDARIA CRUZADA CON PROVISIONAL | R21100600046 | New_Event | Wire Down | Include | Include | Equipment | 352 | 2021-10-06 | 17600 | keep | 0 | Oct | 2021 | 0.011987 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-06 08:36 | 2021-10-06 14:52 | 10 | 006:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE SECUNDARIO | C21100600013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 376 | 2021-10-06 | 3760 | keep | 0 | Oct | 2021 | 0.0025609 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-06 08:44 | 2021-10-06 08:45 | 1593 | 000:01 | T | DESGANCHE | RECIERRE | C21100600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-06 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-10-06 08:45 | 2021-10-06 18:35 | 50 | 009:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100500226 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 590 | 2021-10-06 | 29500 | keep | 0 | Oct | 2021 | 0.020092 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-06 08:45 | 2021-10-06 08:46 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1526 | keep | 0 | Oct | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-10-06 08:46 | 2021-10-06 22:29 | 35 | 013:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21010600204 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 823 | 2021-10-06 | 28805 | keep | 0 | Oct | 2021 | 0.019619 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-10-06 08:47 | 2021-10-06 11:39 | 1 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES | R21100600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-10-06 | 172 | keep | 0 | Oct | 2021 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-06 08:52 | 2021-10-07 18:44 | 20 | 033:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REMPLAZO CAJA PRIMARIA | B21100600053 | New_Event | Cutout Failure | Include | Include | Equipment | 2032 | 2021-10-06 | 40640 | keep | 0 | Oct | 2021 | 0.02768 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-10-06 08:53 | 2021-10-06 13:01 | 12 | 004:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21100600050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2021-10-06 | 2976 | keep | 0 | Oct | 2021 | 0.0020269 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
YAUCO | 2021-10-06 08:53 | 2021-10-06 16:30 | 100 | 007:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21100600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2021-10-06 | 45700 | keep | 0 | Oct | 2021 | 0.031126 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-06 09:00 | 2021-10-06 11:17 | 50 | 002:17 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE CRUCETA | B21100600058 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 137 | 2021-10-06 | 6850 | keep | 0 | Oct | 2021 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-06 09:17 | 2021-10-06 18:40 | 75 | 009:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21100600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 563 | 2021-10-06 | 42225 | keep | 0 | Oct | 2021 | 0.028759 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-10-06 09:21 | 2021-10-06 12:20 | 25 | 002:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21100600061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2021-10-06 | 4475 | keep | 0 | Oct | 2021 | 0.0030479 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-06 09:26 | 2021-10-06 11:12 | 80 | 001:46 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21100600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-10-06 | 8480 | keep | 0 | Oct | 2021 | 0.0057757 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-06 09:30 | 2021-10-06 16:06 | 5 | 006:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100600039 | New_Event | Bad Weather | Include | Include | Weather | 396 | 2021-10-06 | 1980 | keep | 0 | Oct | 2021 | 0.0013486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-10-06 09:43 | 2021-10-06 14:59 | 25 | 005:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21100600070 | New_Event | Cutout Failure | Include | Include | Equipment | 316 | 2021-10-06 | 7900 | keep | 0 | Oct | 2021 | 0.0053807 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2021-10-06 09:54 | 2021-10-06 10:25 | 50 | 000:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA FIJO CONDUCTOR | R21100600056 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2021-10-06 | 1550 | keep | 0 | Oct | 2021 | 0.0010557 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-06 09:55 | 2021-10-07 18:30 | 6 | 032:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21100600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1955 | 2021-10-06 | 11730 | keep | 0 | Oct | 2021 | 0.0079892 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-06 10:04 | 2021-10-06 10:05 | 601 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 601 | keep | 0 | Oct | 2021 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
PONCE | 2021-10-06 10:10 | 2021-10-06 16:10 | 50 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEAS MAL TIEMPO | P21100600038 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-10-06 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-06 10:13 | 2021-10-06 16:08 | 10 | 005:55 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO SE PASO LA CARGA A TRANSFORMADOR ADYACENTE | M21100600055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 355 | 2021-10-06 | 3550 | keep | 0 | Oct | 2021 | 0.0024179 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-06 10:24 | 2021-10-06 16:19 | 50 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2021-10-06 | 17750 | keep | 0 | Oct | 2021 | 0.012089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-06 10:25 | 2021-10-07 10:32 | 1 | 024:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21100600020 | New_Event | Bad Weather | Include | Include | Weather | 1447 | 2021-10-06 | 1447 | keep | 0 | Oct | 2021 | 0.00098555 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-06 10:37 | 2021-10-06 15:35 | 1 | 004:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DOS TRANSFORMADORES QUEMADOS EN MONTURA. UNO DE 15 KVA X 15 KVA Y UNO DE 37.5 KVA X 37.5 KVA. | A21100600049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 298 | 2021-10-06 | 298 | keep | 0 | Oct | 2021 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-06 10:42 | 2021-10-07 17:00 | 10 | 030:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 5 KVA POR UNO DE 15 KVA | M21100600060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1818 | 2021-10-06 | 18180 | keep | 0 | Oct | 2021 | 0.012382 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-06 10:56 | 2021-10-06 13:48 | 10 | 002:52 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21100600030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 172 | 2021-10-06 | 1720 | keep | 0 | Oct | 2021 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-06 11:00 | 2021-10-06 14:01 | 50 | 003:01 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN RISER CONTAMINACION | R21100600065 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 181 | 2021-10-06 | 9050 | keep | 0 | Oct | 2021 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-10-06 11:03 | 2021-10-06 16:09 | 100 | 005:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PRIMARIO | P21100500042 | New_Event | Wire Down | Include | Include | Equipment | 306 | 2021-10-06 | 30600 | keep | 0 | Oct | 2021 | 0.020842 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-06 11:06 | 2021-10-06 13:05 | 65 | 001:59 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | S21100600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-10-06 | 7735 | keep | 0 | Oct | 2021 | 0.0052683 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-10-06 11:09 | 2021-10-06 15:00 | 200 | 003:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | P21100600043 | New_Event | Bad Weather | Include | Include | Weather | 231 | 2021-10-06 | 46200 | keep | 0 | Oct | 2021 | 0.031467 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-06 11:09 | 2021-10-06 16:17 | 60 | 005:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100600063 | New_Event | Bad Weather | Include | Include | Weather | 308 | 2021-10-06 | 18480 | keep | 0 | Oct | 2021 | 0.012587 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-06 11:30 | 2021-10-06 12:12 | 15 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21100500028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-10-06 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-10-06 11:43 | 2021-10-06 16:31 | 65 | 004:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21100600033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-10-06 | 18720 | keep | 0 | Oct | 2021 | 0.01275 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
FAJARDO | 2021-10-06 11:47 | 2021-10-06 13:42 | 4 | 001:55 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR DESGANCHE | R21100600068 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 115 | 2021-10-06 | 460 | keep | 0 | Oct | 2021 | 0.0003133 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-06 12:06 | 2021-10-06 17:12 | 20 | 005:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100600080 | New_Event | Bad Weather | Include | Include | Weather | 306 | 2021-10-06 | 6120 | keep | 0 | Oct | 2021 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-10-06 12:17 | 2021-10-06 14:30 | 2 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100600070 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-10-06 | 266 | keep | 0 | Oct | 2021 | 0.00018117 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-10-06 12:39 | 2021-10-06 14:24 | 50 | 001:45 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS Y SE NORMALIZO RECLOUSER DE LINEA | M21100600087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-10-06 | 5250 | keep | 0 | Oct | 2021 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-06 12:40 | 2021-10-06 17:00 | 20 | 004:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SECUNDARIO EN EL LUGAR | S21100600055 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 260 | 2021-10-06 | 5200 | keep | 0 | Oct | 2021 | 0.0035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-06 12:48 | 2021-10-06 17:00 | 1 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER HACIA ESCUELA | B21100600104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2021-10-06 | 252 | keep | 0 | Oct | 2021 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-10-06 12:57 | 2021-10-06 14:42 | 50 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21100600044 | New_Event |  |  | Include | Wildlife | 105 | 2021-10-06 | 5250 | keep | 0 | Oct | 2021 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-06 12:58 | 2021-10-06 14:18 | 40 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21100600061 | New_Event |  |  | Include | Wildlife | 80 | 2021-10-06 | 3200 | keep | 0 | Oct | 2021 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-06 13:22 | 2021-10-06 18:56 | 6 | 005:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | M21100600098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 334 | 2021-10-06 | 2004 | keep | 0 | Oct | 2021 | 0.0013649 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
HUMACAO | 2021-10-06 13:37 | 2021-10-06 19:46 | 100 | 006:09 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA | C21100600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-10-06 | 36900 | keep | 0 | Oct | 2021 | 0.025132 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-06 13:37 | 2021-10-06 18:30 | 15 | 004:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARARON BARRAS SECUNDARIAS AVERIADAS | M21100600101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 293 | 2021-10-06 | 4395 | keep | 0 | Oct | 2021 | 0.0029934 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-10-06 13:37 | 2021-10-07 15:25 | 20 | 025:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR UNO DE 50 KVA | M21100600102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1548 | 2021-10-06 | 30960 | keep | 0 | Oct | 2021 | 0.021087 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-10-06 13:40 | 2021-10-06 14:44 | 8 | 001:04 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21100600078 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 64 | 2021-10-06 | 512 | keep | 0 | Oct | 2021 | 0.00034872 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-10-06 13:45 | 2021-10-06 14:17 | 1 | 000:32 | P | DESGANCHE | 1 X 40 EN RISER | R21100600080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2021-10-06 | 32 | keep | 0 | Oct | 2021 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-10-06 13:49 | 2021-10-07 17:45 | 150 | 027:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA LINEA ROTA SE ABRIO PUENTES PARA SECCIONALIZAR | M21100600104 | New_Event | Wire Down | Include | Include | Equipment | 1676 | 2021-10-06 | 251400 | keep | 0 | Oct | 2021 | 0.17123 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-06 14:00 | 2021-10-06 17:01 | 70 | 003:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M21100600105 | New_Event | Wire Down | Include | Include | Equipment | 181 | 2021-10-06 | 12670 | keep | 0 | Oct | 2021 | 0.0086295 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-06 14:00 | 2021-10-07 15:30 | 4 | 025:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25 KVA @ 2400V POR UNO DE 25 KVA @ 7620V SE RELOCALIZO EL TRANSFORMADOR POR SITUACION PELIGROSA | M21100600105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1530 | 2021-10-06 | 6120 | keep | 0 | Oct | 2021 | 0.0041683 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-10-06 14:09 | 2021-10-06 15:03 | 90 | 000:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21100600082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-10-06 | 4860 | keep | 0 | Oct | 2021 | 0.0033101 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-06 14:09 | 2021-10-06 15:44 | 80 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21100600002 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2021-10-06 | 7600 | keep | 0 | Oct | 2021 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-10-06 14:48 | 2021-10-06 15:26 | 4 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | B21100500127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2021-10-06 | 152 | keep | 0 | Oct | 2021 | 0.00010353 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-10-06 14:54 | 2021-10-06 20:01 | 25 | 005:07 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE DEJARON PUENTES ABIERTOS HACIA POSTE PARTIDO | B21100600122 | New_Event | Defective Pole | Include | Include | Equipment | 307 | 2021-10-06 | 7675 | keep | 0 | Oct | 2021 | 0.0052274 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-06 14:55 | 2021-10-06 15:48 | 11 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21100600091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-10-06 | 583 | keep | 0 | Oct | 2021 | 0.00039708 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2021-10-06 15:14 | 2021-10-06 21:50 | 100 | 006:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | P21100600082 | New_Event | Cutout Failure | Include | Include | Equipment | 396 | 2021-10-06 | 39600 | keep | 0 | Oct | 2021 | 0.026971 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-06 15:15 | 2021-10-07 11:57 | 10 | 020:42 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REALIZE DESGANCHE | S21100600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1242 | 2021-10-06 | 12420 | keep | 0 | Oct | 2021 | 0.0084592 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-06 15:15 | 2021-10-07 12:38 | 30 | 021:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZE DESGANCHE | S21100600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1283 | 2021-10-06 | 38490 | keep | 0 | Oct | 2021 | 0.026215 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-06 15:25 | 2021-10-06 22:26 | 50 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21100600088 | New_Event | Wire Down | Include | Include | Equipment | 421 | 2021-10-06 | 21050 | keep | 0 | Oct | 2021 | 0.014337 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-06 15:26 | 2021-10-06 17:00 | 50 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | P21100600069 | New_Event |  |  | Include | Wildlife | 94 | 2021-10-06 | 4700 | keep | 0 | Oct | 2021 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-06 15:33 | 2021-10-06 15:37 | 1681 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL CARGA POR EL 1303-04 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-06 | 6724 | keep | 0 | Oct | 2021 | 0.0045797 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-06 15:33 | 2021-10-06 15:37 | 225 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA EL 1303-01 Y EL 1346-06 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-06 | 900 | keep | 0 | Oct | 2021 | 0.00061299 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-06 15:33 | 2021-10-06 15:37 | 1598 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL CARGA POR EL 1303-04 | S21100500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-06 | 6392 | keep | 0 | Oct | 2021 | 0.0043536 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-10-06 15:33 | 2021-10-06 15:37 | 1802 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S21100500076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-06 | 7208 | keep | 0 | Oct | 2021 | 0.0049093 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2021-10-06 15:47 | 2021-10-07 18:23 | 8 | 026:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21100600089 | New_Event | Bad Weather | Include | Include | Weather | 1596 | 2021-10-06 | 12768 | keep | 0 | Oct | 2021 | 0.0086962 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-06 15:56 | 2021-10-06 15:57 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21100600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1310 | keep | 0 | Oct | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-10-06 16:02 | 2021-10-07 13:10 | 25 | 021:08 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE CERRO PROVISIONAL | B21100600139 | New_Event | Defective Pole | Include | Include | Equipment | 1268 | 2021-10-06 | 31700 | keep | 0 | Oct | 2021 | 0.021591 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-10-06 16:03 | 2021-10-06 23:00 | 80 | 006:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21100600128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2021-10-06 | 33360 | keep | 0 | Oct | 2021 | 0.022721 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-06 16:07 | 2021-10-07 13:20 | 15 | 021:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21100600091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1273 | 2021-10-06 | 19095 | keep | 0 | Oct | 2021 | 0.013006 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-06 16:09 | 2021-10-06 19:43 | 50 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL | B21100600142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2021-10-06 | 10700 | keep | 0 | Oct | 2021 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-06 16:10 | 2021-10-06 17:57 | 50 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21100600092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-10-06 | 5350 | keep | 0 | Oct | 2021 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-06 16:10 | 2021-10-06 16:11 | 1310 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B21100600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-06 | 1310 | keep | 0 | Oct | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2021-10-06 16:11 | 2021-10-06 17:39 | 12 | 001:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE DESPEGO CONDUCTOR CRUZADO DE PARARRAYO PRIVADO | B21100600157 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 88 | 2021-10-06 | 1056 | keep | 0 | Oct | 2021 | 0.00071924 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-10-06 16:15 | 2021-10-06 18:10 | 13 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | R21100600097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-10-06 | 1495 | keep | 0 | Oct | 2021 | 0.0010182 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2021-10-06 16:17 | 2021-10-06 16:46 | 14 | 000:29 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | C21160600070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 29 | 2021-10-06 | 406 | keep | 0 | Oct | 2021 | 0.00027652 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2021-10-06 16:24 | 2021-10-07 14:32 | 25 | 022:08 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REMPLAZO AISLADOR | B21100600150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1328 | 2021-10-06 | 33200 | keep | 0 | Oct | 2021 | 0.022612 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-10-06 16:33 | 2021-10-06 17:51 | 10 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21100600073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-10-06 | 780 | keep | 0 | Oct | 2021 | 0.00053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-06 16:34 | 2021-10-06 17:57 | 8 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21100600074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2021-10-06 | 664 | keep | 0 | Oct | 2021 | 0.00045225 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-06 16:35 | 2021-10-06 17:10 | 7 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21100600094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-10-06 | 245 | keep | 0 | Oct | 2021 | 0.00016687 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-10-06 16:36 | 2021-10-06 18:42 | 60 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100600099 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-10-06 | 7560 | keep | 0 | Oct | 2021 | 0.0051491 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-06 16:37 | 2021-10-06 19:07 | 32 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21100600097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-10-06 | 4800 | keep | 0 | Oct | 2021 | 0.0032693 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
FAJARDO | 2021-10-06 16:51 | 2021-10-07 10:29 | 100 | 017:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21100600100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1058 | 2021-10-06 | 105800 | keep | 0 | Oct | 2021 | 0.07206 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-06 16:58 | 2021-10-06 18:45 | 50 | 001:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21100600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2021-10-06 | 5350 | keep | 0 | Oct | 2021 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-06 17:00 | 2021-10-06 20:35 | 30 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100600138 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-10-06 | 6450 | keep | 0 | Oct | 2021 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-06 17:27 | 2021-10-06 19:40 | 1 | 002:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A21100600104 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 133 | 2021-10-06 | 133 | keep | 0 | Oct | 2021 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-06 17:28 | 2021-10-07 15:30 | 1 | 022:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA | A21100600104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1322 | 2021-10-06 | 1322 | keep | 0 | Oct | 2021 | 0.00090041 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-06 17:29 | 2021-10-07 21:24 | 7 | 027:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR UNO DE IGUAL CAPACIDAD | B21100600159 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1675 | 2021-10-06 | 11725 | keep | 0 | Oct | 2021 | 0.0079858 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-10-06 17:39 | 2021-10-06 18:29 | 1310 | 000:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | B21100600157 | Additional_clients | Wire Down | Include | Include | Equipment | 50 | 2021-10-06 | 65500 | keep | 0 | Oct | 2021 | 0.044612 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-06 17:41 | 2021-10-06 17:42 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR EL 6014-02 | M21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 1444 | keep | 0 | Oct | 2021 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-10-06 17:41 | 2021-10-06 17:42 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-01 | M21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 3630 | keep | 0 | Oct | 2021 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
CANOVANAS | 2021-10-06 17:46 | 2021-10-06 19:39 | 70 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA AVERIADA NO FUNDIO FUSIBLE | R21100600105 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2021-10-06 | 7910 | keep | 0 | Oct | 2021 | 0.0053875 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-06 17:46 | 2021-10-07 13:31 | 50 | 019:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA EN EL FID: 17324914 MARCA HUBBER DE 200AMP | M21100600150 | New_Event | Cutout Failure | Include | Include | Equipment | 1185 | 2021-10-06 | 59250 | keep | 0 | Oct | 2021 | 0.040355 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-06 17:47 | 2021-10-07 18:04 | 15 | 024:17 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | C21100600209 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1457 | 2021-10-06 | 21855 | keep | 0 | Oct | 2021 | 0.014885 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-10-06 17:50 | 2021-10-06 18:49 | 8 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21100600106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-10-06 | 472 | keep | 0 | Oct | 2021 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-06 17:56 | 2021-10-06 20:43 | 60 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100600159 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-10-06 | 10020 | keep | 0 | Oct | 2021 | 0.0068246 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-06 17:58 | 2021-10-07 11:48 | 150 | 017:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21100600165 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1070 | 2021-10-06 | 160500 | keep | 0 | Oct | 2021 | 0.10932 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-06 17:59 | 2021-10-06 20:00 | 1 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO SECUNDARIA ROTA POR CAMION | R21100600108 | New_Event |  |  | Include | Wildlife | 121 | 2021-10-06 | 121 | keep | 0 | Oct | 2021 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-06 18:00 | 2021-10-06 18:30 | 4641 | 000:30 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DISPARO INTERRUPTOR SE CERRO MANUAL ELECTRICO POR RTU DOWN | M21100600001 | Additional_clients | Cutout Failure | Include | Include | Equipment | 30 | 2021-10-06 | 139230 | keep | 0 | Oct | 2021 | 0.094829 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-10-06 18:00 | 2021-10-06 21:34 | 100 | 003:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO FUNDIENDO FUSIBLE CONSTANTEMENTE A CAUSA DEL DESGANCHE | M21100600215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-10-06 | 21400 | keep | 0 | Oct | 2021 | 0.014575 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-06 18:01 | 2021-10-06 18:02 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-06 18:01 | 2021-10-06 18:02 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1204-05 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-06 18:13 | 2021-10-06 20:08 | 1271 | 001:55 | T | DESGANCHE | SE RETIRO RAMAS SOBRE LINEAS Y CERRO INTERRUPTOR | R21100600115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-10-06 | 146165 | keep | 0 | Oct | 2021 | 0.099552 | 0.00086567 | Sustained | FALSE | TRUE | Not_TMED_Event | 1271
BAYAMON | 2021-10-06 18:19 | 2021-10-06 19:14 | 8 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100400083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-10-06 | 440 | keep | 0 | Oct | 2021 | 0.00029968 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-06 18:29 | 2021-10-06 20:02 | 600 | 001:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE ABRIO NUEVAMENTE POR SEGURIDAD PARA CERRAR MACHETES | B21100600157 | Partial_restoration | Wire Down | Include | Include | Equipment | 93 | 2021-10-06 | 55800 | keep | 0 | Oct | 2021 | 0.038005 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-06 18:37 | 2021-10-07 13:06 | 3 | 018:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21100600081 | New_Event | Bad Weather | Include | Include | Weather | 1109 | 2021-10-06 | 3327 | keep | 0 | Oct | 2021 | 0.002266 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-10-06 18:39 | 2021-10-08 19:11 | 20 | 048:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO 400 PIES DE SECUNDARIA | S21100600122 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2912 | 2021-10-06 | 58240 | keep | 0 | Oct | 2021 | 0.039667 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-06 19:10 | 2021-10-06 19:11 | 4387 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21100600216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 4387 | keep | 0 | Oct | 2021 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-10-06 19:29 | 2021-10-07 10:23 | 20 | 014:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21100600199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 894 | 2021-10-06 | 17880 | keep | 0 | Oct | 2021 | 0.012178 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-06 19:44 | 2021-10-06 19:46 | 135 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21100600126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-06 | 270 | keep | 0 | Oct | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-10-06 19:47 | 2021-10-06 19:48 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 99% DEL 1909-09 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 222 | keep | 0 | Oct | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-10-06 19:47 | 2021-10-06 19:48 | 4412 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE EL 99% DE LA CARGA ESTA POR EL 1907-03 | S21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 4412 | keep | 0 | Oct | 2021 | 0.003005 | 0.003005 | Momentary | FALSE | FALSE | Not_TMED_Event | 4412
MAYAGÃœEZ | 2021-10-06 19:49 | 2021-10-07 12:46 | 150 | 016:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO ESPACIADOR ROTO | M21100600224 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1017 | 2021-10-06 | 152550 | keep | 0 | Oct | 2021 | 0.1039 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-06 19:56 | 2021-10-08 16:00 | 8 | 044:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 25 KVA | M21100700141 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2644 | 2021-10-06 | 21152 | keep | 0 | Oct | 2021 | 0.014407 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-06 20:02 | 2021-10-06 20:05 | 1310 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRO INTERRUPTOR POR SCADA | B21100600157 | Additional_clients | Wire Down | Include | Include | Equipment | 3 | 2021-10-06 | 3930 | keep | 0 | Oct | 2021 | 0.0026767 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-06 20:09 | 2021-10-06 20:10 | 4028 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21100600195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 4028 | keep | 0 | Oct | 2021 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2021-10-06 20:20 | 2021-10-07 10:36 | 30 | 014:16 | P | DESGANCHE | 1 X 40 EN RISER SE REALIZO DESGANCHE | S21100600128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 856 | 2021-10-06 | 25680 | keep | 0 | Oct | 2021 | 0.017491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-10-06 20:47 | 2021-10-06 21:40 | 30 | 000:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEA PRIMARIA ROTA SE ABRIO PUENTES PARA SECCIONALIZAR | A21100600097 | New_Event | Wire Down | Include | Include | Equipment | 53 | 2021-10-06 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-06 20:57 | 2021-10-06 20:58 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21100600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-06 | 2900 | keep | 0 | Oct | 2021 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BAYAMON | 2021-10-06 21:08 | 2021-10-07 19:19 | 36 | 022:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN AEREO PROVISIONAL | B21100600199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1331 | 2021-10-06 | 47916 | keep | 0 | Oct | 2021 | 0.032635 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2021-10-06 21:18 | 2021-10-07 12:19 | 10 | 015:01 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21100600131 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 901 | 2021-10-06 | 9010 | keep | 0 | Oct | 2021 | 0.0061367 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-06 21:20 | 2021-10-06 22:37 | 50 | 001:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21100600235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-10-06 | 3850 | keep | 0 | Oct | 2021 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-06 21:40 | 2021-10-07 14:29 | 15 | 016:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A21100600097 | Partial_restoration | Wire Down | Include | Include | Equipment | 1009 | 2021-10-06 | 15135 | keep | 0 | Oct | 2021 | 0.010308 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-06 21:59 | 2021-10-07 14:00 | 29 | 016:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21100600203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 961 | 2021-10-06 | 27869 | keep | 0 | Oct | 2021 | 0.018981 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
BAYAMON | 2021-10-07 00:18 | 2021-10-07 01:29 | 1310 | 001:11 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO PATRULLAJE Y SE REPORTA AVERIA POR DESGANCHE A LO LARGO DEL ALIMENTADOR | S21100700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-10-07 | 93010 | keep | 0 | Oct | 2021 | 0.063349 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2021-10-07 02:18 | 2021-10-08 11:36 | 50 | 033:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 NX SE RETIRO RATA | S21100700006 | New_Event |  |  | Include | Wildlife | 1998 | 2021-10-07 | 99900 | keep | 0 | Oct | 2021 | 0.068041 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-07 02:18 | 2021-10-07 12:04 | 50 | 009:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL AEREO | B21100700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 586 | 2021-10-07 | 29300 | keep | 0 | Oct | 2021 | 0.019956 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-10-07 04:22 | 2021-10-07 04:23 | 2106 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21100700000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-10-07 | 2106 | keep | 0 | Oct | 2021 | 0.0014344 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-10-07 04:23 | 2021-10-07 13:04 | 10 | 008:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN SU LLUVIAS | R21100600006 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 521 | 2021-10-07 | 5210 | keep | 0 | Oct | 2021 | 0.0035485 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-07 04:31 | 2021-10-07 14:46 | 80 | 010:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA AVERIADA NO FUNDIO FUSIBLE | C21100600003 | New_Event | Cutout Failure | Include | Include | Equipment | 615 | 2021-10-07 | 49200 | keep | 0 | Oct | 2021 | 0.03351 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-10-07 06:00 | 2021-10-07 12:55 | 36 | 006:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 X 50KVA | R21100700001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 415 | 2021-10-07 | 14940 | keep | 0 | Oct | 2021 | 0.010176 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2021-10-07 06:00 | 2021-10-07 14:20 | 80 | 008:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ROTO SE ABRIO CORTE DE LINEA PARA REPARAR | M21100700004 | New_Event | Wire Down | Include | Include | Equipment | 500 | 2021-10-07 | 40000 | keep | 0 | Oct | 2021 | 0.027244 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-10-07 06:08 | 2021-10-07 14:00 | 300 | 007:52 | P | DESCONECTIVO DEFECTUOSO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS Y SE REMPLAZO MACHETE AVERIADO A LA SALIDA DEL ALIMENTADOR | A21100700001 | New_Event | Switch Failure | Include | Include | Equipment | 472 | 2021-10-07 | 141600 | keep | 0 | Oct | 2021 | 0.096443 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
FAJARDO | 2021-10-07 06:11 | 2021-10-07 11:14 | 7 | 005:03 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21100700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2021-10-07 | 2121 | keep | 0 | Oct | 2021 | 0.0014446 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-10-07 06:27 | 2021-10-07 11:44 | 80 | 005:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C21100700010 | New_Event |  |  | Include | Wildlife | 317 | 2021-10-07 | 25360 | keep | 0 | Oct | 2021 | 0.017273 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-07 06:47 | 2021-10-07 10:26 | 90 | 003:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21100700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-10-07 | 19710 | keep | 0 | Oct | 2021 | 0.013424 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-07 06:49 | 2021-10-07 16:49 | 100 | 010:00 | P | MAL TIEMPO/RAYOS/WET ASH | 11 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100700010 | New_Event | Bad Weather | Include | Include | Weather | 600 | 2021-10-07 | 60000 | keep | 0 | Oct | 2021 | 0.040866 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-07 07:00 | 2021-10-07 13:59 | 50 | 006:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 20 EN CORTES DE LINEA SE RETIRO AVE | B21100700003 | New_Event |  |  | Include | Wildlife | 419 | 2021-10-07 | 20950 | keep | 0 | Oct | 2021 | 0.014269 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-07 07:42 | 2021-10-07 07:44 | 1802 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21060700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-07 | 3604 | keep | 0 | Oct | 2021 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-10-07 07:42 | 2021-10-08 14:00 | 100 | 030:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU Y 1 X 20 EN RISER | B21100700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1818 | 2021-10-07 | 181800 | keep | 0 | Oct | 2021 | 0.12382 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-10-07 08:08 | 2021-10-07 08:09 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 3597 | keep | 0 | Oct | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
AGUADILLA | 2021-10-07 08:16 | 2021-10-08 10:50 | 10 | 026:34 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1594 | 2021-10-07 | 15940 | keep | 0 | Oct | 2021 | 0.010857 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-07 08:17 | 2021-10-07 08:18 | 1615 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | R21100700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-07 | 1615 | keep | 0 | Oct | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-10-07 08:18 | 2021-10-07 16:28 | 15 | 008:10 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21100700031 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 490 | 2021-10-07 | 7350 | keep | 0 | Oct | 2021 | 0.0050061 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-07 08:45 | 2021-10-07 10:21 | 15 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21100700015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2021-10-07 | 1440 | keep | 0 | Oct | 2021 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-07 09:25 | 2021-10-08 11:39 | 11 | 026:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21100700137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1574 | 2021-10-07 | 17314 | keep | 0 | Oct | 2021 | 0.011792 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-10-07 09:37 | 2021-10-07 18:49 | 15 | 009:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21100700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 552 | 2021-10-07 | 8280 | keep | 0 | Oct | 2021 | 0.0056395 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-07 09:39 | 2021-10-07 14:43 | 13 | 005:04 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SECUNDARIO Y TRANSFORMADOR 25KVA POR 25KVA A 4KV | S21100700000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 304 | 2021-10-07 | 3952 | keep | 0 | Oct | 2021 | 0.0026917 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-10-07 09:39 | 2021-10-07 13:33 | 3 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21100700044 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-10-07 | 702 | keep | 0 | Oct | 2021 | 0.00047813 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-10-07 09:41 | 2021-10-07 17:03 | 8 | 007:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21100700023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 442 | 2021-10-07 | 3536 | keep | 0 | Oct | 2021 | 0.0024084 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-10-07 09:43 | 2021-10-07 17:32 | 250 | 007:49 | P | DESGANCHE | 1 X 40 Y 2 X 80 EN CORTES DE LINEAS | R21100700021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 469 | 2021-10-07 | 117250 | keep | 0 | Oct | 2021 | 0.079858 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-10-07 09:46 | 2021-10-07 12:40 | 200 | 002:54 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21100700022 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 174 | 2021-10-07 | 34800 | keep | 0 | Oct | 2021 | 0.023702 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-10-07 09:48 | 2021-10-07 16:36 | 20 | 006:48 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21100700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2021-10-07 | 8160 | keep | 0 | Oct | 2021 | 0.0055577 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-07 09:56 | 2021-10-07 12:10 | 30 | 002:14 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE SECCIONALIZO AVERIA DE POSTE SECUNDARIO PARTIDO | M21100700050 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 134 | 2021-10-07 | 4020 | keep | 0 | Oct | 2021 | 0.002738 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-07 09:59 | 2021-10-08 11:59 | 10 | 025:60 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21100700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1560 | 2021-10-07 | 15600 | keep | 0 | Oct | 2021 | 0.010625 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-07 10:24 | 2021-10-07 10:25 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-01 Y 1346-06 QUE ESTAN POR INTERRUPTOR 1303-04 Y SE CERRO POR SCADA | S21100700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 1681 | keep | 0 | Oct | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-07 10:24 | 2021-10-07 10:25 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-01 Y 1346-06 QUE ESTAN POR INTERRUPTOR 1303-04 Y SE CERRO POR SCADA | S21100700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 1598 | keep | 0 | Oct | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2021-10-07 10:26 | 2021-10-07 11:52 | 20 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFROMADOR Y SE REPARARON CONEXIONES EN BAJANTE SECUNDARIO | A21100500051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-10-07 | 1720 | keep | 0 | Oct | 2021 | 0.0011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-10-07 10:27 | 2021-10-07 17:23 | 100 | 006:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEAS SE REPARO ALAMBRE PRIMARIO PARTIDO Y SE REMPLAZO 3 CAJAS PRIMARIAS EN CORTE DE LINEAS | P21100700028 | New_Event | Wire Down | Include | Include | Equipment | 416 | 2021-10-07 | 41600 | keep | 0 | Oct | 2021 | 0.028334 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-07 10:29 | 2021-10-08 09:40 | 3 | 023:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO | C21100070031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1391 | 2021-10-07 | 4173 | keep | 0 | Oct | 2021 | 0.0028422 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-10-07 10:33 | 2021-10-07 16:38 | 10 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO PUENTE | C21100700033 | New_Event | Wire Down | Include | Include | Equipment | 365 | 2021-10-07 | 3650 | keep | 0 | Oct | 2021 | 0.002486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-07 10:39 | 2021-10-07 12:06 | 1 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSCLOSURE Y 1 X 50 EN RISER | B21100700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-10-07 | 87 | keep | 0 | Oct | 2021 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-07 10:40 | 2021-10-08 11:37 | 5 | 024:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO TRANSFORMADOR | S21100700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1497 | 2021-10-07 | 7485 | keep | 0 | Oct | 2021 | 0.005098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-07 10:40 | 2021-10-08 16:31 | 6 | 029:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO BUSHING Y PISTOLA AVERIADA EN T-84 | C21100700090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1791 | 2021-10-07 | 10746 | keep | 0 | Oct | 2021 | 0.0073191 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-07 11:03 | 2021-10-08 14:39 | 25 | 027:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE | S21100700035 | New_Event | Wire Down | Include | Include | Equipment | 1656 | 2021-10-07 | 41400 | keep | 0 | Oct | 2021 | 0.028197 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-07 11:14 | 2021-10-07 18:15 | 50 | 007:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21100700077 | New_Event | Cutout Failure | Include | Include | Equipment | 421 | 2021-10-07 | 21050 | keep | 0 | Oct | 2021 | 0.014337 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-07 11:45 | 2021-10-07 11:56 | 2 | 000:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO | C21100600034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 11 | 2021-10-07 | 22 | keep | 0 | Oct | 2021 | 1.4984e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-10-07 11:54 | 2021-10-07 15:38 | 15 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | P21100700037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2021-10-07 | 3360 | keep | 0 | Oct | 2021 | 0.0022885 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-07 12:00 | 2021-10-07 17:10 | 50 | 005:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100700030 | New_Event | Bad Weather | Include | Include | Weather | 310 | 2021-10-07 | 15500 | keep | 0 | Oct | 2021 | 0.010557 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-07 12:01 | 2021-10-07 15:27 | 10 | 003:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21100700039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 206 | 2021-10-07 | 2060 | keep | 0 | Oct | 2021 | 0.0014031 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-10-07 12:09 | 2021-10-07 17:00 | 50 | 004:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PRIMARIO | P21100700042 | New_Event | Wire Down | Include | Include | Equipment | 291 | 2021-10-07 | 14550 | keep | 0 | Oct | 2021 | 0.0099099 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-07 12:16 | 2021-10-07 12:17 | 790 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21100700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 790 | keep | 0 | Oct | 2021 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
ARECIBO | 2021-10-07 12:20 | 2021-10-07 13:47 | 12 | 001:27 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL SOTERRADO | A21100700031 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 87 | 2021-10-07 | 1044 | keep | 0 | Oct | 2021 | 0.00071106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-10-07 12:22 | 2021-10-07 13:31 | 2 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21100700032 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2021-10-07 | 138 | keep | 0 | Oct | 2021 | 9.3991e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-07 12:34 | 2021-10-07 18:57 | 15 | 006:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21100700034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 383 | 2021-10-07 | 5745 | keep | 0 | Oct | 2021 | 0.0039129 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-10-07 12:50 | 2021-10-07 17:10 | 50 | 004:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE SUBIO CONDUCTOR PRIMARIO | B21100700046 | New_Event | Wire Down | Include | Include | Equipment | 260 | 2021-10-07 | 13000 | keep | 0 | Oct | 2021 | 0.0088542 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-07 12:53 | 2021-10-07 15:15 | 15 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21100700036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-10-07 | 2130 | keep | 0 | Oct | 2021 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-07 12:59 | 2021-10-08 14:57 | 8 | 025:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES EN SECUNDARIA | C21100700047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1558 | 2021-10-07 | 12464 | keep | 0 | Oct | 2021 | 0.0084892 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-07 13:05 | 2021-10-07 14:40 | 20 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100700098 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-10-07 | 1900 | keep | 0 | Oct | 2021 | 0.0012941 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-07 13:10 | 2021-10-07 18:25 | 11 | 005:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO POSTE IMPACTADO POR CAMION | R21100700056 | New_Event |  |  | Include | Wildlife | 315 | 2021-10-07 | 3465 | keep | 0 | Oct | 2021 | 0.00236 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-10-07 13:16 | 2021-10-07 16:39 | 9 | 003:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA ABIERTA | C21100700049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 203 | 2021-10-07 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-10-07 13:31 | 2021-10-07 14:44 | 1 | 001:13 | P | OTRAS CAUSAS | PROBLEMA INTERNO DEL CLIENTE | M21100700100 | New_Event | Other Causes | Include | Include | Other | 73 | 2021-10-07 | 73 | keep | 0 | Oct | 2021 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-07 13:35 | 2021-10-07 16:18 | 3511 | 002:43 | T | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA AL 1719-15 Y AL 1710-05 DEBIDO A QUE EL 9405-05 PROBO MALO CON SU RISER DE SALIDA ABIERTO | B21100800063 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 163 | 2021-10-07 | 572293 | keep | 0 | Oct | 2021 | 0.38979 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
CAGUAS | 2021-10-07 13:44 | 2021-10-07 17:17 | 55 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEA | C21100700053 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-10-07 | 11715 | keep | 0 | Oct | 2021 | 0.007979 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
VEGA BAJA | 2021-10-07 13:51 | 2021-10-07 20:05 | 7 | 006:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21100700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 374 | 2021-10-07 | 2618 | keep | 0 | Oct | 2021 | 0.0017831 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-10-07 14:01 | 2021-10-08 09:49 | 3 | 019:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR LLUVIAS | R21100700061 | New_Event | Bad Weather | Include | Include | Weather | 1188 | 2021-10-07 | 3564 | keep | 0 | Oct | 2021 | 0.0024274 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2021-10-07 14:09 | 2021-10-07 16:25 | 10 | 002:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDAIA | P21100700052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 136 | 2021-10-07 | 1360 | keep | 0 | Oct | 2021 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-07 14:20 | 2021-10-07 15:24 | 150 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | M21100700004 | New_Event | Wire Down | Include | Include | Equipment | 64 | 2021-10-07 | 9600 | keep | 0 | Oct | 2021 | 0.0065385 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-10-07 14:29 | 2021-10-08 10:30 | 70 | 020:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100700063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1201 | 2021-10-07 | 84070 | keep | 0 | Oct | 2021 | 0.05726 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
FAJARDO | 2021-10-07 14:53 | 2021-10-07 17:17 | 95 | 002:24 | P | DESGANCHE | 2 X 40 Y 2 X 50 EN CORTES DE LINEAS | R21100700065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-10-07 | 13680 | keep | 0 | Oct | 2021 | 0.0093174 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-10-07 15:09 | 2021-10-07 15:40 | 30 | 000:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 5 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100700084 | New_Event | Bad Weather | Include | Include | Weather | 31 | 2021-10-07 | 930 | keep | 0 | Oct | 2021 | 0.00063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-10-07 15:15 | 2021-10-07 15:47 | 8 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO EN PEDESTAL | B21100500235 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-10-07 | 256 | keep | 0 | Oct | 2021 | 0.00017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-10-07 15:21 | 2021-10-07 17:55 | 10 | 002:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21100700067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 154 | 2021-10-07 | 1540 | keep | 0 | Oct | 2021 | 0.0010489 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-07 15:24 | 2021-10-08 11:45 | 10 | 020:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21100700060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1221 | 2021-10-07 | 12210 | keep | 0 | Oct | 2021 | 0.0083162 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-07 15:27 | 2021-10-07 16:52 | 60 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21100700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2021-10-07 | 5100 | keep | 0 | Oct | 2021 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-07 15:29 | 2021-10-07 17:03 | 8 | 001:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100700027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 94 | 2021-10-07 | 752 | keep | 0 | Oct | 2021 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-07 15:34 | 2021-10-07 18:41 | 50 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100700130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-10-07 | 9350 | keep | 0 | Oct | 2021 | 0.0063682 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-07 15:54 | 2021-10-07 18:01 | 15 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21100700048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2021-10-07 | 1905 | keep | 0 | Oct | 2021 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-10-07 15:54 | 2021-10-07 15:55 | 6 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21100700034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-10-07 | 6 | keep | 0 | Oct | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-10-07 15:57 | 2021-10-07 15:58 | 3041 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21100700129 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-07 | 3041 | keep | 0 | Oct | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
VEGA BAJA | 2021-10-07 15:57 | 2021-10-08 16:41 | 6 | 024:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100700026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1484 | 2021-10-07 | 8904 | keep | 0 | Oct | 2021 | 0.0060645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-07 15:58 | 2021-10-07 21:35 | 100 | 005:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | R21100700076 | New_Event | Bad Weather | Include | Include | Weather | 337 | 2021-10-07 | 33700 | keep | 0 | Oct | 2021 | 0.022953 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-07 16:03 | 2021-10-07 16:04 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21100700131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
HUMACAO | 2021-10-07 16:25 | 2021-10-08 14:16 | 50 | 021:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C21100700073 | New_Event | Cutout Failure | Include | Include | Equipment | 1311 | 2021-10-07 | 65550 | keep | 0 | Oct | 2021 | 0.044646 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 1405 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 37935 | keep | 0 | Oct | 2021 | 0.025837 | 0.00095694 | Sustained | FALSE | TRUE | Not_TMED_Event | 1405
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 669 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 18063 | keep | 0 | Oct | 2021 | 0.012303 | 0.00045565 | Sustained | FALSE | TRUE | Not_TMED_Event | 669
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 1527 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 41229 | keep | 0 | Oct | 2021 | 0.028081 | 0.00104 | Sustained | FALSE | TRUE | Not_TMED_Event | 1527
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 1054 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 28458 | keep | 0 | Oct | 2021 | 0.019383 | 0.00071787 | Sustained | FALSE | TRUE | Not_TMED_Event | 1054
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 932 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 25164 | keep | 0 | Oct | 2021 | 0.017139 | 0.00063478 | Sustained | FALSE | TRUE | Not_TMED_Event | 932
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 705 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 19035 | keep | 0 | Oct | 2021 | 0.012965 | 0.00048017 | Sustained | FALSE | TRUE | Not_TMED_Event | 705
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 1521 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 41067 | keep | 0 | Oct | 2021 | 0.027971 | 0.0010359 | Sustained | FALSE | TRUE | Not_TMED_Event | 1521
UTUADO | 2021-10-07 16:26 | 2021-10-07 16:53 | 882 | 000:27 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2400 | A21100700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-10-07 | 23814 | keep | 0 | Oct | 2021 | 0.01622 | 0.00060073 | Sustained | FALSE | TRUE | Not_TMED_Event | 882
BAYAMON | 2021-10-07 16:41 | 2021-10-07 16:47 | 1825 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL CARGA POR EL 1118-09 | S21100700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-07 | 10950 | keep | 0 | Oct | 2021 | 0.007458 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2021-10-07 16:41 | 2021-10-07 16:47 | 4398 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA EL 1118-08 | S21100700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-07 | 26388 | keep | 0 | Oct | 2021 | 0.017973 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
UTUADO | 2021-10-07 16:53 | 2021-10-07 21:16 | 60 | 004:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21100700053 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2021-10-07 | 15780 | keep | 0 | Oct | 2021 | 0.010748 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-07 17:00 | 2021-10-07 23:58 | 225 | 006:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 SE CERRO PUENTE DE LINEA A TRONCAL Y SE REMPLAZO MACHETE | S21100700000 | New_Event | Wire Down | Include | Include | Equipment | 418 | 2021-10-07 | 94050 | keep | 0 | Oct | 2021 | 0.064057 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
SAN JUAN | 2021-10-07 17:00 | 2021-10-07 21:48 | 870 | 004:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO PUENTE DE LINEA TRONCAL Y SE REMPLAZO MACHETE | S21100700000 | New_Event | Wire Down | Include | Include | Equipment | 288 | 2021-10-07 | 250560 | keep | 0 | Oct | 2021 | 0.17066 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
SAN JUAN | 2021-10-07 17:03 | 2021-10-08 10:49 | 10 | 017:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21100700102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1066 | 2021-10-07 | 10660 | keep | 0 | Oct | 2021 | 0.0072605 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-07 17:03 | 2021-10-08 17:20 | 30 | 024:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21100700066 | New_Event | Wire Down | Include | Include | Equipment | 1457 | 2021-10-07 | 43710 | keep | 0 | Oct | 2021 | 0.029771 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-07 17:33 | 2021-10-07 17:34 | 100 | 000:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21100700027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-07 | 100 | keep | 0 | Oct | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-07 17:45 | 2021-10-08 14:15 | 30 | 020:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21100700072 | New_Event | Bad Weather | Include | Include | Weather | 1230 | 2021-10-07 | 36900 | keep | 0 | Oct | 2021 | 0.025132 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-07 17:54 | 2021-10-08 14:13 | 15 | 020:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | A21100700074 | New_Event | Bad Weather | Include | Include | Weather | 1219 | 2021-10-07 | 18285 | keep | 0 | Oct | 2021 | 0.012454 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-10-07 17:55 | 2021-10-07 18:50 | 10 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA | R21100700085 | New_Event |  |  | Include | Wildlife | 55 | 2021-10-07 | 550 | keep | 0 | Oct | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-10-07 17:57 | 2021-10-07 21:06 | 3041 | 003:09 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL INTERRUPTOR SE REMPLAZO AISLADOR ROTO EN TRONCAL DEL ALIMENTADOR | M21100700145 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2021-10-07 | 574749 | keep | 0 | Oct | 2021 | 0.39146 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
VEGA BAJA | 2021-10-07 17:57 | 2021-10-08 12:17 | 15 | 018:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 20 EN GABINETE | B21107000174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1100 | 2021-10-07 | 16500 | keep | 0 | Oct | 2021 | 0.011238 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-07 18:06 | 2021-10-07 20:39 | 49 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 100 CORTE DE LINEA | S21100700106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-10-07 | 7497 | keep | 0 | Oct | 2021 | 0.0051062 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
PONCE | 2021-10-07 18:08 | 2021-10-07 18:09 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100700066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 3114 | keep | 0 | Oct | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
SAN JUAN | 2021-10-07 18:18 | 2021-10-07 18:51 | 95 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21100700086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-10-07 | 3135 | keep | 0 | Oct | 2021 | 0.0021352 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-10-07 18:36 | 2021-10-08 10:33 | 10 | 015:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN TRANSFORMADOR POR MAL TIEMPO | M21100700160 | New_Event | Bad Weather | Include | Include | Weather | 957 | 2021-10-07 | 9570 | keep | 0 | Oct | 2021 | 0.0065181 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-07 18:39 | 2021-10-07 19:49 | 12 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21100700091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-10-07 | 840 | keep | 0 | Oct | 2021 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-10-07 18:45 | 2021-10-07 18:46 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21100700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 732 | keep | 0 | Oct | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
BAYAMON | 2021-10-07 18:48 | 2021-10-09 10:41 | 15 | 039:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21100700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2393 | 2021-10-07 | 35895 | keep | 0 | Oct | 2021 | 0.024448 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
FAJARDO | 2021-10-07 18:50 | 2021-10-08 16:05 | 70 | 021:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21100700095 | New_Event | Bad Weather | Include | Include | Weather | 1275 | 2021-10-07 | 89250 | keep | 0 | Oct | 2021 | 0.060788 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-10-07 18:50 | 2021-10-07 18:51 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21100700086 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-10-07 | 2708 | keep | 0 | Oct | 2021 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-10-07 18:51 | 2021-10-08 09:51 | 10 | 015:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA | R21100700085 | 1st_after_momentary |  |  | Include | Wildlife | 900 | 2021-10-07 | 9000 | keep | 0 | Oct | 2021 | 0.0061299 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-10-07 18:51 | 2021-10-07 20:23 | 300 | 001:32 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | R21100700101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-10-07 | 27600 | keep | 0 | Oct | 2021 | 0.018798 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CANOVANAS | 2021-10-07 19:10 | 2021-10-07 21:38 | 70 | 002:28 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTES DE LINEAS | R21100700104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2021-10-07 | 10360 | keep | 0 | Oct | 2021 | 0.0070561 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-10-07 19:16 | 2021-10-07 21:01 | 200 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE BREAKER PARA REPARAR BAJANTE EN MACHETE | P21100700070 | New_Event | Wire Down | Include | Include | Equipment | 105 | 2021-10-07 | 21000 | keep | 0 | Oct | 2021 | 0.014303 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-10-07 19:20 | 2021-10-08 09:50 | 50 | 014:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21100700116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 870 | 2021-10-07 | 43500 | keep | 0 | Oct | 2021 | 0.029628 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-07 19:20 | 2021-10-07 21:35 | 25 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21100700184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-10-07 | 3375 | keep | 0 | Oct | 2021 | 0.0022987 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-10-07 19:23 | 2021-10-08 13:46 | 46 | 018:23 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75 X 75KVA | R21100700119 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1103 | 2021-10-07 | 50738 | keep | 0 | Oct | 2021 | 0.034557 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
PONCE | 2021-10-07 19:23 | 2021-10-07 21:55 | 200 | 002:32 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEAS DESGANCHE | P21100700076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-10-07 | 30400 | keep | 0 | Oct | 2021 | 0.020705 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-07 19:36 | 2021-10-08 10:49 | 50 | 015:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21100700078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 913 | 2021-10-07 | 45650 | keep | 0 | Oct | 2021 | 0.031092 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-07 19:45 | 2021-10-07 23:09 | 2343 | 003:24 | S | BREAKER DEFECTUOSO O NO OPERA | SE LE RETIRO LA CARGA A LA SUBESTACION SE ENCONTRO BUSHING EN EL 2201-04 AVERIADO, AISLADOR ROTO EN BARRA Y DOS FUSIBLES FUNDIDO EN EL 38 KV | R21100700181 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 204 | 2021-10-07 | 477972 | keep | 0 | Oct | 2021 | 0.32554 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2021-10-07 19:45 | 2021-10-07 23:09 | 1830 | 003:24 | S | BREAKER DEFECTUOSO O NO OPERA | SE LE RETIRO LA CARGA A LA SUBESTACION SE ENCONTRO BUSHING EN EL 2201-04 AVERIADO, AISLADOR ROTO EN BARRA Y DOS FUSIBLES FUNDIDO EN EL 38 KV | R21100700181 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 204 | 2021-10-07 | 373320 | keep | 0 | Oct | 2021 | 0.25427 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2021-10-07 19:45 | 2021-10-07 23:09 | 710 | 003:24 | S | BREAKER DEFECTUOSO O NO OPERA | SE LE RETIRO LA CARGA A LA SUBESTACION SE ENCONTRO BUSHING EN EL 2201-04 AVERIADO, AISLADOR ROTO EN BARRA Y DOS FUSIBLES FUNDIDO EN EL 38 KV | R21100700181 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 204 | 2021-10-07 | 144840 | keep | 0 | Oct | 2021 | 0.09865 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2021-10-07 19:45 | 2021-10-07 23:09 | 969 | 003:24 | S | BREAKER DEFECTUOSO O NO OPERA | SE LE RETIRO LA CARGA A LA SUBESTACION SE ENCONTRO BUSHING EN EL 2201-04 AVERIADO, AISLADOR ROTO EN BARRA Y DOS FUSIBLES FUNDIDO EN EL 38 KV | R21100700181 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 204 | 2021-10-07 | 197676 | keep | 0 | Oct | 2021 | 0.13464 | 0.00065998 | Sustained | FALSE | FALSE | Not_TMED_Event | 969
BAYAMON | 2021-10-07 20:17 | 2021-10-08 10:35 | 60 | 014:18 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21100700156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 858 | 2021-10-07 | 51480 | keep | 0 | Oct | 2021 | 0.035063 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-10-07 20:19 | 2021-10-07 20:50 | 150 | 000:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100700179 | New_Event | Bad Weather | Include | Include | Weather | 31 | 2021-10-07 | 4650 | keep | 0 | Oct | 2021 | 0.0031671 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-07 20:21 | 2021-10-08 11:31 | 30 | 015:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100700180 | New_Event | Bad Weather | Include | Include | Weather | 910 | 2021-10-07 | 27300 | keep | 0 | Oct | 2021 | 0.018594 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-07 20:31 | 2021-10-07 20:57 | 3 | 000:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21100700079 | New_Event | Bad Weather | Include | Include | Weather | 26 | 2021-10-07 | 78 | keep | 0 | Oct | 2021 | 5.3125e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2021-10-07 20:43 | 2021-10-08 11:38 | 144 | 014:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON LAGARTO | R21100700153 | New_Event |  |  | Include | Wildlife | 895 | 2021-10-07 | 128880 | keep | 0 | Oct | 2021 | 0.08778 | 9.8078e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 144
MAYAGÃœEZ | 2021-10-07 20:45 | 2021-10-08 02:50 | 500 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21100700187 | New_Event | Wire Down | Include | Include | Equipment | 365 | 2021-10-07 | 182500 | keep | 0 | Oct | 2021 | 0.1243 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
FAJARDO | 2021-10-07 20:53 | 2021-10-08 08:47 | 30 | 011:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | R21100700176 | New_Event | Bad Weather | Include | Include | Weather | 714 | 2021-10-07 | 21420 | keep | 0 | Oct | 2021 | 0.014589 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-07 21:02 | 2021-10-08 14:08 | 50 | 017:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100700188 | New_Event | Bad Weather | Include | Include | Weather | 1026 | 2021-10-07 | 51300 | keep | 0 | Oct | 2021 | 0.03494 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-07 21:14 | 2021-10-07 21:15 | 2751 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN MACHETE NO FUNDIO FUSIBLE | P21100700101 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-07 | 2751 | keep | 0 | Oct | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
FAJARDO | 2021-10-07 21:18 | 2021-10-08 10:39 | 16 | 013:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | R21100700180 | New_Event | Bad Weather | Include | Include | Weather | 801 | 2021-10-07 | 12816 | keep | 0 | Oct | 2021 | 0.0087289 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-10-07 21:38 | 2021-10-08 12:16 | 5 | 014:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100700199 | New_Event | Bad Weather | Include | Include | Weather | 878 | 2021-10-07 | 4390 | keep | 0 | Oct | 2021 | 0.00299 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-07 21:48 | 2021-10-07 23:58 | 770 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL Y SE REMPLAZO MACHETE | S21100700000 | Partial_restoration | Wire Down | Include | Include | Equipment | 130 | 2021-10-07 | 100100 | keep | 0 | Oct | 2021 | 0.068178 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-07 21:55 | 2021-10-08 14:00 | 150 | 016:05 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21100700253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 965 | 2021-10-07 | 144750 | keep | 0 | Oct | 2021 | 0.098589 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-07 21:55 | 2021-10-08 11:20 | 200 | 013:25 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | A21100700091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 805 | 2021-10-07 | 161000 | keep | 0 | Oct | 2021 | 0.10966 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-07 22:08 | 2021-10-08 09:18 | 50 | 011:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN AEREO PROVISIONAL | S21100700213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 670 | 2021-10-07 | 33500 | keep | 0 | Oct | 2021 | 0.022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-07 22:15 | 2021-10-08 10:40 | 50 | 012:25 | P | TRANSFORMADOR AVERIADO | BUSHING Y PISTOLA QUEMADOS EN T84 SE CERRO N/O EN T83 | C21100800090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 745 | 2021-10-07 | 37250 | keep | 0 | Oct | 2021 | 0.025371 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-07 22:29 | 2021-10-08 11:45 | 150 | 013:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21100700205 | New_Event | Cutout Failure | Include | Include | Equipment | 796 | 2021-10-07 | 119400 | keep | 0 | Oct | 2021 | 0.081323 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-07 22:45 | 2021-10-08 10:26 | 80 | 011:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21100700225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 701 | 2021-10-07 | 56080 | keep | 0 | Oct | 2021 | 0.038196 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-07 23:13 | 2021-10-07 23:14 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21100700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-07 | 199 | keep | 0 | Oct | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
AGUADILLA | 2021-10-07 23:27 | 2021-10-08 14:55 | 15 | 015:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100700209 | New_Event | Bad Weather | Include | Include | Weather | 928 | 2021-10-07 | 13920 | keep | 0 | Oct | 2021 | 0.0094808 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-08 00:37 | 2021-10-08 16:33 | 10 | 015:56 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR | S21100700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2021-10-08 | 9560 | keep | 0 | Oct | 2021 | 0.0065113 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-08 00:40 | 2021-10-08 16:06 | 12 | 015:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE CONECTO SECUNDARIA Y REEMPLAZO POSTE SECUNDARIO ROTO | R21100800002 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 926 | 2021-10-08 | 11112 | keep | 0 | Oct | 2021 | 0.0075683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-08 00:47 | 2021-10-08 10:06 | 40 | 009:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 Y 1 X 30 EN TRANSFORMADOR Y CORTE DE LINEA CRUCE CON AVE | R21100700061 | New_Event |  |  | Include | Wildlife | 559 | 2021-10-08 | 22360 | keep | 0 | Oct | 2021 | 0.015229 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-10-08 01:20 | 2021-10-08 10:24 | 90 | 009:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R21100800005 | New_Event |  |  | Include | Wildlife | 544 | 2021-10-08 | 48960 | keep | 0 | Oct | 2021 | 0.033346 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
FAJARDO | 2021-10-08 03:53 | 2021-10-08 03:54 | 1234 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | R21100800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-08 | 1234 | keep | 0 | Oct | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
MAYAGÃœEZ | 2021-10-08 03:53 | 2021-10-08 13:47 | 12 | 009:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100800010 | New_Event | Bad Weather | Include | Include | Weather | 594 | 2021-10-08 | 7128 | keep | 0 | Oct | 2021 | 0.0048548 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-10-08 03:54 | 2021-10-08 11:37 | 1 | 007:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA LLUVIAS | R21100800048 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 463 | 2021-10-08 | 463 | keep | 0 | Oct | 2021 | 0.00031535 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-08 06:28 | 2021-10-08 12:57 | 30 | 006:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | B21100800005 | New_Event | Cutout Failure | Include | Include | Equipment | 389 | 2021-10-08 | 11670 | keep | 0 | Oct | 2021 | 0.0079484 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-08 06:53 | 2021-10-08 11:32 | 200 | 004:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIAS | R21100800023 | New_Event | Bad Weather | Include | Include | Weather | 279 | 2021-10-08 | 55800 | keep | 0 | Oct | 2021 | 0.038005 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-08 06:56 | 2021-10-08 13:04 | 25 | 006:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2021-10-08 | 9200 | keep | 0 | Oct | 2021 | 0.0062661 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-08 06:57 | 2021-10-08 11:43 | 800 | 004:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO EN TRONCAL | S21100800007 | New_Event | Wire Down | Include | Include | Equipment | 286 | 2021-10-08 | 228800 | keep | 0 | Oct | 2021 | 0.15583 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2021-10-08 06:57 | 2021-10-08 07:58 | 1843 | 001:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR CONDUCTOR EN EL SUELO | C21100800007 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2021-10-08 | 112423 | keep | 0 | Oct | 2021 | 0.076571 | 0.0012553 | Sustained | FALSE | FALSE | Not_TMED_Event | 1843
BAYAMON | 2021-10-08 07:03 | 2021-10-08 07:04 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA 1711 05 | B21100800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 723 | keep | 0 | Oct | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-10-08 07:03 | 2021-10-08 07:04 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1711 02 | B21100800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 1976 | keep | 0 | Oct | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
PONCE | 2021-10-08 07:26 | 2021-10-08 12:45 | 22 | 005:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P21100800006 | New_Event | Bad Weather | Include | Include | Weather | 319 | 2021-10-08 | 7018 | keep | 0 | Oct | 2021 | 0.0047799 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2021-10-08 07:27 | 2021-10-08 15:30 | 6 | 008:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 25 KVA | M21100800019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 483 | 2021-10-08 | 2898 | keep | 0 | Oct | 2021 | 0.0019738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-10-08 07:30 | 2021-10-08 07:31 | 693 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 693 | keep | 0 | Oct | 2021 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
CANOVANAS | 2021-10-08 07:39 | 2021-10-08 10:51 | 400 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 2 X 100 EN CORTE DE LINEA LLUVIAS | R21100800026 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-10-08 | 76800 | keep | 0 | Oct | 2021 | 0.052308 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CAGUAS | 2021-10-08 07:58 | 2021-10-08 14:03 | 300 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO NO CERRO ORDENES | C21100800011 | Partial_restoration | Wire Down | Include | Include | Equipment | 365 | 2021-10-08 | 109500 | keep | 0 | Oct | 2021 | 0.07458 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-08 07:58 | 2021-10-08 09:16 | 75 | 001:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2021-10-08 | 5850 | keep | 0 | Oct | 2021 | 0.0039844 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-10-08 07:59 | 2021-10-08 12:08 | 200 | 004:09 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P21100800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-10-08 | 49800 | keep | 0 | Oct | 2021 | 0.033919 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-08 08:17 | 2021-10-08 08:18 | 3431 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A21100800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-08 | 3431 | keep | 0 | Oct | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-10-08 08:18 | 2021-10-08 12:22 | 100 | 004:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A21100800027 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-10-08 | 24400 | keep | 0 | Oct | 2021 | 0.016619 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-08 08:19 | 2021-10-08 15:41 | 200 | 007:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21100800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 442 | 2021-10-08 | 88400 | keep | 0 | Oct | 2021 | 0.060209 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-08 08:19 | 2021-10-08 11:20 | 14 | 003:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA X 37.5KVA. MARCA HOWARD. 2400/4160V 120/240V. SER:2055094529 FID:19927905 | A21100800009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2021-10-08 | 2534 | keep | 0 | Oct | 2021 | 0.0017259 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2021-10-08 08:23 | 2021-10-08 15:51 | 6 | 007:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 448 | 2021-10-08 | 2688 | keep | 0 | Oct | 2021 | 0.0018308 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-10-08 08:28 | 2021-10-08 12:42 | 425 | 004:14 | T | ERROR HUMANO | DISPARO INTERRUPTOR SE CERRO EN SUBESTACION PERSONAL TRABAJANDO DESGANCHE LINEA 2200 DISPARO ALIMENTADOR LLEVA CARGA 9404 02 | B21100800022 | New_Event | Human Error | Include | Include | Other | 254 | 2021-10-08 | 107950 | keep | 0 | Oct | 2021 | 0.073524 | 0.00028947 | Sustained | FALSE | TRUE | Not_TMED_Event | 425
BAYAMON | 2021-10-08 08:33 | 2021-10-08 12:16 | 10 | 003:43 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PAARA REMPLAZAR POSTE SECUNDARIO PARTIDO Y REALIZAR CAMBIO DE LINEAS SECUNDARIAS | B21100800021 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 223 | 2021-10-08 | 2230 | keep | 0 | Oct | 2021 | 0.0015188 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-10-08 08:40 | 2021-10-08 16:25 | 4 | 007:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO LINEA SECUNDARIA Y CONECTORES | M21100800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 465 | 2021-10-08 | 1860 | keep | 0 | Oct | 2021 | 0.0012668 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
VEGA BAJA | 2021-10-08 08:44 | 2021-10-08 09:53 | 10 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONECTORES SECUNDARIOS | B21100700050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-10-08 | 690 | keep | 0 | Oct | 2021 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-08 08:50 | 2021-10-08 08:51 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A2110080000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BAYAMON | 2021-10-08 08:52 | 2021-10-08 14:41 | 20 | 005:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM DE 50KVA POR UNO DE 75KVA | B21100300105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 349 | 2021-10-08 | 6980 | keep | 0 | Oct | 2021 | 0.004754 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-08 08:55 | 2021-10-08 18:20 | 25 | 009:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ENDEREZO POSTE IMPACTADO POR VEHICULO Y SE CERRO CORTE DE LINEA | B21100800028 | New_Event |  |  | Include | Wildlife | 565 | 2021-10-08 | 14125 | keep | 0 | Oct | 2021 | 0.0096205 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-08 09:02 | 2021-10-08 09:03 | 534 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1519-05 LLEVANDO EL 1519-01 | S21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 534 | keep | 0 | Oct | 2021 | 0.0003637 | 0.0003637 | Momentary | FALSE | FALSE | Not_TMED_Event | 534
BAYAMON | 2021-10-08 09:02 | 2021-10-08 09:03 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO EL 1519-01 | S21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 558 | keep | 0 | Oct | 2021 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
FAJARDO | 2021-10-08 09:04 | 2021-10-08 11:04 | 100 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTES DE LINEA LLUVIAS | R21100800040 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-10-08 | 12000 | keep | 0 | Oct | 2021 | 0.0081731 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-08 09:04 | 2021-10-08 09:05 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A2110080000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BAYAMON | 2021-10-08 09:05 | 2021-10-08 09:06 | 150 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PARTE DE LA CARGA POR 1718-03 | B21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 150 | keep | 0 | Oct | 2021 | 0.00010216 | 0.00010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-10-08 09:05 | 2021-10-08 09:06 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE DE LA CARGA 1710 05 | B21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 2605 | keep | 0 | Oct | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
CAGUAS | 2021-10-08 09:23 | 2021-10-08 11:38 | 6 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO | C21100800025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2021-10-08 | 810 | keep | 0 | Oct | 2021 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-10-08 09:24 | 2021-10-08 18:50 | 8 | 009:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO BUSHING SECUNDARIO A TRANSFORMADOR Y SE REALIZO DESGANCHE | A21100800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 566 | 2021-10-08 | 4528 | keep | 0 | Oct | 2021 | 0.003084 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-10-08 09:33 | 2021-10-08 10:45 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21100700158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-10-08 | 720 | keep | 0 | Oct | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-08 09:40 | 2021-10-08 11:30 | 100 | 001:50 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | A21100800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-10-08 | 11000 | keep | 0 | Oct | 2021 | 0.007492 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-08 09:50 | 2021-10-08 11:25 | 50 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA POR NEUTRAL COMUN EN EL SUELO Y SE SACO ARBOL SOBRE LINEAS NO FUNDIO FUSIBLE | P21100800014 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2021-10-08 | 4750 | keep | 0 | Oct | 2021 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-08 10:09 | 2021-10-08 11:01 | 5 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21100800044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2021-10-08 | 260 | keep | 0 | Oct | 2021 | 0.00017708 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-10-08 10:10 | 2021-10-08 11:48 | 1 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S21100700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2021-10-08 | 98 | keep | 0 | Oct | 2021 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-08 10:20 | 2021-10-09 12:27 | 10 | 026:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO BAJANTE SECUNDARIO | S21100800049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1567 | 2021-10-08 | 15670 | keep | 0 | Oct | 2021 | 0.010673 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-08 10:20 | 2021-10-08 11:28 | 6 | 001:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21100700140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 68 | 2021-10-08 | 408 | keep | 0 | Oct | 2021 | 0.00027789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-08 10:34 | 2021-10-08 14:25 | 6 | 003:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50 KVA POR UNO DE 50 KVA | M21100800055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 231 | 2021-10-08 | 1386 | keep | 0 | Oct | 2021 | 0.000944 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-10-08 10:43 | 2021-10-08 11:44 | 2 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C21100800032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-10-08 | 122 | keep | 0 | Oct | 2021 | 8.3094e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2021-10-08 10:53 | 2021-10-08 15:12 | 100 | 004:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER DE SALIDA AVE CRUZO FASE | P21100800051 | New_Event |  |  | Include | Wildlife | 259 | 2021-10-08 | 25900 | keep | 0 | Oct | 2021 | 0.01764 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-10-08 11:00 | 2021-10-08 12:15 | 10 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN PEDESTAL | P21100800035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-10-08 | 750 | keep | 0 | Oct | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-08 11:10 | 2021-10-08 14:16 | 15 | 003:06 | P | SECUNDARIA/DESGANCHE | SE DESGANCHO Y REPARO SECUNDARIA | R21100800051 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 186 | 2021-10-08 | 2790 | keep | 0 | Oct | 2021 | 0.0019003 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-08 11:19 | 2021-10-08 12:32 | 10 | 001:13 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIA TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | B21100700034 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 73 | 2021-10-08 | 730 | keep | 0 | Oct | 2021 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-08 11:22 | 2021-10-08 18:02 | 1 | 006:40 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | C21100800035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2021-10-08 | 400 | keep | 0 | Oct | 2021 | 0.00027244 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-08 11:28 | 2021-10-08 12:37 | 3 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN RISER | B21100800035 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2021-10-08 | 207 | keep | 0 | Oct | 2021 | 0.00014099 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-08 11:43 | 2021-10-08 12:55 | 1860 | 001:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE CERRO PUENTE ABIERTO EN TRONCAL | S21081000067 | New_Event | Wire Down | Include | Include | Equipment | 72 | 2021-10-08 | 133920 | keep | 0 | Oct | 2021 | 0.091212 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
UTUADO | 2021-10-08 12:02 | 2021-10-08 16:30 | 10 | 004:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR MAL TIEMPO VIENTOS FUERTES | A21100800039 | New_Event | Bad Weather | Include | Include | Weather | 268 | 2021-10-08 | 2680 | keep | 0 | Oct | 2021 | 0.0018253 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-08 12:17 | 2021-10-08 15:10 | 110 | 002:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21100800043 | New_Event |  |  | Include | Wildlife | 173 | 2021-10-08 | 19030 | keep | 0 | Oct | 2021 | 0.012961 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
GUAYAMA | 2021-10-08 12:26 | 2021-10-08 22:05 | 300 | 009:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | VEHICULO IMPACTA POSTE MADERA 40 PIES PRIMARIO Y LO PARTE SE REMPLAZO CON POSTE METAL 45 PIES | P21100800071 | New_Event |  |  | Include | Wildlife | 579 | 2021-10-08 | 173700 | keep | 0 | Oct | 2021 | 0.11831 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-10-08 12:26 | 2021-10-08 18:05 | 10 | 005:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS Y LINEAS SECUNDARIAS | A21100800042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 339 | 2021-10-08 | 3390 | keep | 0 | Oct | 2021 | 0.0023089 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-08 12:31 | 2021-10-08 12:32 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100800045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 551 | keep | 0 | Oct | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2021-10-08 12:49 | 2021-10-08 16:02 | 1 | 003:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN BANCO DE TRANSFORMADOR CRUCE POR AVE | C21100800048 | New_Event |  |  | Include | Wildlife | 193 | 2021-10-08 | 193 | keep | 0 | Oct | 2021 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-10-08 12:56 | 2021-10-08 17:09 | 80 | 004:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21100800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2021-10-08 | 20240 | keep | 0 | Oct | 2021 | 0.013785 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-08 12:59 | 2021-10-08 15:55 | 3 | 002:56 | P | SOBRECARGA | 1 X 50 EN TRANSFORMADOR | S21100800076 | New_Event | Trip Due To Overload | Include | Include | Other | 176 | 2021-10-08 | 528 | keep | 0 | Oct | 2021 | 0.00035962 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-10-08 13:04 | 2021-10-08 13:05 | 726 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1303-03 DE EMERGENCIA POR AEREO PROVISIONAL VIVO EN EL SUELO SE ABRIO EN CALLE ARROYO QUINTAS DE CUPEY | S21100800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-08 | 726 | keep | 0 | Oct | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-10-08 13:04 | 2021-10-08 13:05 | 3932 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRIPTOR 1303-03 LLEVANDO LA CARGA DEL 1346-04 DE EMERGENCIA PARA SECCIONALIZAR AEREO PROVISIONAL VIVO EN EL SUELO | S21100800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-08 | 3932 | keep | 0 | Oct | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-10-08 13:05 | 2021-10-08 15:13 | 80 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO TRAMO PROVISIONAL | S21100700030 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 128 | 2021-10-08 | 10240 | keep | 0 | Oct | 2021 | 0.0069744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-10-08 13:13 | 2021-10-08 18:00 | 6 | 004:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100800061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 287 | 2021-10-08 | 1722 | keep | 0 | Oct | 2021 | 0.0011728 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-10-08 13:25 | 2021-10-08 16:51 | 130 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS SE RETEZO LINEA PRIMARIA | C21100800050 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2021-10-08 | 26780 | keep | 0 | Oct | 2021 | 0.01824 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
ARECIBO | 2021-10-08 13:29 | 2021-10-08 14:28 | 100 | 000:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A21100800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-10-08 | 5900 | keep | 0 | Oct | 2021 | 0.0040185 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-08 13:37 | 2021-10-08 16:30 | 200 | 002:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M21100800085 | New_Event | Wire Down | Include | Include | Equipment | 173 | 2021-10-08 | 34600 | keep | 0 | Oct | 2021 | 0.023566 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-10-08 13:52 | 2021-10-08 14:47 | 60 | 000:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA DE PROVISIONAL AEREO | R21100800062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-10-08 | 3300 | keep | 0 | Oct | 2021 | 0.0022476 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-08 13:59 | 2021-10-08 14:40 | 30 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21100800068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-10-08 | 1230 | keep | 0 | Oct | 2021 | 0.00083775 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-08 14:04 | 2021-10-08 15:32 | 116 | 001:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21100800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-10-08 | 10208 | keep | 0 | Oct | 2021 | 0.0069526 | 7.9007e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 116
BAYAMON | 2021-10-08 14:17 | 2021-10-08 14:18 | 1264 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21100800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 1264 | keep | 0 | Oct | 2021 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2021-10-08 14:22 | 2021-10-08 15:09 | 6 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100700156 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-10-08 | 282 | keep | 0 | Oct | 2021 | 0.00019207 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-10-08 14:50 | 2021-10-08 16:10 | 44 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AUTO IMPACTO POSTE PRIMARIO | P21100800086 | New_Event |  |  | Include | Wildlife | 80 | 2021-10-08 | 3520 | keep | 0 | Oct | 2021 | 0.0023975 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
MAYAGÃœEZ | 2021-10-08 15:02 | 2021-10-08 16:47 | 3522 | 001:45 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-10-08 | 369810 | keep | 0 | Oct | 2021 | 0.25188 | 0.0023988 | Sustained | FALSE | TRUE | Not_TMED_Event | 3522
MAYAGÃœEZ | 2021-10-08 15:02 | 2021-10-08 16:47 | 1337 | 001:45 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-10-08 | 140385 | keep | 0 | Oct | 2021 | 0.095616 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2021-10-08 15:02 | 2021-10-08 16:47 | 2825 | 001:45 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-10-08 | 296625 | keep | 0 | Oct | 2021 | 0.20203 | 0.0019241 | Sustained | FALSE | TRUE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2021-10-08 15:02 | 2021-10-08 16:47 | 1287 | 001:45 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-10-08 | 135135 | keep | 0 | Oct | 2021 | 0.09204 | 0.00087657 | Sustained | FALSE | TRUE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-10-08 15:02 | 2021-10-08 16:47 | 1417 | 001:45 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-10-08 | 148785 | keep | 0 | Oct | 2021 | 0.10134 | 0.00096511 | Sustained | FALSE | TRUE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-10-08 15:02 | 2021-10-08 16:47 | 80 | 001:45 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-10-08 | 8400 | keep | 0 | Oct | 2021 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-10-08 15:02 | 2021-10-08 17:43 | 1633 | 002:41 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-10-08 | 262913 | keep | 0 | Oct | 2021 | 0.17907 | 0.0011122 | Sustained | FALSE | TRUE | Not_TMED_Event | 1633
UTUADO | 2021-10-08 15:02 | 2021-10-08 17:43 | 1624 | 002:41 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 161 | 2021-10-08 | 261464 | keep | 0 | Oct | 2021 | 0.17808 | 0.0011061 | Sustained | FALSE | TRUE | Not_TMED_Event | 1624
FAJARDO | 2021-10-08 15:23 | 2021-10-08 16:17 | 4 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21100800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2021-10-08 | 216 | keep | 0 | Oct | 2021 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-10-08 15:23 | 2021-10-09 15:57 | 50 | 024:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100800070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1474 | 2021-10-08 | 73700 | keep | 0 | Oct | 2021 | 0.050197 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-08 16:03 | 2021-10-08 17:30 | 1 | 001:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100800123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-10-08 | 87 | keep | 0 | Oct | 2021 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-08 16:27 | 2021-10-08 17:28 | 12 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES SECUNDARIOS | S21100800107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-10-08 | 732 | keep | 0 | Oct | 2021 | 0.00049856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-08 16:30 | 2021-10-08 17:12 | 12 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21100800108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-10-08 | 504 | keep | 0 | Oct | 2021 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-10-08 16:43 | 2021-10-08 19:50 | 200 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21100800144 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-10-08 | 37400 | keep | 0 | Oct | 2021 | 0.025473 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-10-08 16:48 | 2021-10-08 18:13 | 200 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21100800151 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2021-10-08 | 17000 | keep | 0 | Oct | 2021 | 0.011579 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-08 17:13 | 2021-10-08 18:05 | 1 | 000:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO CONECTORES EN LINEA PRIMARIA | M21100800159 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2021-10-08 | 52 | keep | 0 | Oct | 2021 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-10-08 17:15 | 2021-10-08 19:25 | 80 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21100800080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-10-08 | 10400 | keep | 0 | Oct | 2021 | 0.0070834 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-08 17:19 | 2021-10-09 15:16 | 50 | 021:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21100800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1317 | 2021-10-08 | 65850 | keep | 0 | Oct | 2021 | 0.04485 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-08 17:32 | 2021-10-08 18:50 | 8 | 001:18 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21100700168 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 78 | 2021-10-08 | 624 | keep | 0 | Oct | 2021 | 0.000425 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-08 17:37 | 2021-10-08 19:56 | 50 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2021-10-08 | 6950 | keep | 0 | Oct | 2021 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 1405 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 2810 | keep | 0 | Oct | 2021 | 0.0019139 | 0.00095694 | Momentary | FALSE | TRUE | Not_TMED_Event | 1405
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 669 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 1338 | keep | 0 | Oct | 2021 | 0.00091131 | 0.00045565 | Momentary | FALSE | TRUE | Not_TMED_Event | 669
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 1527 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 3054 | keep | 0 | Oct | 2021 | 0.0020801 | 0.00104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1527
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 1054 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 2108 | keep | 0 | Oct | 2021 | 0.0014357 | 0.00071787 | Momentary | FALSE | TRUE | Not_TMED_Event | 1054
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 932 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 1864 | keep | 0 | Oct | 2021 | 0.0012696 | 0.00063478 | Momentary | FALSE | TRUE | Not_TMED_Event | 932
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 705 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 1410 | keep | 0 | Oct | 2021 | 0.00096034 | 0.00048017 | Momentary | FALSE | TRUE | Not_TMED_Event | 705
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 1521 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 3042 | keep | 0 | Oct | 2021 | 0.0020719 | 0.0010359 | Momentary | FALSE | TRUE | Not_TMED_Event | 1521
UTUADO | 2021-10-08 17:41 | 2021-10-08 17:43 | 882 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-08 | 1764 | keep | 0 | Oct | 2021 | 0.0012015 | 0.00060073 | Momentary | FALSE | TRUE | Not_TMED_Event | 882
HUMACAO | 2021-10-08 17:53 | 2021-10-08 19:45 | 190 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C21100800084 | New_Event |  |  | Include | Wildlife | 112 | 2021-10-08 | 21280 | keep | 0 | Oct | 2021 | 0.014494 | 0.00012941 | Sustained | FALSE | TRUE | Not_TMED_Event | 190
BAYAMON | 2021-10-08 18:02 | 2021-10-08 18:03 | 114 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1115-5 | S21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 114 | keep | 0 | Oct | 2021 | 7.7645e-05 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
BAYAMON | 2021-10-08 18:02 | 2021-10-08 18:03 | 867 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1115-5 | S21100800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 867 | keep | 0 | Oct | 2021 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
ARECIBO | 2021-10-08 18:05 | 2021-10-09 11:30 | 25 | 017:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZARON AISLADORES | A21100800087 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1045 | 2021-10-08 | 26125 | keep | 0 | Oct | 2021 | 0.017794 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-08 18:16 | 2021-10-08 18:33 | 5 | 000:17 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO Y SE REPARO SECUNDARIA | S21100600152 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 17 | 2021-10-08 | 85 | keep | 0 | Oct | 2021 | 5.7893e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-10-08 18:25 | 2021-10-08 19:56 | 100 | 001:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA Y SE REMPLAZO AISLADOR | B21100800099 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 91 | 2021-10-08 | 9100 | keep | 0 | Oct | 2021 | 0.006198 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-08 18:53 | 2021-10-08 20:56 | 45 | 002:03 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | S21100800135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-10-08 | 5535 | keep | 0 | Oct | 2021 | 0.0037699 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-10-08 18:59 | 2021-10-08 19:00 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21100800110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-08 | 3387 | keep | 0 | Oct | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
AGUADILLA | 2021-10-08 19:08 | 2021-10-08 19:09 | 1057 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21100800173 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-08 | 1057 | keep | 0 | Oct | 2021 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
MAYAGÃœEZ | 2021-10-08 19:12 | 2021-10-09 13:51 | 4 | 018:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON LINEAS SECUNDARIAS | M21100800174 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1119 | 2021-10-08 | 4476 | keep | 0 | Oct | 2021 | 0.0030486 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-10-08 19:19 | 2021-10-08 21:55 | 200 | 002:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21100800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-10-08 | 31200 | keep | 0 | Oct | 2021 | 0.02125 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-10-08 19:24 | 2021-10-08 19:25 | 1057 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21100800175 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-10-08 | 1057 | keep | 0 | Oct | 2021 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
CANOVANAS | 2021-10-08 19:28 | 2021-10-08 21:39 | 164 | 002:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21100800083 | New_Event |  |  | Include | Wildlife | 131 | 2021-10-08 | 21484 | keep | 0 | Oct | 2021 | 0.014633 | 0.0001117 | Sustained | FALSE | TRUE | Not_TMED_Event | 164
UTUADO | 2021-10-08 19:31 | 2021-10-08 23:00 | 200 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21100800095 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2021-10-08 | 41800 | keep | 0 | Oct | 2021 | 0.02847 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-10-08 19:52 | 2021-10-09 09:08 | 190 | 013:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C21100800084 | Partial_restoration |  |  | Include | Wildlife | 796 | 2021-10-08 | 151240 | keep | 0 | Oct | 2021 | 0.10301 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-08 19:53 | 2021-10-09 12:48 | 5 | 016:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21092600125 | New_Event | Bad Weather | Include | Include | Weather | 1015 | 2021-10-08 | 5075 | keep | 0 | Oct | 2021 | 0.0034566 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-08 19:57 | 2021-10-08 20:17 | 10 | 000:20 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21100800100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-10-08 | 200 | keep | 0 | Oct | 2021 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-08 20:17 | 2021-10-09 12:10 | 12 | 015:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | M21100800187 | New_Event | Secondary Wire Down | Include | Include | Equipment | 953 | 2021-10-08 | 11436 | keep | 0 | Oct | 2021 | 0.007789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-08 20:20 | 2021-10-09 14:56 | 14 | 018:36 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR 50KVA X 50KVA | R21100800133 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1116 | 2021-10-08 | 15624 | keep | 0 | Oct | 2021 | 0.010641 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2021-10-08 20:23 | 2021-10-09 12:34 | 120 | 016:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON CHIRINGA | C21100800134 | New_Event |  |  | Include | Wildlife | 971 | 2021-10-08 | 116520 | keep | 0 | Oct | 2021 | 0.079361 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-10-08 20:34 | 2021-10-08 20:41 | 34 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO L-5900 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-08 | 238 | keep | 0 | Oct | 2021 | 0.0001621 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2021-10-08 20:34 | 2021-10-08 20:41 | 19 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO L-5900 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-08 | 133 | keep | 0 | Oct | 2021 | 9.0586e-05 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2021-10-08 21:11 | 2021-10-09 12:35 | 80 | 015:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21100800167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 924 | 2021-10-08 | 73920 | keep | 0 | Oct | 2021 | 0.050347 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-10-08 21:40 | 2021-10-09 00:05 | 559 | 002:25 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1105-04 PARA REEMPLAZO DE MACHETE DE SALIDA QUEMADO. ADEMAS LLEVA LA CARGA DEL 1105-05 | S21100800123 | New_Event | Switch Failure | Include | Include | Equipment | 145 | 2021-10-08 | 81055 | keep | 0 | Oct | 2021 | 0.055206 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2021-10-08 21:40 | 2021-10-09 00:05 | 370 | 002:25 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1105-04 PARA REEMPLAZO DE MACHETE DE SALIDA QUEMADO CARGA POR EL 1105-04 | S21100800123 | New_Event | Switch Failure | Include | Include | Equipment | 145 | 2021-10-08 | 53650 | keep | 0 | Oct | 2021 | 0.036541 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
PONCE | 2021-10-08 22:01 | 2021-10-09 00:17 | 752 | 002:16 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AVERIA SOTERRADA EN MH-29 CALLE MAYOR Y COMERCIO SE SECCIONALIZO EN MH-29 HACIA MH-24 Y EN MH-29 HACIA MH-31 Y SE REALIZO PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO | P21100800114 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 136 | 2021-10-08 | 102272 | keep | 0 | Oct | 2021 | 0.069657 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-10-08 22:01 | 2021-10-09 00:17 | 2696 | 002:16 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | CARGA ALIMENTADOR 5018-04 A TRAVES DE 5011-04 EL CUAL DISPARO POR AVERIA EN MH-29 CALLE MAYOR Y COMERCIO | P21100800114 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 136 | 2021-10-08 | 366656 | keep | 0 | Oct | 2021 | 0.24973 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
CANOVANAS | 2021-10-08 22:43 | 2021-10-09 14:09 | 30 | 015:26 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 SU-A1 REPARO TERMINACION EN SU-B2 | R21100800142 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 926 | 2021-10-08 | 27780 | keep | 0 | Oct | 2021 | 0.018921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-10-08 22:49 | 2021-10-08 22:50 | 3420 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21100800000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-08 | 3420 | keep | 0 | Oct | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-10-08 22:50 | 2021-10-09 11:08 | 90 | 012:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO | C21100800149 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 738 | 2021-10-08 | 66420 | keep | 0 | Oct | 2021 | 0.045238 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-08 23:18 | 2021-10-08 23:27 | 1825 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000-4 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-08 | 16425 | keep | 0 | Oct | 2021 | 0.011187 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-10-08 23:18 | 2021-10-08 23:27 | 47 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000-4 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-08 | 423 | keep | 0 | Oct | 2021 | 0.0002881 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-10-08 23:18 | 2021-10-08 23:27 | 315 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000-4 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-08 | 2835 | keep | 0 | Oct | 2021 | 0.0019309 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-10-08 23:18 | 2021-10-08 23:27 | 2 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000-4 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-08 | 18 | keep | 0 | Oct | 2021 | 1.226e-05 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-10-08 23:18 | 2021-10-08 23:27 | 2391 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000-4 | S21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-10-08 | 21519 | keep | 0 | Oct | 2021 | 0.014656 | 0.0016285 | Sustained | FALSE | TRUE | Not_TMED_Event | 2391
SAN JUAN | 2021-10-08 23:18 | 2021-10-09 02:09 | 3957 | 002:51 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ASEGURO AREA POR POSTE IMPACTADO POR AUTO Y SE CERRO INTERRUPTOR | S21100800000 | New_Event |  |  | Include | Wildlife | 171 | 2021-10-08 | 676647 | keep | 0 | Oct | 2021 | 0.46086 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
CAGUAS | 2021-10-08 23:18 | 2021-10-08 23:26 | 2276 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-08 | 18208 | keep | 0 | Oct | 2021 | 0.012401 | 0.0015502 | Sustained | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-10-08 23:18 | 2021-10-08 23:26 | 777 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-08 | 6216 | keep | 0 | Oct | 2021 | 0.0042337 | 0.00052921 | Sustained | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-10-08 23:18 | 2021-10-08 23:26 | 12 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-08 | 96 | keep | 0 | Oct | 2021 | 6.5385e-05 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-10-08 23:18 | 2021-10-08 23:26 | 1290 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21100800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-10-08 | 10320 | keep | 0 | Oct | 2021 | 0.0070289 | 0.00087861 | Sustained | FALSE | TRUE | Not_TMED_Event | 1290
CAGUAS | 2021-10-08 23:18 | 2021-10-09 11:00 | 200 | 011:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C21100800151 | New_Event |  |  | Include | Wildlife | 702 | 2021-10-08 | 140400 | keep | 0 | Oct | 2021 | 0.095626 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-10-08 23:31 | 2021-10-09 01:17 | 1057 | 001:46 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR DE EMERGENCIA PARA REMOVER TENSOR ENREDADO CON LAS FASES POR IMPACTO DE AUTO A POSTE | M21100800197 | New_Event |  |  | Include | Wildlife | 106 | 2021-10-08 | 112042 | keep | 0 | Oct | 2021 | 0.076311 | 0.00071992 | Sustained | FALSE | FALSE | Not_TMED_Event | 1057
AGUADILLA | 2021-10-08 23:51 | 2021-10-09 00:59 | 1827 | 001:08 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR DE EMERGENCIA PARA REMOVER TENSOR ENREDADO CON LAS FASES POR IMPACTO DE AUTO A POSTE | M21100800197 | New_Event |  |  | Include | Wildlife | 68 | 2021-10-08 | 124236 | keep | 0 | Oct | 2021 | 0.084617 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2021-10-09 00:05 | 2021-10-09 00:06 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21100900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 2039 | keep | 0 | Oct | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2021-10-09 00:17 | 2021-10-09 12:15 | 100 | 011:58 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO BARRA SECA Y PISTOLA EN EL MH-29. | P21100900007 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 718 | 2021-10-09 | 71800 | keep | 0 | Oct | 2021 | 0.048903 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-09 00:22 | 2021-10-09 00:23 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 3603-01 NO RECIERRA, LLEVANDO CARGA DEL 3604-06 | C21100900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 315 | keep | 0 | Oct | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2021-10-09 00:22 | 2021-10-09 00:23 | 2906 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 3603-01 NO RECIERRA, LLEVANDO CARGA DEL 3604-06 | C21100900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 2906 | keep | 0 | Oct | 2021 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
PONCE | 2021-10-09 00:22 | 2021-10-09 11:14 | 70 | 010:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA, IGUANA CRUZO FASE. | P21100900003 | New_Event |  |  | Include | Wildlife | 652 | 2021-10-09 | 45640 | keep | 0 | Oct | 2021 | 0.031085 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-10-09 00:32 | 2021-10-09 03:16 | 2203 | 002:44 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-06 SE SECCIONALIZO TOMA AVERIADA EN SU-31 HACIA CONDOMINIO MONTE GARDEN Y SE CERRO INTERRUPTOR | S21100900006 | New_Event | UG Cable Fault | Include | Include | Equipment | 164 | 2021-10-09 | 361292 | keep | 0 | Oct | 2021 | 0.24607 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2021-10-09 01:44 | 2021-10-09 02:09 | 2391 | 000:25 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA DESCRUZAR LINEA Y ELIMINAR GUIDE POR POSTE IMPACTADO POR AUTO | S21100900000 | New_Event |  |  | Include | Wildlife | 25 | 2021-10-09 | 59775 | keep | 0 | Oct | 2021 | 0.040712 | 0.0016285 | Sustained | FALSE | TRUE | Not_TMED_Event | 2391
BAYAMON | 2021-10-09 01:59 | 2021-10-09 15:51 | 6 | 013:52 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE DESGANCHO Y SE REPARO SECUNDARIA | S21100900031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 832 | 2021-10-09 | 4992 | keep | 0 | Oct | 2021 | 0.0034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-10-09 02:17 | 2021-10-09 13:19 | 90 | 011:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21100900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 662 | 2021-10-09 | 59580 | keep | 0 | Oct | 2021 | 0.04058 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-09 02:30 | 2021-10-09 04:07 | 1447 | 001:37 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1112-04 QUE A SU VEZ LLEVA LA CARGA DEL 1419-09 SE REPORTA CAJA SECA AVERIADA EN MH-38 FRENTE EDIFICIO AQUA BLUE SE SECCIONALIZO Y SE CERRO POR SCADA | S21100900032 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 97 | 2021-10-09 | 140359 | keep | 0 | Oct | 2021 | 0.095598 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-10-09 02:30 | 2021-10-09 04:07 | 266 | 001:37 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1112-04 QUE A SU VEZ LLEVA LA CARGA DEL 1419-09 SE REPORTA CAJA SECA AVERIADA EN MH-38 FRENTE EDIFICIO AQUA BLUE SE SECCIONALIZO Y SE CERRO POR SCADA | S21100900032 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 97 | 2021-10-09 | 25802 | keep | 0 | Oct | 2021 | 0.017574 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
AGUADILLA | 2021-10-09 03:31 | 2021-10-09 10:20 | 50 | 006:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M21100900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2021-10-09 | 20450 | keep | 0 | Oct | 2021 | 0.013928 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-09 04:16 | 2021-10-09 10:24 | 100 | 006:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21100800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2021-10-09 | 36800 | keep | 0 | Oct | 2021 | 0.025064 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-09 04:33 | 2021-10-09 15:16 | 60 | 010:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | B21100900001 | New_Event | Cutout Failure | Include | Include | Equipment | 643 | 2021-10-09 | 38580 | keep | 0 | Oct | 2021 | 0.026277 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-09 05:05 | 2021-10-09 05:06 | 4028 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 4028 | keep | 0 | Oct | 2021 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2021-10-09 05:53 | 2021-10-09 17:12 | 30 | 011:19 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 679 | 2021-10-09 | 20370 | keep | 0 | Oct | 2021 | 0.013874 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-09 06:27 | 2021-10-09 10:17 | 100 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21100900001 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-10-09 | 23000 | keep | 0 | Oct | 2021 | 0.015665 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-09 08:12 | 2021-10-09 12:41 | 88 | 004:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | P21100900018 | New_Event |  |  | Include | Wildlife | 269 | 2021-10-09 | 23672 | keep | 0 | Oct | 2021 | 0.016123 | 5.9936e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 88
BAYAMON | 2021-10-09 08:14 | 2021-10-09 08:15 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE DE LA CARGA 1717 02 | B21100900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 5961 | keep | 0 | Oct | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-10-09 08:14 | 2021-10-09 08:15 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE DE SU CARGA POR EL 1713-05 | B21100900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-10-09 08:16 | 2021-10-09 09:20 | 10 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA TRASPATIO | B21100800039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-10-09 | 640 | keep | 0 | Oct | 2021 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-09 08:32 | 2021-10-09 15:23 | 40 | 006:51 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA REMPLAZO PARARRAYO | C21100900027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 411 | 2021-10-09 | 16440 | keep | 0 | Oct | 2021 | 0.011197 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-09 08:45 | 2021-10-09 10:22 | 30 | 001:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21100800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-10-09 | 2910 | keep | 0 | Oct | 2021 | 0.001982 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-10-09 09:04 | 2021-10-09 17:53 | 15 | 008:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO RISER @ T-3 PARA LLEVAR T-3 A SU LUGAR IMPACTADO POR VEHICULO Y SE REPARO SECUNDARIA AVERIADA EN T-3 | R21100900005 | New_Event |  |  | Include | Wildlife | 529 | 2021-10-09 | 7935 | keep | 0 | Oct | 2021 | 0.0054045 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-09 09:06 | 2021-10-09 09:36 | 25 | 000:30 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA Y SE REPARO CRUCETA PARTIDA | S21100900061 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 30 | 2021-10-09 | 750 | keep | 0 | Oct | 2021 | 0.00051082 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-09 09:08 | 2021-10-09 10:59 | 25 | 001:51 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 20 EN TRANSFORMADOR SE ABRIO CORTE DE LINEA PARA INSTALAR CAJA PRIMARIA A TRANSFORMADOR DIRECTO A LA LINEA Y REPARAR BARRAS SECUNDARIAS EN PEDESTAL | B21100800082 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 111 | 2021-10-09 | 2775 | keep | 0 | Oct | 2021 | 0.00189 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-09 09:13 | 2021-10-09 13:00 | 3 | 003:47 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | M21100800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-10-09 | 681 | keep | 0 | Oct | 2021 | 0.00046383 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-09 09:15 | 2021-10-09 23:00 | 300 | 013:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ALIMENTADOR PARA REEMPLAZAR POSTE IMPACTADO POR AUTO | S21100900082 | New_Event |  |  | Include | Wildlife | 825 | 2021-10-09 | 247500 | keep | 0 | Oct | 2021 | 0.16857 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-10-09 09:24 | 2021-10-10 16:12 | 5 | 030:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFROMADOR Y SE REEMPLAZO SECUNDARIA | A21100900005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1848 | 2021-10-09 | 9240 | keep | 0 | Oct | 2021 | 0.0062933 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-09 09:25 | 2021-10-11 16:36 | 1 | 055:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 10 EN TRANSFORMADOR SE REPARO BAJANTES PRIMARIOS EN TRANSFORMADOR SE REMPLAZO PARARRAYOS AVERIADO Y SE REMPLAZO 2 CAJAS DE POLIMERO 100AMP EN FID 33803073 | A21100900006 | New_Event | Wire Down | Include | Include | Equipment | 3311 | 2021-10-09 | 3311 | keep | 0 | Oct | 2021 | 0.0022551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-10-09 09:31 | 2021-10-09 16:11 | 75 | 006:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 30 EN CORTES DE LINEAS REEMPLAZARON AISLADORES ROTOS | R21100900006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 400 | 2021-10-09 | 30000 | keep | 0 | Oct | 2021 | 0.020433 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-10-09 09:39 | 2021-10-09 15:58 | 1 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R21100900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2021-10-09 | 379 | keep | 0 | Oct | 2021 | 0.00025814 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-09 09:45 | 2021-10-09 10:28 | 100 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A21100800065 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2021-10-09 | 4300 | keep | 0 | Oct | 2021 | 0.0029287 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-10-09 09:52 | 2021-10-09 14:10 | 12 | 004:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21100900013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 258 | 2021-10-09 | 3096 | keep | 0 | Oct | 2021 | 0.0021087 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-09 09:53 | 2021-10-09 10:29 | 5 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN BANCO DE TRANSFORMADOR | S21100900072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-10-09 | 180 | keep | 0 | Oct | 2021 | 0.0001226 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-10-09 10:09 | 2021-10-09 15:58 | 15 | 005:49 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO @ T-12 | B21100900016 | New_Event | UG Cable Fault | Include | Include | Equipment | 349 | 2021-10-09 | 5235 | keep | 0 | Oct | 2021 | 0.0035655 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-10-09 10:15 | 2021-10-09 17:36 | 60 | 007:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2021-10-09 | 26460 | keep | 0 | Oct | 2021 | 0.018022 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-09 10:21 | 2021-10-09 13:08 | 45 | 002:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | B21100900018 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2021-10-09 | 7515 | keep | 0 | Oct | 2021 | 0.0051184 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-09 10:38 | 2021-10-10 10:27 | 30 | 023:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA CRUZADA | A21100900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1429 | 2021-10-09 | 42870 | keep | 0 | Oct | 2021 | 0.029199 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-09 10:44 | 2021-10-09 17:58 | 80 | 007:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21100900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2021-10-09 | 34720 | keep | 0 | Oct | 2021 | 0.023648 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-09 11:06 | 2021-10-09 23:00 | 500 | 011:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ALIMENTADOR PARA REEMPLAZAR POSTE IMPACTADO POR AUTO | S21100900082 | New_Event |  |  | Include | Wildlife | 714 | 2021-10-09 | 357000 | keep | 0 | Oct | 2021 | 0.24315 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
AGUADILLA | 2021-10-09 11:06 | 2021-10-09 12:08 | 4 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21100900023 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2021-10-09 | 248 | keep | 0 | Oct | 2021 | 0.00016891 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-10-09 11:33 | 2021-10-10 20:27 | 1 | 032:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA QUEMADA | A21100900022 | New_Event | Cutout Failure | Include | Include | Equipment | 1974 | 2021-10-09 | 1974 | keep | 0 | Oct | 2021 | 0.0013445 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-09 11:36 | 2021-10-09 12:15 | 4 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTOR SECUNDARIO | A21100800107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-10-09 | 156 | keep | 0 | Oct | 2021 | 0.00010625 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-10-09 11:41 | 2021-10-09 11:42 | 2276 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES LINEA 3000 | C21009000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-09 | 2276 | keep | 0 | Oct | 2021 | 0.0015502 | 0.0015502 | Momentary | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-10-09 11:41 | 2021-10-09 11:42 | 777 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES LINEA 3000 | C21009000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-09 | 777 | keep | 0 | Oct | 2021 | 0.00052921 | 0.00052921 | Momentary | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-10-09 11:41 | 2021-10-09 11:42 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES LINEA 3000 | C21009000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-09 | 12 | keep | 0 | Oct | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-10-09 11:41 | 2021-10-09 11:42 | 1290 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES LINEA 3000 | C21009000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-09 | 1290 | keep | 0 | Oct | 2021 | 0.00087861 | 0.00087861 | Momentary | FALSE | TRUE | Not_TMED_Event | 1290
HUMACAO | 2021-10-09 12:02 | 2021-10-09 17:04 | 20 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A LINEA | C21100900048 | New_Event | Wire Down | Include | Include | Equipment | 302 | 2021-10-09 | 6040 | keep | 0 | Oct | 2021 | 0.0041138 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-09 12:03 | 2021-10-09 19:00 | 20 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21100900023 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2021-10-09 | 8340 | keep | 0 | Oct | 2021 | 0.0056803 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-09 12:17 | 2021-10-09 15:44 | 20 | 003:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21100900027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-10-09 | 4140 | keep | 0 | Oct | 2021 | 0.0028197 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-10-09 12:28 | 2021-10-09 15:01 | 6 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REGULAR TRANSFORMADOR QUEDO EN 125/250V | C21100900052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2021-10-09 | 918 | keep | 0 | Oct | 2021 | 0.00062525 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-09 12:50 | 2021-10-09 19:47 | 5 | 006:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR SE REMPLAZO LINEA SECUNDARIA AVERIADA | A21100900030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 417 | 2021-10-09 | 2085 | keep | 0 | Oct | 2021 | 0.0014201 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-10-09 13:05 | 2021-10-09 16:15 | 30 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21100900041 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2021-10-09 | 5700 | keep | 0 | Oct | 2021 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-09 13:15 | 2021-10-09 14:04 | 15 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21100800091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-10-09 | 735 | keep | 0 | Oct | 2021 | 0.00050061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-10-09 13:30 | 2021-10-10 09:40 | 4 | 020:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO | C21101000056 | New_Event | Wire Down | Include | Include | Equipment | 1210 | 2021-10-09 | 4840 | keep | 0 | Oct | 2021 | 0.0032965 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-10-09 13:32 | 2021-10-09 17:28 | 110 | 003:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21100900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2021-10-09 | 25960 | keep | 0 | Oct | 2021 | 0.017681 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
ARECIBO | 2021-10-09 14:01 | 2021-10-10 11:58 | 40 | 021:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A21100900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1317 | 2021-10-09 | 52680 | keep | 0 | Oct | 2021 | 0.03588 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-09 14:22 | 2021-10-10 12:15 | 20 | 021:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO PARTIDO | A21100900033 | New_Event | Wire Down | Include | Include | Equipment | 1313 | 2021-10-09 | 26260 | keep | 0 | Oct | 2021 | 0.017886 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-09 14:34 | 2021-10-09 16:34 | 60 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21100900105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-10-09 | 7200 | keep | 0 | Oct | 2021 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-09 14:44 | 2021-10-09 14:55 | 1 | 000:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR AVE CRUZO LINEAS | M21100900037 | New_Event |  |  | Include | Wildlife | 11 | 2021-10-09 | 11 | keep | 0 | Oct | 2021 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-09 14:52 | 2021-10-09 16:18 | 60 | 001:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100900045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2021-10-09 | 5160 | keep | 0 | Oct | 2021 | 0.0035145 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-09 15:11 | 2021-10-09 15:12 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21100900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 3941 | keep | 0 | Oct | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
ARECIBO | 2021-10-09 15:36 | 2021-10-09 15:37 | 2231 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21100900042 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-09 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2021-10-09 15:37 | 2021-10-09 21:31 | 100 | 005:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21100900043 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 354 | 2021-10-09 | 35400 | keep | 0 | Oct | 2021 | 0.024111 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-09 15:42 | 2021-10-09 16:16 | 6 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21100800172 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-10-09 | 204 | keep | 0 | Oct | 2021 | 0.00013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-09 15:47 | 2021-10-09 16:32 | 15 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA Y REALIZAR DESGANCHE | A21100900044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-10-09 | 675 | keep | 0 | Oct | 2021 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-09 15:51 | 2021-10-09 17:47 | 6 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21100900111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-10-09 | 696 | keep | 0 | Oct | 2021 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-10-09 15:53 | 2021-10-09 15:54 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21100900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-10-09 15:53 | 2021-10-09 15:54 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21100900042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 3041 | keep | 0 | Oct | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2021-10-09 15:59 | 2021-10-09 17:32 | 10 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21100800064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2021-10-09 | 930 | keep | 0 | Oct | 2021 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-09 16:08 | 2021-10-09 16:10 | 2276 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES EN LA LINEA 3000 | C21100900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-09 | 4552 | keep | 0 | Oct | 2021 | 0.0031003 | 0.0015502 | Momentary | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-10-09 16:08 | 2021-10-09 16:10 | 777 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES EN LA LINEA 3000 | C21100900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-09 | 1554 | keep | 0 | Oct | 2021 | 0.0010584 | 0.00052921 | Momentary | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-10-09 16:08 | 2021-10-09 16:10 | 12 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES EN LA LINEA 3000 | C21100900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-09 | 24 | keep | 0 | Oct | 2021 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-10-09 16:08 | 2021-10-09 16:10 | 1290 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES EN LA LINEA 3000 | C21100900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-09 | 2580 | keep | 0 | Oct | 2021 | 0.0017572 | 0.00087861 | Momentary | FALSE | TRUE | Not_TMED_Event | 1290
ARECIBO | 2021-10-09 16:25 | 2021-10-09 18:35 | 100 | 002:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO LINEA ZAFADA DE AISLADOR | A21100900013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 130 | 2021-10-09 | 13000 | keep | 0 | Oct | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-09 16:26 | 2021-10-09 19:45 | 40 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21100900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2021-10-09 | 7960 | keep | 0 | Oct | 2021 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-09 16:44 | 2021-10-09 19:23 | 8 | 002:39 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21100900030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-10-09 | 1272 | keep | 0 | Oct | 2021 | 0.00086635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-10-09 16:47 | 2021-10-09 17:50 | 10 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21100900072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2021-10-09 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-09 16:54 | 2021-10-10 11:30 | 1 | 018:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTE PRIMARIO | M21100900046 | New_Event | Wire Down | Include | Include | Equipment | 1116 | 2021-10-09 | 1116 | keep | 0 | Oct | 2021 | 0.0007601 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-10-09 16:55 | 2021-10-10 10:19 | 10 | 017:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21100900047 | New_Event | Bad Weather | Include | Include | Weather | 1044 | 2021-10-09 | 10440 | keep | 0 | Oct | 2021 | 0.0071106 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-10-09 17:10 | 2021-10-09 19:32 | 15 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21100900035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-10-09 | 2130 | keep | 0 | Oct | 2021 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-09 17:57 | 2021-10-10 16:07 | 40 | 022:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21100700057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1330 | 2021-10-09 | 53200 | keep | 0 | Oct | 2021 | 0.036234 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-09 18:02 | 2021-10-10 11:15 | 40 | 017:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA | C21100900076 | New_Event | Cutout Failure | Include | Include | Equipment | 1033 | 2021-10-09 | 41320 | keep | 0 | Oct | 2021 | 0.028143 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-09 18:09 | 2021-10-09 18:10 | 1709 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21100900077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 1709 | keep | 0 | Oct | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
SAN JUAN | 2021-10-09 18:26 | 2021-10-09 21:33 | 80 | 003:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR. CRUCE POR IGUANA | R21100900032 | New_Event |  |  | Include | Wildlife | 187 | 2021-10-09 | 14960 | keep | 0 | Oct | 2021 | 0.010189 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-09 18:34 | 2021-10-10 00:35 | 120 | 006:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL | M21100900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2021-10-09 | 43320 | keep | 0 | Oct | 2021 | 0.029505 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-10-09 18:41 | 2021-10-11 12:01 | 20 | 041:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21100900064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2480 | 2021-10-09 | 49600 | keep | 0 | Oct | 2021 | 0.033782 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-09 18:55 | 2021-10-10 12:49 | 10 | 017:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21100900127 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1074 | 2021-10-09 | 10740 | keep | 0 | Oct | 2021 | 0.007315 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-09 19:34 | 2021-10-10 10:43 | 40 | 015:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA | S21100900131 | New_Event | Cutout Failure | Include | Include | Equipment | 909 | 2021-10-09 | 36360 | keep | 0 | Oct | 2021 | 0.024765 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-10-09 19:58 | 2021-10-10 08:20 | 100 | 012:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA SE PATRULLO | R21100900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 742 | 2021-10-09 | 74200 | keep | 0 | Oct | 2021 | 0.050537 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-09 20:33 | 2021-10-10 09:55 | 60 | 013:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21100900064 | New_Event | Bad Weather | Include | Include | Weather | 802 | 2021-10-09 | 48120 | keep | 0 | Oct | 2021 | 0.032774 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-09 20:44 | 2021-10-10 13:50 | 2 | 017:06 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | M21100900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1026 | 2021-10-09 | 2052 | keep | 0 | Oct | 2021 | 0.0013976 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
UTUADO | 2021-10-09 21:37 | 2021-10-10 11:20 | 20 | 013:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21100900062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2021-10-09 | 16460 | keep | 0 | Oct | 2021 | 0.011211 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-10-09 21:39 | 2021-10-10 10:17 | 60 | 012:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21100900063 | New_Event | Bad Weather | Include | Include | Weather | 758 | 2021-10-09 | 45480 | keep | 0 | Oct | 2021 | 0.030976 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-10-09 22:18 | 2021-10-10 09:47 | 80 | 011:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA. SE REEMPLAZO CAJA PRIMARIA QUEMADA. | P21100900048 | New_Event | Cutout Failure | Include | Include | Equipment | 689 | 2021-10-09 | 55120 | keep | 0 | Oct | 2021 | 0.037542 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-09 22:48 | 2021-10-10 09:49 | 20 | 011:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21100800112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 661 | 2021-10-09 | 13220 | keep | 0 | Oct | 2021 | 0.0090041 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-10-09 23:46 | 2021-10-09 23:47 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21100900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-09 | 3041 | keep | 0 | Oct | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2021-10-10 01:16 | 2021-10-10 10:46 | 20 | 009:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | A21100900002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 570 | 2021-10-10 | 11400 | keep | 0 | Oct | 2021 | 0.0077645 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-10-10 02:48 | 2021-10-10 12:02 | 60 | 009:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 554 | 2021-10-10 | 33240 | keep | 0 | Oct | 2021 | 0.02264 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-10 04:53 | 2021-10-10 06:30 | 1310 | 001:37 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR ABRIENDO MACHETES EN CALLE CARDENAS ESQ CALLE CORRIENTE | S21101000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-10-10 | 127070 | keep | 0 | Oct | 2021 | 0.086547 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-10-10 05:15 | 2021-10-10 14:26 | 20 | 009:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 551 | 2021-10-10 | 11020 | keep | 0 | Oct | 2021 | 0.0075057 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-10 05:17 | 2021-10-10 05:19 | 2826 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-10 | 5652 | keep | 0 | Oct | 2021 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
CAGUAS | 2021-10-10 05:36 | 2021-10-10 05:38 | 315 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21101000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-10 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2021-10-10 05:44 | 2021-10-10 10:44 | 6 | 005:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES EN TRANSFORMADOR | C21101000056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 300 | 2021-10-10 | 1800 | keep | 0 | Oct | 2021 | 0.001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-10-10 05:58 | 2021-10-10 05:59 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 3387 | keep | 0 | Oct | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
BAYAMON | 2021-10-10 06:11 | 2021-10-10 09:14 | 15 | 003:03 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21101000005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 183 | 2021-10-10 | 2745 | keep | 0 | Oct | 2021 | 0.0018696 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-10 06:30 | 2021-10-10 07:06 | 500 | 000:36 | P | DESGANCHE | SE REALIZO DESGANCHE DE PALMA Y SE CERRARON MACHETES NUEVAMENTE | S21101000004 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 36 | 2021-10-10 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-10 06:50 | 2021-10-10 11:28 | 50 | 004:38 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21101000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2021-10-10 | 13900 | keep | 0 | Oct | 2021 | 0.0094672 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-10 07:14 | 2021-10-10 08:50 | 40 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21101000002 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2021-10-10 | 3840 | keep | 0 | Oct | 2021 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-10 07:19 | 2021-10-10 07:20 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2402 | keep | 0 | Oct | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-10-10 07:24 | 2021-10-10 19:28 | 10 | 012:04 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE AEREO EXISTENTE A T 49 | B21100900008 | New_Event | UG Cable Fault | Include | Include | Equipment | 724 | 2021-10-10 | 7240 | keep | 0 | Oct | 2021 | 0.0049311 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-10 07:24 | 2021-10-10 07:25 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SECUNDARIO DE PORTATIL #10 | P211010000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 1979 | keep | 0 | Oct | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-10-10 07:24 | 2021-10-10 07:25 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SECUNDARIO DE PORTATIL #10 | P211010000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 5069 | keep | 0 | Oct | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-10-10 07:24 | 2021-10-10 07:25 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SECUNDARIO DE PORTATIL #10 | P211010000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 5063 | keep | 0 | Oct | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
BAYAMON | 2021-10-10 07:48 | 2021-10-10 11:04 | 1399 | 003:16 | S | BREAKER DEFECTUOSO O NO OPERA | SE REMPLAZARON 2 FUSIBLES DE ALTA DE TRANSFORMADOR POR AVERIA DE CONDUCTOR PARTIDO PERTENECIENTE A INTERRUPTOR 1704 03 QUE NO OPERO | B21101000010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 196 | 2021-10-10 | 274204 | keep | 0 | Oct | 2021 | 0.18676 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-10-10 07:48 | 2021-10-10 11:04 | 302 | 003:16 | S | BREAKER DEFECTUOSO O NO OPERA | SE REMPLAZARON 2 FUSIBLES DE ALTA DE TRANSFORMADOR POR AVERIA DE CONDUCTOR PARTIDO PERTENECIENTE A INTERRUPTOR 1704 03 QUE NO OPERO | B21101000010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 196 | 2021-10-10 | 59192 | keep | 0 | Oct | 2021 | 0.040315 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-10-10 07:48 | 2021-10-10 12:25 | 400 | 004:37 | S | BREAKER DEFECTUOSO O NO OPERA | PARTE DE SU CARGA POR 1715 02 CERRANDO MACHETES DE AMARRE EN CALLE COMERIO FRENTE A FARMACIA CRISTINA 5 Y ABRIENDO MACHETES EN CALLE COMERIO FRENTE A CAFETERIA DOMIRRIQUENOS POR AVERIA DE ALAMBRE PARTIDO Y AVERIA DE BOBINA DE TRIP EN INTERRUPTOR | B21101000102 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 277 | 2021-10-10 | 110800 | keep | 0 | Oct | 2021 | 0.075465 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2021-10-10 07:48 | 2021-10-10 11:04 | 573 | 003:16 | S | BREAKER DEFECTUOSO O NO OPERA | SE REMPLAZARON 2 FUSIBLES DE ALTA DE TRANSFORMADOR POR AVERIA DE CONDUCTOR PARTIDO PERTENECIENTE A INTERRUPTOR 1704 03 QUE NO OPERO | B21101000010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 196 | 2021-10-10 | 112308 | keep | 0 | Oct | 2021 | 0.076492 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-10-10 07:48 | 2021-10-10 11:04 | 1313 | 003:16 | S | BREAKER DEFECTUOSO O NO OPERA | SE REMPLAZARON 2 FUSIBLES DE ALTA DE TRANSFORMADOR POR AVERIA DE CONDUCTOR PARTIDO PERTENECIENTE A INTERRUPTOR 1704 03 QUE NO OPERO | B21101000010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 196 | 2021-10-10 | 257348 | keep | 0 | Oct | 2021 | 0.17528 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
PONCE | 2021-10-10 08:00 | 2021-10-10 15:30 | 1 | 007:30 | P | NO SE REPORTO CAUSA | 2 X 20 EN SU-2 NO SE REPORTO CAUSA | P21101000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 450 | 2021-10-10 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-10-10 08:01 | 2021-10-10 08:02 | 1702 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | C21101000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-10 | 1702 | keep | 0 | Oct | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-10-10 08:02 | 2021-10-10 12:19 | 130 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIAS | C21101000007 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 257 | 2021-10-10 | 33410 | keep | 0 | Oct | 2021 | 0.022755 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
CANOVANAS | 2021-10-10 08:15 | 2021-10-10 14:17 | 6 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | R21101000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2021-10-10 | 2172 | keep | 0 | Oct | 2021 | 0.0014793 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-10 08:28 | 2021-10-10 17:08 | 30 | 008:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21101000017 | New_Event | Wire Down | Include | Include | Equipment | 520 | 2021-10-10 | 15600 | keep | 0 | Oct | 2021 | 0.010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-10 08:30 | 2021-10-10 11:45 | 36 | 003:15 | S | PROTECCION DEFECTUOSA | APARENTE AVERIA EN EL 1620-05 PROVOCO QUE ABRIERA POR BACK UP EL MAIN BREAKER DE LA SUBESTACION | S21101000042 | New_Event | Protection Miscoordination | Include | Include | Other | 195 | 2021-10-10 | 7020 | keep | 0 | Oct | 2021 | 0.0047813 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-10 08:30 | 2021-10-10 11:45 | 3718 | 003:15 | S | PROTECCION DEFECTUOSA | APARENTE AVERIA EN EL 1620-05 PROVOCO QUE ABRIERA POR BACK UP EL MAIN BREAKER DE LA SUBESTACION | S21101000042 | New_Event | Protection Miscoordination | Include | Include | Other | 195 | 2021-10-10 | 725010 | keep | 0 | Oct | 2021 | 0.4938 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-10-10 08:30 | 2021-10-10 11:45 | 1073 | 003:15 | S | PROTECCION DEFECTUOSA | APARENTE AVERIA EN EL 1620-05 PROVOCO QUE ABRIERA POR BACK UP EL MAIN BREAKER DE LA SUBESTACION | S21101000042 | New_Event | Protection Miscoordination | Include | Include | Other | 195 | 2021-10-10 | 209235 | keep | 0 | Oct | 2021 | 0.14251 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2021-10-10 08:30 | 2021-10-10 11:45 | 172 | 003:15 | S | PROTECCION DEFECTUOSA | APARENTE AVERIA EN EL 1620-05 PROVOCO QUE ABRIERA POR BACK UP EL MAIN BREAKER DE LA SUBESTACION | S21101000042 | New_Event | Protection Miscoordination | Include | Include | Other | 195 | 2021-10-10 | 33540 | keep | 0 | Oct | 2021 | 0.022844 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-10-10 08:30 | 2021-10-10 14:25 | 1615 | 005:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO Y DISCO QUEMADO Y SE TRANSFIRIO PARTE DE LA CARGA AL 1646-01 | R21101000021 | New_Event | Wire Down | Include | Include | Equipment | 355 | 2021-10-10 | 573325 | keep | 0 | Oct | 2021 | 0.39049 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
UTUADO | 2021-10-10 08:39 | 2021-10-10 15:58 | 20 | 007:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21101000005 | New_Event | Bad Weather | Include | Include | Weather | 439 | 2021-10-10 | 8780 | keep | 0 | Oct | 2021 | 0.00598 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-10-10 08:41 | 2021-10-10 08:42 | 551 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21101000009 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-10 | 551 | keep | 0 | Oct | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
FAJARDO | 2021-10-10 08:46 | 2021-10-10 10:07 | 36 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | R21101000019 | New_Event |  |  | Include | Wildlife | 81 | 2021-10-10 | 2916 | keep | 0 | Oct | 2021 | 0.0019861 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
SAN JUAN | 2021-10-10 08:52 | 2021-10-13 14:44 | 10 | 077:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN RISER Y 1 X 65 EN CORTE DE LINEA CRUCE POR IGUANA | R21101000043 | New_Event |  |  | Include | Wildlife | 4672 | 2021-10-10 | 46720 | keep | 0 | Oct | 2021 | 0.031821 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-10-10 09:00 | 2021-10-11 17:08 | 60 | 032:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21101000011 | New_Event | Wire Down | Include | Include | Equipment | 1928 | 2021-10-10 | 115680 | keep | 0 | Oct | 2021 | 0.078789 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-10 09:10 | 2021-10-12 12:35 | 6 | 051:25 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA | C21101000092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3085 | 2021-10-10 | 18510 | keep | 0 | Oct | 2021 | 0.012607 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-10-10 09:13 | 2021-10-10 15:34 | 50 | 006:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21101000004 | New_Event | Bad Weather | Include | Include | Weather | 381 | 2021-10-10 | 19050 | keep | 0 | Oct | 2021 | 0.012975 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-10 09:15 | 2021-10-10 09:16 | 2558 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR NO SE REPORTO LA CAUSA | A21100900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-10 | 2558 | keep | 0 | Oct | 2021 | 0.0017422 | 0.0017422 | Momentary | FALSE | FALSE | Not_TMED_Event | 2558
ARECIBO | 2021-10-10 09:16 | 2021-10-10 17:11 | 300 | 007:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 200 EN CORTE DE LINEA SE REPARO LINEA PARTIDA Y SE CERRO CORTE DE LINEA | A21101000054 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 475 | 2021-10-10 | 142500 | keep | 0 | Oct | 2021 | 0.097056 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-10-10 09:19 | 2021-10-10 11:48 | 16 | 002:29 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21100900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-10-10 | 2384 | keep | 0 | Oct | 2021 | 0.0016237 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2021-10-10 09:19 | 2021-10-10 11:48 | 50 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA SE PATRULLO | R21101000047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-10-10 | 7450 | keep | 0 | Oct | 2021 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-10 09:23 | 2021-10-10 14:40 | 10 | 005:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P21101000007 | New_Event | Cutout Failure | Include | Include | Equipment | 317 | 2021-10-10 | 3170 | keep | 0 | Oct | 2021 | 0.0021591 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-10 09:30 | 2021-10-10 18:06 | 28 | 008:36 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REEMPLAZAR POSTE PRIMARIO PARTIDO | P21101000001 | New_Event | Defective Pole | Include | Include | Equipment | 516 | 2021-10-10 | 14448 | keep | 0 | Oct | 2021 | 0.0098405 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
BAYAMON | 2021-10-10 09:32 | 2021-10-12 10:52 | 26 | 049:20 | P | NO SE REPORTO CAUSA | 1 X 100 RISER | S21101000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2960 | 2021-10-10 | 76960 | keep | 0 | Oct | 2021 | 0.052417 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2021-10-10 09:38 | 2021-10-10 09:52 | 5 | 000:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE CERRO PUENTE ABIERTO DE LINEA A CAJA | S21101000064 | New_Event | Wire Down | Include | Include | Equipment | 14 | 2021-10-10 | 70 | keep | 0 | Oct | 2021 | 4.7677e-05 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-10-10 09:54 | 2021-10-10 16:34 | 100 | 006:40 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO | S21100900073 | New_Event | Switch Failure | Include | Include | Equipment | 400 | 2021-10-10 | 40000 | keep | 0 | Oct | 2021 | 0.027244 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-10-10 09:59 | 2021-10-10 10:00 | 2092 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2092 | keep | 0 | Oct | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
AGUADILLA | 2021-10-10 10:22 | 2021-10-10 13:25 | 40 | 003:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEA | M21101000011 | New_Event |  |  | Include | Wildlife | 183 | 2021-10-10 | 7320 | keep | 0 | Oct | 2021 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-10 10:27 | 2021-10-10 15:37 | 80 | 005:10 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTES DE LINEA | R21101000075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2021-10-10 | 24800 | keep | 0 | Oct | 2021 | 0.016891 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-10 10:57 | 2021-10-10 19:26 | 14 | 008:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 100KVA POR IGUAL | S21101000093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 509 | 2021-10-10 | 7126 | keep | 0 | Oct | 2021 | 0.0048535 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2021-10-10 11:40 | 2021-10-10 14:07 | 1952 | 002:27 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR. CLIENTE REALIZANDO DESGANCHE CRUZO LINEAS EN TRONCAL DEL ALIMENTADOR. | P21101000019 | New_Event |  |  | Include | Wildlife | 147 | 2021-10-10 | 286944 | keep | 0 | Oct | 2021 | 0.19544 | 0.0013295 | Sustained | FALSE | TRUE | Not_TMED_Event | 1952
HUMACAO | 2021-10-10 11:41 | 2021-10-10 17:01 | 7 | 005:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C21101000021 | New_Event | Cutout Failure | Include | Include | Equipment | 320 | 2021-10-10 | 2240 | keep | 0 | Oct | 2021 | 0.0015257 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CAGUAS | 2021-10-10 12:04 | 2021-10-10 12:05 | 125 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | C21101000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-10 | 125 | keep | 0 | Oct | 2021 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2021-10-10 12:06 | 2021-10-10 12:07 | 2448 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIAS | C21101000023 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-10 | 2448 | keep | 0 | Oct | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2021-10-10 12:13 | 2021-10-10 12:14 | 2448 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIAS | C21101000024 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-10-10 | 2448 | keep | 0 | Oct | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 3130 | keep | 0 | Oct | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 976 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 1952 | keep | 0 | Oct | 2021 | 0.0013295 | 0.00066475 | Momentary | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 548 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 1096 | keep | 0 | Oct | 2021 | 0.00074648 | 0.00037324 | Momentary | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 870 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 2906 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 5812 | keep | 0 | Oct | 2021 | 0.0039585 | 0.0019793 | Momentary | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-10-10 12:21 | 2021-10-10 12:23 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-10 | 4686 | keep | 0 | Oct | 2021 | 0.0031916 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
BAYAMON | 2021-10-10 12:25 | 2021-10-10 12:55 | 648 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TRANSFIRIO PARTE DE CARGA AL 1708 04 CERRANDO MACHETES NO EN CARRETERA 861 LADO WENDYS Y ABRIENDO RISER DE SALIDA EN SUBESTACION SE LEVANTO ALAMBRE PRIMARIO INTERRUPTOR 1704 03 TIENE BOBINA DE TRIP QUEMADA | B21101000102 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-10-10 | 19440 | keep | 0 | Oct | 2021 | 0.01324 | 0.00044135 | Sustained | FALSE | FALSE | Not_TMED_Event | 648
ARECIBO | 2021-10-10 12:32 | 2021-10-10 16:27 | 12 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA POR PAJARO | A21101000050 | New_Event |  |  | Include | Wildlife | 235 | 2021-10-10 | 2820 | keep | 0 | Oct | 2021 | 0.0019207 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
AGUADILLA | 2021-10-10 12:38 | 2021-10-10 13:55 | 10 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21101000018 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-10-10 | 770 | keep | 0 | Oct | 2021 | 0.00052444 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-10-10 12:39 | 2021-10-10 17:42 | 30 | 005:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA POR AISLADOR PARTIDO | A21101000051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 303 | 2021-10-10 | 9090 | keep | 0 | Oct | 2021 | 0.0061912 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-10 12:47 | 2021-10-10 21:39 | 25 | 008:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101000110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 532 | 2021-10-10 | 13300 | keep | 0 | Oct | 2021 | 0.0090586 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-10-10 12:48 | 2021-10-11 12:08 | 100 | 023:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21101000004 | New_Event | Bad Weather | Include | Include | Weather | 1400 | 2021-10-10 | 140000 | keep | 0 | Oct | 2021 | 0.095353 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-10 12:53 | 2021-10-10 16:10 | 100 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO SE REPORTO LA CAUSA | P21101000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-10-10 | 19700 | keep | 0 | Oct | 2021 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-10-10 12:59 | 2021-10-10 20:58 | 10 | 007:59 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO | R21101000110 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 479 | 2021-10-10 | 4790 | keep | 0 | Oct | 2021 | 0.0032624 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-10 13:20 | 2021-10-11 08:19 | 15 | 018:59 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101000113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1139 | 2021-10-10 | 17085 | keep | 0 | Oct | 2021 | 0.011637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-10 13:23 | 2021-10-10 13:26 | 2422 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA POR 1907-04 | S21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-10 | 7266 | keep | 0 | Oct | 2021 | 0.0049488 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2021-10-10 13:23 | 2021-10-10 13:26 | 2466 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA PARTE 1346 03 | S21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-10 | 7398 | keep | 0 | Oct | 2021 | 0.0050387 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2021-10-10 13:33 | 2021-10-10 17:04 | 20 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101000116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2021-10-10 | 4220 | keep | 0 | Oct | 2021 | 0.0028742 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-10 13:56 | 2021-10-10 15:07 | 30 | 001:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | B21101000118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-10-10 | 2130 | keep | 0 | Oct | 2021 | 0.0014507 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-10 14:11 | 2021-10-10 16:37 | 5 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21101000036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-10-10 | 730 | keep | 0 | Oct | 2021 | 0.0004972 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-10 14:14 | 2021-10-10 18:38 | 35 | 004:24 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS | B21101000119 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 264 | 2021-10-10 | 9240 | keep | 0 | Oct | 2021 | 0.0062933 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
YAUCO | 2021-10-10 14:15 | 2021-10-10 17:19 | 60 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21101000032 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2021-10-10 | 11040 | keep | 0 | Oct | 2021 | 0.0075193 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-10 14:25 | 2021-10-10 17:17 | 160 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REEMPLAZO MACHETE QUEMADO CERRO PUENTE Y 2 DISCOS | R21101000021 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2021-10-10 | 27520 | keep | 0 | Oct | 2021 | 0.018744 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
FAJARDO | 2021-10-10 14:25 | 2021-10-10 14:26 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101000123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 1830 | keep | 0 | Oct | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2021-10-10 14:35 | 2021-10-10 17:56 | 4 | 003:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA AJUSTAR TORNILLO EN BARRA DE PEDESTAL | R21101000124 | New_Event | Secondary Wire Down | Include | Include | Equipment | 201 | 2021-10-10 | 804 | keep | 0 | Oct | 2021 | 0.0005476 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-10-10 14:37 | 2021-10-10 18:30 | 279 | 003:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | C21101000043 | New_Event | Wire Down | Include | Include | Equipment | 233 | 2021-10-10 | 65007 | keep | 0 | Oct | 2021 | 0.044276 | 0.00019003 | Sustained | FALSE | TRUE | Not_TMED_Event | 279
SAN JUAN | 2021-10-10 14:44 | 2021-10-12 10:15 | 30 | 043:31 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN RISER SE REMPLAZO PARARRAYO DEFECTUOSO | S21101000181 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2611 | 2021-10-10 | 78330 | keep | 0 | Oct | 2021 | 0.05335 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-10-10 14:45 | 2021-10-10 18:34 | 110 | 003:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL | C21101000044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-10-10 | 25190 | keep | 0 | Oct | 2021 | 0.017157 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
BAYAMON | 2021-10-10 15:04 | 2021-10-10 16:58 | 10 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101000122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2021-10-10 | 1140 | keep | 0 | Oct | 2021 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-10 15:05 | 2021-10-10 18:46 | 30 | 003:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101000123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-10-10 | 6630 | keep | 0 | Oct | 2021 | 0.0045157 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-10-10 15:08 | 2021-10-10 19:29 | 100 | 004:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA MAL TIEMPO | C21101000047 | New_Event | Bad Weather | Include | Include | Weather | 261 | 2021-10-10 | 26100 | keep | 0 | Oct | 2021 | 0.017777 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-10 15:20 | 2021-10-10 15:21 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3604-06 CERRADO POR CONTROL | C21101000052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 315 | keep | 0 | Oct | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2021-10-10 15:20 | 2021-10-10 15:21 | 2906 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 3603-01 CERRADO POR CONTROL | C21101000052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2906 | keep | 0 | Oct | 2021 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
SAN JUAN | 2021-10-10 15:22 | 2021-10-10 19:32 | 6 | 004:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO CRUZADO | R21101000126 | New_Event | Secondary Wire Down | Include | Include | Equipment | 250 | 2021-10-10 | 1500 | keep | 0 | Oct | 2021 | 0.0010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-10 15:32 | 2021-10-10 20:10 | 15 | 004:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21101000032 | New_Event | Wire Down | Include | Include | Equipment | 278 | 2021-10-10 | 4170 | keep | 0 | Oct | 2021 | 0.0028402 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-10 15:59 | 2021-10-10 19:36 | 10 | 003:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | B21101000127 | New_Event | Cutout Failure | Include | Include | Equipment | 217 | 2021-10-10 | 2170 | keep | 0 | Oct | 2021 | 0.001478 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-10-10 16:08 | 2021-10-10 16:09 | 3070 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B21101000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-10 | 3070 | keep | 0 | Oct | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-10-10 16:08 | 2021-10-10 16:09 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2735 | keep | 0 | Oct | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-10-10 16:09 | 2021-10-11 10:38 | 80 | 018:29 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101000137 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1109 | 2021-10-10 | 88720 | keep | 0 | Oct | 2021 | 0.060427 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-10-10 16:29 | 2021-10-11 10:00 | 8 | 017:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | M21101000038 | New_Event | Bad Weather | Include | Include | Weather | 1051 | 2021-10-10 | 8408 | keep | 0 | Oct | 2021 | 0.0057267 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-10-10 16:31 | 2021-10-10 18:38 | 1 | 002:07 | S | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA INTERRUPTOR 2 AVERIADO | S21101000000 | New_Event | Switch Failure | Include | Include | Equipment | 127 | 2021-10-10 | 127 | keep | 0 | Oct | 2021 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-10 16:31 | 2021-10-10 18:38 | 1844 | 002:07 | S | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA INTERRUPTOR 2 AVERIADO | S21101000000 | New_Event | Switch Failure | Include | Include | Equipment | 127 | 2021-10-10 | 234188 | keep | 0 | Oct | 2021 | 0.1595 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2021-10-10 16:31 | 2021-10-10 18:38 | 2422 | 002:07 | S | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA INTERRUPTOR 2 AVERIADO | S21101000000 | New_Event | Switch Failure | Include | Include | Equipment | 127 | 2021-10-10 | 307594 | keep | 0 | Oct | 2021 | 0.2095 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
MAYAGÃœEZ | 2021-10-10 16:33 | 2021-10-10 18:22 | 2 | 001:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA AVERIADA | M21101000028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 109 | 2021-10-10 | 218 | keep | 0 | Oct | 2021 | 0.00014848 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-10-10 16:34 | 2021-10-11 00:16 | 1447 | 007:42 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 462 | 2021-10-10 | 668514 | keep | 0 | Oct | 2021 | 0.45532 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
MAYAGÃœEZ | 2021-10-10 16:42 | 2021-10-10 18:33 | 60 | 001:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21101000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-10-10 | 6660 | keep | 0 | Oct | 2021 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-10 16:48 | 2021-10-11 11:08 | 140 | 018:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C21101000067 | New_Event | Wire Down | Include | Include | Equipment | 1100 | 2021-10-10 | 154000 | keep | 0 | Oct | 2021 | 0.10489 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BARRANQUITAS | 2021-10-10 16:49 | 2021-10-11 10:35 | 50 | 017:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C21101000068 | New_Event | Bad Weather | Include | Include | Weather | 1066 | 2021-10-10 | 53300 | keep | 0 | Oct | 2021 | 0.036302 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-10 17:03 | 2021-10-10 17:07 | 1945 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA FIJAR LINEA PRIMARIA A AISLADOR EN TRONCAL DEL ALIMENTADOR | P21101000046 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-10-10 | 7780 | keep | 0 | Oct | 2021 | 0.0052989 | 0.0013247 | Momentary | FALSE | TRUE | Not_TMED_Event | 1945
YAUCO | 2021-10-10 17:04 | 2021-10-10 19:55 | 1475 | 002:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR. SE REEMPLAZO AISLADOR Y SE FIJO LINEA PRIMARIA | P211010000XX | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 171 | 2021-10-10 | 252225 | keep | 0 | Oct | 2021 | 0.17179 | 0.0010046 | Sustained | FALSE | TRUE | Not_TMED_Event | 1475
ARECIBO | 2021-10-10 17:06 | 2021-10-10 18:54 | 1 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21101000070 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-10-10 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-10 17:18 | 2021-10-11 11:23 | 20 | 018:05 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE DETECTO LA CAUSA | A21101000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1085 | 2021-10-10 | 21700 | keep | 0 | Oct | 2021 | 0.01478 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-10 17:43 | 2021-10-10 20:14 | 70 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101000047 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-10-10 | 10570 | keep | 0 | Oct | 2021 | 0.0071992 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-10-10 17:52 | 2021-10-10 20:55 | 46 | 003:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21101000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-10-10 | 8418 | keep | 0 | Oct | 2021 | 0.0057335 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
MAYAGÃœEZ | 2021-10-10 18:13 | 2021-10-10 18:14 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 470 | keep | 0 | Oct | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
BAYAMON | 2021-10-10 18:23 | 2021-10-10 19:43 | 1310 | 001:20 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | S21101000338 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-10-10 | 104800 | keep | 0 | Oct | 2021 | 0.071379 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2021-10-10 18:23 | 2021-10-10 18:24 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21101000077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2435 | keep | 0 | Oct | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-10 18:26 | 2021-10-11 10:51 | 30 | 016:25 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21101000339 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 985 | 2021-10-10 | 29550 | keep | 0 | Oct | 2021 | 0.020126 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-10 18:30 | 2021-10-10 18:31 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL 60% POR EL 1437-04 Y 40% POR EL 1301-04 | S21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-10 18:30 | 2021-10-10 18:31 | 1397 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1335-04 | S21101000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 1397 | keep | 0 | Oct | 2021 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
SAN JUAN | 2021-10-10 18:30 | 2021-10-10 18:31 | 602 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL | S21101000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-10 | 602 | keep | 0 | Oct | 2021 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
GUAYAMA | 2021-10-10 18:30 | 2021-10-10 19:42 | 55 | 001:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21101000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-10-10 | 3960 | keep | 0 | Oct | 2021 | 0.0026971 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-10-10 18:31 | 2021-10-11 10:30 | 257 | 015:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | S21101000354 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 959 | 2021-10-10 | 246463 | keep | 0 | Oct | 2021 | 0.16786 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
SAN JUAN | 2021-10-10 18:38 | 2021-10-10 18:40 | 928 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA 1422-03 Y 1422-05 | S21101000346 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-10 | 1856 | keep | 0 | Oct | 2021 | 0.0012641 | 0.00063206 | Momentary | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-10-10 18:38 | 2021-10-10 18:40 | 150 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL PARTE POR EL 1338-02 | S21101000346 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-10 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0.00010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-10-10 18:38 | 2021-10-10 18:40 | 637 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1338 02 | S21101000346 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-10 | 1274 | keep | 0 | Oct | 2021 | 0.00086772 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
BAYAMON | 2021-10-10 18:41 | 2021-10-10 19:26 | 10 | 000:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50KVA SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR Y PARARRAYO | B21100900063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2021-10-10 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-10 18:42 | 2021-10-11 14:56 | 250 | 020:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE CERRO PUENTE ABIERTO | A21101000073 | New_Event | Wire Down | Include | Include | Equipment | 1214 | 2021-10-10 | 303500 | keep | 0 | Oct | 2021 | 0.20671 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
GUAYAMA | 2021-10-10 18:48 | 2021-10-10 21:43 | 61 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21101000062 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2021-10-10 | 10675 | keep | 0 | Oct | 2021 | 0.0072707 | 4.1547e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 61
BAYAMON | 2021-10-10 18:50 | 2021-10-10 20:37 | 10 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101000145 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-10-10 | 1070 | keep | 0 | Oct | 2021 | 0.00072877 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-10 19:06 | 2021-10-12 12:52 | 60 | 041:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN CORTE DE LINEA SE REMPLAZO CAJA | S21101000357 | New_Event | Cutout Failure | Include | Include | Equipment | 2506 | 2021-10-10 | 150360 | keep | 0 | Oct | 2021 | 0.10241 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-10-10 19:12 | 2021-10-10 19:13 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 9902-03 EN SERVICIO | C21101000087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-10-10 19:12 | 2021-10-10 19:13 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 9902-02 EN SERVICIO | C21101000087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
HUMACAO | 2021-10-10 19:29 | 2021-10-10 19:30 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 5300 DE JUNCOS A LAS PIEDRAS | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-10 | 676 | keep | 0 | Oct | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | TRUE | Not_TMED_Event | 676
HUMACAO | 2021-10-10 19:29 | 2021-10-10 19:30 | 2873 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 5300 DE JUNCOS A LAS PIEDRAS | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-10 | 2873 | keep | 0 | Oct | 2021 | 0.0019568 | 0.0019568 | Momentary | FALSE | TRUE | Not_TMED_Event | 2873
HUMACAO | 2021-10-10 19:29 | 2021-10-10 19:30 | 3902 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 5300 DE JUNCOS A LAS PIEDRAS | C21101000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-10 | 3902 | keep | 0 | Oct | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | TRUE | Not_TMED_Event | 3902
HUMACAO | 2021-10-10 19:30 | 2021-10-11 16:04 | 100 | 020:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA MAL TIEMPO | C21101000047 | Partial_restoration | Bad Weather | Include | Include | Weather | 1234 | 2021-10-10 | 123400 | keep | 0 | Oct | 2021 | 0.084047 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-10 19:32 | 2021-10-10 19:33 | 390 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO Y SE CERRO POR CONTROL | S21101000368 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-10 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2021-10-10 19:33 | 2021-10-11 16:56 | 40 | 021:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR Y CRUCETA | S21101000384 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1283 | 2021-10-10 | 51320 | keep | 0 | Oct | 2021 | 0.034954 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-10 19:34 | 2021-10-10 22:43 | 15 | 003:09 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | B21101000147 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 189 | 2021-10-10 | 2835 | keep | 0 | Oct | 2021 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-10 19:35 | 2021-10-11 02:55 | 100 | 007:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21101000057 | New_Event | Wire Down | Include | Include | Equipment | 440 | 2021-10-10 | 44000 | keep | 0 | Oct | 2021 | 0.029968 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-10 19:35 | 2021-10-10 21:24 | 200 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR RAYOS | A21101000078 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-10-10 | 21800 | keep | 0 | Oct | 2021 | 0.014848 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-10 19:43 | 2021-10-10 20:04 | 350 | 000:21 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | S21101000338 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 21 | 2021-10-10 | 7350 | keep | 0 | Oct | 2021 | 0.0050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-10 19:46 | 2021-10-10 19:47 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21101000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 1307 | keep | 0 | Oct | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
ARECIBO | 2021-10-10 19:52 | 2021-10-11 11:23 | 20 | 015:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA FID 30681665 | A21101000077 | New_Event | Cutout Failure | Include | Include | Equipment | 931 | 2021-10-10 | 18620 | keep | 0 | Oct | 2021 | 0.012682 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-10-10 19:56 | 2021-10-11 09:10 | 16 | 013:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101000079 | New_Event | Bad Weather | Include | Include | Weather | 794 | 2021-10-10 | 12704 | keep | 0 | Oct | 2021 | 0.0086526 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
HUMACAO | 2021-10-10 20:03 | 2021-10-11 14:07 | 80 | 018:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21101000093 | New_Event | Bad Weather | Include | Include | Weather | 1084 | 2021-10-10 | 86720 | keep | 0 | Oct | 2021 | 0.059065 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-10 20:04 | 2021-10-10 22:32 | 50 | 002:28 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21101000000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-10-10 | 7400 | keep | 0 | Oct | 2021 | 0.0050401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-10 20:30 | 2021-10-10 23:38 | 25 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO CARGA POR EL 1715-02 | B21101000066 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2021-10-10 | 4700 | keep | 0 | Oct | 2021 | 0.0032011 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-10-10 20:37 | 2021-10-11 10:37 | 125 | 014:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA RATON CRUZO LA LINEA | A21101000082 | New_Event |  |  | Include | Wildlife | 840 | 2021-10-10 | 105000 | keep | 0 | Oct | 2021 | 0.071515 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
HUMACAO | 2021-10-10 20:41 | 2021-10-10 20:42 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21101000097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2021-10-10 20:43 | 2021-10-10 20:44 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21101000098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-10 | 2126 | keep | 0 | Oct | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
VEGA BAJA | 2021-10-10 20:47 | 2021-10-11 09:24 | 50 | 012:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21101000171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 757 | 2021-10-10 | 37850 | keep | 0 | Oct | 2021 | 0.025779 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-10 20:51 | 2021-10-11 06:20 | 264 | 009:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P21101000080 | New_Event | Bad Weather | Include | Include | Weather | 569 | 2021-10-10 | 150216 | keep | 0 | Oct | 2021 | 0.10231 | 0.00017981 | Sustained | FALSE | TRUE | Not_TMED_Event | 264
MAYAGÃœEZ | 2021-10-10 21:07 | 2021-10-11 10:15 | 20 | 013:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M21101000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 788 | 2021-10-10 | 15760 | keep | 0 | Oct | 2021 | 0.010734 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-10 21:12 | 2021-10-11 17:07 | 30 | 019:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M21101000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1195 | 2021-10-10 | 35850 | keep | 0 | Oct | 2021 | 0.024417 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-10 21:31 | 2021-10-11 12:43 | 50 | 015:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101000177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 912 | 2021-10-10 | 45600 | keep | 0 | Oct | 2021 | 0.031058 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-10 21:32 | 2021-10-11 12:22 | 6 | 014:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 75KVA X 75KVA 2400/4160V 120/240V MARCA ERMCU SER:82011973268 FID:18420797 | M21101000068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 890 | 2021-10-10 | 5340 | keep | 0 | Oct | 2021 | 0.003637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-10 21:40 | 2021-10-11 12:06 | 30 | 014:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO BAJANTES SECUNDARIOS | A21101000083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 866 | 2021-10-10 | 25980 | keep | 0 | Oct | 2021 | 0.017695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-10-10 22:03 | 2021-10-11 | 100 | 001:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-10-10 | 11700 | keep | 0 | Oct | 2021 | 0.0079688 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-10 22:05 | 2021-10-11 09:57 | 20 | 011:52 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA POR DESGANCHE | M21101000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 712 | 2021-10-10 | 14240 | keep | 0 | Oct | 2021 | 0.0096988 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-10 22:36 | 2021-10-11 21:14 | 80 | 022:38 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN RISER SE REMPLAZO PARARAYO EN SU-1 | B21101000186 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1358 | 2021-10-10 | 108640 | keep | 0 | Oct | 2021 | 0.073994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-10-10 22:40 | 2021-10-11 15:00 | 349 | 016:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE CERRO 2 BAJANTES DE MACHETE A LINEA | R21101000139 | New_Event | Wire Down | Include | Include | Equipment | 980 | 2021-10-10 | 342020 | keep | 0 | Oct | 2021 | 0.23295 | 0.0002377 | Sustained | FALSE | TRUE | Not_TMED_Event | 349
MAYAGÃœEZ | 2021-10-10 22:41 | 2021-10-11 13:07 | 10 | 014:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON CAJAS PRIMARIAS DEFECTUOSAS MARCA CHAIST 100AMP | M21101000073 | New_Event | Cutout Failure | Include | Include | Equipment | 866 | 2021-10-10 | 8660 | keep | 0 | Oct | 2021 | 0.0058983 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-10 23:01 | 2021-10-11 02:00 | 300 | 002:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE ABREN PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA LINEA PRIMARIA PARTIDA Y SE CERRO N/O CON ALIMENTADOR 5013-2 FRENTE A JUANA DIAZ TC | P21101000089 | New_Event | Wire Down | Include | Include | Equipment | 179 | 2021-10-10 | 53700 | keep | 0 | Oct | 2021 | 0.036575 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-10 23:30 | 2021-10-11 20:12 | 200 | 020:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | M21101000077 | New_Event | Cutout Failure | Include | Include | Equipment | 1242 | 2021-10-10 | 248400 | keep | 0 | Oct | 2021 | 0.16918 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-10-10 23:38 | 2021-10-11 01:01 | 35 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ENTRE URB. FOREST HILL CALLE COMERIO Y CALLE #2 CARR 167 PARA CERRAR PUENTE ABIERTO | B21101000066 | Additional_clients | Wire Down | Include | Include | Equipment | 83 | 2021-10-10 | 2905 | keep | 0 | Oct | 2021 | 0.0019786 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-10 23:49 | 2021-10-11 19:22 | 25 | 019:33 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE CERRO PUENTES | B21101000191 | New_Event | Defective Pole | Include | Include | Equipment | 1173 | 2021-10-10 | 29325 | keep | 0 | Oct | 2021 | 0.019973 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2021-10-11 00:04 | 2021-10-11 12:40 | 200 | 012:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | P21101000023 | New_Event | Wire Down | Include | Include | Equipment | 756 | 2021-10-11 | 151200 | keep | 0 | Oct | 2021 | 0.10298 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-10-11 00:06 | 2021-10-11 00:07 | 635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 635 | keep | 0 | Oct | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
BAYAMON | 2021-10-11 00:25 | 2021-10-11 09:41 | 20 | 009:16 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2021-10-11 | 11120 | keep | 0 | Oct | 2021 | 0.0075738 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-11 00:25 | 2021-10-11 11:26 | 60 | 011:01 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTE DE LINEA DIFERENTES | B21101100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 661 | 2021-10-11 | 39660 | keep | 0 | Oct | 2021 | 0.027012 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-11 01:37 | 2021-10-11 01:38 | 418 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 418 | keep | 0 | Oct | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
FAJARDO | 2021-10-11 01:52 | 2021-10-11 10:18 | 30 | 008:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA BAMBUAS SOBRE LINEA | R21101100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2021-10-11 | 15180 | keep | 0 | Oct | 2021 | 0.010339 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-11 02:41 | 2021-10-11 16:59 | 1 | 014:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 858 | 2021-10-11 | 858 | keep | 0 | Oct | 2021 | 0.00058438 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-10-11 02:46 | 2021-10-11 10:00 | 79 | 007:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA | P21101100003 | New_Event | Bad Weather | Include | Include | Weather | 434 | 2021-10-11 | 34286 | keep | 0 | Oct | 2021 | 0.023352 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
ARECIBO | 2021-10-11 02:48 | 2021-10-11 10:29 | 1 | 007:41 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO CRUZADO | A21101100001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 461 | 2021-10-11 | 461 | keep | 0 | Oct | 2021 | 0.00031399 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-10-11 03:35 | 2021-10-11 10:06 | 150 | 006:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101100002 | New_Event | Bad Weather | Include | Include | Weather | 391 | 2021-10-11 | 58650 | keep | 0 | Oct | 2021 | 0.039946 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-10-11 03:37 | 2021-10-11 03:38 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 308 | keep | 0 | Oct | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
PONCE | 2021-10-11 03:44 | 2021-10-11 19:17 | 100 | 015:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE DEJO OTRO CORTE DE LINEA ABIERTO POR ALAMBRE EN EL PISO SE DEJARA PARA EL OTRO DIA | P21101100004 | New_Event | Wire Down | Include | Include | Equipment | 933 | 2021-10-11 | 93300 | keep | 0 | Oct | 2021 | 0.063546 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-11 04:04 | 2021-10-11 04:05 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 1342 | keep | 0 | Oct | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CANOVANAS | 2021-10-11 04:32 | 2021-10-11 04:33 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 7621 | keep | 0 | Oct | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CAGUAS | 2021-10-11 04:34 | 2021-10-11 04:36 | 906 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | C21101100020 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-10-11 | 1812 | keep | 0 | Oct | 2021 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2021-10-11 04:36 | 2021-10-12 19:23 | 164 | 038:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE LEVANTO ALAMBRE PRIMARIO | C21101200041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 2327 | 2021-10-11 | 381628 | keep | 0 | Oct | 2021 | 0.25993 | 0.0001117 | Sustained | FALSE | TRUE | Not_TMED_Event | 164
CAGUAS | 2021-10-11 04:37 | 2021-10-11 12:27 | 130 | 007:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA LLUVIAS | C21101100011 | New_Event | Bad Weather | Include | Include | Weather | 470 | 2021-10-11 | 61100 | keep | 0 | Oct | 2021 | 0.041615 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-10-11 04:59 | 2021-10-11 10:21 | 100 | 005:22 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN RISER SE REPARO TERMINACION | B21101100004 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 322 | 2021-10-11 | 32200 | keep | 0 | Oct | 2021 | 0.021931 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-10-11 05:23 | 2021-10-11 11:48 | 59 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21101100018 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2021-10-11 | 22715 | keep | 0 | Oct | 2021 | 0.015471 | 4.0185e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 59
SAN JUAN | 2021-10-11 05:25 | 2021-10-11 09:11 | 345 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO CARGA POR 1619-02 | R21101100005 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-10-11 | 77970 | keep | 0 | Oct | 2021 | 0.053105 | 0.00023498 | Sustained | FALSE | TRUE | Not_TMED_Event | 345
CAGUAS | 2021-10-11 05:48 | 2021-10-11 10:20 | 120 | 004:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21101100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-10-11 | 32640 | keep | 0 | Oct | 2021 | 0.022231 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
CAGUAS | 2021-10-11 05:51 | 2021-10-11 19:38 | 112 | 013:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21101100023 | New_Event | Bad Weather | Include | Include | Weather | 827 | 2021-10-11 | 92624 | keep | 0 | Oct | 2021 | 0.063086 | 7.6283e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 112
CAGUAS | 2021-10-11 05:59 | 2021-10-11 16:22 | 62 | 010:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21101100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2021-10-11 | 38626 | keep | 0 | Oct | 2021 | 0.026308 | 4.2228e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 62
CAGUAS | 2021-10-11 06:08 | 2021-10-11 11:35 | 300 | 005:27 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21101100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2021-10-11 | 98100 | keep | 0 | Oct | 2021 | 0.066815 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-11 06:10 | 2021-10-11 18:30 | 100 | 012:20 | P | MAL TIEMPO/RAYOS/WET ASH | 6 X 40 Y 3 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101100009 | New_Event | Bad Weather | Include | Include | Weather | 740 | 2021-10-11 | 74000 | keep | 0 | Oct | 2021 | 0.050401 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-11 06:52 | 2021-10-11 06:54 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO | B21101100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 4468 | keep | 0 | Oct | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-10-11 06:54 | 2021-10-11 10:33 | 1085 | 003:39 | T | DESGANCHE | DISPARO INTERRUPTOR SE CERRO POR SCADA SE REALIZO DESGANCHE | S21101100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-10-11 | 237615 | keep | 0 | Oct | 2021 | 0.16184 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
YAUCO | 2021-10-11 06:55 | 2021-10-11 08:50 | 105 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P21101100007 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-10-11 | 12075 | keep | 0 | Oct | 2021 | 0.0082242 | 7.1515e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 105
BARRANQUITAS | 2021-10-11 07:02 | 2021-10-11 12:53 | 100 | 005:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2021-10-11 | 35100 | keep | 0 | Oct | 2021 | 0.023906 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-11 07:10 | 2021-10-11 07:11 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 3597 | keep | 0 | Oct | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-10-11 07:11 | 2021-10-12 10:46 | 40 | 027:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101100072 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1655 | 2021-10-11 | 66200 | keep | 0 | Oct | 2021 | 0.045089 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-11 07:11 | 2021-10-11 12:39 | 60 | 005:28 | P | HERRAJE ROTO O PODRIDO | 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE REEMPLAZO CRUCETA | R21101100015 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 328 | 2021-10-11 | 19680 | keep | 0 | Oct | 2021 | 0.013404 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-11 07:34 | 2021-10-11 11:39 | 2 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21101000005 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-10-11 | 490 | keep | 0 | Oct | 2021 | 0.00033374 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-10-11 07:38 | 2021-10-11 18:24 | 55 | 010:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21101100041 | New_Event | Bad Weather | Include | Include | Weather | 646 | 2021-10-11 | 35530 | keep | 0 | Oct | 2021 | 0.024199 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CAGUAS | 2021-10-11 07:57 | 2021-10-11 07:58 | 1342 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIAS | C21101100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-11 | 1342 | keep | 0 | Oct | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-10-11 08:00 | 2021-10-11 15:44 | 200 | 007:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA REPARO 2 BAJANTES QUEMADOS | C21101100048 | New_Event | Wire Down | Include | Include | Equipment | 464 | 2021-10-11 | 92800 | keep | 0 | Oct | 2021 | 0.063206 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-10-11 08:02 | 2021-10-11 12:04 | 20 | 004:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R21101100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-10-11 | 4840 | keep | 0 | Oct | 2021 | 0.0032965 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
GUAYAMA | 2021-10-11 08:09 | 2021-10-11 10:36 | 10 | 002:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR DESCARGA ELECTRICA | P21101100008 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2021-10-11 | 1470 | keep | 0 | Oct | 2021 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-11 08:09 | 2021-10-11 10:45 | 15 | 002:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P21101100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-10-11 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-11 08:13 | 2021-10-11 11:33 | 100 | 003:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21101100054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-10-11 | 20000 | keep | 0 | Oct | 2021 | 0.013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-11 08:17 | 2021-10-11 14:12 | 40 | 005:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-10-11 | 14200 | keep | 0 | Oct | 2021 | 0.0096716 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-10-11 08:27 | 2021-10-11 08:28 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 3041 | keep | 0 | Oct | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2021-10-11 08:29 | 2021-10-11 16:12 | 40 | 007:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2021-10-11 | 18520 | keep | 0 | Oct | 2021 | 0.012614 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-11 08:32 | 2021-10-12 14:09 | 1 | 029:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101100016 | New_Event | Bad Weather | Include | Include | Weather | 1777 | 2021-10-11 | 1777 | keep | 0 | Oct | 2021 | 0.0012103 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-11 08:35 | 2021-10-11 08:37 | 3718 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S21101100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 7436 | keep | 0 | Oct | 2021 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
YAUCO | 2021-10-11 08:42 | 2021-10-12 17:47 | 76 | 033:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X80 EN CORTE DE LINEA. SE LEVANTO ALAMBRE PRIMARIO | P21101100012 | New_Event | Wire Down | Include | Include | Equipment | 1985 | 2021-10-11 | 150860 | keep | 0 | Oct | 2021 | 0.10275 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
SAN JUAN | 2021-10-11 08:43 | 2021-10-11 12:23 | 30 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA Y 1 X 25 EN SU | S21101100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-10-11 | 6600 | keep | 0 | Oct | 2021 | 0.0044952 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-10-11 08:45 | 2021-10-11 20:21 | 10 | 011:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | C21101100069 | New_Event | Bad Weather | Include | Include | Weather | 696 | 2021-10-11 | 6960 | keep | 0 | Oct | 2021 | 0.0047404 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-11 08:51 | 2021-10-11 15:30 | 60 | 006:39 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-1 | B21101100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 399 | 2021-10-11 | 23940 | keep | 0 | Oct | 2021 | 0.016305 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-10-11 08:52 | 2021-10-11 11:23 | 75 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-10-11 | 11325 | keep | 0 | Oct | 2021 | 0.0077134 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-10-11 08:53 | 2021-10-11 19:43 | 50 | 010:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | S21101100046 | New_Event | Cutout Failure | Include | Include | Equipment | 650 | 2021-10-11 | 32500 | keep | 0 | Oct | 2021 | 0.022136 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-11 08:56 | 2021-10-12 11:41 | 3 | 026:45 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRARON RAMAS | M21101100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1605 | 2021-10-11 | 4815 | keep | 0 | Oct | 2021 | 0.0032795 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-10-11 08:59 | 2021-10-11 16:09 | 40 | 007:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES | A21101100010 | New_Event | Cutout Failure | Include | Include | Equipment | 430 | 2021-10-11 | 17200 | keep | 0 | Oct | 2021 | 0.011715 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-11 09:02 | 2021-10-12 13:32 | 150 | 028:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101100020 | New_Event | Bad Weather | Include | Include | Weather | 1710 | 2021-10-11 | 256500 | keep | 0 | Oct | 2021 | 0.1747 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-11 09:03 | 2021-10-11 20:21 | 15 | 011:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21101100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 678 | 2021-10-11 | 10170 | keep | 0 | Oct | 2021 | 0.0069267 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-10-11 09:12 | 2021-10-11 17:08 | 1 | 007:56 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA Y 1 X 25 EN RISER | B21101100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2021-10-11 | 476 | keep | 0 | Oct | 2021 | 0.0003242 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-11 09:15 | 2021-10-11 14:39 | 10 | 005:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21101100014 | New_Event | Bad Weather | Include | Include | Weather | 324 | 2021-10-11 | 3240 | keep | 0 | Oct | 2021 | 0.0022067 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-11 09:20 | 2021-10-11 18:22 | 22 | 009:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2021-10-11 | 11924 | keep | 0 | Oct | 2021 | 0.0081214 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
BARRANQUITAS | 2021-10-11 09:22 | 2021-10-11 14:07 | 75 | 004:45 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21101100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-10-11 | 21375 | keep | 0 | Oct | 2021 | 0.014558 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-10-11 09:23 | 2021-10-12 20:50 | 14 | 035:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2127 | 2021-10-11 | 29778 | keep | 0 | Oct | 2021 | 0.020282 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
HUMACAO | 2021-10-11 09:25 | 2021-10-11 12:52 | 40 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR | C21101100088 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2021-10-11 | 8280 | keep | 0 | Oct | 2021 | 0.0056395 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-10-11 09:25 | 2021-10-11 13:16 | 1742 | 003:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | FUERTES LLUVIAS DISPARO SE REEMPLAZO CAJA QUEMADA | C21101100000 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2021-10-11 | 402402 | keep | 0 | Oct | 2021 | 0.27407 | 0.0011865 | Sustained | FALSE | FALSE | Not_TMED_Event | 1742
PONCE | 2021-10-11 09:27 | 2021-10-11 22:16 | 15 | 012:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA PARTIDA | P21404400017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 769 | 2021-10-11 | 11535 | keep | 0 | Oct | 2021 | 0.0078564 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-10-11 09:29 | 2021-10-11 14:40 | 35 | 005:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | P21101100018 | New_Event | Wire Down | Include | Include | Equipment | 311 | 2021-10-11 | 10885 | keep | 0 | Oct | 2021 | 0.0074137 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-10-11 09:37 | 2021-10-11 13:34 | 2276 | 003:57 | T | DESGANCHE | DISPARO SE RETIRARON BAMBUAS SOBRE LINEAS | C21101100102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-10-11 | 539412 | keep | 0 | Oct | 2021 | 0.36739 | 0.0015502 | Sustained | FALSE | TRUE | Not_TMED_Event | 2276
CANOVANAS | 2021-10-11 09:38 | 2021-10-11 10:44 | 8 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21101000136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-10-11 | 528 | keep | 0 | Oct | 2021 | 0.00035962 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-11 09:38 | 2021-10-11 17:40 | 15 | 008:02 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO 2 POSTES DE METAL Y 1 DE MADERA Y SE CERRO CORTE DE LINEA | M21101100031 | New_Event | Defective Pole | Include | Include | Equipment | 482 | 2021-10-11 | 7230 | keep | 0 | Oct | 2021 | 0.0049243 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-11 09:39 | 2021-10-11 09:44 | 10 | 000:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES SECUNDARIOS Y SE SECIIONALIZO TOMA AVERIADA | S21101000379 | New_Event | Secondary Wire Down | Include | Include | Equipment | 5 | 2021-10-11 | 50 | keep | 0 | Oct | 2021 | 3.4055e-05 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-11 09:39 | 2021-10-11 09:45 | 3 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37800 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-11 | 18 | keep | 0 | Oct | 2021 | 1.226e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-10-11 09:39 | 2021-10-11 09:45 | 3957 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37800 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-11 | 23742 | keep | 0 | Oct | 2021 | 0.016171 | 0.0026951 | Sustained | FALSE | TRUE | Not_TMED_Event | 3957
BAYAMON | 2021-10-11 09:39 | 2021-10-11 09:45 | 58 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37800 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-11 | 348 | keep | 0 | Oct | 2021 | 0.00023702 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
SAN JUAN | 2021-10-11 09:39 | 2021-10-11 09:45 | 386 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37800 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-11 | 2316 | keep | 0 | Oct | 2021 | 0.0015774 | 0.0002629 | Sustained | FALSE | TRUE | Not_TMED_Event | 386
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 108 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 432 | keep | 0 | Oct | 2021 | 0.00029423 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 1368 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 5472 | keep | 0 | Oct | 2021 | 0.003727 | 0.00093174 | Momentary | FALSE | TRUE | Not_TMED_Event | 1368
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 2064 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 8256 | keep | 0 | Oct | 2021 | 0.0056231 | 0.0014058 | Momentary | FALSE | TRUE | Not_TMED_Event | 2064
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 1681 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA CARGA 1346 04 Y 1346 06 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 6724 | keep | 0 | Oct | 2021 | 0.0045797 | 0.0011449 | Momentary | FALSE | TRUE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 2435 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA CARGA 1346 04 Y 1346 06 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 9740 | keep | 0 | Oct | 2021 | 0.0066339 | 0.0016585 | Momentary | FALSE | TRUE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 726 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA CARGA 1346 04 Y 1346 06 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 2904 | keep | 0 | Oct | 2021 | 0.0019779 | 0.00049448 | Momentary | FALSE | TRUE | Not_TMED_Event | 726
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 225 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA CARGA 1346 04 Y 1346 06 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 900 | keep | 0 | Oct | 2021 | 0.00061299 | 0.00015325 | Momentary | FALSE | TRUE | Not_TMED_Event | 225
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 870 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA CARGA 1346 04 Y 1346 06 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 3480 | keep | 0 | Oct | 2021 | 0.0023702 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 3932 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CARGA POR 1303 03 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 15728 | keep | 0 | Oct | 2021 | 0.010712 | 0.0026781 | Momentary | FALSE | TRUE | Not_TMED_Event | 3932
SAN JUAN | 2021-10-11 09:44 | 2021-10-11 09:48 | 1598 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CARGA POR 1303 05 | S21101100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 6392 | keep | 0 | Oct | 2021 | 0.0043536 | 0.0010884 | Momentary | FALSE | TRUE | Not_TMED_Event | 1598
SAN JUAN | 2021-10-11 09:48 | 2021-10-11 09:51 | 10 | 000:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES SECUNDARIOS Y SE SECIIONALIZO TOMA AVERIADA | S21101000379 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 3 | 2021-10-11 | 30 | keep | 0 | Oct | 2021 | 2.0433e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 09:50 | 2021-10-11 09:56 | 828 | 000:06 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL PARTE DE SU CARGA POR 1206 04 | S21101100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-11 | 4968 | keep | 0 | Oct | 2021 | 0.0033837 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2021-10-11 09:50 | 2021-10-11 09:56 | 1900 | 000:06 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL PARTE DE SU CARGA POR 1206 04 | S21101100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-11 | 11400 | keep | 0 | Oct | 2021 | 0.0077645 | 0.0012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 1900
SAN JUAN | 2021-10-11 09:50 | 2021-10-11 09:56 | 1799 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL LLEVA PARTE 1204 04 1204 03 Y 1303 02 | S21101100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-11 | 10794 | keep | 0 | Oct | 2021 | 0.0073517 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-10-11 09:50 | 2021-10-11 09:56 | 300 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL PARTE DE SU CARGA POR 1206 04 | S21101100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-11 | 1800 | keep | 0 | Oct | 2021 | 0.001226 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-11 09:51 | 2021-10-11 09:59 | 1681 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303 04 | S21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-10-11 | 13448 | keep | 0 | Oct | 2021 | 0.0091594 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-11 09:51 | 2021-10-11 10:00 | 540 | 000:09 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA POR 1529-15 | S21101100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-10-11 | 4860 | keep | 0 | Oct | 2021 | 0.0033101 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
SAN JUAN | 2021-10-11 09:51 | 2021-10-11 09:59 | 1598 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303 04 | S21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-10-11 | 12784 | keep | 0 | Oct | 2021 | 0.0087071 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-10-11 09:51 | 2021-10-11 10:00 | 1802 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA EL 30% 1346-02 | S21101100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-10-11 | 16218 | keep | 0 | Oct | 2021 | 0.011046 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-10-11 09:52 | 2021-10-11 14:59 | 1 | 005:07 | P | DESGANCHE | 3 X 30 EN RISER SE REALIZO DESGANCHE | B21101100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-10-11 | 307 | keep | 0 | Oct | 2021 | 0.0002091 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-11 09:53 | 2021-10-11 09:54 | 3432 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PORTATIL | S21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 3432 | keep | 0 | Oct | 2021 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2021-10-11 09:53 | 2021-10-11 09:54 | 1381 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PORTATIL | S21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 1381 | keep | 0 | Oct | 2021 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
CAGUAS | 2021-10-11 09:53 | 2021-10-11 15:28 | 100 | 005:35 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA | C21101100218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-10-11 | 33500 | keep | 0 | Oct | 2021 | 0.022817 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-11 09:59 | 2021-10-11 10:33 | 10 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES SECUNDARIOS Y SE SECIIONALIZO TOMA AVERIADA | S21101000379 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-10-11 | 340 | keep | 0 | Oct | 2021 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-11 10:02 | 2021-10-11 13:24 | 928 | 003:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE PATRULLO Y NO SE ENCONTRO CAUSA LLEVA CARGA 1422 05 | S21101100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-10-11 | 187456 | keep | 0 | Oct | 2021 | 0.12768 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-10-11 10:02 | 2021-10-11 13:24 | 150 | 003:22 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE PATRULLO Y NO SE ENCONTRO CAUSA PARTE POR EL 1338-02 | S21101100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-10-11 | 30300 | keep | 0 | Oct | 2021 | 0.020637 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-10-11 10:02 | 2021-10-11 13:24 | 637 | 003:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE PATRULLO Y NO SE ENCONTRO CAUSA CARGA POR 1338 02 | S21101100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-10-11 | 128674 | keep | 0 | Oct | 2021 | 0.087639 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 137 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 548 | keep | 0 | Oct | 2021 | 0.00037324 | 9.331e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 457 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 1828 | keep | 0 | Oct | 2021 | 0.001245 | 0.00031126 | Momentary | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 1225 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 0.00083434 | Momentary | FALSE | TRUE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 1452 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 5808 | keep | 0 | Oct | 2021 | 0.0039558 | 0.00098895 | Momentary | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 616 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 2464 | keep | 0 | Oct | 2021 | 0.0016782 | 0.00041955 | Momentary | FALSE | TRUE | Not_TMED_Event | 616
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 3432 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 13728 | keep | 0 | Oct | 2021 | 0.0093501 | 0.0023375 | Momentary | FALSE | TRUE | Not_TMED_Event | 3432
SAN JUAN | 2021-10-11 10:12 | 2021-10-11 10:16 | 553 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-11 | 2212 | keep | 0 | Oct | 2021 | 0.0015066 | 0.00037665 | Momentary | FALSE | TRUE | Not_TMED_Event | 553
FAJARDO | 2021-10-11 10:15 | 2021-10-11 14:43 | 5 | 004:28 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE REALIZO DESGANCHE | R21101100040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 268 | 2021-10-11 | 1340 | keep | 0 | Oct | 2021 | 0.00091267 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-11 10:21 | 2021-10-11 10:40 | 4028 | 000:19 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B21101100038 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 19 | 2021-10-11 | 76532 | keep | 0 | Oct | 2021 | 0.052126 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
CAGUAS | 2021-10-11 10:25 | 2021-10-12 11:08 | 90 | 024:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21101100134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1483 | 2021-10-11 | 133470 | keep | 0 | Oct | 2021 | 0.090906 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 137 | 008:06 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 66582 | keep | 0 | Oct | 2021 | 0.045349 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 457 | 008:06 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 222102 | keep | 0 | Oct | 2021 | 0.15127 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 1225 | 008:06 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN L-3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 595350 | keep | 0 | Oct | 2021 | 0.40549 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 1452 | 008:06 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN L-3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 705672 | keep | 0 | Oct | 2021 | 0.48063 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 616 | 008:06 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN L-3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 299376 | keep | 0 | Oct | 2021 | 0.2039 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 3432 | 008:06 | P | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO L-3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 1667952 | keep | 0 | Oct | 2021 | 1.136 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2021-10-11 10:26 | 2021-10-11 18:32 | 553 | 008:06 | P | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO L-3600 | S21101100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 486 | 2021-10-11 | 268758 | keep | 0 | Oct | 2021 | 0.18305 | 0.00037665 | Sustained | FALSE | FALSE | Not_TMED_Event | 553
CANOVANAS | 2021-10-11 10:29 | 2021-10-12 14:06 | 6 | 027:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | R21101100050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1657 | 2021-10-11 | 9942 | keep | 0 | Oct | 2021 | 0.0067715 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-10-11 10:33 | 2021-10-11 12:47 | 40 | 002:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO AISLADORES | C21101000015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 134 | 2021-10-11 | 5360 | keep | 0 | Oct | 2021 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-11 10:38 | 2021-10-11 10:40 | 418 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S21101100155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 836 | keep | 0 | Oct | 2021 | 0.0005694 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-10-11 10:40 | 2021-10-11 12:51 | 100 | 002:11 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN RISER SE REPARO TERMINACION | B21101100004 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 131 | 2021-10-11 | 13100 | keep | 0 | Oct | 2021 | 0.0089224 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-11 10:42 | 2021-10-11 13:21 | 25 | 002:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA AVERIADO MISMA CAPACIDAD | A21101100102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 159 | 2021-10-11 | 3975 | keep | 0 | Oct | 2021 | 0.0027074 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-10-11 10:58 | 2021-10-11 13:18 | 9 | 002:20 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | C21101100000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 140 | 2021-10-11 | 1260 | keep | 0 | Oct | 2021 | 0.00085818 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-10-11 11:01 | 2021-10-12 18:46 | 30 | 031:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 20 EN TRANSFORMADOR SE REMPLAZO PUENTE | S21101100182 | New_Event | Wire Down | Include | Include | Equipment | 1905 | 2021-10-11 | 57150 | keep | 0 | Oct | 2021 | 0.038925 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-10-11 11:01 | 2021-10-11 15:50 | 150 | 004:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 2 X 40 EN CORTES DE LINEA MAL TIEMPO | C21101100144 | New_Event | Bad Weather | Include | Include | Weather | 289 | 2021-10-11 | 43350 | keep | 0 | Oct | 2021 | 0.029525 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-10-11 11:01 | 2021-10-11 13:05 | 80 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21101100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-10-11 | 9920 | keep | 0 | Oct | 2021 | 0.0067565 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-11 11:04 | 2021-10-11 22:07 | 470 | 011:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PARTIDO | M21101100055 | New_Event | Wire Down | Include | Include | Equipment | 663 | 2021-10-11 | 311610 | keep | 0 | Oct | 2021 | 0.21224 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-10-11 11:04 | 2021-10-11 11:05 | 2483 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | M21101100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-11 | 2483 | keep | 0 | Oct | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-10-11 11:05 | 2021-10-11 11:06 | 2483 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21101100000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-10-11 | 2483 | keep | 0 | Oct | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
BAYAMON | 2021-10-11 11:08 | 2021-10-11 11:09 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 112 | keep | 0 | Oct | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
ARECIBO | 2021-10-11 11:10 | 2021-10-11 12:18 | 1 | 001:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA PRIMARIA | A21101100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-10-11 | 68 | keep | 0 | Oct | 2021 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BARRANQUITAS | 2021-10-11 11:12 | 2021-10-11 15:46 | 30 | 004:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21101100145 | New_Event | Bad Weather | Include | Include | Weather | 274 | 2021-10-11 | 8220 | keep | 0 | Oct | 2021 | 0.0055986 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-11 11:17 | 2021-10-11 19:48 | 80 | 008:31 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 Y 1 X 80 EN CORTES DE LINEA SE REPARO TERMINACION EN AEREO PROVISIONAL | R21101100058 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 511 | 2021-10-11 | 40880 | keep | 0 | Oct | 2021 | 0.027843 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-11 11:18 | 2021-10-11 15:50 | 10 | 004:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21101100147 | New_Event | Bad Weather | Include | Include | Weather | 272 | 2021-10-11 | 2720 | keep | 0 | Oct | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-11 11:24 | 2021-10-11 16:55 | 10 | 005:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21101100149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 331 | 2021-10-11 | 3310 | keep | 0 | Oct | 2021 | 0.0022544 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-11 11:24 | 2021-10-11 13:45 | 1 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21101100028 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2021-10-11 | 141 | keep | 0 | Oct | 2021 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-11 11:28 | 2021-10-11 18:01 | 50 | 006:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2021-10-11 | 19650 | keep | 0 | Oct | 2021 | 0.013384 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-11 11:43 | 2021-10-11 18:37 | 30 | 006:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101100159 | New_Event | Bad Weather | Include | Include | Weather | 414 | 2021-10-11 | 12420 | keep | 0 | Oct | 2021 | 0.0084592 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-10-11 11:44 | 2021-10-11 11:45 | 1924 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211011000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 1924 | keep | 0 | Oct | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
SAN JUAN | 2021-10-11 11:49 | 2021-10-11 17:50 | 40 | 006:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y 1 X 30 SE REALIZO DESGANCHE | S21101100203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2021-10-11 | 14440 | keep | 0 | Oct | 2021 | 0.009835 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-10-11 11:53 | 2021-10-11 17:56 | 100 | 006:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1X100 EN CORTE DE LINEA POR FUERTES LLUVIAS | P21101100049 | New_Event | Bad Weather | Include | Include | Weather | 363 | 2021-10-11 | 36300 | keep | 0 | Oct | 2021 | 0.024724 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-11 11:55 | 2021-10-11 11:57 | 1862 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE CANOVANAS TC A BARRAZAS | R21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-11 | 3724 | keep | 0 | Oct | 2021 | 0.0025364 | 0.0012682 | Momentary | FALSE | TRUE | Not_TMED_Event | 1862
SAN JUAN | 2021-10-11 11:55 | 2021-10-11 11:57 | 1613 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE CANOVANAS TC A BARRAZAS | R21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-11 | 3226 | keep | 0 | Oct | 2021 | 0.0021972 | 0.0010986 | Momentary | FALSE | TRUE | Not_TMED_Event | 1613
SAN JUAN | 2021-10-11 11:55 | 2021-10-11 11:57 | 1448 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE CANOVANAS TC A BARRAZAS | R21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-11 | 2896 | keep | 0 | Oct | 2021 | 0.0019725 | 0.00098623 | Momentary | FALSE | TRUE | Not_TMED_Event | 1448
BAYAMON | 2021-10-11 11:57 | 2021-10-11 17:08 | 50 | 005:11 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2021-10-11 | 15550 | keep | 0 | Oct | 2021 | 0.010591 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-11 12:03 | 2021-10-11 14:48 | 778 | 002:45 | T | DESGANCHE | INTERRUPTOR HIZO LAS 3 OPERACIONES Y QUEDO FUERA SE ENCONTRO ARBOL SOBRE LINEA SU CARGA ESTA POR EL 5011-05 | P21101100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-10-11 | 128370 | keep | 0 | Oct | 2021 | 0.087432 | 0.00052989 | Sustained | FALSE | TRUE | Not_TMED_Event | 778
PONCE | 2021-10-11 12:03 | 2021-10-11 15:35 | 1746 | 003:32 | T | DESGANCHE | INTERRUPTOR HIZO LAS 3 OPERACIONES Y QUEDO FUERA. SE ENCONTRO ARBOL SOBRE LINEA SU CARGA ESTA POR EL 5011-05 | P21101100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-10-11 | 370152 | keep | 0 | Oct | 2021 | 0.25211 | 0.0011892 | Sustained | FALSE | TRUE | Not_TMED_Event | 1746
PONCE | 2021-10-11 12:03 | 2021-10-11 14:07 | 113 | 002:04 | T | DESGANCHE | INTERRUPTOR HIZO LAS 3 OPERACIONES Y QUEDO FUERA SE ENCONTRO ARBOL SOBRE LINEA | P21101100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-10-11 | 14012 | keep | 0 | Oct | 2021 | 0.0095435 | 7.6964e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 113
HUMACAO | 2021-10-11 12:04 | 2021-10-11 13:45 | 50 | 001:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101100179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-10-11 | 5050 | keep | 0 | Oct | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-11 12:04 | 2021-10-11 18:29 | 120 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100032 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2021-10-11 | 46200 | keep | 0 | Oct | 2021 | 0.031467 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
YAUCO | 2021-10-11 12:06 | 2021-10-11 18:40 | 50 | 006:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1X50 EN CORTE DE LINEA POR MAL TIEMPO | P21101100060 | New_Event | Bad Weather | Include | Include | Weather | 394 | 2021-10-11 | 19700 | keep | 0 | Oct | 2021 | 0.013418 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-11 12:06 | 2021-10-11 12:07 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
UTUADO | 2021-10-11 12:42 | 2021-10-11 17:56 | 80 | 005:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100038 | New_Event | Bad Weather | Include | Include | Weather | 314 | 2021-10-11 | 25120 | keep | 0 | Oct | 2021 | 0.017109 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-11 12:45 | 2021-10-11 16:15 | 30 | 003:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | M21101100083 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2021-10-11 | 6300 | keep | 0 | Oct | 2021 | 0.0042909 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-11 12:47 | 2021-10-12 12:26 | 10 | 023:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN CORTE DE LINEA SE REMPLAZO BAJANTE SECUNDARIO QUEMADO | S21101100251 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1419 | 2021-10-11 | 14190 | keep | 0 | Oct | 2021 | 0.0096647 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-11 12:48 | 2021-10-11 18:17 | 40 | 005:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | M21101100084 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2021-10-11 | 13160 | keep | 0 | Oct | 2021 | 0.0089632 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-11 13:00 | 2021-10-11 16:05 | 20 | 003:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21101100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-10-11 | 3700 | keep | 0 | Oct | 2021 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-11 13:06 | 2021-10-11 13:08 | 761 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1421 01 | S21101100268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 1522 | keep | 0 | Oct | 2021 | 0.0010366 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-10-11 13:06 | 2021-10-11 13:08 | 1498 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1310 04 | S21101100268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 2996 | keep | 0 | Oct | 2021 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2021-10-11 13:09 | 2021-10-11 14:37 | 761 | 001:28 | T | DESGANCHE | SE ABRIO N/O CALLE 11 #1033 VILLA NEVAREZ CONTRA 1421-1 Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO 100% | S21101100276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-10-11 | 66968 | keep | 0 | Oct | 2021 | 0.045612 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-10-11 13:14 | 2021-10-11 13:17 | 530 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA PARTE DE SU CARGA POR 1529-15 | S21101100280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-11 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 0.00036098 | Momentary | FALSE | FALSE | Not_TMED_Event | 530
BAYAMON | 2021-10-11 13:14 | 2021-10-11 13:17 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 30% 1346-02 | S21101100280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-11 | 5406 | keep | 0 | Oct | 2021 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-10-11 13:19 | 2021-10-11 13:20 | 1498 | 000:01 | T | DESGANCHE | SE ABRIO N/O CALLE 11 #1033 VILLA NEVAREZ CONTRA 1421-1 Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO 100% | S21101100276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-11 | 1498 | keep | 0 | Oct | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
FAJARDO | 2021-10-11 13:20 | 2021-10-11 15:57 | 20 | 002:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21101100095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-10-11 | 3140 | keep | 0 | Oct | 2021 | 0.0021386 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-11 13:24 | 2021-10-11 13:51 | 100 | 000:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101100101 | New_Event | Bad Weather | Include | Include | Weather | 27 | 2021-10-11 | 2700 | keep | 0 | Oct | 2021 | 0.001839 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-11 13:26 | 2021-10-11 14:10 | 928 | 000:44 | T | DESGANCHE | SE ABRIO MACHETE AVE UNIVERSIDAD ESQ MUÃ‘OZ SE PROBO INTERRUPTOR QUEDO EN SERVICIO 60% QUEDO FUERA 1422-5 Y PARTE 1422-3 | S21101100298 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-10-11 | 40832 | keep | 0 | Oct | 2021 | 0.02781 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 13:26 | 2021-10-11 16:15 | 150 | 002:49 | P | DESGANCHE | SE ABRIO MACHETE AVE UNIVERSIDAD ESQ MUÃ‘OZ SE PROBO INTERRUPTOR QUEDO EN SERVICIO 60% PARTE POR EL 1338-02 | S21101100298 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-10-11 | 25350 | keep | 0 | Oct | 2021 | 0.017266 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 13:26 | 2021-10-11 16:15 | 637 | 002:49 | T | DESGANCHE | SE ABRIO MACHETE AVE UNIVERSIDAD ESQ MUÃ‘OZ SE PROBO INTERRUPTOR QUEDO EN SERVICIO 60% CARGA POR 1338 02 | S21101100298 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-10-11 | 107653 | keep | 0 | Oct | 2021 | 0.073322 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-10-11 13:26 | 2021-10-11 15:32 | 591 | 002:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1400 | P21101100117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2021-10-11 | 74466 | keep | 0 | Oct | 2021 | 0.050718 | 0.00040253 | Sustained | FALSE | TRUE | Not_TMED_Event | 591
MAYAGÃœEZ | 2021-10-11 13:33 | 2021-10-12 11:08 | 30 | 021:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21101100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1295 | 2021-10-11 | 38850 | keep | 0 | Oct | 2021 | 0.026461 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-11 13:34 | 2021-10-11 15:58 | 6 | 002:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21101100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-10-11 | 864 | keep | 0 | Oct | 2021 | 0.00058847 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-11 13:34 | 2021-10-11 16:04 | 8 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA POR LLUVIAS | M21101100107 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2021-10-11 | 1200 | keep | 0 | Oct | 2021 | 0.00081731 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
CAGUAS | 2021-10-11 13:35 | 2021-10-11 14:57 | 2276 | 001:22 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | C21101100102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-10-11 | 186632 | keep | 0 | Oct | 2021 | 0.12711 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
AGUADILLA | 2021-10-11 13:41 | 2021-10-11 13:42 | 1827 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21101100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-11 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-10-11 13:42 | 2021-10-11 18:40 | 1 | 004:58 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO PALMA | M21101100118 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 298 | 2021-10-11 | 298 | keep | 0 | Oct | 2021 | 0.00020297 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-11 13:43 | 2021-10-11 16:54 | 12 | 003:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100041 | New_Event | Bad Weather | Include | Include | Weather | 191 | 2021-10-11 | 2292 | keep | 0 | Oct | 2021 | 0.0015611 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-10-11 13:48 | 2021-10-11 15:35 | 1862 | 001:47 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION PARA CERRAR PUENTE EN LA LINEA 3100 | R21101100071 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 107 | 2021-10-11 | 199234 | keep | 0 | Oct | 2021 | 0.1357 | 0.0012682 | Sustained | FALSE | TRUE | Not_TMED_Event | 1862
SAN JUAN | 2021-10-11 13:48 | 2021-10-11 15:35 | 1613 | 001:47 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION PARA CERRAR PUENTE EN LA LINEA 3100 | R21101100071 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 107 | 2021-10-11 | 172591 | keep | 0 | Oct | 2021 | 0.11755 | 0.0010986 | Sustained | FALSE | TRUE | Not_TMED_Event | 1613
SAN JUAN | 2021-10-11 13:48 | 2021-10-11 15:35 | 1448 | 001:47 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION PARA CERRAR PUENTE EN LA LINEA 3100 | R21101100071 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 107 | 2021-10-11 | 154936 | keep | 0 | Oct | 2021 | 0.10553 | 0.00098623 | Sustained | FALSE | TRUE | Not_TMED_Event | 1448
MAYAGÃœEZ | 2021-10-11 13:51 | 2021-10-12 17:44 | 200 | 027:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO | M21101100112 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1673 | 2021-10-11 | 334600 | keep | 0 | Oct | 2021 | 0.22789 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-10-11 13:51 | 2021-10-11 13:54 | 6285 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR MAL TIEMPO | M21101100113 | Additional_clients | Bad Weather | Include | Include | Weather | 3 | 2021-10-11 | 18855 | keep | 0 | Oct | 2021 | 0.012842 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-11 13:53 | 2021-10-11 13:54 | 752 | 000:01 | T | DESGANCHE | RECIERRE | P21101100124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-11 | 752 | keep | 0 | Oct | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-10-11 13:54 | 2021-10-11 20:15 | 80 | 006:21 | P | DESGANCHE | 1X80 EN CORTE DE LINEA POR DESGANCHE | P21101100202 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 381 | 2021-10-11 | 30480 | keep | 0 | Oct | 2021 | 0.02076 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-11 13:54 | 2021-10-11 17:01 | 100 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101100101 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 187 | 2021-10-11 | 18700 | keep | 0 | Oct | 2021 | 0.012736 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-11 14:00 | 2021-10-11 18:08 | 40 | 004:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONECTO BAJANTE DE CAJA A LINEA | C21101100234 | New_Event | Wire Down | Include | Include | Equipment | 248 | 2021-10-11 | 9920 | keep | 0 | Oct | 2021 | 0.0067565 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-11 14:02 | 2021-10-11 17:17 | 3 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21101100119 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2021-10-11 | 585 | keep | 0 | Oct | 2021 | 0.00039844 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
UTUADO | 2021-10-11 14:02 | 2021-10-11 18:41 | 30 | 004:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100045 | New_Event | Bad Weather | Include | Include | Weather | 279 | 2021-10-11 | 8370 | keep | 0 | Oct | 2021 | 0.0057008 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-11 14:07 | 2021-10-11 19:25 | 25 | 005:18 | P | DESGANCHE | SE ABRE MACHETE RAMAL 8 FTE. COUNTRY CLUB ARBOL SOBRE LINEA | S21101100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2021-10-11 | 7950 | keep | 0 | Oct | 2021 | 0.0054147 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-11 14:10 | 2021-10-11 14:12 | 557 | 000:02 | P | DESGANCHE | SE ABRIO MACHETE AVE UNIVERSIDAD ESQ MUÃ‘OZ SE PROBO INTERRUPTOR QUEDO EN SERVICIO 60% QUEDO FUERA 1422-5 Y PARTE 1422-3 | S21101100298 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-11 | 1114 | keep | 0 | Oct | 2021 | 0.00075874 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-11 14:10 | 2021-10-11 14:12 | 3630 | 000:02 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA | M21101100127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 7260 | keep | 0 | Oct | 2021 | 0.0049448 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2021-10-11 14:11 | 2021-10-11 19:07 | 60 | 004:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-10-11 | 17760 | keep | 0 | Oct | 2021 | 0.012096 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-10-11 14:11 | 2021-10-11 19:17 | 500 | 005:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y SE CERRO CORTE DE LINEA | M21101100123 | New_Event | Wire Down | Include | Include | Equipment | 306 | 2021-10-11 | 153000 | keep | 0 | Oct | 2021 | 0.10421 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
SAN JUAN | 2021-10-11 14:12 | 2021-10-11 16:15 | 928 | 002:03 | T | DESGANCHE | SE ABRIO MACHETE CALLE BALDORIOTY ESQ JAIME BENITEZ 1422-5 PARTE 1422-3 Y 70% DEL 1338-2 | S21101100298 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-10-11 | 114144 | keep | 0 | Oct | 2021 | 0.077743 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-10-11 14:14 | 2021-10-11 17:23 | 125 | 003:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN RISER MAL TIEMPO | R21101100099 | New_Event | Bad Weather | Include | Include | Weather | 189 | 2021-10-11 | 23625 | keep | 0 | Oct | 2021 | 0.016091 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-10-11 14:17 | 2021-10-11 15:35 | 3630 | 001:18 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO NADA | M21101100127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-11 | 283140 | keep | 0 | Oct | 2021 | 0.19285 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2021-10-11 14:24 | 2021-10-12 10:01 | 60 | 019:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21101100109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1177 | 2021-10-11 | 70620 | keep | 0 | Oct | 2021 | 0.048099 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-11 14:33 | 2021-10-12 12:19 | 100 | 021:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21101100233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1306 | 2021-10-11 | 130600 | keep | 0 | Oct | 2021 | 0.088951 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-11 14:35 | 2021-10-12 18:51 | 33 | 028:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 75KVA EN EL FID:17265395 MARCA:PP #SERIE:18A400815 VOLTAJES 2.4/4.16KV 120/240V | M21101100155 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1696 | 2021-10-11 | 55968 | keep | 0 | Oct | 2021 | 0.03812 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2021-10-11 14:36 | 2021-10-11 15:27 | 810 | 000:51 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR AVERIA DE POSTE QUEMANDOSE | M21101100159 | New_Event | Defective Pole | Include | Include | Equipment | 51 | 2021-10-11 | 41310 | keep | 0 | Oct | 2021 | 0.028136 | 0.00055169 | Sustained | FALSE | FALSE | Not_TMED_Event | 810
ARECIBO | 2021-10-11 14:36 | 2021-10-11 17:35 | 30 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100048 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-10-11 | 5370 | keep | 0 | Oct | 2021 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-10-11 14:43 | 2021-10-11 18:24 | 30 | 003:41 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REMPLAZO PARARRAYO | C21101100240 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 221 | 2021-10-11 | 6630 | keep | 0 | Oct | 2021 | 0.0045157 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-11 14:47 | 2021-10-11 15:16 | 1712 | 000:29 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO. NO RECERRO. POR MAL TIEMPO | P21101100150 | New_Event | Bad Weather | Include | Include | Weather | 29 | 2021-10-11 | 49648 | keep | 0 | Oct | 2021 | 0.033815 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-10-11 14:47 | 2021-10-11 15:16 | 7 | 000:29 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR NO HIZO RECIERRE POR FUERTES LLUVIAS | P21101100150 | New_Event | Bad Weather | Include | Include | Weather | 29 | 2021-10-11 | 203 | keep | 0 | Oct | 2021 | 0.00013826 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-11 14:49 | 2021-10-12 14:13 | 15 | 023:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1404 | 2021-10-11 | 21060 | keep | 0 | Oct | 2021 | 0.014344 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-11 14:49 | 2021-10-11 14:50 | 2720 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21101100050 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-11 | 2720 | keep | 0 | Oct | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-10-11 14:50 | 2021-10-12 09:49 | 4 | 018:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO | A21101100088 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1139 | 2021-10-11 | 4556 | keep | 0 | Oct | 2021 | 0.0031031 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-10-11 14:55 | 2021-10-11 16:40 | 7 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21101100093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-10-11 | 735 | keep | 0 | Oct | 2021 | 0.00050061 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-10-11 14:55 | 2021-10-11 17:07 | 30 | 002:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE DE BAMBUA | R21101100101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-10-11 | 3960 | keep | 0 | Oct | 2021 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-11 14:57 | 2021-10-11 16:20 | 1138 | 001:23 | P | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | C21101100044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-10-11 | 94454 | keep | 0 | Oct | 2021 | 0.064332 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-10-11 15:02 | 2021-10-11 16:01 | 40 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101100113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-10-11 | 2360 | keep | 0 | Oct | 2021 | 0.0016074 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-11 15:07 | 2021-10-11 18:01 | 60 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21101100176 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-10-11 | 10440 | keep | 0 | Oct | 2021 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-11 15:08 | 2021-10-12 10:27 | 1 | 019:19 | P | NO SE REPORTO CAUSA | 2 X 80 EN SU-22A A TRANSCLOSURE | R21101100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1159 | 2021-10-11 | 1159 | keep | 0 | Oct | 2021 | 0.00078939 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-11 15:08 | 2021-10-11 15:09 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL #10 | P21101100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 1979 | keep | 0 | Oct | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-10-11 15:08 | 2021-10-11 15:09 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL #10 | P21101100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 5069 | keep | 0 | Oct | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-10-11 15:08 | 2021-10-11 15:09 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL #10 | P21101100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 5063 | keep | 0 | Oct | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
HUMACAO | 2021-10-11 15:11 | 2021-10-11 16:49 | 30 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101100252 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2021-10-11 | 2940 | keep | 0 | Oct | 2021 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-10-11 15:18 | 2021-10-11 17:10 | 4 | 001:52 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA RETIRAR POSTE VACANTE | R21101100114 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 112 | 2021-10-11 | 448 | keep | 0 | Oct | 2021 | 0.00030513 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-10-11 15:31 | 2021-10-11 19:10 | 50 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100053 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-10-11 | 10950 | keep | 0 | Oct | 2021 | 0.007458 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-11 15:34 | 2021-10-11 17:45 | 200 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100055 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-10-11 | 26200 | keep | 0 | Oct | 2021 | 0.017845 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-10-11 15:35 | 2021-10-11 16:40 | 1300 | 001:05 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA | P21101100055 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-10-11 | 84500 | keep | 0 | Oct | 2021 | 0.057553 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-11 15:37 | 2021-10-11 19:46 | 100 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 50 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100056 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-10-11 | 24900 | keep | 0 | Oct | 2021 | 0.016959 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-11 15:41 | 2021-10-11 18:50 | 20 | 003:09 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO AVERIA SOTERRADA | A21101100058 | New_Event | UG Cable Fault | Include | Include | Equipment | 189 | 2021-10-11 | 3780 | keep | 0 | Oct | 2021 | 0.0025745 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-10-11 15:44 | 2021-10-11 15:45 | 1526 | 000:01 | T | TRANSFORMADOR AVERIADO | RECERRO | B21101100000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-10-11 | 1526 | keep | 0 | Oct | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-10-11 15:45 | 2021-10-12 13:03 | 10 | 021:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 X 75KVA | B21101000154 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1278 | 2021-10-11 | 12780 | keep | 0 | Oct | 2021 | 0.0087044 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-11 15:52 | 2021-10-11 16:45 | 10 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21101100269 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-10-11 | 530 | keep | 0 | Oct | 2021 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-11 15:55 | 2021-10-12 12:11 | 90 | 020:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R21101100122 | New_Event | Cutout Failure | Include | Include | Equipment | 1216 | 2021-10-11 | 109440 | keep | 0 | Oct | 2021 | 0.074539 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-11 15:56 | 2021-10-11 18:15 | 35 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101100197 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2021-10-11 | 4865 | keep | 0 | Oct | 2021 | 0.0033135 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-11 15:59 | 2021-10-11 16:00 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21101100126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2021-10-11 16:02 | 2021-10-11 17:42 | 100 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21101100205 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-10-11 | 10000 | keep | 0 | Oct | 2021 | 0.006811 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-11 16:10 | 2021-10-11 16:11 | 2147 | 000:01 | T | DESGANCHE | RECERRO | B21101100131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-11 | 2147 | keep | 0 | Oct | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2021-10-11 16:15 | 2021-10-11 20:14 | 372 | 003:59 | P | DESGANCHE | SE ABRIO MACHETE CALLE BALDORIOTY ESQ JAIME BENITEZ 1422-5 PARTE 1422-3 Y 70% DEL 1338-2 | S21101100298 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-10-11 | 88908 | keep | 0 | Oct | 2021 | 0.060555 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 16:15 | 2021-10-11 20:14 | 150 | 003:59 | P | DESGANCHE | SE ABRIO MACHETE CALLE BALDORIOTY ESQ JAIME BENITEZ PARTE POR EL 1338-02 | S21101100298 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-10-11 | 35850 | keep | 0 | Oct | 2021 | 0.024417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-11 16:18 | 2021-10-11 19:18 | 30 | 003:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101100279 | New_Event | Bad Weather | Include | Include | Weather | 180 | 2021-10-11 | 5400 | keep | 0 | Oct | 2021 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-11 16:19 | 2021-10-11 16:20 | 2147 | 000:01 | T | DESGANCHE | RECERRO | B21101100138 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-11 | 2147 | keep | 0 | Oct | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
CAGUAS | 2021-10-11 16:20 | 2021-10-11 18:05 | 2276 | 001:45 | T | DESGANCHE | REALIZO DESGANCHE EN 3 PUNTOS Y CERRO PUENTE | C21101100280 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-10-11 | 238980 | keep | 0 | Oct | 2021 | 0.16277 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-11 16:20 | 2021-10-11 18:22 | 150 | 002:02 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100140 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-10-11 | 18300 | keep | 0 | Oct | 2021 | 0.012464 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-11 16:22 | 2021-10-11 17:15 | 2 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100065 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-10-11 | 106 | keep | 0 | Oct | 2021 | 7.2196e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-11 16:23 | 2021-10-11 19:44 | 50 | 003:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100066 | New_Event | Bad Weather | Include | Include | Weather | 201 | 2021-10-11 | 10050 | keep | 0 | Oct | 2021 | 0.006845 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-11 16:24 | 2021-10-11 17:49 | 50 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100067 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-10-11 | 4250 | keep | 0 | Oct | 2021 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-11 16:31 | 2021-10-11 16:35 | 2203 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE VERIFICO CON PERSONAL REALIZANDO EXPLORATORIA Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO | S21101100425 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-10-11 | 8812 | keep | 0 | Oct | 2021 | 0.0060018 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2021-10-11 16:31 | 2021-10-13 14:22 | 20 | 045:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21101100149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2751 | 2021-10-11 | 55020 | keep | 0 | Oct | 2021 | 0.037474 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-10-11 16:38 | 2021-10-11 17:55 | 100 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES LLUVIAS | P21101100200 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-10-11 | 7700 | keep | 0 | Oct | 2021 | 0.0052444 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-11 16:41 | 2021-10-11 17:43 | 50 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 Y 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100070 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2021-10-11 | 3100 | keep | 0 | Oct | 2021 | 0.0021114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-11 16:49 | 2021-10-11 20:01 | 2483 | 003:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR NEUTRAL PARTIDO DEL 6601-02 | M21101100055 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2021-10-11 | 476736 | keep | 0 | Oct | 2021 | 0.3247 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
PONCE | 2021-10-11 16:53 | 2021-10-11 16:54 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211011000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 449 | keep | 0 | Oct | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
VEGA BAJA | 2021-10-11 16:54 | 2021-10-11 18:35 | 20 | 001:41 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B21101100168 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 101 | 2021-10-11 | 2020 | keep | 0 | Oct | 2021 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-10-11 16:56 | 2021-10-11 18:22 | 60 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21101100125 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-10-11 | 5160 | keep | 0 | Oct | 2021 | 0.0035145 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-11 16:59 | 2021-10-11 22:42 | 55 | 005:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21101100461 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2021-10-11 | 18865 | keep | 0 | Oct | 2021 | 0.012849 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-10-11 17:00 | 2021-10-12 14:10 | 30 | 021:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101100173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1270 | 2021-10-11 | 38100 | keep | 0 | Oct | 2021 | 0.02595 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-11 17:05 | 2021-10-12 21:21 | 20 | 028:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN EL FID:24889377 MARCA:CHIST DE 100AMP | M21101100243 | New_Event | Cutout Failure | Include | Include | Equipment | 1696 | 2021-10-11 | 33920 | keep | 0 | Oct | 2021 | 0.023103 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-11 17:10 | 2021-10-12 10:20 | 50 | 017:10 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRARON RAMAS SOBRE LAS LINEAS | M21101100245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1030 | 2021-10-11 | 51500 | keep | 0 | Oct | 2021 | 0.035076 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-11 17:10 | 2021-10-11 22:26 | 50 | 005:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | B21101100181 | New_Event | Wire Down | Include | Include | Equipment | 316 | 2021-10-11 | 15800 | keep | 0 | Oct | 2021 | 0.010761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-11 17:15 | 2021-10-11 17:21 | 530 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA ABRIR MACHETE Y Y SECCIONALIZAR Y REPARAR PUENTE PRIMARIO CARGA POR EL 1529-15 | S21101100478 | New_Event | Wire Down | Include | Include | Equipment | 6 | 2021-10-11 | 3180 | keep | 0 | Oct | 2021 | 0.0021659 | 0.00036098 | Sustained | FALSE | FALSE | Not_TMED_Event | 530
BAYAMON | 2021-10-11 17:15 | 2021-10-11 17:21 | 1802 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA ABRIR MACHETE Y SECCIONALIZAR Y REPARAR PUENTE PRIMARIO LLEVA EL 30% 1346-02 | S21101100478 | New_Event | Wire Down | Include | Include | Equipment | 6 | 2021-10-11 | 10812 | keep | 0 | Oct | 2021 | 0.007364 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2021-10-11 17:17 | 2021-10-12 11:25 | 4 | 018:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | A21101100073 | New_Event | Bad Weather | Include | Include | Weather | 1088 | 2021-10-11 | 4352 | keep | 0 | Oct | 2021 | 0.0029641 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
PONCE | 2021-10-11 17:21 | 2021-10-11 18:40 | 520 | 001:19 | T | DESGANCHE | HIZO LOS 3 CICLOS DE RECIERRE Y QUEDO FUERA. SE SACO ARBOL SOBRE LINEA | P21101100207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-10-11 | 41080 | keep | 0 | Oct | 2021 | 0.027979 | 0.00035417 | Sustained | TRUE | TRUE | Not_TMED_Event | 520
ARECIBO | 2021-10-11 17:26 | 2021-10-11 20:51 | 20 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE REMPLAZO SECUNDARIA CRUZADA | A21101100075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2021-10-11 | 4100 | keep | 0 | Oct | 2021 | 0.0027925 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-11 17:35 | 2021-10-12 10:48 | 40 | 017:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA | S21101100211 | New_Event | Cutout Failure | Include | Include | Equipment | 1033 | 2021-10-11 | 41320 | keep | 0 | Oct | 2021 | 0.028143 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-10-11 17:39 | 2021-10-11 19:43 | 100 | 002:04 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P21101100214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-10-11 | 12400 | keep | 0 | Oct | 2021 | 0.0084456 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-11 17:41 | 2021-10-11 18:24 | 12 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21101100300 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-10-11 | 516 | keep | 0 | Oct | 2021 | 0.00035145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-11 17:46 | 2021-10-11 18:58 | 45 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21101100128 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2021-10-11 | 3240 | keep | 0 | Oct | 2021 | 0.0022067 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-10-11 17:51 | 2021-10-11 19:40 | 25 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100079 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-10-11 | 2725 | keep | 0 | Oct | 2021 | 0.001856 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-10-11 17:53 | 2021-10-12 11:17 | 3 | 017:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | P21101100224 | New_Event | Bad Weather | Include | Include | Weather | 1044 | 2021-10-11 | 3132 | keep | 0 | Oct | 2021 | 0.0021332 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-10-11 17:56 | 2021-10-11 19:59 | 100 | 002:03 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA | C21101100302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-10-11 | 12300 | keep | 0 | Oct | 2021 | 0.0083775 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-10-11 18:01 | 2021-10-11 20:57 | 50 | 002:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE 100A | P21101100227 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2021-10-11 | 8800 | keep | 0 | Oct | 2021 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-11 18:02 | 2021-10-11 23:07 | 842 | 005:05 | T | DESGANCHE | DISPARO DE INTERRUPTOR NO RECERRO SE PROBO QUEDO ABIERTO SE ABRIO MACHETE EN LA PR-20 MARGINAL MARTINEZ NADAL ANTES TECNICA Y SE CERRO BREAKER QUEDO 20% EN SERVICIO | S21101100512 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2021-10-11 | 256810 | keep | 0 | Oct | 2021 | 0.17491 | 0.00057348 | Sustained | FALSE | FALSE | Not_TMED_Event | 842
YAUCO | 2021-10-11 18:09 | 2021-10-12 11:13 | 100 | 017:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101100230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1024 | 2021-10-11 | 102400 | keep | 0 | Oct | 2021 | 0.069744 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-11 18:10 | 2021-10-11 20:12 | 12 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101100081 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2021-10-11 | 1464 | keep | 0 | Oct | 2021 | 0.00099712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-10-11 18:20 | 2021-10-11 19:32 | 45 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO | R21101100132 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2021-10-11 | 3240 | keep | 0 | Oct | 2021 | 0.0022067 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
FAJARDO | 2021-10-11 18:26 | 2021-10-12 10:06 | 70 | 015:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21101100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 940 | 2021-10-11 | 65800 | keep | 0 | Oct | 2021 | 0.044816 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-10-11 18:30 | 2021-10-11 20:01 | 15 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTAFUSIBLE | B21101100205 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2021-10-11 | 1365 | keep | 0 | Oct | 2021 | 0.0009297 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-11 18:32 | 2021-10-12 13:03 | 50 | 018:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101100530 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1111 | 2021-10-11 | 55550 | keep | 0 | Oct | 2021 | 0.037835 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-11 18:33 | 2021-10-11 23:35 | 120 | 005:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21101100292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2021-10-11 | 36240 | keep | 0 | Oct | 2021 | 0.024683 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 2231 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 2231 | keep | 0 | Oct | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | Not_TMED_Event | 2231
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 1923 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 1923 | keep | 0 | Oct | 2021 | 0.0013097 | 0.0013097 | Momentary | FALSE | TRUE | Not_TMED_Event | 1923
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 1066 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 1066 | keep | 0 | Oct | 2021 | 0.00072605 | 0.00072605 | Momentary | FALSE | TRUE | Not_TMED_Event | 1066
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 141 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 141 | keep | 0 | Oct | 2021 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 141
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 2107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 2107 | keep | 0 | Oct | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | TRUE | Not_TMED_Event | 2107
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 308 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 308 | keep | 0 | Oct | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | TRUE | Not_TMED_Event | 308
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 2697 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 2697 | keep | 0 | Oct | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | TRUE | Not_TMED_Event | 2697
ARECIBO | 2021-10-11 18:33 | 2021-10-11 18:34 | 67 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21101100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-11 | 67 | keep | 0 | Oct | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 67
VEGA BAJA | 2021-10-11 18:36 | 2021-10-12 09:56 | 100 | 015:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO | B21101100208 | New_Event | Wire Down | Include | Include | Equipment | 920 | 2021-10-11 | 92000 | keep | 0 | Oct | 2021 | 0.062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-10-11 18:42 | 2021-10-11 19:57 | 2276 | 001:15 | T | DESGANCHE | DISPARO | C21101100318 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-10-11 | 170700 | keep | 0 | Oct | 2021 | 0.11626 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-11 18:46 | 2021-10-11 19:52 | 530 | 001:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL CERRAR MACHETE FTE. CUARTEL MUNICIPAL SE ABRIO Y SE CERRO INTERRUPTOR 100% EN SERVICIO QUEDA FUERA 10% DEL 1346-2 PARTE DE LA CARGA SE ENCUENTRA POR EL 1529-15 | S21101100540 | Partial_restoration | Wire Down | Include | Include | Equipment | 66 | 2021-10-11 | 34980 | keep | 0 | Oct | 2021 | 0.023825 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-11 18:46 | 2021-10-11 19:52 | 1802 | 001:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL CERRAR MACHETE FTE. CUARTEL MUNICIPAL SE ABRIO Y SE CERRO INTERRUPTOR 100% EN SERVICIO QUEDA FUERA 10% DEL 1346-2 | S21101100540 | Partial_restoration | Wire Down | Include | Include | Equipment | 66 | 2021-10-11 | 118932 | keep | 0 | Oct | 2021 | 0.081004 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-11 18:57 | 2021-10-12 14:34 | 1 | 019:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO | C21101100325 | New_Event | Bad Weather | Include | Include | Weather | 1177 | 2021-10-11 | 1177 | keep | 0 | Oct | 2021 | 0.00080165 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-11 19:05 | 2021-10-11 20:36 | 234 | 001:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P21101100262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 91 | 2021-10-11 | 21294 | keep | 0 | Oct | 2021 | 0.014503 | 0.00015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 234
PONCE | 2021-10-11 19:05 | 2021-10-11 20:36 | 2468 | 001:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P21101100262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 91 | 2021-10-11 | 224588 | keep | 0 | Oct | 2021 | 0.15297 | 0.0016809 | Sustained | FALSE | TRUE | Not_TMED_Event | 2468
CAGUAS | 2021-10-11 19:16 | 2021-10-12 15:08 | 225 | 019:52 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTES Y SE CERRO N/O PARA SECCIONALIZAR | C21101100334 | New_Event | Defective Pole | Include | Include | Equipment | 1192 | 2021-10-11 | 268200 | keep | 0 | Oct | 2021 | 0.18267 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
CANOVANAS | 2021-10-11 19:20 | 2021-10-11 19:41 | 15 | 000:21 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO | R21101100135 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 21 | 2021-10-11 | 315 | keep | 0 | Oct | 2021 | 0.00021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-11 19:21 | 2021-10-11 19:24 | 2000 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL CARGA POR 1619-02 | R21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-11 | 6000 | keep | 0 | Oct | 2021 | 0.0040866 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2021-10-11 19:21 | 2021-10-11 19:22 | 1026 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR CAJA QUEMADA CERRADO POR CONTROL | R21101100058 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-11 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-10-11 19:25 | 2021-10-11 20:31 | 35 | 001:06 | P | DESGANCHE | SE ABRE MACHETE RAMAL 8 FTE. COUNTRY CLUB ARBOL SOBRE LINEA SE REALIZO DESGANCHE | S21101100000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-10-11 | 2310 | keep | 0 | Oct | 2021 | 0.0015733 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-11 19:25 | 2021-10-12 10:55 | 70 | 015:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101100336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 930 | 2021-10-11 | 65100 | keep | 0 | Oct | 2021 | 0.044339 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-10-11 19:26 | 2021-10-11 19:45 | 1026 | 000:19 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REEMPLAZAR CAJA PRIMARIA AVERIADA | R21101100058 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 19 | 2021-10-11 | 19494 | keep | 0 | Oct | 2021 | 0.013277 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
PONCE | 2021-10-11 19:30 | 2021-10-12 12:24 | 6 | 016:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | P21101100254 | New_Event | Wire Down | Include | Include | Equipment | 1014 | 2021-10-11 | 6084 | keep | 0 | Oct | 2021 | 0.0041438 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-10-11 19:52 | 2021-10-12 14:17 | 53 | 018:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL CERRAR MACHETE FTE. CUARTEL MUNICIPAL SE ABRIO Y SE CERRO INTERRUPTOR 100% EN SERVICIO QUEDA FUERA 10% DEL 1346-2 PARTE DE LA CARGA SE ENCUENTRA POR EL 1529-15 | S21101100540 | Partial_restoration | Wire Down | Include | Include | Equipment | 1105 | 2021-10-11 | 58565 | keep | 0 | Oct | 2021 | 0.039888 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-11 19:58 | 2021-10-11 21:17 | 2276 | 001:19 | T | DESGANCHE | DISPARO RETIRO PENCAS DE LAS LINEAS | C21101100318 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-10-11 | 179804 | keep | 0 | Oct | 2021 | 0.12246 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-11 20:02 | 2021-10-12 18:02 | 175 | 022:00 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101100345 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1320 | 2021-10-11 | 231000 | keep | 0 | Oct | 2021 | 0.15733 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
SAN JUAN | 2021-10-11 20:14 | 2021-10-11 20:16 | 928 | 000:02 | T | DESGANCHE | DISPARO AL CERRAR MACHETE CALLE BALDORIOTY DE CASTRO Y SE ENCONTRO ARBOL SOBRE LINEA Y SE ABRIO MACHETE Y SE CERRO INTERRUPTOR 90% EN SERVICIO LLEVA 1422-5 Y PARTE DEL 1422-3 | S21101100579 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-11 | 1856 | keep | 0 | Oct | 2021 | 0.0012641 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 20:14 | 2021-10-11 20:16 | 150 | 000:02 | P | DESGANCHE | DISPARO AL CERRAR MACHETE CALLE BALDORIOTY DE CASTRO Y SE ENCONTRO ARBOL SOBRE LINEA Y SE ABRIO MACHETE Y SE CERRO INTERRUPTOR PARTE POR EL 1338-02 | S21101100579 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-11 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 20:14 | 2021-10-11 20:16 | 637 | 000:02 | T | DESGANCHE | DISPARO AL CERRAR MACHETE CALLE BALDORIOTY DE CASTRO Y SE ENCONTRO ARBOL SOBRE LINEA Y SE ABRIO MACHETE Y SE CERRO INTERRUPTOR CARGA POR 1338 02 | S21101100579 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-11 | 1274 | keep | 0 | Oct | 2021 | 0.00086772 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-11 20:16 | 2021-10-11 21:11 | 93 | 000:55 | P | DESGANCHE | SE CERRO MACHETES EN LA BALDORIOTY 100% EN SERVICIO | S21101100579 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-10-11 | 5115 | keep | 0 | Oct | 2021 | 0.0034838 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2021-10-11 20:16 | 2021-10-11 21:11 | 150 | 000:55 | P | DESGANCHE | SE CERRO MACHETES EN LA BALDORIOTY 100% EN SERVICIO PARTE POR EL 1338-02 | S21101100579 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-10-11 | 8250 | keep | 0 | Oct | 2021 | 0.005619 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-10-11 20:19 | 2021-10-12 11:27 | 95 | 015:08 | P | OTRAS CAUSAS | 1 X 100 EN SU-64 SE DEJO ABIERTO HACIA BOVEDA DE MARLIN I CON PROBLEMA INTERIOR | R21101100150 | New_Event | Other Causes | Include | Include | Other | 908 | 2021-10-11 | 86260 | keep | 0 | Oct | 2021 | 0.058751 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
HUMACAO | 2021-10-11 20:27 | 2021-10-12 16:00 | 12 | 019:33 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21101100352 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1173 | 2021-10-11 | 14076 | keep | 0 | Oct | 2021 | 0.0095871 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
HUMACAO | 2021-10-11 20:31 | 2021-10-12 20:01 | 71 | 023:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21101100358 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1410 | 2021-10-11 | 100110 | keep | 0 | Oct | 2021 | 0.068184 | 4.8358e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 71
MAYAGÃœEZ | 2021-10-11 20:48 | 2021-10-11 20:56 | 100 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21101100314 | New_Event | Bad Weather | Include | Include | Weather | 8 | 2021-10-11 | 800 | keep | 0 | Oct | 2021 | 0.00054488 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-10-11 20:51 | 2021-10-12 09:59 | 45 | 013:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21101100154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 788 | 2021-10-11 | 35460 | keep | 0 | Oct | 2021 | 0.024152 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-10-11 21:17 | 2021-10-11 23:36 | 300 | 002:19 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LEVANTO NEUTRAL PRIMARIO | C21101100318 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-10-11 | 41700 | keep | 0 | Oct | 2021 | 0.028402 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-10-11 21:17 | 2021-10-12 11:00 | 10 | 013:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADAS | P21101100268 | New_Event | Secondary Wire Down | Include | Include | Equipment | 823 | 2021-10-11 | 8230 | keep | 0 | Oct | 2021 | 0.0056054 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-11 21:27 | 2021-10-11 21:28 | 853 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21101100363 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 853 | keep | 0 | Oct | 2021 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
SAN JUAN | 2021-10-11 21:32 | 2021-10-12 11:52 | 11 | 014:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21101100158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2021-10-11 | 9460 | keep | 0 | Oct | 2021 | 0.0064432 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-10-11 22:14 | 2021-10-12 12:58 | 8 | 014:44 | P | FUEGO | 2 X 15 EN TRANSFORMADOR CRUCE POR FUEGO EN IGLESIA | C21101100368 | New_Event | Fire | Include | Include | Public | 884 | 2021-10-11 | 7072 | keep | 0 | Oct | 2021 | 0.0048167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2021-10-11 22:26 | 2021-10-12 10:24 | 6 | 011:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA DE 100 AMP | P21101100272 | New_Event | Cutout Failure | Include | Include | Equipment | 718 | 2021-10-11 | 4308 | keep | 0 | Oct | 2021 | 0.0029342 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-11 22:31 | 2021-10-12 10:43 | 45 | 012:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21101100093 | New_Event | Bad Weather | Include | Include | Weather | 732 | 2021-10-11 | 32940 | keep | 0 | Oct | 2021 | 0.022435 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-10-11 22:41 | 2021-10-12 10:26 | 65 | 011:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21101100372 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 705 | 2021-10-11 | 45825 | keep | 0 | Oct | 2021 | 0.031211 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-10-11 22:41 | 2021-10-12 17:14 | 12 | 018:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21101100371 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1113 | 2021-10-11 | 13356 | keep | 0 | Oct | 2021 | 0.0090967 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-10-11 22:49 | 2021-10-12 10:35 | 15 | 011:46 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M21101100319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 706 | 2021-10-11 | 10590 | keep | 0 | Oct | 2021 | 0.0072128 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-11 23:05 | 2021-10-12 14:23 | 10 | 015:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y LEVANTARON CONDUCTOR CON DOS DISCOS | C21101100373 | New_Event | Cutout Failure | Include | Include | Equipment | 918 | 2021-10-11 | 9180 | keep | 0 | Oct | 2021 | 0.0062525 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-10-11 23:07 | 2021-10-11 23:17 | 674 | 000:10 | P | DESGANCHE | SE CERRO MACHETE EN LA PR-20 MARGINAL MARTINEZ NADAL ANTES TECNICA 100% EN SERVICIO | S21101100512 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 10 | 2021-10-11 | 6740 | keep | 0 | Oct | 2021 | 0.0045906 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-10-11 23:09 | 2021-10-11 23:10 | 1047 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21101100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-11 | 1047 | keep | 0 | Oct | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2021-10-11 23:10 | 2021-10-12 17:00 | 150 | 017:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21101100321 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1070 | 2021-10-11 | 160500 | keep | 0 | Oct | 2021 | 0.10932 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-10-11 23:16 | 2021-10-13 15:51 | 30 | 040:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101100251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2435 | 2021-10-11 | 73050 | keep | 0 | Oct | 2021 | 0.049754 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-11 23:22 | 2021-10-11 23:51 | 842 | 000:29 | T | DESGANCHE | DISPARO NO RECERRO SE ABRIO MACHETE AVE. MARTINEZ NADAL CARR.20 SALIDA SOTERRADA INT.177 QUEDO EN SERVICIO 20% | S21101100612 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-10-11 | 24418 | keep | 0 | Oct | 2021 | 0.016631 | 0.00057348 | Sustained | FALSE | FALSE | Not_TMED_Event | 842
AGUADILLA | 2021-10-11 23:33 | 2021-10-11 23:34 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21101100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2021-10-11 23:40 | 2021-10-11 23:42 | 2888 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A21101100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-11 | 5776 | keep | 0 | Oct | 2021 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
MAYAGÃœEZ | 2021-10-11 23:48 | 2021-10-12 10:20 | 40 | 010:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRARON RAMAS SOBRE LAS LINEAS | M21101100327 | New_Event | Vegetation Contact | Include | Include | Vegetation | 632 | 2021-10-11 | 25280 | keep | 0 | Oct | 2021 | 0.017218 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-11 23:49 | 2021-10-12 16:38 | 150 | 016:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGNCHE | C21101100377 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2021-10-11 | 151350 | keep | 0 | Oct | 2021 | 0.10308 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-11 23:50 | 2021-10-11 23:51 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE COLOCO RR EN OFF Y SE REALIZO PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO TIENE LA CARGA DEL 5010-04 | P21101100276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 1712 | keep | 0 | Oct | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-10-11 23:50 | 2021-10-11 23:51 | 7 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 5005-03 CON LA CARGA DEL 5010-04 NO RECERRO SE COLOCO RR EN OFF Y SE REALIZO PRUEBA A INTERRUPTOR 5005-03 QUEDANDO EN SERVICIO | P21101100276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-11 | 7 | keep | 0 | Oct | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-11 23:51 | 2021-10-12 00:55 | 336 | 001:04 | P | DESGANCHE | SE ABRIO MACHETE DETRAS DEALER FIAT GUAYNABO PARA SECCIONALIZAR TRAMO DESGANCHE Y SE CERRO MACHETE PR-20 MARTINEZ NADAL INT.177 40% EN SERVICIO | S21101100612 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-10-11 | 21504 | keep | 0 | Oct | 2021 | 0.014646 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-11 23:56 | 2021-10-12 13:45 | 35 | 013:49 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21101100097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 829 | 2021-10-11 | 29015 | keep | 0 | Oct | 2021 | 0.019762 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-10-12 00:23 | 2021-10-12 00:24 | 75 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO NO SE REPORTA CAUSA | P21401200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 75 | keep | 0 | Oct | 2021 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2021-10-12 00:47 | 2021-10-12 13:27 | 60 | 012:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21101200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 760 | 2021-10-12 | 45600 | keep | 0 | Oct | 2021 | 0.031058 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-12 00:55 | 2021-10-12 22:10 | 800 | 021:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE HIZO DESGANCHE 100% EN SERVICIO | S21101200040 | New_Event | Wire Down | Include | Include | Equipment | 1275 | 2021-10-12 | 1020000 | keep | 0 | Oct | 2021 | 0.69472 | 0.00054488 | Sustained | FALSE | TRUE | Not_TMED_Event | 800
SAN JUAN | 2021-10-12 01:06 | 2021-10-12 01:07 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-5 CARGA POR 1206-04 | S21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-12 01:06 | 2021-10-12 01:07 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-5 | S21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
PONCE | 2021-10-12 01:38 | 2021-10-12 10:11 | 50 | 008:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2021-10-12 | 25650 | keep | 0 | Oct | 2021 | 0.01747 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-12 01:45 | 2021-10-12 14:16 | 50 | 012:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21101200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 751 | 2021-10-12 | 37550 | keep | 0 | Oct | 2021 | 0.025575 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-12 02:21 | 2021-10-12 02:22 | 635 | 000:01 | T | DESGANCHE | RECIERRE | R21101200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-12 | 635 | keep | 0 | Oct | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2021-10-12 02:22 | 2021-10-12 11:16 | 90 | 008:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21101200003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 534 | 2021-10-12 | 48060 | keep | 0 | Oct | 2021 | 0.032733 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-12 02:49 | 2021-10-12 10:28 | 52 | 007:39 | P | NO SE REPORTO CAUSA | 1 X 100 CORTE DE LINEA | S21101200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2021-10-12 | 23868 | keep | 0 | Oct | 2021 | 0.016256 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
GUAYAMA | 2021-10-12 03:00 | 2021-10-12 10:24 | 50 | 007:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2021-10-12 | 22200 | keep | 0 | Oct | 2021 | 0.01512 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-12 03:20 | 2021-10-12 09:28 | 60 | 006:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21101200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2021-10-12 | 22080 | keep | 0 | Oct | 2021 | 0.015039 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-12 04:01 | 2021-10-12 16:19 | 80 | 012:18 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA REEMPLAZO POSTE | R21101200013 | New_Event | Defective Pole | Include | Include | Equipment | 738 | 2021-10-12 | 59040 | keep | 0 | Oct | 2021 | 0.040212 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-12 04:11 | 2021-10-12 04:17 | 828 | 000:06 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 3600 CARGA POR EL 1206-04 | S21101200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-12 | 4968 | keep | 0 | Oct | 2021 | 0.0033837 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
SAN JUAN | 2021-10-12 04:11 | 2021-10-12 04:17 | 10211 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-37900 LLEVA 1204-5 CARGA POR 1206-04 | S21101200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-12 | 61266 | keep | 0 | Oct | 2021 | 0.041728 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-12 04:11 | 2021-10-12 04:17 | 641 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 | S21101200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-12 | 3846 | keep | 0 | Oct | 2021 | 0.0026195 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-12 04:11 | 2021-10-12 04:17 | 733 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 | S21101200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-12 | 4398 | keep | 0 | Oct | 2021 | 0.0029955 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-10-12 04:11 | 2021-10-12 04:17 | 4133 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 LLEVA 1204-5 | S21101200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-12 | 24798 | keep | 0 | Oct | 2021 | 0.01689 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-12 04:11 | 2021-10-12 04:17 | 1799 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 LLEVA 40% 1204-4 Y 60% 1204-3 Y 60 AMP. DEL 1303-2 | S21101200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-12 | 10794 | keep | 0 | Oct | 2021 | 0.0073517 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-10-12 05:11 | 2021-10-12 05:12 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21101200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 3718 | keep | 0 | Oct | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-10-12 05:12 | 2021-10-12 19:05 | 50 | 013:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S21101200044 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 833 | 2021-10-12 | 41650 | keep | 0 | Oct | 2021 | 0.028368 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-10-12 05:15 | 2021-10-12 05:17 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA PARTE 1206-3 | S21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-12 | 3230 | keep | 0 | Oct | 2021 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CAGUAS | 2021-10-12 05:58 | 2021-10-12 12:22 | 195 | 006:24 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21101200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2021-10-12 | 74880 | keep | 0 | Oct | 2021 | 0.051 | 0.00013281 | Sustained | FALSE | TRUE | Not_TMED_Event | 195
UTUADO | 2021-10-12 06:05 | 2021-10-12 11:50 | 100 | 005:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21101200005 | New_Event | Bad Weather | Include | Include | Weather | 345 | 2021-10-12 | 34500 | keep | 0 | Oct | 2021 | 0.023498 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-10-12 06:09 | 2021-10-12 06:10 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 2106 | keep | 0 | Oct | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2021-10-12 06:15 | 2021-10-12 06:17 | 4381 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-12 | 8762 | keep | 0 | Oct | 2021 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-10-12 06:17 | 2021-10-12 11:52 | 1 | 005:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21101100035 | New_Event | Bad Weather | Include | Include | Weather | 335 | 2021-10-12 | 335 | keep | 0 | Oct | 2021 | 0.00022817 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-12 06:25 | 2021-10-12 11:39 | 20 | 005:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA Y PARARRAYOS | C21101200014 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2021-10-12 | 6280 | keep | 0 | Oct | 2021 | 0.0042773 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-12 06:26 | 2021-10-12 12:17 | 90 | 005:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R21101200019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 351 | 2021-10-12 | 31590 | keep | 0 | Oct | 2021 | 0.021516 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-10-12 06:40 | 2021-10-12 18:51 | 71 | 012:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 731 | 2021-10-12 | 51901 | keep | 0 | Oct | 2021 | 0.03535 | 4.8358e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 71
HUMACAO | 2021-10-12 06:44 | 2021-10-12 15:04 | 676 | 008:20 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EL LA LINEA 5300 | C21101200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 500 | 2021-10-12 | 338000 | keep | 0 | Oct | 2021 | 0.23021 | 0.00046042 | Sustained | FALSE | TRUE | Not_TMED_Event | 676
HUMACAO | 2021-10-12 06:44 | 2021-10-12 15:04 | 2873 | 008:20 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EL LA LINEA 5300 | C21101200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 500 | 2021-10-12 | 1436500 | keep | 0 | Oct | 2021 | 0.97839 | 0.0019568 | Sustained | FALSE | TRUE | Not_TMED_Event | 2873
HUMACAO | 2021-10-12 06:44 | 2021-10-12 15:04 | 3902 | 008:20 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EL LA LINEA 5300 | C21101200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 500 | 2021-10-12 | 1951000 | keep | 0 | Oct | 2021 | 1.3288 | 0.0026576 | Sustained | FALSE | TRUE | Not_TMED_Event | 3902
HUMACAO | 2021-10-12 07:00 | 2021-10-12 10:50 | 50 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | C21101200026 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2021-10-12 | 11500 | keep | 0 | Oct | 2021 | 0.0078326 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-10-12 07:10 | 2021-10-12 14:42 | 1 | 007:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN BANCO DE TRANSFORMADORES MAL TIEMPO | C21101200030 | New_Event | Bad Weather | Include | Include | Weather | 452 | 2021-10-12 | 452 | keep | 0 | Oct | 2021 | 0.00030786 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-10-12 07:14 | 2021-10-12 07:15 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO REALIZO RECIERRE SE COLOCO RR EN OFF Y SE REALIZO PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO | P21101200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 1945 | keep | 0 | Oct | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
PONCE | 2021-10-12 07:25 | 2021-10-12 15:45 | 50 | 008:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21101200011 | New_Event | Bad Weather | Include | Include | Weather | 500 | 2021-10-12 | 25000 | keep | 0 | Oct | 2021 | 0.017027 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-12 07:29 | 2021-10-12 18:55 | 40 | 011:26 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21101200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 686 | 2021-10-12 | 27440 | keep | 0 | Oct | 2021 | 0.018689 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-12 07:39 | 2021-10-12 07:40 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 112 | keep | 0 | Oct | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2021-10-12 07:41 | 2021-10-12 14:17 | 160 | 006:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER MAL TIEMPO | S21101200057 | New_Event | Bad Weather | Include | Include | Weather | 396 | 2021-10-12 | 63360 | keep | 0 | Oct | 2021 | 0.043154 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
PONCE | 2021-10-12 07:43 | 2021-10-12 16:20 | 100 | 008:37 | P | MAL TIEMPO/RAYOS/WET ASH | 2X50 EN CORTE DE LINEA POR FUERTES VIENTOS | P21101200014 | New_Event | Bad Weather | Include | Include | Weather | 517 | 2021-10-12 | 51700 | keep | 0 | Oct | 2021 | 0.035213 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-12 07:44 | 2021-10-12 10:13 | 25 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21101200015 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2021-10-12 | 3725 | keep | 0 | Oct | 2021 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-10-12 07:46 | 2021-10-12 18:06 | 300 | 010:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAMBIO DE CAJA QUEMADA | A21101200006 | New_Event | Cutout Failure | Include | Include | Equipment | 620 | 2021-10-12 | 186000 | keep | 0 | Oct | 2021 | 0.12668 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-10-12 07:59 | 2021-10-12 22:29 | 50 | 014:30 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B21101200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 870 | 2021-10-12 | 43500 | keep | 0 | Oct | 2021 | 0.029628 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-12 08:09 | 2021-10-12 12:48 | 79 | 004:39 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21101200066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2021-10-12 | 22041 | keep | 0 | Oct | 2021 | 0.015012 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
BAYAMON | 2021-10-12 08:13 | 2021-10-12 11:26 | 200 | 003:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN TRONCAL | B21101200027 | New_Event | Wire Down | Include | Include | Equipment | 193 | 2021-10-12 | 38600 | keep | 0 | Oct | 2021 | 0.02629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-10-12 08:29 | 2021-10-12 20:22 | 50 | 011:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | S21101200072 | New_Event | Wire Down | Include | Include | Equipment | 713 | 2021-10-12 | 35650 | keep | 0 | Oct | 2021 | 0.024281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-12 08:31 | 2021-10-12 13:37 | 50 | 005:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21101200031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 306 | 2021-10-12 | 15300 | keep | 0 | Oct | 2021 | 0.010421 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-12 08:34 | 2021-10-12 16:23 | 30 | 007:49 | P | CABLE SOTERRADO AVERIADO | SE INSTALO JUMPER EN SU POR CABLE SOTERRADO AVERIADO RADIAL | B21101200034 | New_Event | UG Cable Fault | Include | Include | Equipment | 469 | 2021-10-12 | 14070 | keep | 0 | Oct | 2021 | 0.009583 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-10-12 08:34 | 2021-10-12 17:22 | 30 | 008:48 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEAS SE REALIZO DESGANCHE | B21101200114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 528 | 2021-10-12 | 15840 | keep | 0 | Oct | 2021 | 0.010789 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-12 08:44 | 2021-10-12 10:50 | 80 | 002:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21101200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-10-12 | 10080 | keep | 0 | Oct | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-12 08:47 | 2021-10-12 10:41 | 50 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101200078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2021-10-12 | 5700 | keep | 0 | Oct | 2021 | 0.0038822 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-12 08:59 | 2021-10-12 12:16 | 73 | 003:17 | P | NO SE REPORTO CAUSA | 2 X 100 CORTE DE LINEA | S21101200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-10-12 | 14381 | keep | 0 | Oct | 2021 | 0.0097948 | 4.972e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 73
SAN JUAN | 2021-10-12 09:03 | 2021-10-12 11:23 | 49 | 002:20 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21101200081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-10-12 | 6860 | keep | 0 | Oct | 2021 | 0.0046723 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
SAN JUAN | 2021-10-12 09:03 | 2021-10-12 12:41 | 49 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21101200083 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-10-12 | 10682 | keep | 0 | Oct | 2021 | 0.0072755 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
VEGA BAJA | 2021-10-12 09:14 | 2021-10-12 11:00 | 30 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO | B21101200028 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-10-12 | 3180 | keep | 0 | Oct | 2021 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-12 09:21 | 2021-10-12 14:15 | 200 | 004:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 25 CORTE DE LINEA POR RAYOS | A21101200016 | New_Event | Bad Weather | Include | Include | Weather | 294 | 2021-10-12 | 58800 | keep | 0 | Oct | 2021 | 0.040048 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-12 09:22 | 2021-10-12 10:38 | 1 | 001:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | S21101000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-10-12 | 76 | keep | 0 | Oct | 2021 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-12 09:26 | 2021-10-12 21:51 | 40 | 012:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | B21101200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 745 | 2021-10-12 | 29800 | keep | 0 | Oct | 2021 | 0.020297 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-12 09:26 | 2021-10-12 09:27 | 222 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO LLEVA EL 99% DEL 1909-09 | S21101200089 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-12 | 222 | keep | 0 | Oct | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-10-12 09:26 | 2021-10-12 09:27 | 4412 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO 99% DE LA CARGA POR EL 1907-03 | S21101200089 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-12 | 4412 | keep | 0 | Oct | 2021 | 0.003005 | 0.003005 | Momentary | FALSE | FALSE | Not_TMED_Event | 4412
BAYAMON | 2021-10-12 09:27 | 2021-10-12 15:59 | 1 | 006:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN RISER SE REMPLAZO CAJA PRIMARIA EN RISER | S21101200135 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 392 | 2021-10-12 | 392 | keep | 0 | Oct | 2021 | 0.00026699 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-12 09:31 | 2021-10-12 15:09 | 1 | 005:38 | P | ESTRUCTURA AVERIADA | REEMPLAZO DE POSTE DE MADERA AVERIADO POR METAL DE 45 PIES | A21101000004 | New_Event | Defective Pole | Include | Include | Equipment | 338 | 2021-10-12 | 338 | keep | 0 | Oct | 2021 | 0.00023021 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-12 09:44 | 2021-10-12 17:45 | 70 | 008:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | A21101200020 | New_Event | Cutout Failure | Include | Include | Equipment | 481 | 2021-10-12 | 33670 | keep | 0 | Oct | 2021 | 0.022932 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-10-12 09:52 | 2021-10-12 15:00 | 100 | 005:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA | S21101100066 | New_Event | Wire Down | Include | Include | Equipment | 308 | 2021-10-12 | 30800 | keep | 0 | Oct | 2021 | 0.020978 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-10-12 09:53 | 2021-10-12 15:04 | 1 | 005:11 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21101200040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 311 | 2021-10-12 | 311 | keep | 0 | Oct | 2021 | 0.00021182 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-12 09:56 | 2021-10-12 11:07 | 8 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | S21101100093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-10-12 | 568 | keep | 0 | Oct | 2021 | 0.00038686 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-10-12 09:56 | 2021-10-12 12:48 | 200 | 002:52 | P | LINEA DE TRANSMISION 38KV | SECCIONALIZARON PUENTE ABIERTO EN LINEA 5300 | C21101200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 172 | 2021-10-12 | 34400 | keep | 0 | Oct | 2021 | 0.02343 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-10-12 09:56 | 2021-10-12 10:00 | 1494 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | B21101200000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-10-12 | 5976 | keep | 0 | Oct | 2021 | 0.0040702 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
CANOVANAS | 2021-10-12 09:59 | 2021-10-12 12:55 | 10 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21101200041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2021-10-12 | 1760 | keep | 0 | Oct | 2021 | 0.0011987 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-12 10:00 | 2021-10-12 11:25 | 100 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21101100220 | Partial_restoration | Wire Down | Include | Include | Equipment | 85 | 2021-10-12 | 8500 | keep | 0 | Oct | 2021 | 0.0057893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-12 10:36 | 2021-10-12 17:23 | 100 | 006:47 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21101200110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2021-10-12 | 40700 | keep | 0 | Oct | 2021 | 0.027721 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-12 10:50 | 2021-10-12 12:15 | 5 | 001:25 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | A21101200031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 85 | 2021-10-12 | 425 | keep | 0 | Oct | 2021 | 0.00028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-12 11:06 | 2021-10-12 11:07 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 3941 | keep | 0 | Oct | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-10-12 11:07 | 2021-10-12 19:17 | 1 | 008:10 | P | NO SE REPORTO CAUSA | 2 X 40 EN SU | B21101200111 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 490 | 2021-10-12 | 490 | keep | 0 | Oct | 2021 | 0.00033374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-10-12 11:15 | 2021-10-12 11:16 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101200165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 1606 | keep | 0 | Oct | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
AGUADILLA | 2021-10-12 11:23 | 2021-10-12 11:28 | 1428 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-12 | 7140 | keep | 0 | Oct | 2021 | 0.004863 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
BAYAMON | 2021-10-12 11:40 | 2021-10-12 18:32 | 6 | 006:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DESGANCHE TOMA Y SECUNDARIA | S21101100599 | New_Event | Secondary Wire Down | Include | Include | Equipment | 412 | 2021-10-12 | 2472 | keep | 0 | Oct | 2021 | 0.0016837 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-12 11:43 | 2021-10-12 13:23 | 25 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-10-12 | 2500 | keep | 0 | Oct | 2021 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-10-12 11:55 | 2021-10-12 14:04 | 1 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21101200040 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-10-12 | 129 | keep | 0 | Oct | 2021 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-12 11:57 | 2021-10-12 19:24 | 20 | 007:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PARTIDA | A21101200041 | New_Event | Wire Down | Include | Include | Equipment | 447 | 2021-10-12 | 8940 | keep | 0 | Oct | 2021 | 0.006089 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-12 12:00 | 2021-10-13 12:50 | 35 | 024:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | S21101200050 | New_Event | Wire Down | Include | Include | Equipment | 1490 | 2021-10-12 | 52150 | keep | 0 | Oct | 2021 | 0.035519 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-10-12 12:15 | 2021-10-12 17:49 | 40 | 005:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA AVERIADA EN CORTE DE LINEA VER EVENTO M21101200114 | M21101200046 | New_Event | Cutout Failure | Include | Include | Equipment | 334 | 2021-10-12 | 13360 | keep | 0 | Oct | 2021 | 0.0090994 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-12 12:16 | 2021-10-12 17:56 | 12 | 005:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA SOTERRADA AVERIADA POR PERSONAL DE ACUEDUCTOS | B21101200085 | New_Event |  |  | Include | Wildlife | 340 | 2021-10-12 | 4080 | keep | 0 | Oct | 2021 | 0.0027789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-12 12:18 | 2021-10-12 15:21 | 140 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | R21101200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-10-12 | 25620 | keep | 0 | Oct | 2021 | 0.01745 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
BAYAMON | 2021-10-12 12:29 | 2021-10-12 15:31 | 10 | 003:02 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21101200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-10-12 | 1820 | keep | 0 | Oct | 2021 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-10-12 12:30 | 2021-10-12 12:31 | 2747 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21101200055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 2747 | keep | 0 | Oct | 2021 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
CAGUAS | 2021-10-12 12:35 | 2021-10-12 15:37 | 175 | 003:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE DESGANCHO ARBOL | C21101200198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-10-12 | 31850 | keep | 0 | Oct | 2021 | 0.021693 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
YAUCO | 2021-10-12 12:41 | 2021-10-12 12:42 | 80 | 000:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101100139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-12 | 80 | keep | 0 | Oct | 2021 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-12 12:52 | 2021-10-13 16:03 | 10 | 027:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S21101100140 | New_Event | Wire Down | Include | Include | Equipment | 1631 | 2021-10-12 | 16310 | keep | 0 | Oct | 2021 | 0.011109 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
PONCE | 2021-10-12 12:53 | 2021-10-12 22:05 | 5 | 009:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | P21101200058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 552 | 2021-10-12 | 2760 | keep | 0 | Oct | 2021 | 0.0018798 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-10-12 13:01 | 2021-10-13 16:30 | 15 | 027:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21101200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1649 | 2021-10-12 | 24735 | keep | 0 | Oct | 2021 | 0.016847 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-12 13:06 | 2021-10-13 10:09 | 60 | 021:03 | P | PARARRAYOS DEFECTUOSO | 1 X 50 Y 1 X 30 EN CORTES DE LINEA SE REMPLAZO PARARRAYO | S21101200093 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1263 | 2021-10-12 | 75780 | keep | 0 | Oct | 2021 | 0.051613 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-12 13:06 | 2021-10-12 18:13 | 2 | 005:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21101200046 | New_Event | Bad Weather | Include | Include | Weather | 307 | 2021-10-12 | 614 | keep | 0 | Oct | 2021 | 0.00041819 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-10-12 13:07 | 2021-10-13 10:45 | 1 | 021:38 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | S21101200141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1298 | 2021-10-12 | 1298 | keep | 0 | Oct | 2021 | 0.00088406 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-10-12 13:43 | 2021-10-12 15:15 | 1 | 001:32 | P | DESGANCHE | 1 X 15 EN RISER | R21101200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-10-12 | 92 | keep | 0 | Oct | 2021 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-12 13:45 | 2021-10-12 16:41 | 175 | 002:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN RAISER POR CAJA PRIMARIA QUEMADA | P21101200065 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2021-10-12 | 30800 | keep | 0 | Oct | 2021 | 0.020978 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
VEGA BAJA | 2021-10-12 13:51 | 2021-10-12 15:01 | 10 | 001:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA A POSTE DE METAL POR POSTE PARTIDO | B21101200059 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 70 | 2021-10-12 | 700 | keep | 0 | Oct | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-12 13:52 | 2021-10-12 19:14 | 472 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | C21101200230 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2021-10-12 | 151984 | keep | 0 | Oct | 2021 | 0.10352 | 0.00032148 | Sustained | FALSE | TRUE | Not_TMED_Event | 472
ARECIBO | 2021-10-12 13:53 | 2021-10-12 15:18 | 200 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 1 X 100 EN CORTE DE LINEA POR RAYO | A21101200055 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-10-12 | 17000 | keep | 0 | Oct | 2021 | 0.011579 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-12 13:54 | 2021-10-12 16:41 | 30 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21101200056 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-10-12 | 5010 | keep | 0 | Oct | 2021 | 0.0034123 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-10-12 13:59 | 2021-10-12 19:07 | 50 | 005:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN CORTE DE LINEA Y 1X20 EN TRANSFORMADOR SE CAMBIO CAJA PRIMARIA QUEMADA | P21101200067 | New_Event | Cutout Failure | Include | Include | Equipment | 308 | 2021-10-12 | 15400 | keep | 0 | Oct | 2021 | 0.010489 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-12 14:05 | 2021-10-12 18:28 | 60 | 004:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101200063 | New_Event | Bad Weather | Include | Include | Weather | 263 | 2021-10-12 | 15780 | keep | 0 | Oct | 2021 | 0.010748 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-12 14:07 | 2021-10-12 17:17 | 10 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21101200061 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-10-12 | 1900 | keep | 0 | Oct | 2021 | 0.0012941 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-12 14:08 | 2021-10-12 14:47 | 2435 | 000:39 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO MAL TIEMPO EN EL AREA LLEVA 20% 1204-2 Y 60AMP.1206-4 | S21101200156 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-10-12 | 94965 | keep | 0 | Oct | 2021 | 0.06468 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
HUMACAO | 2021-10-12 14:08 | 2021-10-12 14:09 | 2299 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21101200236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 2299 | keep | 0 | Oct | 2021 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
SAN JUAN | 2021-10-12 14:10 | 2021-10-12 14:48 | 1598 | 000:38 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO MAL TIEMPO LLEVA 1303-1 Y 1346-6 | S21101200000 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-10-12 | 60724 | keep | 0 | Oct | 2021 | 0.041359 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-10-12 14:10 | 2021-10-12 14:48 | 225 | 000:38 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO MAL TIEMPO LLEVA 1303-1 Y 1346-6 | S21101200000 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-10-12 | 8550 | keep | 0 | Oct | 2021 | 0.0058234 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-12 14:10 | 2021-10-12 14:46 | 870 | 000:36 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO MAL TIEMPO LLEVA 1303-4 | S21101200000 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2021-10-12 | 31320 | keep | 0 | Oct | 2021 | 0.021332 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-10-12 14:10 | 2021-10-12 14:48 | 1598 | 000:38 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO MAL TIEMPO LLEVA 1303-1 Y 1346-6 | S21101200000 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-10-12 | 60724 | keep | 0 | Oct | 2021 | 0.041359 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-10-12 14:14 | 2021-10-12 16:45 | 12 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN TRANSFORMADOR DESCARGA ELECTRICA | R21101200080 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-10-12 | 1812 | keep | 0 | Oct | 2021 | 0.0012341 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:26 | 137 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-12 | 1507 | keep | 0 | Oct | 2021 | 0.0010264 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:26 | 457 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-12 | 5027 | keep | 0 | Oct | 2021 | 0.0034239 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:26 | 1225 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-12 | 13475 | keep | 0 | Oct | 2021 | 0.0091778 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:26 | 1452 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-12 | 15972 | keep | 0 | Oct | 2021 | 0.010878 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:26 | 616 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-12 | 6776 | keep | 0 | Oct | 2021 | 0.0046151 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:26 | 3432 | 000:11 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-12 | 37752 | keep | 0 | Oct | 2021 | 0.025713 | 0.0023375 | Sustained | FALSE | TRUE | Not_TMED_Event | 3432
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:37 | 660 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-12 | 14520 | keep | 0 | Oct | 2021 | 0.0098895 | 0.00044952 | Sustained | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:37 | 435 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-12 | 9570 | keep | 0 | Oct | 2021 | 0.0065181 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:37 | 259 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-12 | 5698 | keep | 0 | Oct | 2021 | 0.0038809 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:37 | 686 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-12 | 15092 | keep | 0 | Oct | 2021 | 0.010279 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2021-10-12 14:15 | 2021-10-12 14:37 | 953 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-10-12 | 20966 | keep | 0 | Oct | 2021 | 0.01428 | 0.00064908 | Sustained | FALSE | FALSE | Not_TMED_Event | 953
BAYAMON | 2021-10-12 14:17 | 2021-10-12 14:50 | 530 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR NO RECERRO SE PROBO QUEDO EN SERVICIO PARTE DE SU CARGA POR EL 1529-15 | S21101100540 | Additional_clients | Wire Down | Include | Include | Equipment | 33 | 2021-10-12 | 17490 | keep | 0 | Oct | 2021 | 0.011912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-12 14:17 | 2021-10-12 14:50 | 1802 | 000:33 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO LLEVA 30% 1346-2 SE PROBO QUEDO EN SERVICIO | S21101200165 | New_Event | Bad Weather | Include | Include | Weather | 33 | 2021-10-12 | 59466 | keep | 0 | Oct | 2021 | 0.040502 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
CANOVANAS | 2021-10-12 14:19 | 2021-10-12 17:50 | 50 | 003:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE QUEMADO | R21101200081 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2021-10-12 | 10550 | keep | 0 | Oct | 2021 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-12 14:27 | 2021-10-12 14:53 | 10 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21101200060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-10-12 | 260 | keep | 0 | Oct | 2021 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-12 14:33 | 2021-10-12 14:36 | 1501 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21101200103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-12 | 4503 | keep | 0 | Oct | 2021 | 0.003067 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-10-12 14:34 | 2021-10-12 14:35 | 2422 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1346-03 | S21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 2422 | keep | 0 | Oct | 2021 | 0.0016496 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2021-10-12 14:34 | 2021-10-12 14:35 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA CARGA DEL 1346-03 | S21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 2466 | keep | 0 | Oct | 2021 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2021-10-12 14:34 | 2021-10-12 14:35 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1907-03 | S21101200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 4456 | keep | 0 | Oct | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2021-10-12 14:44 | 2021-10-12 22:31 | 100 | 007:47 | P | DESCONECTIVO DEFECTUOSO | 6 X 50 EN CORTE DE LINEA Y 2 X 30 EN CORTE DE LINEA SE REMPLAZO PISTOLA | B21101200106 | New_Event | Switch Failure | Include | Include | Equipment | 467 | 2021-10-12 | 46700 | keep | 0 | Oct | 2021 | 0.031807 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-12 14:46 | 2021-10-12 17:27 | 10 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101200108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-10-12 | 1610 | keep | 0 | Oct | 2021 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-12 14:47 | 2021-10-13 13:47 | 15 | 023:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101300071 | New_Event | Bad Weather | Include | Include | Weather | 1380 | 2021-10-12 | 20700 | keep | 0 | Oct | 2021 | 0.014099 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-12 14:51 | 2021-10-13 11:41 | 60 | 020:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101200234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1250 | 2021-10-12 | 75000 | keep | 0 | Oct | 2021 | 0.051082 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-10-12 15:02 | 2021-10-13 13:40 | 130 | 022:38 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21101200256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1358 | 2021-10-12 | 176540 | keep | 0 | Oct | 2021 | 0.12024 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
UTUADO | 2021-10-12 15:04 | 2021-10-12 17:24 | 150 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR RAYOS | A21101200073 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-10-12 | 21000 | keep | 0 | Oct | 2021 | 0.014303 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-10-12 15:07 | 2021-10-13 10:02 | 10 | 018:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101200074 | New_Event | Bad Weather | Include | Include | Weather | 1135 | 2021-10-12 | 11350 | keep | 0 | Oct | 2021 | 0.0077304 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-12 15:08 | 2021-10-12 19:06 | 80 | 003:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 Y 1 X 40 EN CORTE DE LINEA POR RAYO | A21101200075 | New_Event | Bad Weather | Include | Include | Weather | 238 | 2021-10-12 | 19040 | keep | 0 | Oct | 2021 | 0.012968 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-10-12 15:09 | 2021-10-13 16:11 | 5 | 025:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21101200261 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1502 | 2021-10-12 | 7510 | keep | 0 | Oct | 2021 | 0.005115 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-12 15:16 | 2021-10-12 21:13 | 10 | 005:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101200116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 357 | 2021-10-12 | 3570 | keep | 0 | Oct | 2021 | 0.0024315 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-12 15:17 | 2021-10-12 16:20 | 75 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21101200078 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-10-12 | 4725 | keep | 0 | Oct | 2021 | 0.0032182 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-10-12 15:21 | 2021-10-12 16:39 | 20 | 001:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21101200113 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2021-10-12 | 1560 | keep | 0 | Oct | 2021 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-10-12 15:22 | 2021-10-12 17:31 | 10 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A21101200080 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-10-12 | 1290 | keep | 0 | Oct | 2021 | 0.00087861 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-12 15:27 | 2021-10-12 17:53 | 40 | 002:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL DE LAS LINEAS | M21101200081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-10-12 | 5840 | keep | 0 | Oct | 2021 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-12 15:31 | 2021-10-12 18:46 | 1 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REEMPLAZO BAJANTES SECUNDARIOS | R21101200089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2021-10-12 | 195 | keep | 0 | Oct | 2021 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-12 15:31 | 2021-10-12 18:40 | 45 | 003:09 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21101200120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2021-10-12 | 8505 | keep | 0 | Oct | 2021 | 0.0057927 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BARRANQUITAS | 2021-10-12 15:39 | 2021-10-12 19:17 | 15 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21101200270 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-10-12 | 3270 | keep | 0 | Oct | 2021 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-12 15:43 | 2021-10-13 12:12 | 60 | 020:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA 1 X 20 EN TRANSFORMADOR Y 1 X 15 EN OTRO RAYOS | B21101200124 | New_Event | Bad Weather | Include | Include | Weather | 1229 | 2021-10-12 | 73740 | keep | 0 | Oct | 2021 | 0.050224 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-12 15:43 | 2021-10-12 19:55 | 100 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR RAYOS | A21101200087 | New_Event | Bad Weather | Include | Include | Weather | 252 | 2021-10-12 | 25200 | keep | 0 | Oct | 2021 | 0.017164 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-12 15:43 | 2021-10-12 16:37 | 20 | 000:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21101100087 | New_Event | Bad Weather | Include | Include | Weather | 54 | 2021-10-12 | 1080 | keep | 0 | Oct | 2021 | 0.00073558 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-12 15:51 | 2021-10-12 19:16 | 2174 | 003:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR 7802-03 POR SEGURIDAD A PETICION DE ALVIN LUGO POR LINEA PRIMARIA ROTA LA SALIDA DEL ALIMENTADOR SE REPARO LA CONDICION Y SE CERRO EL INTERRUPTOR LLEVA LA CARGA DEL 7802-01 | M21101200088 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2021-10-12 | 445670 | keep | 0 | Oct | 2021 | 0.30354 | 0.0014807 | Sustained | FALSE | TRUE | Not_TMED_Event | 2174
MAYAGÃœEZ | 2021-10-12 15:51 | 2021-10-12 19:18 | 64 | 003:27 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR 7802-03 POR SEGURIDAD A PETICION DE ALVIN LUGO POR LINEA PRIMARIA ROTA LA SALIDA DEL ALIMENTADOR SE REPARO LA CONDICION Y SE CERRO EL INTERRUPTOR | M21101200088 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2021-10-12 | 13248 | keep | 0 | Oct | 2021 | 0.0090232 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
BARRANQUITAS | 2021-10-12 15:51 | 2021-10-12 18:57 | 10 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21101200275 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-10-12 | 1860 | keep | 0 | Oct | 2021 | 0.0012668 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-12 15:53 | 2021-10-12 19:34 | 150 | 003:41 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN CORTES DE LINEA DESGANCHO Y REEMPLAZO PORTAFUSIBLE | R21101200091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-10-12 | 33150 | keep | 0 | Oct | 2021 | 0.022578 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-12 16:11 | 2021-10-12 16:58 | 10 | 000:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO HOT CLAMP | P21101200082 | New_Event | Wire Down | Include | Include | Equipment | 47 | 2021-10-12 | 470 | keep | 0 | Oct | 2021 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-12 16:14 | 2021-10-13 09:48 | 60 | 017:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21101200282 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1054 | 2021-10-12 | 63240 | keep | 0 | Oct | 2021 | 0.043072 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-12 16:18 | 2021-10-12 19:15 | 4 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21101200049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2021-10-12 | 708 | keep | 0 | Oct | 2021 | 0.00048222 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-12 16:25 | 2021-10-13 10:00 | 50 | 017:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21101200104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1055 | 2021-10-12 | 52750 | keep | 0 | Oct | 2021 | 0.035928 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-12 16:28 | 2021-10-12 16:59 | 1 | 000:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21101200096 | New_Event |  |  | Include | Wildlife | 31 | 2021-10-12 | 31 | keep | 0 | Oct | 2021 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-12 16:30 | 2021-10-13 12:00 | 2 | 019:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21101200103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1170 | 2021-10-12 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
AGUADILLA | 2021-10-12 16:33 | 2021-10-12 18:55 | 200 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101200105 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-10-12 | 28400 | keep | 0 | Oct | 2021 | 0.019343 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-10-12 16:41 | 2021-10-13 16:27 | 20 | 023:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | C21101200287 | New_Event | Bad Weather | Include | Include | Weather | 1426 | 2021-10-12 | 28520 | keep | 0 | Oct | 2021 | 0.019425 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-12 16:48 | 2021-10-12 20:01 | 130 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21101200028 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-10-12 | 25090 | keep | 0 | Oct | 2021 | 0.017089 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
AGUADILLA | 2021-10-12 16:49 | 2021-10-12 18:23 | 1 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO AVERIADO EN TRANSFORMADOR Y SE REMPLAZO CAJA EN FID:23786895 MARCA:CHIST 100AMP | M21101200108 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-10-12 | 94 | keep | 0 | Oct | 2021 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-10-12 16:50 | 2021-10-12 16:55 | 2286 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-12 | 11430 | keep | 0 | Oct | 2021 | 0.0077849 | 0.001557 | Momentary | FALSE | TRUE | Not_TMED_Event | 2286
FAJARDO | 2021-10-12 16:50 | 2021-10-12 16:55 | 693 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-12 | 3465 | keep | 0 | Oct | 2021 | 0.00236 | 0.000472 | Momentary | FALSE | TRUE | Not_TMED_Event | 693
ARECIBO | 2021-10-12 16:50 | 2021-10-12 19:09 | 100 | 002:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A21101200109 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 139 | 2021-10-12 | 13900 | keep | 0 | Oct | 2021 | 0.0094672 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-12 16:51 | 2021-10-13 10:57 | 16 | 018:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21101200109 | New_Event | Bad Weather | Include | Include | Weather | 1086 | 2021-10-12 | 17376 | keep | 0 | Oct | 2021 | 0.011835 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
BAYAMON | 2021-10-12 16:54 | 2021-10-12 18:01 | 80 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | S21101200008 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-10-12 | 5360 | keep | 0 | Oct | 2021 | 0.0036507 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-10-12 16:55 | 2021-10-13 17:00 | 45 | 024:05 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P21101200086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1445 | 2021-10-12 | 65025 | keep | 0 | Oct | 2021 | 0.044288 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-12 17:03 | 2021-10-13 11:45 | 30 | 018:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101200114 | New_Event | Bad Weather | Include | Include | Weather | 1122 | 2021-10-12 | 33660 | keep | 0 | Oct | 2021 | 0.022926 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-12 17:06 | 2021-10-13 11:13 | 75 | 018:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO TRES CAJAS CAJAS PRIMARIAS AVERIADAS | A21101200118 | New_Event | Cutout Failure | Include | Include | Equipment | 1087 | 2021-10-12 | 81525 | keep | 0 | Oct | 2021 | 0.055526 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-10-12 17:07 | 2021-10-12 18:23 | 80 | 001:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21101200275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-10-12 | 6080 | keep | 0 | Oct | 2021 | 0.0041411 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-12 17:08 | 2021-10-13 11:19 | 30 | 018:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101200148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1091 | 2021-10-12 | 32730 | keep | 0 | Oct | 2021 | 0.022292 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-12 17:13 | 2021-10-12 20:21 | 5 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21101200122 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-10-12 | 940 | keep | 0 | Oct | 2021 | 0.00064023 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
ARECIBO | 2021-10-12 17:15 | 2021-10-13 16:29 | 10 | 023:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101200124 | New_Event | Bad Weather | Include | Include | Weather | 1394 | 2021-10-12 | 13940 | keep | 0 | Oct | 2021 | 0.0094945 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-12 17:23 | 2021-10-12 18:21 | 100 | 000:58 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE HIZO DESGANCHE Y SE RETEZO LINEA | S21101200110 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-10-12 | 5800 | keep | 0 | Oct | 2021 | 0.0039504 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-12 17:24 | 2021-10-13 14:52 | 180 | 021:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21101200128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1288 | 2021-10-12 | 231840 | keep | 0 | Oct | 2021 | 0.15791 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
VEGA BAJA | 2021-10-12 17:27 | 2021-10-12 17:29 | 2610 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21101200154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-12 | 5220 | keep | 0 | Oct | 2021 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
BARRANQUITAS | 2021-10-12 17:43 | 2021-10-12 23:38 | 50 | 005:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101200298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-10-12 | 17750 | keep | 0 | Oct | 2021 | 0.012089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-12 17:49 | 2021-10-12 18:20 | 1509 | 000:31 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO EL INTERRUPTOR AUTORIZADO POR CHRISTIAN FELICIANO PARA REMPLAZAR CAJA AVERIADA EN EL FID: 19537647 MARCA CHIST 100AMP CON FUSIBLE DE 100AMP | M21101200114 | Additional_clients | Cutout Failure | Include | Include | Equipment | 31 | 2021-10-12 | 46779 | keep | 0 | Oct | 2021 | 0.031861 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-12 17:54 | 2021-10-12 20:31 | 10 | 002:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21101200115 | New_Event | Wire Down | Include | Include | Equipment | 157 | 2021-10-12 | 1570 | keep | 0 | Oct | 2021 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-12 17:55 | 2021-10-13 21:51 | 15 | 027:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21101200160 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1676 | 2021-10-12 | 25140 | keep | 0 | Oct | 2021 | 0.017123 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-12 17:59 | 2021-10-13 14:15 | 30 | 020:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21101200304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1216 | 2021-10-12 | 36480 | keep | 0 | Oct | 2021 | 0.024846 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-12 18:00 | 2021-10-13 11:13 | 55 | 017:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21101200293 | New_Event | Wire Down | Include | Include | Equipment | 1033 | 2021-10-12 | 56815 | keep | 0 | Oct | 2021 | 0.038696 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-10-12 18:18 | 2021-10-12 18:19 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTROR CON EL RECIERRE EN OFF SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21101200119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 2999 | keep | 0 | Oct | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | TRUE | Not_TMED_Event | 2999
SAN JUAN | 2021-10-12 18:21 | 2021-10-12 22:09 | 60 | 003:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA PORTAFUSIBLE | S21101200309 | New_Event | Cutout Failure | Include | Include | Equipment | 228 | 2021-10-12 | 13680 | keep | 0 | Oct | 2021 | 0.0093174 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-12 18:21 | 2021-10-13 11:35 | 518 | 017:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO SALIDA DEL CONVERTIDOR PARA REEMPLAZAR DOS PUENTES ABIERTOS, NO FUNDIO FUSIBLE. | C21101200308 | New_Event | Wire Down | Include | Include | Equipment | 1034 | 2021-10-12 | 535612 | keep | 0 | Oct | 2021 | 0.3648 | 0.00035281 | Sustained | FALSE | FALSE | Not_TMED_Event | 518
SAN JUAN | 2021-10-12 18:22 | 2021-10-12 20:12 | 40 | 001:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21101200313 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-10-12 | 4400 | keep | 0 | Oct | 2021 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-12 18:27 | 2021-10-14 14:51 | 50 | 044:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21101200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2664 | 2021-10-12 | 133200 | keep | 0 | Oct | 2021 | 0.090722 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-12 18:30 | 2021-10-13 14:20 | 12 | 019:50 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101100167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1190 | 2021-10-12 | 14280 | keep | 0 | Oct | 2021 | 0.009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-12 18:41 | 2021-10-13 16:13 | 10 | 021:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21101200324 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1292 | 2021-10-12 | 12920 | keep | 0 | Oct | 2021 | 0.0087998 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-12 18:42 | 2021-10-12 22:52 | 60 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101200122 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2021-10-12 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-12 18:44 | 2021-10-12 19:32 | 50 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21101200316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2021-10-12 | 2400 | keep | 0 | Oct | 2021 | 0.0016346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-12 18:51 | 2021-10-13 17:34 | 15 | 022:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21101200171 | New_Event | Wire Down | Include | Include | Equipment | 1363 | 2021-10-12 | 20445 | keep | 0 | Oct | 2021 | 0.013925 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
FAJARDO | 2021-10-12 18:56 | 2021-10-13 10:08 | 45 | 015:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21101200113 | New_Event | Bad Weather | Include | Include | Weather | 912 | 2021-10-12 | 41040 | keep | 0 | Oct | 2021 | 0.027952 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-10-12 18:56 | 2021-10-13 11:39 | 25 | 016:43 | P | OTRAS CAUSAS | 1 X 20 EN SU-12 @ T-12 SE LIMPIO T-12 CONTAMINADO | C21101200320 | New_Event | Other Causes | Include | Include | Other | 1003 | 2021-10-12 | 25075 | keep | 0 | Oct | 2021 | 0.017078 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-10-12 19:24 | 2021-10-12 19:25 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101200095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-12 | 527 | keep | 0 | Oct | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
UTUADO | 2021-10-12 19:25 | 2021-10-13 16:10 | 20 | 020:45 | P | ESTRUCTURA AVERIADA | 2 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE SE ENDEREZO POSTE PRIMARIO Y SE INSTALO 2 CAJAS PRIMARIAS EN EL FID:1001653919 MARCA CHAINT DE 100AMP REMPLAZO DE XMER | A21101200141 | New_Event | Defective Pole | Include | Include | Equipment | 1245 | 2021-10-12 | 24900 | keep | 0 | Oct | 2021 | 0.016959 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-10-12 19:25 | 2021-10-13 09:00 | 150 | 013:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101200142 | New_Event | Bad Weather | Include | Include | Weather | 815 | 2021-10-12 | 122250 | keep | 0 | Oct | 2021 | 0.083264 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-12 19:31 | 2021-10-13 11:28 | 80 | 015:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA | P21101200092 | New_Event | Cutout Failure | Include | Include | Equipment | 957 | 2021-10-12 | 76560 | keep | 0 | Oct | 2021 | 0.052145 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-10-12 19:36 | 2021-10-13 20:14 | 1 | 024:38 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101200180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1478 | 2021-10-12 | 1478 | keep | 0 | Oct | 2021 | 0.0010067 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-12 19:51 | 2021-10-13 15:17 | 6 | 019:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M21101200129 | New_Event | Bad Weather | Include | Include | Weather | 1166 | 2021-10-12 | 6996 | keep | 0 | Oct | 2021 | 0.0047649 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
HUMACAO | 2021-10-12 20:15 | 2021-10-13 17:16 | 7 | 021:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21101200328 | New_Event | Bad Weather | Include | Include | Weather | 1261 | 2021-10-12 | 8827 | keep | 0 | Oct | 2021 | 0.006012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-12 20:16 | 2021-10-12 22:45 | 50 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21101200338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-10-12 | 7450 | keep | 0 | Oct | 2021 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-12 20:21 | 2021-10-13 14:00 | 35 | 017:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR SE HIZO DESGANCHE MASIVO | P21101200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1059 | 2021-10-12 | 37065 | keep | 0 | Oct | 2021 | 0.025245 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-10-12 21:43 | 2021-10-12 23:43 | 35 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101200136 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-10-12 | 4200 | keep | 0 | Oct | 2021 | 0.0028606 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-10-12 22:20 | 2021-10-13 10:53 | 15 | 012:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | C21101200336 | New_Event | Secondary Wire Down | Include | Include | Equipment | 753 | 2021-10-12 | 11295 | keep | 0 | Oct | 2021 | 0.007693 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-12 22:41 | 2021-10-13 17:07 | 7 | 018:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101200146 | New_Event | Bad Weather | Include | Include | Weather | 1106 | 2021-10-12 | 7742 | keep | 0 | Oct | 2021 | 0.005273 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-10-13 00:31 | 2021-10-13 09:52 | 60 | 009:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R21101300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 561 | 2021-10-13 | 33660 | keep | 0 | Oct | 2021 | 0.022926 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-10-13 00:47 | 2021-10-13 12:08 | 10 | 011:21 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | C21101300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 681 | 2021-10-13 | 6810 | keep | 0 | Oct | 2021 | 0.0046383 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-13 00:49 | 2021-10-13 00:50 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3332 | keep | 0 | Oct | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
MAYAGÃœEZ | 2021-10-13 01:03 | 2021-10-13 14:46 | 60 | 013:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA POR MAL TIEMPO | M21101300003 | New_Event | Bad Weather | Include | Include | Weather | 823 | 2021-10-13 | 49380 | keep | 0 | Oct | 2021 | 0.033632 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-13 01:29 | 2021-10-13 01:32 | 215 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | B21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-13 | 645 | keep | 0 | Oct | 2021 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-10-13 01:32 | 2021-10-13 10:43 | 36 | 009:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU | B21101300002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 551 | 2021-10-13 | 19836 | keep | 0 | Oct | 2021 | 0.01351 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-13 01:39 | 2021-10-13 10:22 | 50 | 008:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 523 | 2021-10-13 | 26150 | keep | 0 | Oct | 2021 | 0.017811 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-13 01:44 | 2021-10-13 07:52 | 266 | 006:08 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRO PB2501-03F MAL TIEMPO | R21101300004 | New_Event | Bad Weather | Include | Include | Weather | 368 | 2021-10-13 | 97888 | keep | 0 | Oct | 2021 | 0.066671 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
HUMACAO | 2021-10-13 02:08 | 2021-10-13 02:09 | 2450 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO | C21101300001 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-13 | 2450 | keep | 0 | Oct | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-10-13 02:09 | 2021-10-13 17:24 | 30 | 015:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21101300018 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 915 | 2021-10-13 | 27450 | keep | 0 | Oct | 2021 | 0.018696 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-13 02:25 | 2021-10-13 13:24 | 143 | 010:59 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTOR MAIN DE BARRA 13KV POR QUE 1404-06 NO OPERO SE TRANSFIRIO LA CARGA DEL 1404-06 AL 1111-02 Y SE TRABAJO PROTECCION DE INTERRUPTOR | S21101300011 | New_Event | Protection Miscoordination | Include | Include | Other | 659 | 2021-10-13 | 94237 | keep | 0 | Oct | 2021 | 0.064184 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2021-10-13 02:25 | 2021-10-13 15:05 | 1357 | 012:40 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTOR MAIN DE BARRA 13KV POR QUE 1404-06 NO OPERO EN AVERIA SE CERRO INTERRUPTOR Y SE NORMALIZARON CARGAS | S21101300011 | New_Event | Protection Miscoordination | Include | Include | Other | 760 | 2021-10-13 | 1031320 | keep | 0 | Oct | 2021 | 0.70243 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
SAN JUAN | 2021-10-13 02:25 | 2021-10-13 15:05 | 328 | 012:40 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTOR MAIN DE BARRA 13KV POR QUE 1404-06 NO OPERO EN AVERIA SE CERRO INTERRUPTOR Y SE NORMALIZARON CARGAS | S21101300011 | New_Event | Protection Miscoordination | Include | Include | Other | 760 | 2021-10-13 | 249280 | keep | 0 | Oct | 2021 | 0.16978 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
SAN JUAN | 2021-10-13 02:25 | 2021-10-13 13:01 | 485 | 010:36 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTOR MAIN DE BARRA 13KV POR QUE 1404-06 NO OPERO EN AVERIA SE TRANSFIRIO LA CARGA DEL 1404-09 AL 1420-01 | S21101300011 | New_Event | Protection Miscoordination | Include | Include | Other | 636 | 2021-10-13 | 308460 | keep | 0 | Oct | 2021 | 0.21009 | 0.00033033 | Sustained | FALSE | FALSE | Not_TMED_Event | 485
VEGA BAJA | 2021-10-13 02:26 | 2021-10-13 02:27 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 27 | keep | 0 | Oct | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
AGUADILLA | 2021-10-13 02:34 | 2021-10-13 18:25 | 15 | 015:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR LO MISMO | M21101300009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 951 | 2021-10-13 | 14265 | keep | 0 | Oct | 2021 | 0.0097158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 02:50 | 2021-10-13 02:51 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 1346-5 PARTE DEL 1348-8 Y PARTE DEL 1303-2 | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-13 02:50 | 2021-10-13 02:51 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1346-5 PARTE DEL 1348-8 Y PARTE DEL 1303-2 CARGA 1401-08 | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 922 | keep | 0 | Oct | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-10-13 02:50 | 2021-10-13 02:51 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 1346-5 PARTE DEL 1348-8 Y PARTE DEL 1303-2 CARGA POR EL 1401-08 | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-13 02:50 | 2021-10-13 02:51 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1346-5 PARTE DEL 1348-8 Y PARTE DEL 1303-2 | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2021-10-13 03:17 | 2021-10-13 03:18 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M21101300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3458 | keep | 0 | Oct | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2021-10-13 03:40 | 2021-10-13 10:51 | 110 | 007:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21101300005 | New_Event | Bad Weather | Include | Include | Weather | 431 | 2021-10-13 | 47410 | keep | 0 | Oct | 2021 | 0.032291 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
GUAYAMA | 2021-10-13 04:01 | 2021-10-13 13:00 | 155 | 008:59 | P | TRANSFORMADOR AVERIADO | 1 X 80 EN CORTE DE LINEA SE ENCONTRO TRANSFORMADOR DE 37.5 KVA A 4160VOLTS QUEMADO POR LO MISMO | P21101300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 539 | 2021-10-13 | 83545 | keep | 0 | Oct | 2021 | 0.056902 | 0.00010557 | Sustained | FALSE | TRUE | Not_TMED_Event | 155
FAJARDO | 2021-10-13 04:56 | 2021-10-13 04:57 | 2722 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21101300012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-13 | 2722 | keep | 0 | Oct | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2021-10-13 04:57 | 2021-10-13 04:59 | 25 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | R21101300020 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-10-13 | 50 | keep | 0 | Oct | 2021 | 3.4055e-05 | 1.7027e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-10-13 04:59 | 2021-10-13 05:00 | 2722 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21101300012 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-13 | 2722 | keep | 0 | Oct | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2021-10-13 05:00 | 2021-10-13 12:52 | 25 | 007:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | R21101300020 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 472 | 2021-10-13 | 11800 | keep | 0 | Oct | 2021 | 0.0080369 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-13 05:03 | 2021-10-13 05:05 | 320 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | B21101300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-13 | 640 | keep | 0 | Oct | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
FAJARDO | 2021-10-13 05:12 | 2021-10-13 11:56 | 17 | 006:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE RETIRO CULEBRA DE LA CAJA PRIMARIA | R21101300014 | New_Event |  |  | Include | Wildlife | 404 | 2021-10-13 | 6868 | keep | 0 | Oct | 2021 | 0.0046778 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2021-10-13 05:21 | 2021-10-13 05:22 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21101300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1478 | keep | 0 | Oct | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
FAJARDO | 2021-10-13 05:43 | 2021-10-13 12:00 | 30 | 006:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN SU-1 MAL TIEMPO | R21101300019 | New_Event | Bad Weather | Include | Include | Weather | 377 | 2021-10-13 | 11310 | keep | 0 | Oct | 2021 | 0.0077032 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-13 05:45 | 2021-10-13 09:30 | 50 | 003:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21101300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-10-13 | 11250 | keep | 0 | Oct | 2021 | 0.0076623 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-13 05:47 | 2021-10-13 10:05 | 45 | 004:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21101300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2021-10-13 | 11610 | keep | 0 | Oct | 2021 | 0.0079075 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-10-13 05:48 | 2021-10-13 18:06 | 60 | 012:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 738 | 2021-10-13 | 44280 | keep | 0 | Oct | 2021 | 0.030159 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-13 05:52 | 2021-10-13 12:50 | 20 | 006:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21101300013 | New_Event | Wire Down | Include | Include | Equipment | 418 | 2021-10-13 | 8360 | keep | 0 | Oct | 2021 | 0.005694 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-10-13 06:14 | 2021-10-13 12:33 | 60 | 006:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2021-10-13 | 22740 | keep | 0 | Oct | 2021 | 0.015488 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-10-13 06:15 | 2021-10-13 12:56 | 25 | 006:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | R21101300025 | New_Event |  |  | Include | Wildlife | 401 | 2021-10-13 | 10025 | keep | 0 | Oct | 2021 | 0.006828 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-13 06:16 | 2021-10-13 10:55 | 85 | 004:39 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R21101300026 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 279 | 2021-10-13 | 23715 | keep | 0 | Oct | 2021 | 0.016152 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
BARRANQUITAS | 2021-10-13 06:19 | 2021-10-13 06:20 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1834 | keep | 0 | Oct | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
CAGUAS | 2021-10-13 06:49 | 2021-10-13 16:52 | 1 | 010:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21101300015 | New_Event | Cutout Failure | Include | Include | Equipment | 603 | 2021-10-13 | 603 | keep | 0 | Oct | 2021 | 0.0004107 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
YAUCO | 2021-10-13 06:58 | 2021-10-13 14:35 | 44 | 007:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21101300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2021-10-13 | 20108 | keep | 0 | Oct | 2021 | 0.013695 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
BAYAMON | 2021-10-13 07:12 | 2021-10-13 13:03 | 50 | 005:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2021-10-13 | 17550 | keep | 0 | Oct | 2021 | 0.011953 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-13 07:12 | 2021-10-14 12:14 | 10 | 029:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA POR UNO DE IGUAL CAPACIDAD | B21101300011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1742 | 2021-10-13 | 17420 | keep | 0 | Oct | 2021 | 0.011865 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-13 07:14 | 2021-10-13 10:25 | 50 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-10-13 | 9550 | keep | 0 | Oct | 2021 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-13 07:29 | 2021-10-13 07:30 | 4702 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO Y SE CERRO POR SCADA | B21101300013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-13 | 4702 | keep | 0 | Oct | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BAYAMON | 2021-10-13 07:29 | 2021-10-13 18:24 | 50 | 010:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 655 | 2021-10-13 | 32750 | keep | 0 | Oct | 2021 | 0.022306 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-13 07:34 | 2021-10-14 19:33 | 15 | 035:59 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO | B21101300016 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2159 | 2021-10-13 | 32385 | keep | 0 | Oct | 2021 | 0.022057 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-13 07:41 | 2021-10-13 18:20 | 100 | 010:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | S21101300042 | New_Event | Wire Down | Include | Include | Equipment | 639 | 2021-10-13 | 63900 | keep | 0 | Oct | 2021 | 0.043522 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-13 08:07 | 2021-10-13 15:25 | 20 | 007:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300009 | New_Event | Bad Weather | Include | Include | Weather | 438 | 2021-10-13 | 8760 | keep | 0 | Oct | 2021 | 0.0059664 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-10-13 08:11 | 2021-10-13 10:04 | 52 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | P21101300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2021-10-13 | 5876 | keep | 0 | Oct | 2021 | 0.0040021 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
GUAYAMA | 2021-10-13 08:14 | 2021-10-13 13:15 | 148 | 005:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P21101300018 | New_Event | Bad Weather | Include | Include | Weather | 301 | 2021-10-13 | 44548 | keep | 0 | Oct | 2021 | 0.030341 | 0.0001008 | Sustained | FALSE | TRUE | Not_TMED_Event | 148
BAYAMON | 2021-10-13 08:15 | 2021-10-13 23:43 | 15 | 015:28 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO | B21101300021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 928 | 2021-10-13 | 13920 | keep | 0 | Oct | 2021 | 0.0094808 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-13 08:23 | 2021-10-13 14:58 | 60 | 006:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M21101300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2021-10-13 | 23700 | keep | 0 | Oct | 2021 | 0.016142 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-10-13 08:27 | 2021-10-13 11:53 | 1 | 003:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C21101300029 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2021-10-13 | 206 | keep | 0 | Oct | 2021 | 0.00014031 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-13 08:32 | 2021-10-13 15:17 | 20 | 006:45 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21101200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2021-10-13 | 8100 | keep | 0 | Oct | 2021 | 0.0055169 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
GUAYAMA | 2021-10-13 08:42 | 2021-10-13 08:43 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 4279 | keep | 0 | Oct | 2021 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
ARECIBO | 2021-10-13 08:46 | 2021-10-13 09:50 | 50 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21101300006 | New_Event | Wire Down | Include | Include | Equipment | 64 | 2021-10-13 | 3200 | keep | 0 | Oct | 2021 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-13 08:48 | 2021-10-13 13:46 | 15 | 004:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR Y SE RETIRO CULEBRA | S21101300062 | New_Event |  |  | Include | Wildlife | 298 | 2021-10-13 | 4470 | keep | 0 | Oct | 2021 | 0.0030445 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-13 08:56 | 2021-10-13 08:57 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1976 | keep | 0 | Oct | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-10-13 09:03 | 2021-10-13 20:07 | 30 | 011:04 | P | ESTRUCTURA AVERIADA | 3 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO EN EL FID:33776060 DE 45' MADERA | A21101300013 | New_Event | Defective Pole | Include | Include | Equipment | 664 | 2021-10-13 | 19920 | keep | 0 | Oct | 2021 | 0.013567 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-13 09:04 | 2021-10-13 18:04 | 10 | 009:00 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO | B21101300031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 540 | 2021-10-13 | 5400 | keep | 0 | Oct | 2021 | 0.0036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-13 09:14 | 2021-10-13 14:09 | 15 | 004:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101200085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2021-10-13 | 4425 | keep | 0 | Oct | 2021 | 0.0030138 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-13 09:23 | 2021-10-13 12:50 | 15 | 003:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | M21101300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-10-13 | 3105 | keep | 0 | Oct | 2021 | 0.0021148 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 09:45 | 2021-10-13 15:15 | 175 | 005:30 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21101300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-10-13 | 57750 | keep | 0 | Oct | 2021 | 0.039333 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
BAYAMON | 2021-10-13 09:46 | 2021-10-14 10:02 | 100 | 024:16 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21101300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1456 | 2021-10-13 | 145600 | keep | 0 | Oct | 2021 | 0.099167 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-13 09:50 | 2021-10-13 14:00 | 60 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU | S21101300075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2021-10-13 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-10-13 10:08 | 2021-10-13 12:35 | 1 | 002:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21101300028 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2021-10-13 | 147 | keep | 0 | Oct | 2021 | 0.00010012 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-13 10:09 | 2021-10-13 14:00 | 45 | 003:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | R21101300058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 231 | 2021-10-13 | 10395 | keep | 0 | Oct | 2021 | 0.00708 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-13 10:10 | 2021-10-13 12:15 | 14 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21101300008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-10-13 | 1750 | keep | 0 | Oct | 2021 | 0.0011919 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
CAGUAS | 2021-10-13 10:18 | 2021-10-13 14:30 | 225 | 004:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 100 EN CORTE DE LINEA CAMION IMPACTO POSTE DEL TELEFONO | C21101300050 | New_Event |  |  | Include | Wildlife | 252 | 2021-10-13 | 56700 | keep | 0 | Oct | 2021 | 0.038618 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
CAGUAS | 2021-10-13 10:18 | 2021-10-13 13:00 | 15 | 002:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ROTA | C21101300049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 162 | 2021-10-13 | 2430 | keep | 0 | Oct | 2021 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-10-13 10:18 | 2021-10-14 22:34 | 70 | 036:16 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN CORTE DE LINEA PARARRAYO AVERIADO | B21101300038 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2176 | 2021-10-13 | 152320 | keep | 0 | Oct | 2021 | 0.10374 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-10-13 10:19 | 2021-10-13 19:11 | 16 | 008:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PM PARA REEMPLAZO DE SECUNDARIA | R21101300061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 532 | 2021-10-13 | 8512 | keep | 0 | Oct | 2021 | 0.0057975 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2021-10-13 10:24 | 2021-10-14 14:23 | 20 | 027:59 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21101300034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1679 | 2021-10-13 | 33580 | keep | 0 | Oct | 2021 | 0.022871 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-10-13 10:30 | 2021-10-14 12:56 | 12 | 026:26 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | B21101300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1586 | 2021-10-13 | 19032 | keep | 0 | Oct | 2021 | 0.012963 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-10-13 10:33 | 2021-10-14 18:07 | 5 | 031:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR SUMERGIBLE DE 100 KVA AVERIADO | C21101300055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1894 | 2021-10-13 | 9470 | keep | 0 | Oct | 2021 | 0.00645 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-13 10:42 | 2021-10-13 20:26 | 150 | 009:44 | P | DESGANCHE | SE REALIZO DESGANCHE | B21101300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 584 | 2021-10-13 | 87600 | keep | 0 | Oct | 2021 | 0.059664 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-10-13 10:45 | 2021-10-13 13:31 | 1 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2021-10-13 | 166 | keep | 0 | Oct | 2021 | 0.00011306 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-13 10:48 | 2021-10-13 10:49 | 2524 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR CRUCE POR AVE CERRADO POR CONTROL | R21101300063 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-13 | 2524 | keep | 0 | Oct | 2021 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2021-10-13 10:49 | 2021-10-13 14:09 | 30 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21101300064 | 1st_after_momentary |  |  | Include | Wildlife | 200 | 2021-10-13 | 6000 | keep | 0 | Oct | 2021 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-10-13 10:50 | 2021-10-13 16:52 | 3 | 006:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR | P21101300033 | New_Event | Cutout Failure | Include | Include | Equipment | 362 | 2021-10-13 | 1086 | keep | 0 | Oct | 2021 | 0.00073967 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-13 10:56 | 2021-10-13 10:57 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21101300043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
VEGA BAJA | 2021-10-13 10:59 | 2021-10-13 22:36 | 30 | 011:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21101300044 | New_Event | Cutout Failure | Include | Include | Equipment | 697 | 2021-10-13 | 20910 | keep | 0 | Oct | 2021 | 0.014242 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-13 11:05 | 2021-10-13 12:00 | 4 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21101100044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-10-13 | 220 | keep | 0 | Oct | 2021 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-10-13 11:09 | 2021-10-13 16:09 | 2 | 005:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300090 | New_Event | Bad Weather | Include | Include | Weather | 300 | 2021-10-13 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-10-13 11:15 | 2021-10-13 14:44 | 225 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R21101300068 | New_Event | Bad Weather | Include | Include | Weather | 209 | 2021-10-13 | 47025 | keep | 0 | Oct | 2021 | 0.032029 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
ARECIBO | 2021-10-13 11:20 | 2021-10-13 12:07 | 30 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101300027 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2021-10-13 | 1410 | keep | 0 | Oct | 2021 | 0.00096034 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-13 11:24 | 2021-10-13 19:46 | 50 | 008:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2021-10-13 | 25100 | keep | 0 | Oct | 2021 | 0.017095 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-13 11:25 | 2021-10-13 16:02 | 15 | 004:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA DEL TRANSFORMADOR | R21101300069 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2021-10-13 | 4155 | keep | 0 | Oct | 2021 | 0.00283 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 11:34 | 2021-10-13 11:37 | 3 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 9 | keep | 0 | Oct | 2021 | 6.1299e-06 | 2.0433e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-10-13 11:34 | 2021-10-13 11:37 | 3957 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 11871 | keep | 0 | Oct | 2021 | 0.0080853 | 0.0026951 | Momentary | FALSE | TRUE | Not_TMED_Event | 3957
BAYAMON | 2021-10-13 11:34 | 2021-10-13 11:37 | 58 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 174 | keep | 0 | Oct | 2021 | 0.00011851 | 3.9504e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 58
SAN JUAN | 2021-10-13 11:34 | 2021-10-13 11:37 | 386 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 1158 | keep | 0 | Oct | 2021 | 0.00078871 | 0.0002629 | Momentary | FALSE | TRUE | Not_TMED_Event | 386
AGUADILLA | 2021-10-13 11:44 | 2021-10-13 12:45 | 20 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO VARIAS TOMAS Y CONEXION EN TRANSFORMADOR | M21101300077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-10-13 | 1220 | keep | 0 | Oct | 2021 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-13 11:52 | 2021-10-13 15:49 | 10 | 003:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-10-13 | 2370 | keep | 0 | Oct | 2021 | 0.0016142 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-13 11:54 | 2021-10-14 14:52 | 1 | 026:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101300059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1618 | 2021-10-13 | 1618 | keep | 0 | Oct | 2021 | 0.001102 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-13 11:56 | 2021-10-13 20:38 | 72 | 008:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER HACIA SU-1 MAL TIEMPO | R21101300074 | New_Event | Bad Weather | Include | Include | Weather | 522 | 2021-10-13 | 37584 | keep | 0 | Oct | 2021 | 0.025598 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
CANOVANAS | 2021-10-13 11:59 | 2021-10-13 17:45 | 11 | 005:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMDOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R21101300075 | New_Event | Cutout Failure | Include | Include | Equipment | 346 | 2021-10-13 | 3806 | keep | 0 | Oct | 2021 | 0.0025922 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2021-10-13 12:16 | 2021-10-13 21:35 | 12 | 009:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300030 | New_Event | Bad Weather | Include | Include | Weather | 559 | 2021-10-13 | 6708 | keep | 0 | Oct | 2021 | 0.0045688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-10-13 12:17 | 2021-10-13 18:50 | 1 | 006:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101300077 | New_Event | Bad Weather | Include | Include | Weather | 393 | 2021-10-13 | 393 | keep | 0 | Oct | 2021 | 0.00026767 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-10-13 12:23 | 2021-10-13 14:08 | 80 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101300092 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2021-10-13 | 8400 | keep | 0 | Oct | 2021 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-13 12:34 | 2021-10-13 13:43 | 188 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR PUENTE ABIERTO DEL 3005-01 Y PODER NORMALIZAR SU CARGA TRANSFERIDA AL 3007-04 | C21101300006 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2021-10-13 | 12972 | keep | 0 | Oct | 2021 | 0.0088352 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
VEGA BAJA | 2021-10-13 12:40 | 2021-10-14 20:54 | 20 | 032:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101300065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1934 | 2021-10-13 | 38680 | keep | 0 | Oct | 2021 | 0.026345 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-10-13 12:40 | 2021-10-14 00:29 | 1859 | 011:49 | T | DESGANCHE | DISPARO DE INTERRUPTOR | B21101300065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 709 | 2021-10-13 | 1318031 | keep | 0 | Oct | 2021 | 0.8977 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
SAN JUAN | 2021-10-13 12:49 | 2021-10-13 14:00 | 5 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21101300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2021-10-13 | 355 | keep | 0 | Oct | 2021 | 0.00024179 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-13 12:49 | 2021-10-15 10:32 | 30 | 045:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA RAYOS | S21101300109 | New_Event | Bad Weather | Include | Include | Weather | 2743 | 2021-10-13 | 82290 | keep | 0 | Oct | 2021 | 0.056047 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-10-13 13:00 | 2021-10-13 14:24 | 6 | 001:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | R21101300083 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2021-10-13 | 504 | keep | 0 | Oct | 2021 | 0.00034327 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
GUAYAMA | 2021-10-13 13:00 | 2021-10-13 16:25 | 12 | 003:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA A 4.16KV | P21101300062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 205 | 2021-10-13 | 2460 | keep | 0 | Oct | 2021 | 0.0016755 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-13 13:11 | 2021-10-13 13:12 | 1225 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1225 | keep | 0 | Oct | 2021 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
MAYAGÃœEZ | 2021-10-13 13:12 | 2021-10-13 17:50 | 30 | 004:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21101300099 | New_Event | Bad Weather | Include | Include | Weather | 278 | 2021-10-13 | 8340 | keep | 0 | Oct | 2021 | 0.0056803 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-13 13:21 | 2021-10-13 21:37 | 300 | 008:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTES LLUVIAS Y RAYOS | S21101300118 | New_Event | Bad Weather | Include | Include | Weather | 496 | 2021-10-13 | 148800 | keep | 0 | Oct | 2021 | 0.10135 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-10-13 13:41 | 2021-10-14 10:17 | 1 | 020:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21101300089 | New_Event | Bad Weather | Include | Include | Weather | 1236 | 2021-10-13 | 1236 | keep | 0 | Oct | 2021 | 0.00084183 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-13 13:42 | 2021-10-13 15:20 | 30 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A21101300037 | New_Event |  |  | Include | Wildlife | 98 | 2021-10-13 | 2940 | keep | 0 | Oct | 2021 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-13 13:43 | 2021-10-13 15:09 | 188 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE CERRO PUENTES Y NORMALIZO LAS CARGAS DEL 3005-01 Y 3007-04 | C21101300006 | Partial_restoration | Wire Down | Include | Include | Equipment | 86 | 2021-10-13 | 16168 | keep | 0 | Oct | 2021 | 0.011012 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-10-13 13:48 | 2021-10-13 13:52 | 934 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 3736 | keep | 0 | Oct | 2021 | 0.0025446 | 0.00063614 | Momentary | FALSE | TRUE | Not_TMED_Event | 934
UTUADO | 2021-10-13 13:48 | 2021-10-13 13:52 | 4 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 16 | keep | 0 | Oct | 2021 | 1.0898e-05 | 2.7244e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-10-13 13:48 | 2021-10-13 13:52 | 1479 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 5916 | keep | 0 | Oct | 2021 | 0.0040294 | 0.0010073 | Momentary | FALSE | TRUE | Not_TMED_Event | 1479
UTUADO | 2021-10-13 13:48 | 2021-10-13 13:52 | 1841 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 7364 | keep | 0 | Oct | 2021 | 0.0050156 | 0.0012539 | Momentary | FALSE | TRUE | Not_TMED_Event | 1841
UTUADO | 2021-10-13 13:48 | 2021-10-13 13:52 | 1950 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 7800 | keep | 0 | Oct | 2021 | 0.0053125 | 0.0013281 | Momentary | FALSE | TRUE | Not_TMED_Event | 1950
BAYAMON | 2021-10-13 13:49 | 2021-10-13 13:50 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1002-01 LLEVANDO 1001-01, 1001-02 Y 1001-03 | S21101300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1 | keep | 0 | Oct | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-13 13:49 | 2021-10-13 13:50 | 47 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1002-01 LLEVANDO 1001-01, 1001-02 Y 1001-03 | S21101300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 47 | keep | 0 | Oct | 2021 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2021-10-13 13:49 | 2021-10-13 13:50 | 245 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1002-01 LLEVANDO 1001-01, 1001-02 Y 1001-03 | S21101300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 245 | keep | 0 | Oct | 2021 | 0.00016687 | 0.00016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 245
BAYAMON | 2021-10-13 13:49 | 2021-10-13 13:50 | 35 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVANDO 1001-01, 1001-02 Y 1001-03 | S21101300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 35 | keep | 0 | Oct | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-10-13 13:49 | 2021-10-13 13:50 | 948 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21101300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 948 | keep | 0 | Oct | 2021 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
SAN JUAN | 2021-10-13 13:50 | 2021-10-13 15:09 | 3046 | 001:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR 3 VECES QUEDO FUERA SE SECCIONALIZO NEUTRAL PRIMARIO Y TENSOR CRUZADO CON LA LINEA | R21101300090 | New_Event | Wire Down | Include | Include | Equipment | 79 | 2021-10-13 | 240634 | keep | 0 | Oct | 2021 | 0.16389 | 0.0020746 | Sustained | FALSE | TRUE | Not_TMED_Event | 3046
HUMACAO | 2021-10-13 13:50 | 2021-10-13 13:51 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2021-10-13 13:51 | 2021-10-13 13:52 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 726 | keep | 0 | Oct | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-10-13 13:51 | 2021-10-13 13:52 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3932 | keep | 0 | Oct | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
MAYAGÃœEZ | 2021-10-13 13:55 | 2021-10-13 18:43 | 7 | 004:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES | M21101300107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 288 | 2021-10-13 | 2016 | keep | 0 | Oct | 2021 | 0.0013731 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-13 14:04 | 2021-10-14 11:31 | 5 | 021:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21101300110 | New_Event | Bad Weather | Include | Include | Weather | 1287 | 2021-10-13 | 6435 | keep | 0 | Oct | 2021 | 0.0043828 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-13 14:07 | 2021-10-13 14:13 | 3718 | 000:06 | T | DESGANCHE | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S21101300145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2021-10-13 | 22308 | keep | 0 | Oct | 2021 | 0.015194 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-10-13 14:15 | 2021-10-13 14:18 | 225 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS CARGA POR EL 1304-05 Y LLEVA 1303-01 Y 1346-06 | S21101300000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2021-10-13 | 675 | keep | 0 | Oct | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-13 14:15 | 2021-10-13 14:18 | 870 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS LLEVA EL 1303-04 | S21101300000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2021-10-13 | 2610 | keep | 0 | Oct | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2021-10-13 14:18 | 2021-10-14 17:15 | 40 | 026:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE CAMBIARON 2 CAJAS PRIMARIAS QUEMADAS DE 200 AMPERES | P21101300053 | New_Event | Cutout Failure | Include | Include | Equipment | 1617 | 2021-10-13 | 64680 | keep | 0 | Oct | 2021 | 0.044053 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-13 14:20 | 2021-10-13 15:17 | 2435 | 000:57 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS | S21101300161 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-10-13 | 138795 | keep | 0 | Oct | 2021 | 0.094533 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-13 14:20 | 2021-10-13 15:15 | 870 | 000:55 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS LLEVA EL 1303-04 | S21101300161 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 55 | 2021-10-13 | 47850 | keep | 0 | Oct | 2021 | 0.03259 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-10-13 14:22 | 2021-10-13 20:47 | 60 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 Y 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101300118 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2021-10-13 | 23100 | keep | 0 | Oct | 2021 | 0.015733 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-13 14:24 | 2021-10-13 14:49 | 4133 | 000:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2021-10-13 | 103325 | keep | 0 | Oct | 2021 | 0.070374 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 14:30 | 137 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 548 | keep | 0 | Oct | 2021 | 0.00037324 | 9.331e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 14:30 | 457 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 1828 | keep | 0 | Oct | 2021 | 0.001245 | 0.00031126 | Momentary | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 14:30 | 1225 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 0.00083434 | Momentary | FALSE | TRUE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 14:30 | 1452 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 5808 | keep | 0 | Oct | 2021 | 0.0039558 | 0.00098895 | Momentary | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 14:30 | 616 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 2464 | keep | 0 | Oct | 2021 | 0.0016782 | 0.00041955 | Momentary | FALSE | TRUE | Not_TMED_Event | 616
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 15:52 | 858 | 001:26 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 20% DE LA CARGA POR EL 1303-02 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 86 | 2021-10-13 | 73788 | keep | 0 | Oct | 2021 | 0.050257 | 0.00058438 | Sustained | FALSE | TRUE | Not_TMED_Event | 858
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 15:52 | 552 | 001:26 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 86 | 2021-10-13 | 47472 | keep | 0 | Oct | 2021 | 0.032333 | 0.00037596 | Sustained | FALSE | TRUE | Not_TMED_Event | 552
SAN JUAN | 2021-10-13 14:26 | 2021-10-13 15:16 | 225 | 000:50 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR SCADA RAYOS CARGA POR EL 1304-05 Y LLEVA 1303-01 Y 1346-06 | S21101300161 | New_Event | Cutout Failure | Include | Include | Equipment | 50 | 2021-10-13 | 11250 | keep | 0 | Oct | 2021 | 0.0076623 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
AGUADILLA | 2021-10-13 14:29 | 2021-10-14 15:03 | 200 | 024:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21101300120 | New_Event | Wire Down | Include | Include | Equipment | 1474 | 2021-10-13 | 294800 | keep | 0 | Oct | 2021 | 0.20079 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-13 14:30 | 2021-10-13 14:40 | 172 | 000:10 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS | S21101300192 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-10-13 | 1720 | keep | 0 | Oct | 2021 | 0.0011715 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-10-13 14:30 | 2021-10-13 18:45 | 15 | 004:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA INSTALO POSTE | C21101300050 | Partial_restoration |  |  | Include | Wildlife | 255 | 2021-10-13 | 3825 | keep | 0 | Oct | 2021 | 0.0026052 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-13 14:30 | 2021-10-13 18:35 | 30 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M21101300121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2021-10-13 | 7350 | keep | 0 | Oct | 2021 | 0.0050061 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-10-13 14:30 | 2021-10-13 18:16 | 80 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA FID:33828106 MARCA:CHINT 100AMP | A21101300042 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2021-10-13 | 18080 | keep | 0 | Oct | 2021 | 0.012314 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-13 14:31 | 2021-10-13 17:35 | 76 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA. SE CAMBIO PORTA FUSIBLE QUEMADO | P21101300054 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2021-10-13 | 13984 | keep | 0 | Oct | 2021 | 0.0095244 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
SAN JUAN | 2021-10-13 14:33 | 2021-10-13 15:29 | 3718 | 000:56 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | S21101300192 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-10-13 | 208208 | keep | 0 | Oct | 2021 | 0.14181 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-13 14:35 | 2021-10-13 14:36 | 1132 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21101300103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1132 | keep | 0 | Oct | 2021 | 0.000771 | 0.000771 | Momentary | FALSE | FALSE | Not_TMED_Event | 1132
SAN JUAN | 2021-10-13 14:38 | 2021-10-13 17:43 | 1132 | 003:05 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 3 VECES QUEDO FUERA NO SE ENCONTRO NADA CERRADO POR CONTROL | R21101300104 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 185 | 2021-10-13 | 209420 | keep | 0 | Oct | 2021 | 0.14264 | 0.000771 | Sustained | FALSE | FALSE | Not_TMED_Event | 1132
VEGA BAJA | 2021-10-13 14:38 | 2021-10-14 17:42 | 15 | 027:04 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B21101300080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1624 | 2021-10-13 | 24360 | keep | 0 | Oct | 2021 | 0.016591 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 14:40 | 2021-10-13 14:41 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-13 14:42 | 2021-10-13 14:43 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 1384 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 13840 | keep | 0 | Oct | 2021 | 0.0094264 | 0.00094264 | Sustained | FALSE | TRUE | Not_TMED_Event | 1384
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 869 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 8690 | keep | 0 | Oct | 2021 | 0.0059187 | 0.00059187 | Sustained | FALSE | TRUE | Not_TMED_Event | 869
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 15:20 | 6481 | 000:36 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS | S21101300000 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2021-10-13 | 233316 | keep | 0 | Oct | 2021 | 0.15891 | 0.0044142 | Sustained | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 601 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 6010 | keep | 0 | Oct | 2021 | 0.0040934 | 0.00040934 | Sustained | FALSE | TRUE | Not_TMED_Event | 601
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 640 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 6400 | keep | 0 | Oct | 2021 | 0.004359 | 0.0004359 | Sustained | FALSE | TRUE | Not_TMED_Event | 640
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 1699 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 16990 | keep | 0 | Oct | 2021 | 0.011572 | 0.0011572 | Sustained | FALSE | TRUE | Not_TMED_Event | 1699
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 892 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 8920 | keep | 0 | Oct | 2021 | 0.0060754 | 0.00060754 | Sustained | FALSE | TRUE | Not_TMED_Event | 892
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:54 | 1066 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-13 | 10660 | keep | 0 | Oct | 2021 | 0.0072605 | 0.00072605 | Sustained | FALSE | TRUE | Not_TMED_Event | 1066
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:45 | 331 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3600 DE SABANA LLANA A LOS ANGELES | R21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 331 | keep | 0 | Oct | 2021 | 0.00022544 | 0.00022544 | Momentary | FALSE | TRUE | Not_TMED_Event | 331
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:45 | 234 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3600 DE SABANA LLANA A LOS ANGELES | R21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 234 | keep | 0 | Oct | 2021 | 0.00015938 | 0.00015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 234
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:45 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3600 DE SABANA LLANA A LOS ANGELES | R21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 2179 | keep | 0 | Oct | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
SAN JUAN | 2021-10-13 14:44 | 2021-10-13 14:45 | 5062 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 3600 DE SABANA LLANA A LOS ANGELES | R21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 5062 | keep | 0 | Oct | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | TRUE | Not_TMED_Event | 5062
SAN JUAN | 2021-10-13 14:45 | 2021-10-13 18:05 | 225 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R21101300068 | Partial_restoration | Bad Weather | Include | Include | Weather | 200 | 2021-10-13 | 45000 | keep | 0 | Oct | 2021 | 0.030649 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-10-13 14:51 | 2021-10-13 20:28 | 25 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21101300087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2021-10-13 | 8425 | keep | 0 | Oct | 2021 | 0.0057382 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-13 14:52 | 2021-10-13 14:55 | 100 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-13 14:52 | 2021-10-13 14:55 | 644 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 1932 | keep | 0 | Oct | 2021 | 0.0013159 | 0.00043863 | Momentary | FALSE | TRUE | Not_TMED_Event | 644
SAN JUAN | 2021-10-13 14:52 | 2021-10-13 14:55 | 525 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 1575 | keep | 0 | Oct | 2021 | 0.0010727 | 0.00035758 | Momentary | FALSE | TRUE | Not_TMED_Event | 525
SAN JUAN | 2021-10-13 14:52 | 2021-10-13 14:55 | 45 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 3.0649e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-10-13 14:52 | 2021-10-13 14:55 | 418 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-13 | 1254 | keep | 0 | Oct | 2021 | 0.00085409 | 0.0002847 | Momentary | FALSE | TRUE | Not_TMED_Event | 418
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 137 | 000:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 8083 | keep | 0 | Oct | 2021 | 0.0055053 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 457 | 000:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 26963 | keep | 0 | Oct | 2021 | 0.018364 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 1225 | 000:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 72275 | keep | 0 | Oct | 2021 | 0.049226 | 0.00083434 | Sustained | FALSE | TRUE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 1452 | 000:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 85668 | keep | 0 | Oct | 2021 | 0.058348 | 0.00098895 | Sustained | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 616 | 000:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 36344 | keep | 0 | Oct | 2021 | 0.024754 | 0.00041955 | Sustained | FALSE | TRUE | Not_TMED_Event | 616
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 3432 | 000:59 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 202488 | keep | 0 | Oct | 2021 | 0.13791 | 0.0023375 | Sustained | FALSE | TRUE | Not_TMED_Event | 3432
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 552 | 000:59 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 32568 | keep | 0 | Oct | 2021 | 0.022182 | 0.00037596 | Sustained | FALSE | TRUE | Not_TMED_Event | 552
SAN JUAN | 2021-10-13 14:53 | 2021-10-13 15:52 | 4944 | 000:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 59 | 2021-10-13 | 291696 | keep | 0 | Oct | 2021 | 0.19867 | 0.0033673 | Sustained | FALSE | TRUE | Not_TMED_Event | 4944
SAN JUAN | 2021-10-13 14:55 | 2021-10-13 15:15 | 1290 | 000:20 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS CARGA POR EL 1401-08 | S21101300000 | New_Event | Bad Weather | Include | Include | Weather | 20 | 2021-10-13 | 25800 | keep | 0 | Oct | 2021 | 0.017572 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2021-10-13 14:55 | 2021-10-13 15:15 | 135 | 000:20 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS LLEVA 1346-05 Y PARTE 1348-08 | S21101300000 | New_Event | Bad Weather | Include | Include | Weather | 20 | 2021-10-13 | 2700 | keep | 0 | Oct | 2021 | 0.001839 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2021-10-13 14:58 | 2021-10-13 17:31 | 1 | 002:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-10-13 | 153 | keep | 0 | Oct | 2021 | 0.00010421 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-13 14:59 | 2021-10-13 15:00 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21101300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
PONCE | 2021-10-13 14:59 | 2021-10-13 15:00 | 65 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU | P21101300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 65 | keep | 0 | Oct | 2021 | 4.4271e-05 | 4.4271e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-10-13 15:00 | 2021-10-13 15:27 | 4133 | 000:27 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA RAYOS | S21101300000 | New_Event | Bad Weather | Include | Include | Weather | 27 | 2021-10-13 | 111591 | keep | 0 | Oct | 2021 | 0.076004 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-13 15:02 | 2021-10-13 15:03 | 844 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 844 | keep | 0 | Oct | 2021 | 0.00057484 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2021-10-13 15:03 | 2021-10-13 19:09 | 10 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21101300509 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-10-13 | 2460 | keep | 0 | Oct | 2021 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-13 15:05 | 2021-10-13 20:18 | 600 | 005:13 | P | PARARRAYOS DEFECTUOSO | SE CERRO MACHETES DEL 1404-07 QUE ESTA POR EL 1404-06 Y SE TRANSFIRIERON AL 1111-02 | S21101300011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 313 | 2021-10-13 | 187800 | keep | 0 | Oct | 2021 | 0.12791 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CANOVANAS | 2021-10-13 15:05 | 2021-10-13 15:50 | 2580 | 000:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 DE CANOVANAS TC A LAS MERCEDES | R21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2021-10-13 | 116100 | keep | 0 | Oct | 2021 | 0.079075 | 0.0017572 | Sustained | FALSE | TRUE | Not_TMED_Event | 2580
CANOVANAS | 2021-10-13 15:05 | 2021-10-13 15:50 | 500 | 000:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 DE CANOVANAS TC A LAS MERCEDES | R21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2021-10-13 | 22500 | keep | 0 | Oct | 2021 | 0.015325 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-10-13 15:05 | 2021-10-13 15:40 | 4 | 000:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A21101300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2021-10-13 | 140 | keep | 0 | Oct | 2021 | 9.5353e-05 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-10-13 15:06 | 2021-10-13 16:35 | 10 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21101300050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2021-10-13 | 890 | keep | 0 | Oct | 2021 | 0.00060617 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-10-13 15:07 | 2021-10-14 11:31 | 200 | 020:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | A21101300052 | New_Event | Cutout Failure | Include | Include | Equipment | 1224 | 2021-10-13 | 244800 | keep | 0 | Oct | 2021 | 0.16673 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
GUAYAMA | 2021-10-13 15:10 | 2021-10-13 15:11 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211013000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 464 | keep | 0 | Oct | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
SAN JUAN | 2021-10-13 15:12 | 2021-10-13 15:13 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1799 | keep | 0 | Oct | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-10-13 15:13 | 2021-10-14 14:16 | 25 | 023:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21101300607 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1383 | 2021-10-13 | 34575 | keep | 0 | Oct | 2021 | 0.023549 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-13 15:13 | 2021-10-14 20:07 | 36 | 028:54 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 30 EN CORTE DE LINEA | B21101300090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1734 | 2021-10-13 | 62424 | keep | 0 | Oct | 2021 | 0.042517 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
SAN JUAN | 2021-10-13 15:15 | 2021-10-13 16:30 | 30 | 001:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA AVERIADA (NO FUNDIO FUSIBLE) LLEVA LA CARGA DEL 1303-04 | S21101300044 | New_Event | Cutout Failure | Include | Include | Equipment | 75 | 2021-10-13 | 2250 | keep | 0 | Oct | 2021 | 0.0015325 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-13 15:15 | 2021-10-13 18:59 | 50 | 003:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO AISLADORES | S21101300312 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 224 | 2021-10-13 | 11200 | keep | 0 | Oct | 2021 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-13 15:18 | 2021-10-13 16:28 | 40 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | R21101300151 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-10-13 | 2800 | keep | 0 | Oct | 2021 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-10-13 15:21 | 2021-10-14 12:05 | 12 | 020:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21101300100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1244 | 2021-10-13 | 14928 | keep | 0 | Oct | 2021 | 0.010167 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-13 15:22 | 2021-10-14 13:07 | 1 | 021:45 | P | DESGANCHE | 2 X 15 EN BANCO DE TRANSFORMADOR | R21101300159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1305 | 2021-10-13 | 1305 | keep | 0 | Oct | 2021 | 0.00088883 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-13 15:23 | 2021-10-13 15:24 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21101300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1827 | keep | 0 | Oct | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2021-10-13 15:27 | 2021-10-13 19:37 | 100 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA RAYOS | S21101300492 | Partial_restoration | Bad Weather | Include | Include | Weather | 250 | 2021-10-13 | 25000 | keep | 0 | Oct | 2021 | 0.017027 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-13 15:27 | 2021-10-14 09:33 | 200 | 018:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 200 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | M21101300160 | New_Event | Bad Weather | Include | Include | Weather | 1086 | 2021-10-13 | 217200 | keep | 0 | Oct | 2021 | 0.14793 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-10-13 15:29 | 2021-10-13 18:30 | 250 | 003:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | S21101300396 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-10-13 | 45250 | keep | 0 | Oct | 2021 | 0.03082 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-13 15:29 | 2021-10-13 19:04 | 50 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR RAYOS | M21101300129 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-10-13 | 10750 | keep | 0 | Oct | 2021 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-13 15:29 | 2021-10-14 19:57 | 3 | 028:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21101300060 | New_Event | Bad Weather | Include | Include | Weather | 1708 | 2021-10-13 | 5124 | keep | 0 | Oct | 2021 | 0.0034899 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-10-13 15:32 | 2021-10-13 18:49 | 30 | 003:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21101300103 | New_Event |  |  | Include | Wildlife | 197 | 2021-10-13 | 5910 | keep | 0 | Oct | 2021 | 0.0040253 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-13 15:36 | 2021-10-13 19:42 | 100 | 004:06 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | M21101300133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-10-13 | 24600 | keep | 0 | Oct | 2021 | 0.016755 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-13 15:36 | 2021-10-13 21:27 | 50 | 005:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21101300134 | New_Event | Bad Weather | Include | Include | Weather | 351 | 2021-10-13 | 17550 | keep | 0 | Oct | 2021 | 0.011953 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-13 15:37 | 2021-10-13 17:55 | 60 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21101300098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-10-13 | 8280 | keep | 0 | Oct | 2021 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-13 15:37 | 2021-10-15 10:10 | 4 | 042:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21101300136 | New_Event | Bad Weather | Include | Include | Weather | 2553 | 2021-10-13 | 10212 | keep | 0 | Oct | 2021 | 0.0069553 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-10-13 15:45 | 2021-10-13 17:21 | 75 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR CONTACTO DE AVE | P21101300050 | New_Event |  |  | Include | Wildlife | 96 | 2021-10-13 | 7200 | keep | 0 | Oct | 2021 | 0.0049039 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-10-13 15:46 | 2021-10-13 15:47 | 3654 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE PROBO Y QUEDO EN SERVICIO SE VERIFICO NO PERSONAL EN LAS LINEAS | A21101300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3654 | keep | 0 | Oct | 2021 | 0.0024887 | 0.0024887 | Momentary | FALSE | TRUE | Not_TMED_Event | 3654
BAYAMON | 2021-10-13 15:46 | 2021-10-13 19:41 | 2678 | 003:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | B21101300102 | New_Event | Wire Down | Include | Include | Equipment | 235 | 2021-10-13 | 629330 | keep | 0 | Oct | 2021 | 0.42863 | 0.001824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2678
FAJARDO | 2021-10-13 15:47 | 2021-10-13 17:04 | 25 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21101300166 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-10-13 | 1925 | keep | 0 | Oct | 2021 | 0.0013111 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-13 15:47 | 2021-10-13 22:12 | 15 | 006:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21101300069 | New_Event | Cutout Failure | Include | Include | Equipment | 385 | 2021-10-13 | 5775 | keep | 0 | Oct | 2021 | 0.0039333 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-13 15:49 | 2021-10-14 20:07 | 15 | 028:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | B21101300103 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1698 | 2021-10-13 | 25470 | keep | 0 | Oct | 2021 | 0.017348 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-13 15:49 | 2021-10-14 15:47 | 60 | 023:58 | P | TRANSFORMADOR AVERIADO | 1 X 65 Y 1 X 40 EN CORTE DE LINEA | B21101300103 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1438 | 2021-10-13 | 86280 | keep | 0 | Oct | 2021 | 0.058765 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-13 15:52 | 2021-10-14 11:00 | 80 | 019:08 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101300209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1148 | 2021-10-13 | 91840 | keep | 0 | Oct | 2021 | 0.062552 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-13 15:52 | 2021-10-13 23:34 | 200 | 007:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A21101300068 | New_Event | Wire Down | Include | Include | Equipment | 462 | 2021-10-13 | 92400 | keep | 0 | Oct | 2021 | 0.062933 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-10-13 15:52 | 2021-10-13 16:09 | 150 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR Y 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300070 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2021-10-13 | 2550 | keep | 0 | Oct | 2021 | 0.0017368 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-13 15:54 | 2021-10-13 20:42 | 922 | 004:48 | T | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO INTERRUPTOR 1401-08. LLEVANDO LA CARGA DEL 1346-05 Y PARTE DEL 1348-08 | S21101300433 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-10-13 | 265536 | keep | 0 | Oct | 2021 | 0.18086 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-10-13 15:54 | 2021-10-13 20:42 | 645 | 004:48 | P | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO INTERRUPTOR. LLEVANDO LA CARGA DEL 1346-05 Y PARTE DEL 1348-08 | S21101300433 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-10-13 | 185760 | keep | 0 | Oct | 2021 | 0.12652 | 0.00043931 | Sustained | FALSE | FALSE | Not_TMED_Event | 645
SAN JUAN | 2021-10-13 15:54 | 2021-10-13 20:42 | 135 | 004:48 | T | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO INTERRUPTOR. LLEVANDO LA CARGA DEL 1346-05 Y PARTE DEL 1348-08 | S21101300433 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-10-13 | 38880 | keep | 0 | Oct | 2021 | 0.026481 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2021-10-13 16:00 | 2021-10-13 18:50 | 45 | 002:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M21101300144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-10-13 | 7650 | keep | 0 | Oct | 2021 | 0.0052104 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-10-13 16:01 | 2021-10-13 16:04 | 4702 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO Y SE CERRO POR CONTROL | B21101300108 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-10-13 | 14106 | keep | 0 | Oct | 2021 | 0.0096075 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-10-13 16:04 | 2021-10-13 16:32 | 4702 | 000:28 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR | B21101300102 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2021-10-13 | 131656 | keep | 0 | Oct | 2021 | 0.08967 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
SAN JUAN | 2021-10-13 16:09 | 2021-10-13 16:31 | 80 | 000:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS Y RAYOS | S21101300467 | New_Event | Bad Weather | Include | Include | Weather | 22 | 2021-10-13 | 1760 | keep | 0 | Oct | 2021 | 0.0011987 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 1405 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 1405 | keep | 0 | Oct | 2021 | 0.00095694 | 0.00095694 | Momentary | FALSE | TRUE | Not_TMED_Event | 1405
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 669 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 669 | keep | 0 | Oct | 2021 | 0.00045565 | 0.00045565 | Momentary | FALSE | TRUE | Not_TMED_Event | 669
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 1527 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 1527 | keep | 0 | Oct | 2021 | 0.00104 | 0.00104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1527
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 1054 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 1054 | keep | 0 | Oct | 2021 | 0.00071787 | 0.00071787 | Momentary | FALSE | TRUE | Not_TMED_Event | 1054
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 932 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 932 | keep | 0 | Oct | 2021 | 0.00063478 | 0.00063478 | Momentary | FALSE | TRUE | Not_TMED_Event | 932
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:13 | 1633 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 6532 | keep | 0 | Oct | 2021 | 0.0044489 | 0.0011122 | Momentary | FALSE | TRUE | Not_TMED_Event | 1633
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:13 | 1624 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-13 | 6496 | keep | 0 | Oct | 2021 | 0.0044244 | 0.0011061 | Momentary | FALSE | TRUE | Not_TMED_Event | 1624
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 705 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 705 | keep | 0 | Oct | 2021 | 0.00048017 | 0.00048017 | Momentary | FALSE | TRUE | Not_TMED_Event | 705
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 1521 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 1521 | keep | 0 | Oct | 2021 | 0.0010359 | 0.0010359 | Momentary | FALSE | TRUE | Not_TMED_Event | 1521
UTUADO | 2021-10-13 16:09 | 2021-10-13 16:10 | 882 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2400 | A21101300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-13 | 882 | keep | 0 | Oct | 2021 | 0.00060073 | 0.00060073 | Momentary | FALSE | TRUE | Not_TMED_Event | 882
HUMACAO | 2021-10-13 16:10 | 2021-10-13 19:42 | 6 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21101300109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2021-10-13 | 1272 | keep | 0 | Oct | 2021 | 0.00086635 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-10-13 16:13 | 2021-10-13 19:00 | 150 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR Y 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300070 | Partial_restoration | Bad Weather | Include | Include | Weather | 167 | 2021-10-13 | 25050 | keep | 0 | Oct | 2021 | 0.017061 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-10-13 16:13 | 2021-10-13 16:58 | 2 | 000:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300090 | Partial_restoration | Bad Weather | Include | Include | Weather | 45 | 2021-10-13 | 90 | keep | 0 | Oct | 2021 | 6.1299e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-10-13 16:19 | 2021-10-14 09:50 | 85 | 017:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21101300170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1051 | 2021-10-13 | 89335 | keep | 0 | Oct | 2021 | 0.060846 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
ARECIBO | 2021-10-13 16:19 | 2021-10-14 10:29 | 8 | 018:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101300076 | New_Event | Bad Weather | Include | Include | Weather | 1090 | 2021-10-13 | 8720 | keep | 0 | Oct | 2021 | 0.0059392 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
ARECIBO | 2021-10-13 16:20 | 2021-10-13 20:29 | 1 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300077 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-10-13 | 249 | keep | 0 | Oct | 2021 | 0.00016959 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-13 16:22 | 2021-10-14 08:41 | 1 | 016:19 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101300149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 979 | 2021-10-13 | 979 | keep | 0 | Oct | 2021 | 0.00066679 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
YAUCO | 2021-10-13 16:24 | 2021-10-15 18:10 | 136 | 049:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE HIZO DESGANCHE Y SE LLEVO LINEA AL AISLADOR | P21101300084 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2986 | 2021-10-13 | 406096 | keep | 0 | Oct | 2021 | 0.27659 | 9.2629e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 136
PONCE | 2021-10-13 16:28 | 2021-10-14 13:00 | 50 | 020:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE CERRO PUENTE | P21101300071 | New_Event | Wire Down | Include | Include | Equipment | 1232 | 2021-10-13 | 61600 | keep | 0 | Oct | 2021 | 0.041955 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-13 16:30 | 2021-10-14 12:44 | 12 | 020:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A2110130079 | New_Event | Bad Weather | Include | Include | Weather | 1214 | 2021-10-13 | 14568 | keep | 0 | Oct | 2021 | 0.0099222 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
ARECIBO | 2021-10-13 16:30 | 2021-10-13 16:31 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21101300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3431 | keep | 0 | Oct | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2021-10-13 16:31 | 2021-10-13 18:01 | 200 | 001:30 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21101300111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-10-13 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-10-13 16:32 | 2021-10-13 17:59 | 700 | 001:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO MACHETES | B21101300102 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 87 | 2021-10-13 | 60900 | keep | 0 | Oct | 2021 | 0.041479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-13 16:34 | 2021-10-13 17:46 | 1058 | 001:12 | P | NO SE REPORTO CAUSA | DISPARO PORTATIL #8 QUE LLEVA 50% DEL 1348-08, 20% DEL 1348-06 Y 20% DEL 1336-08 Y SE CERRO INTERRUPTOR DE LA BAJA DE LA PORTATIL | S21101300497 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-10-13 | 76176 | keep | 0 | Oct | 2021 | 0.051883 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2021-10-13 16:34 | 2021-10-13 17:46 | 260 | 001:12 | P | NO SE REPORTO CAUSA | DISPARO PORTATIL #8 QUE LLEVA 50% DEL 1348-08, 20% DEL 1348-06 Y 20% DEL 1336-08 Y SE CERRO INTERRUPTOR DE LA BAJA DE LA PORTATIL | S21101300497 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-10-13 | 18720 | keep | 0 | Oct | 2021 | 0.01275 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
SAN JUAN | 2021-10-13 16:34 | 2021-10-13 17:46 | 645 | 001:12 | P | NO SE REPORTO CAUSA | DISPARO PORTATIL #8 QUE LLEVA 50% DEL 1348-08, 20% DEL 1348-06 Y 20% DEL 1336-08 Y SE CERRO INTERRUPTOR DE LA BAJA DE LA PORTATIL | S21101300497 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-10-13 | 46440 | keep | 0 | Oct | 2021 | 0.03163 | 0.00043931 | Sustained | FALSE | FALSE | Not_TMED_Event | 645
MAYAGÃœEZ | 2021-10-13 16:38 | 2021-10-14 17:30 | 6 | 024:52 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE REPARO LINEA SECUNDARIA | M21101300151 | New_Event | Defective Pole | Include | Include | Equipment | 1492 | 2021-10-13 | 8952 | keep | 0 | Oct | 2021 | 0.0060972 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
SAN JUAN | 2021-10-13 16:41 | 2021-10-14 11:12 | 65 | 018:31 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21101300503 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1111 | 2021-10-13 | 72215 | keep | 0 | Oct | 2021 | 0.049185 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
HUMACAO | 2021-10-13 16:41 | 2021-10-13 18:21 | 7 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIO | C21101300119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2021-10-13 | 700 | keep | 0 | Oct | 2021 | 0.00047677 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-13 16:47 | 2021-10-14 10:42 | 50 | 017:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA Y SE REALIZO PODA | S21101300512 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1075 | 2021-10-13 | 53750 | keep | 0 | Oct | 2021 | 0.036609 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-10-13 16:52 | 2021-10-14 12:18 | 50 | 019:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21101300076 | New_Event | Bad Weather | Include | Include | Weather | 1166 | 2021-10-13 | 58300 | keep | 0 | Oct | 2021 | 0.039708 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-13 16:53 | 2021-10-13 17:18 | 1 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21101300152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2021-10-13 | 25 | keep | 0 | Oct | 2021 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-13 16:56 | 2021-10-13 18:45 | 120 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTES LLUVIAS Y RAYOS | S21101300526 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-10-13 | 13080 | keep | 0 | Oct | 2021 | 0.0089087 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
CAGUAS | 2021-10-13 17:00 | 2021-10-14 19:11 | 35 | 026:11 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL SU-17 AL T-12 AVERIA VIEJA DEL T-14 AL T-13 SE CONSTRUYO AEREO PROVISIONAL HACIA T-12 | C21101300123 | New_Event | UG Cable Fault | Include | Include | Equipment | 1571 | 2021-10-13 | 54985 | keep | 0 | Oct | 2021 | 0.03745 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2021-10-13 17:00 | 2021-10-14 11:40 | 1 | 018:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | C21101300123 | New_Event | Cutout Failure | Include | Include | Equipment | 1120 | 2021-10-13 | 1120 | keep | 0 | Oct | 2021 | 0.00076283 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-13 17:01 | 2021-10-13 18:16 | 75 | 001:15 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA SE SECCIONALIZO POSTE PARTIDO | S21101300531 | New_Event | Defective Pole | Include | Include | Equipment | 75 | 2021-10-13 | 5625 | keep | 0 | Oct | 2021 | 0.0038312 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-10-13 17:09 | 2021-10-14 19:45 | 35 | 026:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21101300537 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1596 | 2021-10-13 | 55860 | keep | 0 | Oct | 2021 | 0.038046 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
AGUADILLA | 2021-10-13 17:10 | 2021-10-14 20:09 | 15 | 026:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 3 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES QUEMADO EN CAJA DE TRANSFORMADOR | M21101300161 | New_Event | Cutout Failure | Include | Include | Equipment | 1619 | 2021-10-13 | 24285 | keep | 0 | Oct | 2021 | 0.01654 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 17:16 | 2021-10-14 12:22 | 100 | 019:06 | P | DESGANCHE | 2 X 100 EN CORTE DELINEA Y SE REALIZO DESGANCHE | S21101300546 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1146 | 2021-10-13 | 114600 | keep | 0 | Oct | 2021 | 0.078054 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-13 17:16 | 2021-10-14 10:17 | 25 | 017:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR | B21101300160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1021 | 2021-10-13 | 25525 | keep | 0 | Oct | 2021 | 0.017385 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-13 17:22 | 2021-10-13 18:19 | 35 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300093 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-10-13 | 1995 | keep | 0 | Oct | 2021 | 0.0013588 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-10-13 17:29 | 2021-10-13 20:49 | 90 | 003:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M21101300166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-10-13 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
YAUCO | 2021-10-13 17:30 | 2021-10-14 16:24 | 50 | 022:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA PARA SECCIONALIZAR AVERIA SE ABRIERON PUENTES HAY ALAMBRE ZAFADO DE PIN EN EL BO RIO PRIETO SECTOR URSULA 136 CLIENTES APROX EN LA BOMBA DE AAA SE DEJA PARA MANANA | P21101300084 | New_Event | Wire Down | Include | Include | Equipment | 1374 | 2021-10-13 | 68700 | keep | 0 | Oct | 2021 | 0.046791 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-13 17:31 | 2021-10-15 16:01 | 1 | 046:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101300100 | New_Event | Bad Weather | Include | Include | Weather | 2790 | 2021-10-13 | 2790 | keep | 0 | Oct | 2021 | 0.0019003 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-13 17:33 | 2021-10-13 19:17 | 2777 | 001:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO LINEA PRIMARIA ROTA Y SE CERRO EL INTERRUPTOR | A21101300097 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2021-10-13 | 288808 | keep | 0 | Oct | 2021 | 0.19671 | 0.0018914 | Sustained | FALSE | TRUE | Not_TMED_Event | 2777
GUAYAMA | 2021-10-13 17:34 | 2021-10-13 19:43 | 50 | 002:09 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P21101300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-10-13 | 6450 | keep | 0 | Oct | 2021 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-13 17:38 | 2021-10-13 19:39 | 40 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300101 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-10-13 | 4840 | keep | 0 | Oct | 2021 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-13 17:41 | 2021-10-13 19:43 | 80 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO ANTENA ENREDADA SOBRE LINEAS | S21101300575 | New_Event |  |  | Include | Wildlife | 122 | 2021-10-13 | 9760 | keep | 0 | Oct | 2021 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-10-13 17:41 | 2021-10-13 17:42 | 652 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101300170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 652 | keep | 0 | Oct | 2021 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-10-13 17:41 | 2021-10-13 17:43 | 2704 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21101300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-13 | 5408 | keep | 0 | Oct | 2021 | 0.0036834 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2021-10-13 17:42 | 2021-10-14 09:51 | 40 | 016:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101300526 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 969 | 2021-10-13 | 38760 | keep | 0 | Oct | 2021 | 0.026399 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-13 17:44 | 2021-10-13 17:45 | 4188 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R21101300179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-13 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-10-13 17:45 | 2021-10-14 11:09 | 70 | 017:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21101300183 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1044 | 2021-10-13 | 73080 | keep | 0 | Oct | 2021 | 0.049774 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-10-13 17:50 | 2021-10-14 12:13 | 25 | 018:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE LINEA | S21101300586 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1103 | 2021-10-13 | 27575 | keep | 0 | Oct | 2021 | 0.018781 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-13 18:00 | 2021-10-14 11:15 | 65 | 017:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101300596 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1035 | 2021-10-13 | 67275 | keep | 0 | Oct | 2021 | 0.045821 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
FAJARDO | 2021-10-13 18:01 | 2021-10-14 10:43 | 80 | 016:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 65 EN CORTE DE LINEA | R21101300186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1002 | 2021-10-13 | 80160 | keep | 0 | Oct | 2021 | 0.054597 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-10-13 18:05 | 2021-10-14 11:06 | 10 | 017:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR RAYOS | B21101300182 | New_Event | Bad Weather | Include | Include | Weather | 1021 | 2021-10-13 | 10210 | keep | 0 | Oct | 2021 | 0.006954 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-13 18:06 | 2021-10-13 20:54 | 150 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300125 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2021-10-13 | 25200 | keep | 0 | Oct | 2021 | 0.017164 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-10-13 18:06 | 2021-10-13 19:32 | 10 | 001:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 X 37.5 | B21101300007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 86 | 2021-10-13 | 860 | keep | 0 | Oct | 2021 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-13 18:07 | 2021-10-13 23:37 | 20 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101300127 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2021-10-13 | 6600 | keep | 0 | Oct | 2021 | 0.0044952 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-13 18:13 | 2021-10-13 18:14 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21101300186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 1533 | keep | 0 | Oct | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
MAYAGÃœEZ | 2021-10-13 18:14 | 2021-10-13 18:33 | 60 | 000:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21101300174 | New_Event | Bad Weather | Include | Include | Weather | 19 | 2021-10-13 | 1140 | keep | 0 | Oct | 2021 | 0.00077645 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-13 18:14 | 2021-10-13 21:49 | 80 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21101300185 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2021-10-13 | 17200 | keep | 0 | Oct | 2021 | 0.011715 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-13 18:18 | 2021-10-14 12:22 | 100 | 018:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PRIMARIO PARTIDO | P21101300088 | New_Event | Wire Down | Include | Include | Equipment | 1084 | 2021-10-13 | 108400 | keep | 0 | Oct | 2021 | 0.073831 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-13 18:22 | 2021-10-13 21:48 | 60 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN SU-4C SE LEVANTO PROVISIONAL AEREO | R21101300192 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2021-10-13 | 12360 | keep | 0 | Oct | 2021 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-10-13 18:25 | 2021-10-14 10:53 | 487 | 016:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21101300129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 988 | 2021-10-13 | 481156 | keep | 0 | Oct | 2021 | 0.32771 | 0.00033169 | Sustained | FALSE | TRUE | Not_TMED_Event | 487
MAYAGÃœEZ | 2021-10-13 18:26 | 2021-10-14 09:25 | 25 | 014:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M21101300175 | New_Event |  |  | Include | Wildlife | 899 | 2021-10-13 | 22475 | keep | 0 | Oct | 2021 | 0.015308 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-10-13 18:27 | 2021-10-13 18:28 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101300091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 527 | keep | 0 | Oct | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
VEGA BAJA | 2021-10-13 18:28 | 2021-10-14 13:28 | 1 | 019:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 5 EN TRANSFORMADOR SE REPARO EN PEDESTAL | B21101300192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1140 | 2021-10-13 | 1140 | keep | 0 | Oct | 2021 | 0.00077645 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-13 18:31 | 2021-10-14 18:08 | 10 | 023:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR Y SE CERRO PUENTE DE LINEA A CAJA | S21101300614 | New_Event | Cutout Failure | Include | Include | Equipment | 1417 | 2021-10-13 | 14170 | keep | 0 | Oct | 2021 | 0.0096511 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-13 18:32 | 2021-10-14 12:00 | 65 | 017:28 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21101300616 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1048 | 2021-10-13 | 68120 | keep | 0 | Oct | 2021 | 0.046396 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-10-13 18:32 | 2021-10-14 09:49 | 70 | 015:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21101300195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 917 | 2021-10-13 | 64190 | keep | 0 | Oct | 2021 | 0.04372 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-10-13 18:41 | 2021-10-14 16:00 | 40 | 021:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101300195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1279 | 2021-10-13 | 51160 | keep | 0 | Oct | 2021 | 0.034845 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 4098 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 24588 | keep | 0 | Oct | 2021 | 0.016747 | 0.0027911 | Sustained | FALSE | FALSE | Not_TMED_Event | 4098
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 956 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 5736 | keep | 0 | Oct | 2021 | 0.0039068 | 0.00065113 | Sustained | FALSE | FALSE | Not_TMED_Event | 956
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 1839 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 11034 | keep | 0 | Oct | 2021 | 0.0075152 | 0.0012525 | Sustained | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 1778 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 10668 | keep | 0 | Oct | 2021 | 0.0072659 | 0.001211 | Sustained | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 1376 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 8256 | keep | 0 | Oct | 2021 | 0.0056231 | 0.00093719 | Sustained | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 293 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 1758 | keep | 0 | Oct | 2021 | 0.0011974 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2021-10-13 18:43 | 2021-10-13 18:49 | 1215 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA BARRA DE 38 KV DE DAGUAO TC | R21101300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-13 | 7290 | keep | 0 | Oct | 2021 | 0.0049652 | 0.00082753 | Sustained | FALSE | FALSE | Not_TMED_Event | 1215
UTUADO | 2021-10-13 18:48 | 2021-10-13 20:34 | 60 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101300142 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-10-13 | 6360 | keep | 0 | Oct | 2021 | 0.0043318 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-10-13 19:07 | 2021-10-14 11:18 | 60 | 016:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101300627 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 971 | 2021-10-13 | 58260 | keep | 0 | Oct | 2021 | 0.039681 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-13 19:13 | 2021-10-14 14:40 | 40 | 019:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21101300150 | New_Event | Bad Weather | Include | Include | Weather | 1167 | 2021-10-13 | 46680 | keep | 0 | Oct | 2021 | 0.031794 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-13 19:13 | 2021-10-14 14:40 | 2 | 019:27 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA SOBRE LINEA | A21101300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1167 | 2021-10-13 | 2334 | keep | 0 | Oct | 2021 | 0.0015897 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-10-13 19:14 | 2021-10-15 11:30 | 8 | 040:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 37.5 KVA | M21101300184 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2416 | 2021-10-13 | 19328 | keep | 0 | Oct | 2021 | 0.013164 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-13 19:14 | 2021-10-14 21:21 | 8 | 026:07 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR EL JOURNEYMAN INFORMO QUE LE NOTIFICO A SU SUPERVISOR QUE EL TRANSFORMADOR TIENE LIQUEO DE ACEITE Y SE VE EN MALAS CONDICIONES | M21101300184 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1567 | 2021-10-13 | 12536 | keep | 0 | Oct | 2021 | 0.0085382 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-13 19:16 | 2021-10-14 11:11 | 35 | 015:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101300201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 955 | 2021-10-13 | 33425 | keep | 0 | Oct | 2021 | 0.022766 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-10-13 19:17 | 2021-10-13 21:16 | 100 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A21101300097 | Partial_restoration | Wire Down | Include | Include | Equipment | 119 | 2021-10-13 | 11900 | keep | 0 | Oct | 2021 | 0.008105 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-10-13 19:20 | 2021-10-13 20:49 | 100 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101300136 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-10-13 | 8900 | keep | 0 | Oct | 2021 | 0.0060617 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-13 19:23 | 2021-10-14 22:32 | 15 | 027:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M21101400169 | New_Event | Cutout Failure | Include | Include | Equipment | 1629 | 2021-10-13 | 24435 | keep | 0 | Oct | 2021 | 0.016643 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 19:36 | 2021-10-14 15:32 | 50 | 019:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21110130063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1196 | 2021-10-13 | 59800 | keep | 0 | Oct | 2021 | 0.04073 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-13 19:38 | 2021-10-14 13:04 | 30 | 017:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21101300640 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1046 | 2021-10-13 | 31380 | keep | 0 | Oct | 2021 | 0.021373 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-13 19:41 | 2021-10-14 21:44 | 10 | 026:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B21101300211 | Partial_restoration | Wire Down | Include | Include | Equipment | 1563 | 2021-10-13 | 15630 | keep | 0 | Oct | 2021 | 0.010646 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-13 20:11 | 2021-10-13 22:37 | 50 | 002:26 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21101300649 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-10-13 | 7300 | keep | 0 | Oct | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-13 20:11 | 2021-10-13 20:12 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101300147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3701 | keep | 0 | Oct | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2021-10-13 20:18 | 2021-10-13 21:00 | 150 | 000:42 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN TRANSFORMADOR Y SE RETIRO PARARRAYO SE CERRO MACHETES DEL 1404-07 QUE ESTA POR EL 1404-06 Y SE TRANSFIRIERON AL 1111-02 | S21101300011 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 42 | 2021-10-13 | 6300 | keep | 0 | Oct | 2021 | 0.0042909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-13 20:21 | 2021-10-13 20:22 | 17 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO REALIZANDO OPERACIONES PARA IDENTIFICAR POSIBLE AVERIA EN EL 1404-07 QUE ESTA PARCIAL POR EL 1111-02. ESTA LLEVANDO TAMBIEN EL 1404-06 | S21101300000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-13 | 17 | keep | 0 | Oct | 2021 | 1.1579e-05 | 1.1579e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2021-10-13 20:21 | 2021-10-13 20:22 | 143 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO 1111-02 REALIZANDO OPERACIONES PARA IDENTIFICAR POSIBLE AVERIA EN EL 1404-07 QUE ESTA PARCIAL POR EL 1111-02. ESTA LLEVANDO TAMBIEN EL 1404-06 | S21101300000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-13 | 143 | keep | 0 | Oct | 2021 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2021-10-13 20:32 | 2021-10-14 10:06 | 35 | 013:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21101300657 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 814 | 2021-10-13 | 28490 | keep | 0 | Oct | 2021 | 0.019404 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-10-13 20:49 | 2021-10-14 10:10 | 25 | 013:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21101300664 | New_Event | Vegetation Contact | Include | Include | Vegetation | 801 | 2021-10-13 | 20025 | keep | 0 | Oct | 2021 | 0.013639 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-10-13 20:49 | 2021-10-13 20:50 | 1510 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21101300155 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-13 | 1510 | keep | 0 | Oct | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-10-13 20:50 | 2021-10-14 11:18 | 57 | 014:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C21101300169 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 868 | 2021-10-13 | 49476 | keep | 0 | Oct | 2021 | 0.033698 | 3.8822e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 57
YAUCO | 2021-10-13 20:54 | 2021-10-15 15:02 | 11 | 042:08 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 25 KVA A 4160 VOLTS QUEMADO | P21101300099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2528 | 2021-10-13 | 27808 | keep | 0 | Oct | 2021 | 0.01894 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2021-10-13 20:54 | 2021-10-14 10:30 | 15 | 013:36 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR QUEMADO DE 25KVA-4160 VOLTIOS SE DEJA PARA MANANA | P21101300099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 816 | 2021-10-13 | 12240 | keep | 0 | Oct | 2021 | 0.0083366 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-13 21:00 | 2021-10-14 14:49 | 65 | 017:49 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA | S21101300667 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1069 | 2021-10-13 | 69485 | keep | 0 | Oct | 2021 | 0.047326 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-10-13 21:05 | 2021-10-14 10:37 | 400 | 013:32 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA PRIMARIA | A21101300162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 812 | 2021-10-13 | 324800 | keep | 0 | Oct | 2021 | 0.22122 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
UTUADO | 2021-10-13 21:07 | 2021-10-13 22:15 | 3 | 001:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101300163 | New_Event | Bad Weather | Include | Include | Weather | 68 | 2021-10-13 | 204 | keep | 0 | Oct | 2021 | 0.00013894 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-10-13 21:09 | 2021-10-14 12:00 | 100 | 014:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101300164 | New_Event | Bad Weather | Include | Include | Weather | 891 | 2021-10-13 | 89100 | keep | 0 | Oct | 2021 | 0.060686 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-13 21:11 | 2021-10-13 21:12 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RE CLOSE RELAY EN OFF | M21101300203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-13 | 3458 | keep | 0 | Oct | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
ARECIBO | 2021-10-13 21:12 | 2021-10-14 16:30 | 10 | 019:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA PARTIDA | A21101300165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1158 | 2021-10-13 | 11580 | keep | 0 | Oct | 2021 | 0.0078871 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-13 21:18 | 2021-10-14 10:53 | 12 | 013:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYOS Y SE DESGANCHO | C21101300174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2021-10-13 | 9780 | keep | 0 | Oct | 2021 | 0.0066611 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-10-13 21:49 | 2021-10-14 11:00 | 65 | 013:11 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21101300673 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 791 | 2021-10-13 | 51415 | keep | 0 | Oct | 2021 | 0.035019 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-10-13 22:07 | 2021-10-14 15:20 | 40 | 017:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P21101300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1033 | 2021-10-13 | 41320 | keep | 0 | Oct | 2021 | 0.028143 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-13 22:08 | 2021-10-13 23:23 | 1 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S21101300676 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-10-13 | 75 | keep | 0 | Oct | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-13 22:30 | 2021-10-14 10:52 | 30 | 012:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101300209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 742 | 2021-10-13 | 22260 | keep | 0 | Oct | 2021 | 0.015161 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-13 23:24 | 2021-10-14 11:38 | 100 | 012:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN CORTE DE LINEA MSLINK 8276304 NO FUNDIO FUSIBLE | P21101300104 | New_Event | Cutout Failure | Include | Include | Equipment | 734 | 2021-10-13 | 73400 | keep | 0 | Oct | 2021 | 0.049992 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-13 23:43 | 2021-10-14 13:18 | 35 | 013:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21101300682 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2021-10-13 | 28525 | keep | 0 | Oct | 2021 | 0.019428 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-10-14 00:07 | 2021-10-14 09:58 | 90 | 009:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R21101400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 591 | 2021-10-14 | 53190 | keep | 0 | Oct | 2021 | 0.036227 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-14 01:14 | 2021-10-14 15:32 | 50 | 014:18 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21101400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 858 | 2021-10-14 | 42900 | keep | 0 | Oct | 2021 | 0.029219 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-14 02:43 | 2021-10-14 20:15 | 50 | 017:32 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-3 CABLE SOTERRADO AVERIADO DE PM-11 A PM-9. SE INSTALO AEREO PROVISIONAL DE PM-11 A PM-9 | M21101400002 | New_Event | UG Cable Fault | Include | Include | Equipment | 1052 | 2021-10-14 | 52600 | keep | 0 | Oct | 2021 | 0.035826 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-10-14 03:42 | 2021-10-14 03:43 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
FAJARDO | 2021-10-14 03:46 | 2021-10-14 03:47 | 2286 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3100 | R21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 2286 | keep | 0 | Oct | 2021 | 0.001557 | 0.001557 | Momentary | FALSE | TRUE | Not_TMED_Event | 2286
FAJARDO | 2021-10-14 03:46 | 2021-10-14 03:47 | 693 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3100 | R21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 693 | keep | 0 | Oct | 2021 | 0.000472 | 0.000472 | Momentary | FALSE | TRUE | Not_TMED_Event | 693
FAJARDO | 2021-10-14 03:47 | 2021-10-14 13:04 | 95 | 009:17 | P | NO SE REPORTO CAUSA | 1 X 100 Y 2 X 80 EN CORTES DE LINEAS | R21101400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 557 | 2021-10-14 | 52915 | keep | 0 | Oct | 2021 | 0.03604 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-10-14 04:58 | 2021-10-14 04:59 | 2861 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO | B21101400003 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-14 | 2861 | keep | 0 | Oct | 2021 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
CAGUAS | 2021-10-14 05:04 | 2021-10-14 05:05 | 2448 | 000:01 | T | DESGANCHE | RECIERRE | C21101400260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-14 | 2448 | keep | 0 | Oct | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
SAN JUAN | 2021-10-14 05:24 | 2021-10-14 05:26 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21101400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-14 | 3362 | keep | 0 | Oct | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-14 05:24 | 2021-10-14 05:26 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1304-05 | S21101400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-14 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-14 05:24 | 2021-10-14 05:26 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA EL 1303-04 | S21101400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-14 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-10-14 05:24 | 2021-10-14 05:26 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21101400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-14 | 3196 | keep | 0 | Oct | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2021-10-14 05:31 | 2021-10-14 12:16 | 300 | 006:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21101400008 | New_Event | Wire Down | Include | Include | Equipment | 405 | 2021-10-14 | 121500 | keep | 0 | Oct | 2021 | 0.082753 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-10-14 06:00 | 2021-10-14 21:31 | 10 | 015:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE 37.5KVA | S21101400023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 931 | 2021-10-14 | 9310 | keep | 0 | Oct | 2021 | 0.006341 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-14 06:25 | 2021-10-14 19:19 | 60 | 012:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | C21101300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 774 | 2021-10-14 | 46440 | keep | 0 | Oct | 2021 | 0.03163 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-14 07:03 | 2021-10-14 19:29 | 20 | 012:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO (NO FUNDIO FUSIBLE) | S21101400013 | New_Event | Wire Down | Include | Include | Equipment | 746 | 2021-10-14 | 14920 | keep | 0 | Oct | 2021 | 0.010162 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-10-14 07:03 | 2021-10-15 13:29 | 60 | 030:26 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1826 | 2021-10-14 | 109560 | keep | 0 | Oct | 2021 | 0.074621 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-14 07:05 | 2021-10-14 17:20 | 15 | 010:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21101400011 | New_Event | Bad Weather | Include | Include | Weather | 615 | 2021-10-14 | 9225 | keep | 0 | Oct | 2021 | 0.0062831 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-14 07:26 | 2021-10-14 09:54 | 2861 | 002:28 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA SECCIONALIZAR POSTE IMPACTADO | B21101400008 | 1st_after_momentary |  |  | Include | Wildlife | 148 | 2021-10-14 | 423428 | keep | 0 | Oct | 2021 | 0.28839 | 0.0019486 | Sustained | FALSE | FALSE | Not_TMED_Event | 2861
MAYAGÃœEZ | 2021-10-14 07:40 | 2021-10-14 11:40 | 8 | 004:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M21101400022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 240 | 2021-10-14 | 1920 | keep | 0 | Oct | 2021 | 0.0013077 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-10-14 07:42 | 2021-10-14 13:01 | 30 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2021-10-14 | 9570 | keep | 0 | Oct | 2021 | 0.0065181 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-14 07:42 | 2021-10-14 11:43 | 23 | 004:01 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P21101400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-10-14 | 5543 | keep | 0 | Oct | 2021 | 0.0037753 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
AGUADILLA | 2021-10-14 07:50 | 2021-10-14 19:55 | 25 | 012:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101400027 | New_Event | Bad Weather | Include | Include | Weather | 725 | 2021-10-14 | 18125 | keep | 0 | Oct | 2021 | 0.012345 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
GUAYAMA | 2021-10-14 07:54 | 2021-10-14 12:24 | 50 | 004:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEAS DESGANCHE | P21101400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2021-10-14 | 13500 | keep | 0 | Oct | 2021 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-14 08:01 | 2021-10-14 11:09 | 15 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101300123 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-10-14 | 2820 | keep | 0 | Oct | 2021 | 0.0019207 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-10-14 08:07 | 2021-10-14 08:08 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P211014000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-10-14 | 464 | keep | 0 | Oct | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2021-10-14 08:08 | 2021-10-14 09:06 | 100 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA AVE RUZO LINEAS | P21101400011 | 1st_after_momentary |  |  | Include | Wildlife | 58 | 2021-10-14 | 5800 | keep | 0 | Oct | 2021 | 0.0039504 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-14 08:18 | 2021-10-14 16:42 | 130 | 008:24 | P | NO SE REPORTO CAUSA | 1 X 200 EN RISER | S21101400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 504 | 2021-10-14 | 65520 | keep | 0 | Oct | 2021 | 0.044625 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2021-10-14 08:20 | 2021-10-14 12:58 | 40 | 004:38 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21101400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2021-10-14 | 11120 | keep | 0 | Oct | 2021 | 0.0075738 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-14 08:28 | 2021-10-14 10:20 | 11 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21101400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-10-14 | 1232 | keep | 0 | Oct | 2021 | 0.00083911 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-10-14 08:29 | 2021-10-14 11:57 | 50 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101300021 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2021-10-14 | 10400 | keep | 0 | Oct | 2021 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-14 08:32 | 2021-10-14 13:28 | 35 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER HACIA SU-1 | S21101400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2021-10-14 | 10360 | keep | 0 | Oct | 2021 | 0.0070561 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-10-14 08:34 | 2021-10-14 16:57 | 25 | 008:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21101400024 | New_Event | Wire Down | Include | Include | Equipment | 503 | 2021-10-14 | 12575 | keep | 0 | Oct | 2021 | 0.0085648 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-10-14 08:34 | 2021-10-14 15:30 | 50 | 006:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA FUNDIO EN PRUEBA DE CORTE DE LINEA CONDUCTOR EN EL SUELO | C21101400024 | New_Event | Wire Down | Include | Include | Equipment | 416 | 2021-10-14 | 20800 | keep | 0 | Oct | 2021 | 0.014167 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-14 08:36 | 2021-10-14 15:57 | 8 | 007:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFROMADOR POR MAL TIEMPO | A21101400022 | New_Event | Bad Weather | Include | Include | Weather | 441 | 2021-10-14 | 3528 | keep | 0 | Oct | 2021 | 0.0024029 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-14 08:41 | 2021-10-14 14:15 | 2067 | 005:34 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M21101400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-10-14 | 690378 | keep | 0 | Oct | 2021 | 0.47021 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
BAYAMON | 2021-10-14 08:43 | 2021-10-15 17:26 | 10 | 032:43 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 25KVA | S21101400055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1963 | 2021-10-14 | 19630 | keep | 0 | Oct | 2021 | 0.01337 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-14 08:56 | 2021-10-14 15:26 | 1 | 006:30 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO PENCA DE LA LINEA | C21101400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2021-10-14 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-14 09:06 | 2021-10-14 09:07 | 247 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R21101400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 247 | keep | 0 | Oct | 2021 | 0.00016823 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
AGUADILLA | 2021-10-14 09:10 | 2021-10-15 10:10 | 10 | 025:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101400063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1500 | 2021-10-14 | 15000 | keep | 0 | Oct | 2021 | 0.010216 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-14 09:15 | 2021-10-14 09:17 | 1825 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-14 | 3650 | keep | 0 | Oct | 2021 | 0.002486 | 0.001243 | Momentary | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-10-14 09:15 | 2021-10-14 09:17 | 47 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-14 | 94 | keep | 0 | Oct | 2021 | 6.4023e-05 | 3.2011e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-10-14 09:15 | 2021-10-14 09:17 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-14 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-10-14 09:15 | 2021-10-14 09:17 | 2 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-14 | 4 | keep | 0 | Oct | 2021 | 2.7244e-06 | 1.3622e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-10-14 09:15 | 2021-10-14 09:17 | 2391 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-14 | 4782 | keep | 0 | Oct | 2021 | 0.003257 | 0.0016285 | Momentary | FALSE | TRUE | Not_TMED_Event | 2391
CAGUAS | 2021-10-14 09:15 | 2021-10-14 09:31 | 2276 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 36416 | keep | 0 | Oct | 2021 | 0.024803 | 0.0015502 | Sustained | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-10-14 09:15 | 2021-10-14 09:31 | 777 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 12432 | keep | 0 | Oct | 2021 | 0.0084674 | 0.00052921 | Sustained | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-10-14 09:15 | 2021-10-14 09:31 | 12 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 192 | keep | 0 | Oct | 2021 | 0.00013077 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-10-14 09:15 | 2021-10-14 09:31 | 1290 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE MONACILLOS A CAGUAS | C21101400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 20640 | keep | 0 | Oct | 2021 | 0.014058 | 0.00087861 | Sustained | FALSE | TRUE | Not_TMED_Event | 1290
CAGUAS | 2021-10-14 09:16 | 2021-10-14 16:29 | 4 | 007:13 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA ABRIR PUENTES Y REEMPLAZAR POSTE PRIMARIO PODRIDO FINAL DE LINEA | C21101400031 | New_Event | Defective Pole | Include | Include | Equipment | 433 | 2021-10-14 | 1732 | keep | 0 | Oct | 2021 | 0.0011797 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-10-14 09:26 | 2021-10-14 09:27 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21101400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 3957 | keep | 0 | Oct | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2021-10-14 09:29 | 2021-10-14 09:30 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21101400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 3957 | keep | 0 | Oct | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
AGUADILLA | 2021-10-14 09:38 | 2021-10-14 20:07 | 5 | 010:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101400057 | New_Event | Bad Weather | Include | Include | Weather | 629 | 2021-10-14 | 3145 | keep | 0 | Oct | 2021 | 0.002142 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-10-14 09:39 | 2021-10-14 12:25 | 168 | 002:46 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE DESGANCHO | C21101400045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-10-14 | 27888 | keep | 0 | Oct | 2021 | 0.018994 | 0.00011442 | Sustained | FALSE | TRUE | Not_TMED_Event | 168
YAUCO | 2021-10-14 09:39 | 2021-10-14 17:49 | 1 | 008:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO ENCONTRARON CAUSA | P21101400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2021-10-14 | 490 | keep | 0 | Oct | 2021 | 0.00033374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-14 09:47 | 2021-10-14 12:55 | 80 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101400062 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-10-14 | 15040 | keep | 0 | Oct | 2021 | 0.010244 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-14 09:54 | 2021-10-14 12:41 | 1300 | 002:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ENDEREZO POSTES Y LINEAS Y SE NORMALIZO CARGAS | B21101400008 | Partial_restoration |  |  | Include | Wildlife | 167 | 2021-10-14 | 217100 | keep | 0 | Oct | 2021 | 0.14787 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-14 10:09 | 2021-10-14 18:00 | 50 | 007:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101400101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2021-10-14 | 23550 | keep | 0 | Oct | 2021 | 0.01604 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-14 10:17 | 2021-10-15 08:50 | 2 | 022:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21101400033 | New_Event | Bad Weather | Include | Include | Weather | 1353 | 2021-10-14 | 2706 | keep | 0 | Oct | 2021 | 0.001843 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-10-14 10:45 | 2021-10-14 21:18 | 60 | 010:33 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA Y SE LLEVO TRANSFORMADOR A SU LUGAR | S21101400085 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 633 | 2021-10-14 | 37980 | keep | 0 | Oct | 2021 | 0.025868 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-10-14 10:48 | 2021-10-14 18:10 | 15 | 007:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21101400040 | New_Event | Bad Weather | Include | Include | Weather | 442 | 2021-10-14 | 6630 | keep | 0 | Oct | 2021 | 0.0045157 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-14 10:53 | 2021-10-14 18:55 | 10 | 008:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA POR UNO DE 50KVA FID7189044 | S21101400089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 482 | 2021-10-14 | 4820 | keep | 0 | Oct | 2021 | 0.0032829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-14 10:54 | 2021-10-14 18:32 | 125 | 007:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE RETEZO TENSOR | C21101400056 | New_Event |  |  | Include | Wildlife | 458 | 2021-10-14 | 57250 | keep | 0 | Oct | 2021 | 0.038993 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
YAUCO | 2021-10-14 10:56 | 2021-10-14 17:06 | 80 | 006:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21101400028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2021-10-14 | 29600 | keep | 0 | Oct | 2021 | 0.02016 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-14 10:57 | 2021-10-14 11:00 | 17 | 000:03 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA ABRIR AMARRE EN SU-22 CONTRA 1404-06 POR NO HABER DESPEJE PARA LAS OPERACIONES | S21101400000 | New_Event | Other Causes | Include | Include | Other | 3 | 2021-10-14 | 51 | keep | 0 | Oct | 2021 | 3.4736e-05 | 1.1579e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2021-10-14 10:57 | 2021-10-14 11:00 | 143 | 000:03 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA ABRIR AMARRE EN SU-22 CONTRA 1404-06 POR NO HABER DESPEJE PARA LAS OPERACIONES | S21101400000 | New_Event | Other Causes | Include | Include | Other | 3 | 2021-10-14 | 429 | keep | 0 | Oct | 2021 | 0.00029219 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2021-10-14 10:58 | 2021-10-14 10:59 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21101400038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
GUAYAMA | 2021-10-14 10:58 | 2021-10-14 13:03 | 100 | 002:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE. | P21101400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-10-14 | 12500 | keep | 0 | Oct | 2021 | 0.0085137 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-14 11:05 | 2021-10-14 14:44 | 1 | 003:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | R21101400039 | New_Event |  |  | Include | Wildlife | 219 | 2021-10-14 | 219 | keep | 0 | Oct | 2021 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-10-14 11:10 | 2021-10-14 16:06 | 1 | 004:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21101400059 | New_Event | Cutout Failure | Include | Include | Equipment | 296 | 2021-10-14 | 296 | keep | 0 | Oct | 2021 | 0.0002016 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-14 11:10 | 2021-10-14 11:36 | 6 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101300123 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-10-14 | 156 | keep | 0 | Oct | 2021 | 0.00010625 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
HUMACAO | 2021-10-14 11:21 | 2021-10-14 14:46 | 133 | 003:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101400070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-10-14 | 27265 | keep | 0 | Oct | 2021 | 0.01857 | 9.0586e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 133
CAGUAS | 2021-10-14 11:24 | 2021-10-14 11:25 | 2448 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C21101400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-14 | 2448 | keep | 0 | Oct | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2021-10-14 11:25 | 2021-10-14 18:15 | 225 | 006:50 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO IGUANA Y SE REALIZO DESGANCHE | C21101400080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 410 | 2021-10-14 | 92250 | keep | 0 | Oct | 2021 | 0.062831 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
GUAYAMA | 2021-10-14 11:43 | 2021-10-14 16:42 | 10 | 004:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE SACO AGUA DEL PEDESTAL SECUNDARIO Y SE REPARARON BARRAS SECUNDARIAS EN EL PEDESTAL. | P21101400033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 299 | 2021-10-14 | 2990 | keep | 0 | Oct | 2021 | 0.0020365 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-14 11:46 | 2021-10-14 17:20 | 45 | 005:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21101400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-10-14 | 15030 | keep | 0 | Oct | 2021 | 0.010237 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-10-14 11:49 | 2021-10-14 11:50 | 3718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P211014000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-10-14 | 3718 | keep | 0 | Oct | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-10-14 11:50 | 2021-10-14 14:31 | 50 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN CORTE DE LINEA POR CONTACTO DE AVE | P21101400041 | 1st_after_momentary |  |  | Include | Wildlife | 161 | 2021-10-14 | 8050 | keep | 0 | Oct | 2021 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-14 12:00 | 2021-10-14 15:40 | 10 | 003:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 25KVA POR UNO DE 37.5KVA FID33673139 | S21101400155 | New_Event | Service Transformer Failure | Include | Include | Equipment | 220 | 2021-10-14 | 2200 | keep | 0 | Oct | 2021 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-14 12:09 | 2021-10-14 16:24 | 10 | 004:15 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21101400112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2021-10-14 | 2550 | keep | 0 | Oct | 2021 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-14 12:18 | 2021-10-14 15:20 | 12 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21101400114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2021-10-14 | 2184 | keep | 0 | Oct | 2021 | 0.0014875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-14 12:20 | 2021-10-14 14:35 | 40 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-10-14 | 5400 | keep | 0 | Oct | 2021 | 0.0036779 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-14 12:27 | 2021-10-14 18:05 | 60 | 005:38 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | S21101400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2021-10-14 | 20280 | keep | 0 | Oct | 2021 | 0.013813 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-14 12:35 | 2021-10-14 19:01 | 60 | 006:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | S21101400118 | New_Event | Cutout Failure | Include | Include | Equipment | 386 | 2021-10-14 | 23160 | keep | 0 | Oct | 2021 | 0.015774 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-10-14 12:39 | 2021-10-14 15:05 | 4 | 002:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE RETIRO IGUANA DE LA LINEA | R21101400042 | New_Event |  |  | Include | Wildlife | 146 | 2021-10-14 | 584 | keep | 0 | Oct | 2021 | 0.00039776 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-10-14 12:48 | 2021-10-14 14:21 | 10 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101400120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-10-14 | 930 | keep | 0 | Oct | 2021 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-14 13:00 | 2021-10-14 15:49 | 20 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21092900189 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-10-14 | 3380 | keep | 0 | Oct | 2021 | 0.0023021 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-14 13:19 | 2021-10-14 16:32 | 60 | 003:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE BAMBUAS | B21101400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-10-14 | 11580 | keep | 0 | Oct | 2021 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-10-14 13:19 | 2021-10-14 15:20 | 11 | 002:01 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | R21101400045 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 121 | 2021-10-14 | 1331 | keep | 0 | Oct | 2021 | 0.00090654 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-10-14 13:31 | 2021-10-14 16:16 | 15 | 002:45 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RETIRAR POSTE PARTIDO Y RELOCALIZAR LINEA SECUNDARIA | S21101400131 | New_Event | Defective Pole | Include | Include | Equipment | 165 | 2021-10-14 | 2475 | keep | 0 | Oct | 2021 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-10-14 13:31 | 2021-10-14 16:20 | 45 | 002:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101400137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-10-14 | 7605 | keep | 0 | Oct | 2021 | 0.0051797 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-14 13:32 | 2021-10-14 17:18 | 30 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR Y 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A21101400056 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-10-14 | 6780 | keep | 0 | Oct | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-10-14 13:38 | 2021-10-14 15:34 | 10 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONECTORES EN PEDESTAL SECUNDARIO | P21101400045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-10-14 | 1160 | keep | 0 | Oct | 2021 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-14 13:50 | 2021-10-14 15:33 | 10 | 001:43 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR Y REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD EN EL FID:19787502 MARCA:HOWARD INDUSTRIES #SERIE:1852751418 VOLTAJES: 4160/7200 120/240 | M21101400105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 103 | 2021-10-14 | 1030 | keep | 0 | Oct | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-14 13:58 | 2021-10-14 17:41 | 60 | 003:43 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-10-14 | 13380 | keep | 0 | Oct | 2021 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-14 14:01 | 2021-10-14 17:50 | 30 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PARTIDO Y SE CERRO CORTE DE LINEA | A21101400060 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2021-10-14 | 6870 | keep | 0 | Oct | 2021 | 0.0046791 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-14 14:04 | 2021-10-16 14:00 | 30 | 047:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CONVERTIDOR PARA REPARO NEUTRAL PRIMARIO | A21101400061 | New_Event | Wire Down | Include | Include | Equipment | 2876 | 2021-10-14 | 86280 | keep | 0 | Oct | 2021 | 0.058765 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-10-14 14:07 | 2021-10-14 20:46 | 100 | 006:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | S21101400140 | New_Event | Wire Down | Include | Include | Equipment | 399 | 2021-10-14 | 39900 | keep | 0 | Oct | 2021 | 0.027176 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-14 14:07 | 2021-10-14 20:07 | 40 | 006:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 360 | 2021-10-14 | 14400 | keep | 0 | Oct | 2021 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-14 14:08 | 2021-10-15 12:20 | 10 | 022:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | A21101400062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1332 | 2021-10-14 | 13320 | keep | 0 | Oct | 2021 | 0.0090722 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-14 14:10 | 2021-10-14 18:05 | 300 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR IGUANA CRUZO FASE A TIERRA | M21101400141 | New_Event |  |  | Include | Wildlife | 235 | 2021-10-14 | 70500 | keep | 0 | Oct | 2021 | 0.048017 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-10-14 14:15 | 2021-10-14 15:40 | 80 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21101400143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2021-10-14 | 6800 | keep | 0 | Oct | 2021 | 0.0046314 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-14 14:15 | 2021-10-14 15:24 | 1450 | 001:09 | P | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M21101400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-10-14 | 100050 | keep | 0 | Oct | 2021 | 0.068144 | 0.00098759 | Sustained | FALSE | FALSE | Not_TMED_Event | 1450
BAYAMON | 2021-10-14 14:17 | 2021-10-14 16:36 | 100 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S21140000146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2021-10-14 | 13900 | keep | 0 | Oct | 2021 | 0.0094672 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-14 14:32 | 2021-10-14 16:15 | 150 | 001:43 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21101400082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-10-14 | 15450 | keep | 0 | Oct | 2021 | 0.010523 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-10-14 14:35 | 2021-10-14 14:36 | 2907 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21101400149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 2907 | keep | 0 | Oct | 2021 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
HUMACAO | 2021-10-14 14:36 | 2021-10-14 17:40 | 65 | 003:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21101400150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-10-14 | 11960 | keep | 0 | Oct | 2021 | 0.0081459 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-10-14 14:43 | 2021-10-14 15:42 | 1310 | 000:59 | T | DESGANCHE | SE ABRIO MACHETES EN CALLE CARDENAS ESQ CALLE CORRIENTE Y SE CERRO INTERRUPTOR | S21101400151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-10-14 | 77290 | keep | 0 | Oct | 2021 | 0.052642 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
HUMACAO | 2021-10-14 14:56 | 2021-10-14 18:47 | 1 | 003:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE RISER | C21101400155 | New_Event | Wire Down | Include | Include | Equipment | 231 | 2021-10-14 | 231 | keep | 0 | Oct | 2021 | 0.00015733 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-10-14 15:03 | 2021-10-14 16:00 | 60 | 000:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R21101400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-10-14 | 3420 | keep | 0 | Oct | 2021 | 0.0023293 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-14 15:24 | 2021-10-14 15:39 | 2067 | 000:15 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M21101400044 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 15 | 2021-10-14 | 31005 | keep | 0 | Oct | 2021 | 0.021117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-14 15:27 | 2021-10-14 16:23 | 70 | 000:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21101300070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-10-14 | 3920 | keep | 0 | Oct | 2021 | 0.0026699 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-10-14 15:30 | 2021-10-14 18:00 | 75 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21101400162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-10-14 | 11250 | keep | 0 | Oct | 2021 | 0.0076623 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-10-14 15:39 | 2021-10-14 16:19 | 1200 | 000:40 | P | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M21101400044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 40 | 2021-10-14 | 48000 | keep | 0 | Oct | 2021 | 0.032693 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-14 15:42 | 2021-10-14 18:30 | 80 | 002:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21110140015 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 168 | 2021-10-14 | 13440 | keep | 0 | Oct | 2021 | 0.0091539 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-14 15:42 | 2021-10-14 16:10 | 600 | 000:28 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES CALLE CARDENAS | S21101400151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2021-10-14 | 16800 | keep | 0 | Oct | 2021 | 0.011442 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-10-14 15:43 | 2021-10-14 21:49 | 60 | 006:06 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | S21101400170 | New_Event | Defective Pole | Include | Include | Equipment | 366 | 2021-10-14 | 21960 | keep | 0 | Oct | 2021 | 0.014957 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-14 15:44 | 2021-10-14 18:42 | 5668 | 002:58 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 0060 EN AVERIA DEL 1646-01 SE CERRO PUENTE Y SE REEMPLAZO AISLADOR ROTO. | R21101400061 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-10-14 | 1008904 | keep | 0 | Oct | 2021 | 0.68716 | 0.0038604 | Sustained | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2021-10-14 15:44 | 2021-10-14 15:58 | 1026 | 000:14 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 0060 EN AVERIA DEL 1646-01 SE CERRO PUENTE Y SE REEMPLAZO AISLADOR ROTO. | R21101400061 | New_Event | Wire Down | Include | Include | Equipment | 14 | 2021-10-14 | 14364 | keep | 0 | Oct | 2021 | 0.0097833 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-10-14 15:44 | 2021-10-14 15:58 | 3046 | 000:14 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 0060 EN AVERIA DEL 1646-01 SE CERRO PUENTE Y SE REEMPLAZO AISLADOR ROTO. | R21101400061 | New_Event | Wire Down | Include | Include | Equipment | 14 | 2021-10-14 | 42644 | keep | 0 | Oct | 2021 | 0.029045 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-10-14 15:44 | 2021-10-14 15:58 | 2891 | 000:14 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 0060 EN AVERIA DEL 1646-01 SE CERRO PUENTE Y SE REEMPLAZO AISLADOR ROTO. | R21101400061 | New_Event | Wire Down | Include | Include | Equipment | 14 | 2021-10-14 | 40474 | keep | 0 | Oct | 2021 | 0.027567 | 0.001969 | Sustained | FALSE | FALSE | Not_TMED_Event | 2891
UTUADO | 2021-10-14 16:05 | 2021-10-14 22:14 | 30 | 006:09 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 1 X 30 EN CORTES DE LINEAS DISTINTOS Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101400074 | New_Event | Bad Weather | Include | Include | Weather | 369 | 2021-10-14 | 11070 | keep | 0 | Oct | 2021 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-14 16:06 | 2021-10-14 19:00 | 2276 | 002:54 | S | PROTECCION DEFECTUOSA | SE REALIZO VIA LIBRE DE EMERGENCIA INTERRUPTOR 3014-04 SIN PROTECCION Y 3014-03 CON MACHETE QUEMADO. SE REEMPLAZO EL MACHETE QUEMADO PARA QUE INTERRUPTOR ASUMIERA LA CARGA | C21101400171 | New_Event | Protection Miscoordination | Include | Include | Other | 174 | 2021-10-14 | 396024 | keep | 0 | Oct | 2021 | 0.26973 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2021-10-14 16:06 | 2021-10-14 19:00 | 777 | 002:54 | S | PROTECCION DEFECTUOSA | SE REALIZO VIA LIBRE DE EMERGENCIA INTERRUPTOR 3014-04 SIN PROTECCION Y 3014-03 CON MACHETE QUEMADO. SE REEMPLAZO EL MACHETE QUEMADO PARA QUE INTERRUPTOR ASUMIERA LA CARGA | C21101400171 | New_Event | Protection Miscoordination | Include | Include | Other | 174 | 2021-10-14 | 135198 | keep | 0 | Oct | 2021 | 0.092083 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2021-10-14 16:06 | 2021-10-14 19:00 | 12 | 002:54 | S | PROTECCION DEFECTUOSA | SE REALIZO VIA LIBRE DE EMERGENCIA INTERRUPTOR 3014-04 SIN PROTECCION Y 3014-03 CON MACHETE QUEMADO. SE REEMPLAZO EL MACHETE QUEMADO PARA QUE INTERRUPTOR ASUMIERA LA CARGA | C21101400171 | New_Event | Protection Miscoordination | Include | Include | Other | 174 | 2021-10-14 | 2088 | keep | 0 | Oct | 2021 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-10-14 16:06 | 2021-10-14 19:00 | 1290 | 002:54 | S | PROTECCION DEFECTUOSA | SE REALIZO VIA LIBRE DE EMERGENCIA INTERRUPTOR 3014-04 SIN PROTECCION Y 3014-03 CON MACHETE QUEMADO. SE REEMPLAZO EL MACHETE QUEMADO PARA QUE INTERRUPTOR ASUMIERA LA CARGA | C21101400171 | New_Event | Protection Miscoordination | Include | Include | Other | 174 | 2021-10-14 | 224460 | keep | 0 | Oct | 2021 | 0.15288 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
AGUADILLA | 2021-10-14 16:14 | 2021-10-14 17:17 | 15 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101400067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-10-14 | 945 | keep | 0 | Oct | 2021 | 0.00064364 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-14 16:19 | 2021-10-14 16:37 | 2067 | 000:18 | T | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE ABRIO INTERRUPTOR PARA CERRAR MACHETES EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR, PROBO MALO, SE VOLVIO A ABRIR MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M21101400044 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 18 | 2021-10-14 | 37206 | keep | 0 | Oct | 2021 | 0.025341 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-14 16:21 | 2021-10-14 17:34 | 100 | 001:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A21101400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-10-14 | 7300 | keep | 0 | Oct | 2021 | 0.004972 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-14 16:27 | 2021-10-14 16:53 | 20 | 000:26 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | S21101400182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2021-10-14 | 520 | keep | 0 | Oct | 2021 | 0.00035417 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-14 16:28 | 2021-10-14 16:58 | 7 | 000:30 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21101400054 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 30 | 2021-10-14 | 210 | keep | 0 | Oct | 2021 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-14 16:30 | 2021-10-14 17:41 | 800 | 001:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO GOI ABRIENDO MACHETES PARA LLEVAR CONDUCTOR VIVO ZAFADO DE AISLADOR QUE ESTABA ENCIMA DE TENSOR | S21101400179 | New_Event | Wire Down | Include | Include | Equipment | 71 | 2021-10-14 | 56800 | keep | 0 | Oct | 2021 | 0.038686 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
MAYAGÃœEZ | 2021-10-14 16:37 | 2021-10-14 18:45 | 1200 | 002:08 | P | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR Y SE REALIZO DESGANCHE | M21101400044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-10-14 | 153600 | keep | 0 | Oct | 2021 | 0.10462 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-14 16:58 | 2021-10-14 18:25 | 150 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN RAISER Y 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE CAJA DE RAISER | P21101400062 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2021-10-14 | 13050 | keep | 0 | Oct | 2021 | 0.0088883 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-14 17:01 | 2021-10-14 20:11 | 2 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21101400078 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-10-14 | 380 | keep | 0 | Oct | 2021 | 0.00025882 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-14 17:03 | 2021-10-14 18:28 | 75 | 001:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21101300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-10-14 | 6375 | keep | 0 | Oct | 2021 | 0.004342 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-10-14 17:04 | 2021-10-14 21:48 | 809 | 004:44 | P | DESGANCHE | 1 X 140 SE REALIZO DESGANCHE Y SE REEMPLAZO AISLADOR QUEMADO | R21101400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-10-14 | 229756 | keep | 0 | Oct | 2021 | 0.15649 | 0.00055101 | Sustained | FALSE | FALSE | Not_TMED_Event | 809
FAJARDO | 2021-10-14 17:07 | 2021-10-14 18:04 | 15 | 000:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R21101400107 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2021-10-14 | 855 | keep | 0 | Oct | 2021 | 0.00058234 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-14 17:30 | 2021-10-15 11:52 | 70 | 018:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101400193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1102 | 2021-10-14 | 77140 | keep | 0 | Oct | 2021 | 0.05254 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-10-14 17:42 | 2021-10-15 13:06 | 30 | 019:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21101400101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1164 | 2021-10-14 | 34920 | keep | 0 | Oct | 2021 | 0.023784 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-10-14 17:47 | 2021-10-14 19:47 | 7 | 002:00 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR POR SOBRE CARGA | A21101400082 | New_Event | Trip Due To Overload | Include | Include | Other | 120 | 2021-10-14 | 840 | keep | 0 | Oct | 2021 | 0.00057212 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-14 17:51 | 2021-10-15 11:47 | 50 | 017:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21101400254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1076 | 2021-10-14 | 53800 | keep | 0 | Oct | 2021 | 0.036643 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-14 18:00 | 2021-10-14 21:00 | 30 | 003:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR MAL TIEMPO | A21101400083 | New_Event | Bad Weather | Include | Include | Weather | 180 | 2021-10-14 | 5400 | keep | 0 | Oct | 2021 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-14 18:05 | 2021-10-15 18:50 | 10 | 024:45 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21101400257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1485 | 2021-10-14 | 14850 | keep | 0 | Oct | 2021 | 0.010114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-14 18:07 | 2021-10-14 19:54 | 4 | 001:47 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO BAJANTES SECUNDARIO Y SE DEJO SECCIONALIZADO POSTE SECUNDARIO PARTIDO | C21101400206 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 107 | 2021-10-14 | 428 | keep | 0 | Oct | 2021 | 0.00029151 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-10-14 18:12 | 2021-10-14 22:20 | 60 | 004:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON CAMION | C21101400161 | New_Event |  |  | Include | Wildlife | 248 | 2021-10-14 | 14880 | keep | 0 | Oct | 2021 | 0.010135 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-14 18:19 | 2021-10-15 14:12 | 30 | 019:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B21101400107 | New_Event | Wire Down | Include | Include | Equipment | 1193 | 2021-10-14 | 35790 | keep | 0 | Oct | 2021 | 0.024376 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-14 18:20 | 2021-10-14 19:41 | 40 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN AEREO PROVISIONAL | S21101400258 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-10-14 | 3240 | keep | 0 | Oct | 2021 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-10-14 18:27 | 2021-10-15 11:31 | 10 | 017:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21101400211 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1024 | 2021-10-14 | 10240 | keep | 0 | Oct | 2021 | 0.0069744 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-14 18:30 | 2021-10-15 17:29 | 15 | 022:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA RETIRO TENSOR CRUZANDO LINEA | C21101400212 | New_Event |  |  | Include | Wildlife | 1379 | 2021-10-14 | 20685 | keep | 0 | Oct | 2021 | 0.014088 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-10-14 18:30 | 2021-10-14 18:31 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101400111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 2610 | keep | 0 | Oct | 2021 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2021-10-14 18:30 | 2021-10-14 18:32 | 3076 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21101400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-14 | 6152 | keep | 0 | Oct | 2021 | 0.0041901 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
ARECIBO | 2021-10-14 18:40 | 2021-10-14 19:36 | 50 | 000:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21101400087 | New_Event | Bad Weather | Include | Include | Weather | 56 | 2021-10-14 | 2800 | keep | 0 | Oct | 2021 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-14 18:42 | 2021-10-15 17:25 | 650 | 022:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE Y REEMPLAZO AISLADOR ROTO | C21101400216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1363 | 2021-10-14 | 885950 | keep | 0 | Oct | 2021 | 0.60342 | 0.00044271 | Sustained | FALSE | TRUE | Not_TMED_Event | 650
MAYAGÃœEZ | 2021-10-14 18:45 | 2021-10-14 19:06 | 2067 | 000:21 | T | DESGANCHE | SE SE REALIZO DESGANCHE Y SE ABRIO INTERRUPTOR PARA CERRAR MACHETES EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR, PROBO MALO, SE VOLVIO A ABRIR MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M21101400044 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 21 | 2021-10-14 | 43407 | keep | 0 | Oct | 2021 | 0.029564 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-14 18:48 | 2021-10-14 22:58 | 106 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA, NO SE REPORTARON LAS CAUSAS. | P21101400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2021-10-14 | 26500 | keep | 0 | Oct | 2021 | 0.018049 | 7.2196e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 106
CAGUAS | 2021-10-14 19:00 | 2021-10-16 13:50 | 1 | 042:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21101400059 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 2570 | 2021-10-14 | 2570 | keep | 0 | Oct | 2021 | 0.0017504 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-14 19:00 | 2021-10-15 09:50 | 1 | 014:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | C21101400220 | New_Event | Secondary Wire Down | Include | Include | Equipment | 890 | 2021-10-14 | 890 | keep | 0 | Oct | 2021 | 0.00060617 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-14 19:06 | 2021-10-14 19:45 | 1200 | 000:39 | P | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR Y SE REALIZO DESGANCHE | M21101400044 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 39 | 2021-10-14 | 46800 | keep | 0 | Oct | 2021 | 0.031875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-14 19:07 | 2021-10-15 10:50 | 40 | 015:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21101400090 | New_Event | Bad Weather | Include | Include | Weather | 943 | 2021-10-14 | 37720 | keep | 0 | Oct | 2021 | 0.025691 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-14 19:19 | 2021-10-15 12:01 | 95 | 016:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21101400228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1002 | 2021-10-14 | 95190 | keep | 0 | Oct | 2021 | 0.064833 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-10-14 19:24 | 2021-10-14 21:36 | 30 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101400124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-10-14 | 3960 | keep | 0 | Oct | 2021 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 137 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101400292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 2192 | keep | 0 | Oct | 2021 | 0.001493 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 457 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101400292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 7312 | keep | 0 | Oct | 2021 | 0.0049802 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 1225 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101400201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 19600 | keep | 0 | Oct | 2021 | 0.013349 | 0.00083434 | Sustained | FALSE | TRUE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 1452 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101400201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 23232 | keep | 0 | Oct | 2021 | 0.015823 | 0.00098895 | Sustained | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 616 | 000:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101400201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 9856 | keep | 0 | Oct | 2021 | 0.0067129 | 0.00041955 | Sustained | FALSE | TRUE | Not_TMED_Event | 616
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 3500 | 000:16 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 LLEVA 40% 1204-3 Y 80% 1204-2 POR PORTATIL #22 | S21101200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 56000 | keep | 0 | Oct | 2021 | 0.038141 | 0.0023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 3500
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 19:45 | 600 | 000:16 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 LLEVA 40% 1204-3 Y 80% 1204-2 POR PORTATIL #22 | S21101400286 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2021-10-14 | 9600 | keep | 0 | Oct | 2021 | 0.0065385 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 20:57 | 10211 | 001:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES EN CARR 846 Y SE CERRO INTERRUPTOR 1206-03 ENTRANDO EN SERVICIO 60% DE SU CARGA. CONDUCTOR EN EL SUELO Y MACHETE QUEMADO. 1204-05 ESTA TRANSFERIDO AL 1206-03 | S21101400275 | New_Event | Wire Down | Include | Include | Equipment | 88 | 2021-10-14 | 898568 | keep | 0 | Oct | 2021 | 0.61201 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-14 19:29 | 2021-10-14 20:14 | 4133 | 000:45 | T | DESGANCHE | SE ABRIERON MACHETES N/O CONTRA EL 1204-05 POR ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR | S21101400275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-10-14 | 185985 | keep | 0 | Oct | 2021 | 0.12667 | 0.002815 | Sustained | FALSE | TRUE | Not_TMED_Event | 4133
VEGA BAJA | 2021-10-14 19:30 | 2021-10-14 22:35 | 7 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B21101400125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2021-10-14 | 1295 | keep | 0 | Oct | 2021 | 0.00088202 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
ARECIBO | 2021-10-14 19:35 | 2021-10-14 21:01 | 70 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21101400095 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-10-14 | 6020 | keep | 0 | Oct | 2021 | 0.0041002 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-14 19:45 | 2021-10-14 19:58 | 2067 | 000:13 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE ABRIO INTERRUPTOR PARA CERRAR MACHETES EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M21101400044 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 13 | 2021-10-14 | 26871 | keep | 0 | Oct | 2021 | 0.018302 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-14 19:54 | 2021-10-14 21:00 | 60 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101400306 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-10-14 | 3960 | keep | 0 | Oct | 2021 | 0.0026971 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-14 19:54 | 2021-10-15 11:24 | 25 | 015:30 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21101400127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 930 | 2021-10-14 | 23250 | keep | 0 | Oct | 2021 | 0.015835 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-14 19:58 | 2021-10-15 18:22 | 1 | 022:24 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101300149 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1344 | 2021-10-14 | 1344 | keep | 0 | Oct | 2021 | 0.00091539 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-14 19:58 | 2021-10-14 20:23 | 874 | 000:25 | P | DESGANCHE | SE CERRO CORTE DE LINEA QUE SE HABIA ABIERTO PARA SECCIONALIZAR Y PATRULLAR | M21101400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-10-14 | 21850 | keep | 0 | Oct | 2021 | 0.014882 | 0.00059528 | Sustained | FALSE | TRUE | Not_TMED_Event | 874
BAYAMON | 2021-10-14 20:05 | 2021-10-14 22:16 | 40 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101400316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-10-14 | 5240 | keep | 0 | Oct | 2021 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-14 20:06 | 2021-10-15 14:42 | 40 | 018:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101400317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1116 | 2021-10-14 | 44640 | keep | 0 | Oct | 2021 | 0.030404 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 3070 | keep | 0 | Oct | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | TRUE | Not_TMED_Event | 3070
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 2735 | keep | 0 | Oct | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | TRUE | Not_TMED_Event | 2735
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 1070 | keep | 0 | Oct | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | TRUE | Not_TMED_Event | 1070
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 1647 | keep | 0 | Oct | 2021 | 0.0011218 | 0.0011218 | Momentary | FALSE | TRUE | Not_TMED_Event | 1647
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 3295 | keep | 0 | Oct | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | TRUE | Not_TMED_Event | 3295
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 1180 | keep | 0 | Oct | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | TRUE | Not_TMED_Event | 1180
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | TRUE | Not_TMED_Event | 320
BAYAMON | 2021-10-14 20:07 | 2021-10-14 20:08 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA TRANSMISION 36100 | B21101400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-14 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | TRUE | Not_TMED_Event | 2234
BAYAMON | 2021-10-14 20:08 | 2021-10-15 13:23 | 36 | 017:15 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 30 EN CORTE DE LINEA | B21101300090 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1035 | 2021-10-14 | 37260 | keep | 0 | Oct | 2021 | 0.025378 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-14 20:08 | 2021-10-15 11:57 | 40 | 015:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 949 | 2021-10-14 | 37960 | keep | 0 | Oct | 2021 | 0.025854 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-14 20:08 | 2021-10-16 14:38 | 15 | 042:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | B21101300103 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2550 | 2021-10-14 | 38250 | keep | 0 | Oct | 2021 | 0.026052 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-14 20:14 | 2021-10-14 20:43 | 20 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO (NO FUNDIO FUSIBLE) | S21101400013 | New_Event | Wire Down | Include | Include | Equipment | 29 | 2021-10-14 | 580 | keep | 0 | Oct | 2021 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-10-14 20:23 | 2021-10-14 22:25 | 1 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101400097 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2021-10-14 | 122 | keep | 0 | Oct | 2021 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BARRANQUITAS | 2021-10-14 20:31 | 2021-10-15 11:41 | 60 | 015:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101400238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 910 | 2021-10-14 | 54600 | keep | 0 | Oct | 2021 | 0.037188 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-14 20:42 | 2021-10-14 20:43 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21101400140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 2402 | keep | 0 | Oct | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
SAN JUAN | 2021-10-14 20:43 | 2021-10-14 20:57 | 4133 | 000:14 | T | DESGANCHE | DISPARO 1206-03 LLEVANDO 1204-5. SE ABRIO MACHETES N/O DEL 1204-05 EN CARR 846 DANDO SERVICIO A 60% DEL 1204-05. ARBOL SOBRE LINEA | S21101400349 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 14 | 2021-10-14 | 57862 | keep | 0 | Oct | 2021 | 0.03941 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-14 20:54 | 2021-10-15 19:25 | 10 | 022:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | A21101400098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1351 | 2021-10-14 | 13510 | keep | 0 | Oct | 2021 | 0.0092016 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-14 20:57 | 2021-10-14 22:47 | 450 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | S21101400349 | Partial_restoration | Wire Down | Include | Include | Equipment | 110 | 2021-10-14 | 49500 | keep | 0 | Oct | 2021 | 0.033714 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-14 20:57 | 2021-10-14 21:36 | 2000 | 000:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES EN PARQUES VILLAS DE CANEY CALLE GUAYAMA Y SE CERRARON MACHETES EN CARR 846 PARA REALIZAR GOI DEBIDO A CONDUCTOR EN EL SUELO Y MACHETES AVERIADOS | S21101400275 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-10-14 | 78000 | keep | 0 | Oct | 2021 | 0.053125 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2021-10-14 20:57 | 2021-10-15 10:38 | 20 | 013:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO (NO FUNDIO FUSIBLE) | S21101400013 | Partial_restoration | Wire Down | Include | Include | Equipment | 821 | 2021-10-14 | 16420 | keep | 0 | Oct | 2021 | 0.011184 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-14 21:16 | 2021-10-14 21:17 | 2888 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21101400099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-14 | 2888 | keep | 0 | Oct | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2021-10-14 21:36 | 2021-10-15 16:48 | 10 | 019:12 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 20 EN RISER SE REMPLAZO TERMINACION AVERIADA | A21101400101 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1152 | 2021-10-14 | 11520 | keep | 0 | Oct | 2021 | 0.0078462 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-14 22:02 | 2021-10-15 10:27 | 25 | 012:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R21101400132 | New_Event | Cutout Failure | Include | Include | Equipment | 745 | 2021-10-14 | 18625 | keep | 0 | Oct | 2021 | 0.012685 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-10-14 23:34 | 2021-10-15 09:25 | 1 | 009:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21101400261 | New_Event | Bad Weather | Include | Include | Weather | 591 | 2021-10-14 | 591 | keep | 0 | Oct | 2021 | 0.00040253 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-14 23:48 | 2021-10-15 11:16 | 125 | 011:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R21101400133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 688 | 2021-10-14 | 86000 | keep | 0 | Oct | 2021 | 0.058574 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
ARECIBO | 2021-10-15 00:07 | 2021-10-15 11:30 | 400 | 011:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21101500001 | New_Event | Bad Weather | Include | Include | Weather | 683 | 2021-10-15 | 273200 | keep | 0 | Oct | 2021 | 0.18608 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CAGUAS | 2021-10-15 01:47 | 2021-10-15 14:17 | 325 | 012:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101500005 | New_Event | Bad Weather | Include | Include | Weather | 750 | 2021-10-15 | 243750 | keep | 0 | Oct | 2021 | 0.16602 | 0.00022136 | Sustained | FALSE | TRUE | Not_TMED_Event | 325
ARECIBO | 2021-10-15 01:56 | 2021-10-15 10:05 | 80 | 008:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21101500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2021-10-15 | 39120 | keep | 0 | Oct | 2021 | 0.026644 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-15 03:02 | 2021-10-15 11:11 | 4 | 008:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | R21101500006 | New_Event | Cutout Failure | Include | Include | Equipment | 489 | 2021-10-15 | 1956 | keep | 0 | Oct | 2021 | 0.0013322 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-10-15 03:38 | 2021-10-15 14:48 | 180 | 011:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 1 X 30 EN CORTES DE LINEAS MAL TIEMPO | C21101500006 | New_Event | Bad Weather | Include | Include | Weather | 670 | 2021-10-15 | 120600 | keep | 0 | Oct | 2021 | 0.08214 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
HUMACAO | 2021-10-15 03:47 | 2021-10-15 10:33 | 3833 | 006:46 | S | PROTECCION DEFECTUOSA | REEMPLAZO 1 X 125 SLOW SPEED, SE ENCONTRO AUXILIAR DE TRIP DEL 2601-01 AVERIADO. SE TRANSFIRIO CARGA AL 2601-02 | C21101500034 | New_Event | Protection Miscoordination | Include | Include | Other | 406 | 2021-10-15 | 1556198 | keep | 0 | Oct | 2021 | 1.0599 | 0.0026106 | Sustained | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2021-10-15 03:47 | 2021-10-15 10:20 | 181 | 006:33 | S | PROTECCION DEFECTUOSA | REEMPLAZO 1 X 125 SLOW SPEED, SE ENCONTRO AUXILIAR DE TRIP DEL 2601-01 AVERIADO. SE TRANSFIRIO CARGA AL 2601-02 | C21101500034 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-10-15 | 71133 | keep | 0 | Oct | 2021 | 0.048448 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2021-10-15 03:47 | 2021-10-15 10:20 | 2299 | 006:33 | S | PROTECCION DEFECTUOSA | REEMPLAZO 1 X 125 SLOW SPEED, SE ENCONTRO AUXILIAR DE TRIP DEL 2601-01 AVERIADO. SE TRANSFIRIO CARGA AL 2601-02 | C21101500034 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-10-15 | 903507 | keep | 0 | Oct | 2021 | 0.61537 | 0.0015658 | Sustained | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2021-10-15 03:47 | 2021-10-15 10:20 | 776 | 006:33 | S | PROTECCION DEFECTUOSA | REEMPLAZO 1 X 125 SLOW SPEED, SE ENCONTRO AUXILIAR DE TRIP DEL 2601-01 AVERIADO. SE TRANSFIRIO CARGA AL 2601-02 | C21101500034 | New_Event | Protection Miscoordination | Include | Include | Other | 393 | 2021-10-15 | 304968 | keep | 0 | Oct | 2021 | 0.20771 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
CANOVANAS | 2021-10-15 03:51 | 2021-10-15 13:16 | 22 | 009:25 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTES DE LINEA SE REALIZO DESGANCHE | R21101500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 565 | 2021-10-15 | 12430 | keep | 0 | Oct | 2021 | 0.008466 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
SAN JUAN | 2021-10-15 06:00 | 2021-10-15 18:38 | 10 | 012:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO 50' DE SECUNDARIA | S21101500008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 758 | 2021-10-15 | 7580 | keep | 0 | Oct | 2021 | 0.0051627 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-15 06:25 | 2021-10-15 10:15 | 110 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21101500049 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-10-15 | 25300 | keep | 0 | Oct | 2021 | 0.017232 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
CAGUAS | 2021-10-15 06:38 | 2021-10-15 09:08 | 95 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER MAL TIEMPO | C21101500055 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2021-10-15 | 14250 | keep | 0 | Oct | 2021 | 0.0097056 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2021-10-15 06:50 | 2021-10-15 17:51 | 1 | 011:01 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21101500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 661 | 2021-10-15 | 661 | keep | 0 | Oct | 2021 | 0.0004502 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-15 06:59 | 2021-10-15 11:26 | 7 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2021-10-15 | 1869 | keep | 0 | Oct | 2021 | 0.001273 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-10-15 07:20 | 2021-10-15 07:21 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO | R21101500019 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-15 | 2708 | keep | 0 | Oct | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-10-15 07:21 | 2021-10-15 07:58 | 407 | 000:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 400 Y 3 X 80 EN CORTES DE LINEA VEHICULO IMPACTO LINEAS | R21101500031 | 1st_after_momentary |  |  | Include | Wildlife | 37 | 2021-10-15 | 15059 | keep | 0 | Oct | 2021 | 0.010257 | 0.00027721 | Sustained | FALSE | TRUE | Not_TMED_Event | 407
VEGA BAJA | 2021-10-15 07:29 | 2021-10-15 10:50 | 1 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21101500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2021-10-15 | 201 | keep | 0 | Oct | 2021 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-15 07:32 | 2021-10-15 07:33 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 27 | keep | 0 | Oct | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2021-10-15 07:38 | 2021-10-15 14:45 | 10 | 007:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE 37.5KVA | S21101500026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 427 | 2021-10-15 | 4270 | keep | 0 | Oct | 2021 | 0.0029083 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-15 07:38 | 2021-10-15 12:35 | 7 | 004:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R21101500023 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2021-10-15 | 2079 | keep | 0 | Oct | 2021 | 0.001416 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-10-15 07:43 | 2021-10-16 10:50 | 50 | 027:07 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | A21101500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1627 | 2021-10-15 | 81350 | keep | 0 | Oct | 2021 | 0.055407 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-15 07:45 | 2021-10-15 13:07 | 200 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C21101500069 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2021-10-15 | 64400 | keep | 0 | Oct | 2021 | 0.043863 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-15 07:49 | 2021-10-15 12:15 | 35 | 004:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | S21101400029 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2021-10-15 | 9310 | keep | 0 | Oct | 2021 | 0.006341 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-10-15 07:58 | 2021-10-15 07:59 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO | R21101500027 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-10-15 | 2708 | keep | 0 | Oct | 2021 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-10-15 07:59 | 2021-10-15 10:00 | 407 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 400 Y 3 X 80 EN CORTES DE LINEA VEHICULO IMPACTO LINEAS | R21101500031 | 1st_after_momentary |  |  | Include | Wildlife | 121 | 2021-10-15 | 49247 | keep | 0 | Oct | 2021 | 0.033542 | 0.00027721 | Sustained | FALSE | TRUE | Not_TMED_Event | 407
ARECIBO | 2021-10-15 08:03 | 2021-10-15 08:35 | 70 | 000:32 | P | DESGANCHE | 1 X 80 EN CONVERTIDOR SE RETIRO RAMA | A21101500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2021-10-15 | 2240 | keep | 0 | Oct | 2021 | 0.0015257 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2021-10-15 08:06 | 2021-10-15 13:52 | 6 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANFORMADOR | B21101500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2021-10-15 | 2076 | keep | 0 | Oct | 2021 | 0.001414 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-15 08:08 | 2021-10-15 11:39 | 12 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21101500035 | New_Event |  |  | Include | Wildlife | 211 | 2021-10-15 | 2532 | keep | 0 | Oct | 2021 | 0.0017245 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-10-15 08:10 | 2021-10-15 12:15 | 2 | 004:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15KVA | A21101500008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 245 | 2021-10-15 | 490 | keep | 0 | Oct | 2021 | 0.00033374 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-10-15 08:11 | 2021-10-15 21:13 | 14 | 013:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21101500077 | New_Event | Bad Weather | Include | Include | Weather | 782 | 2021-10-15 | 10948 | keep | 0 | Oct | 2021 | 0.0074566 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2021-10-15 08:29 | 2021-10-15 11:08 | 1 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN BANCO DE TRANSFORMADOR CRUCE POR AVE | C21101500086 | New_Event |  |  | Include | Wildlife | 159 | 2021-10-15 | 159 | keep | 0 | Oct | 2021 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-15 08:54 | 2021-10-15 15:40 | 65 | 006:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21101500090 | New_Event | Bad Weather | Include | Include | Weather | 406 | 2021-10-15 | 26390 | keep | 0 | Oct | 2021 | 0.017974 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-10-15 09:06 | 2021-10-15 09:50 | 5 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO EN PEDESTAL | B21101500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-10-15 | 220 | keep | 0 | Oct | 2021 | 0.00014984 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-15 09:13 | 2021-10-15 18:19 | 10 | 009:06 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B21101500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 546 | 2021-10-15 | 5460 | keep | 0 | Oct | 2021 | 0.0037188 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-15 09:16 | 2021-10-15 09:51 | 275 | 000:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO CHIRINGA DE LA LINEA | R21101500046 | New_Event |  |  | Include | Wildlife | 35 | 2021-10-15 | 9625 | keep | 0 | Oct | 2021 | 0.0065555 | 0.0001873 | Sustained | FALSE | TRUE | Not_TMED_Event | 275
MAYAGÃœEZ | 2021-10-15 09:17 | 2021-10-15 10:58 | 2 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21101500013 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-10-15 | 202 | keep | 0 | Oct | 2021 | 0.00013758 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-10-15 09:23 | 2021-10-15 11:06 | 6 | 001:43 | P | DESGANCHE | SE ABRIO TRANSFORMADOR SE RETIRO ARBOL Y SE REPARO SECUNDARIA | B21101500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-10-15 | 618 | keep | 0 | Oct | 2021 | 0.00042092 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-15 09:24 | 2021-10-15 17:38 | 30 | 008:14 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS SE CERRO CORTE DE LINEAS | A21101500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 494 | 2021-10-15 | 14820 | keep | 0 | Oct | 2021 | 0.010094 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-15 09:39 | 2021-10-15 10:01 | 6 | 000:22 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO | B21101400074 | New_Event | Defective Pole | Include | Include | Equipment | 22 | 2021-10-15 | 132 | keep | 0 | Oct | 2021 | 8.9905e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-15 09:43 | 2021-10-15 10:42 | 18 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21101400080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-10-15 | 1062 | keep | 0 | Oct | 2021 | 0.00072332 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2021-10-15 09:43 | 2021-10-16 11:46 | 12 | 026:03 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | B21101500033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1563 | 2021-10-15 | 18756 | keep | 0 | Oct | 2021 | 0.012775 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-10-15 09:45 | 2021-10-15 21:45 | 7 | 012:00 | P | NO SE REPORTO CAUSA | SE ENCONTRO CAJAS DEL TRANSFORMADOR ABIERTAS SE CERRARON NO SE REMPLAZO FUSIBLE | M21101500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 720 | 2021-10-15 | 5040 | keep | 0 | Oct | 2021 | 0.0034327 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-10-15 10:01 | 2021-10-15 10:51 | 1394 | 000:50 | T | DESGANCHE | DISPARO INTERRUPTOR NO HAY COMUNICACION CERRADO POR SCADA DESPUES DE HABER INSPECCIONADO EN LA SUBESTACION | R21101500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2021-10-15 | 69700 | keep | 0 | Oct | 2021 | 0.047472 | 0.00094945 | Sustained | FALSE | FALSE | Not_TMED_Event | 1394
BAYAMON | 2021-10-15 10:02 | 2021-10-15 11:05 | 6 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21101400093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-10-15 | 378 | keep | 0 | Oct | 2021 | 0.00025745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-15 10:10 | 2021-10-15 11:30 | 45 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PALOMA CRUZO FASE | P21101500011 | New_Event |  |  | Include | Wildlife | 80 | 2021-10-15 | 3600 | keep | 0 | Oct | 2021 | 0.0024519 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
VEGA BAJA | 2021-10-15 10:17 | 2021-10-15 15:37 | 1 | 005:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN RISER | B21101500035 | New_Event | Wire Down | Include | Include | Equipment | 320 | 2021-10-15 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-10-15 10:30 | 2021-10-15 12:35 | 32 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21101400081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-10-15 | 4000 | keep | 0 | Oct | 2021 | 0.0027244 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
AGUADILLA | 2021-10-15 10:32 | 2021-10-15 11:47 | 10 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101400163 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-10-15 | 750 | keep | 0 | Oct | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-15 10:34 | 2021-10-15 10:35 | 3833 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2601-02 LLEVANDO LA CARGA DEL 2601-01 | C21101500115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 3833 | keep | 0 | Oct | 2021 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2021-10-15 10:34 | 2021-10-15 10:35 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2601-02 LLEVANDO LA CARGA DEL 2601-01 | C21101500115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 181 | keep | 0 | Oct | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2021-10-15 10:38 | 2021-10-15 10:48 | 10211 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21101500076 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2021-10-15 | 102110 | keep | 0 | Oct | 2021 | 0.069547 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-15 10:38 | 2021-10-15 10:48 | 4133 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21101500076 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2021-10-15 | 41330 | keep | 0 | Oct | 2021 | 0.02815 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-10-15 10:40 | 2021-10-15 16:58 | 50 | 006:18 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REPARO NEUTRAL Y SE REALIZO DESGANCHE | S21101500078 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 378 | 2021-10-15 | 18900 | keep | 0 | Oct | 2021 | 0.012873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-15 10:40 | 2021-10-15 10:50 | 3 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101500008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2021-10-15 | 30 | keep | 0 | Oct | 2021 | 2.0433e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-10-15 10:48 | 2021-10-15 11:17 | 20 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO (NO FUNDIO FUSIBLE) | S21101500013 | Partial_restoration | Wire Down | Include | Include | Equipment | 29 | 2021-10-15 | 580 | keep | 0 | Oct | 2021 | 0.00039504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-10-15 10:51 | 2021-10-15 16:38 | 80 | 005:47 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE DESGANCHO | R21101500089 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 347 | 2021-10-15 | 27760 | keep | 0 | Oct | 2021 | 0.018907 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-15 10:57 | 2021-10-15 15:38 | 10 | 004:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO | S21101500088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 281 | 2021-10-15 | 2810 | keep | 0 | Oct | 2021 | 0.0019139 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-15 11:00 | 2021-10-15 17:56 | 130 | 006:56 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE POR LA COMPAÃ‘IA XPERT'S | M21101500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2021-10-15 | 54080 | keep | 0 | Oct | 2021 | 0.036834 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
SAN JUAN | 2021-10-15 11:11 | 2021-10-15 11:18 | 14 | 000:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL FUERA AISLADOR ROTO | R21101500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 7 | 2021-10-15 | 98 | keep | 0 | Oct | 2021 | 6.6747e-05 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-10-15 11:15 | 2021-10-15 11:16 | 5191 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1710-05 Y SE CERRO POR SCADA LLEVA 50% DEL 9405-05 | B21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 5191 | keep | 0 | Oct | 2021 | 0.0035356 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2021-10-15 11:15 | 2021-10-15 11:16 | 1700 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1710-05 Y SE CERRO POR SCADA LLEVA 50% DEL 9405-05 | B2110150000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 1700 | keep | 0 | Oct | 2021 | 0.0011579 | 0.0011579 | Momentary | FALSE | FALSE | Not_TMED_Event | 1700
AGUADILLA | 2021-10-15 11:16 | 2021-10-15 16:30 | 50 | 005:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-10-15 | 15700 | keep | 0 | Oct | 2021 | 0.010693 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-15 11:17 | 2021-10-15 11:39 | 10211 | 000:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR SITUACION DE PELIGRO CONDUCTOR EN EL SUELO CARGA TRANSFERIDA AL 1206-03 | S21101500076 | Partial_restoration | Wire Down | Include | Include | Equipment | 22 | 2021-10-15 | 224642 | keep | 0 | Oct | 2021 | 0.153 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-15 11:17 | 2021-10-15 11:39 | 4133 | 000:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR SITUACION DE PELIGRO CONDUCTOR EN EL SUELO. ADEMAS LLEVA LA CARGA DEL 1204-05 | S21101500076 | Additional_clients | Wire Down | Include | Include | Equipment | 22 | 2021-10-15 | 90926 | keep | 0 | Oct | 2021 | 0.061929 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-15 11:17 | 2021-10-15 13:10 | 12 | 001:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | A21101500031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 113 | 2021-10-15 | 1356 | keep | 0 | Oct | 2021 | 0.00092357 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-10-15 11:24 | 2021-10-15 16:50 | 15 | 005:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-10-15 | 4890 | keep | 0 | Oct | 2021 | 0.0033306 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-15 11:31 | 2021-10-16 15:35 | 3 | 028:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANASFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M21101500036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1684 | 2021-10-15 | 5052 | keep | 0 | Oct | 2021 | 0.0034409 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-10-15 11:39 | 2021-10-15 15:04 | 20 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO (NO FUNDIO FUSIBLE) | S21101400013 | Partial_restoration | Wire Down | Include | Include | Equipment | 205 | 2021-10-15 | 4100 | keep | 0 | Oct | 2021 | 0.0027925 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-15 11:51 | 2021-10-15 17:25 | 200 | 005:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-10-15 | 66800 | keep | 0 | Oct | 2021 | 0.045497 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-15 11:54 | 2021-10-15 11:55 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21101500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2021-10-15 11:57 | 2021-10-15 17:17 | 30 | 005:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500037 | New_Event | Bad Weather | Include | Include | Weather | 320 | 2021-10-15 | 9600 | keep | 0 | Oct | 2021 | 0.0065385 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-15 11:59 | 2021-10-15 12:02 | 837 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1401-06 | S21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-15 | 2511 | keep | 0 | Oct | 2021 | 0.0017102 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-10-15 11:59 | 2021-10-15 12:02 | 908 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1401-06 | S21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-15 | 2724 | keep | 0 | Oct | 2021 | 0.0018553 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
GUAYAMA | 2021-10-15 12:12 | 2021-10-15 12:42 | 6 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 5 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA | P21101500018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-10-15 | 180 | keep | 0 | Oct | 2021 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-15 12:13 | 2021-10-15 15:25 | 35 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101500046 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-10-15 | 6720 | keep | 0 | Oct | 2021 | 0.004577 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-10-15 12:16 | 2021-10-15 15:17 | 10 | 003:01 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE ELIMINO PARARRAYO | S21101500114 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 181 | 2021-10-15 | 1810 | keep | 0 | Oct | 2021 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-15 12:16 | 2021-10-15 12:17 | 23 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 23 | keep | 0 | Oct | 2021 | 1.5665e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 23
UTUADO | 2021-10-15 12:29 | 2021-10-15 14:05 | 180 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21101500042 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2021-10-15 | 17280 | keep | 0 | Oct | 2021 | 0.011769 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
ARECIBO | 2021-10-15 12:48 | 2021-10-15 12:49 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
AGUADILLA | 2021-10-15 12:52 | 2021-10-15 17:35 | 100 | 004:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERO CAJA PRIMARIA EN CORTE DE LINEA EN MALAS CONDICIONES NO SE REMPLAZO | M21101500051 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2021-10-15 | 28300 | keep | 0 | Oct | 2021 | 0.019275 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-10-15 12:57 | 2021-10-15 15:33 | 75 | 002:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R21101500083 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2021-10-15 | 11700 | keep | 0 | Oct | 2021 | 0.0079688 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-10-15 13:00 | 2021-10-15 14:34 | 150 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES EN CARR PR-834 RELACIONADO AL EVENTO S21101500076 | S21101500122 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-10-15 | 14100 | keep | 0 | Oct | 2021 | 0.0096034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-15 13:05 | 2021-10-15 20:02 | 70 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101500054 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2021-10-15 | 29190 | keep | 0 | Oct | 2021 | 0.019881 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-10-15 13:07 | 2021-10-15 13:08 | 3701 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21101500152 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-15 | 3701 | keep | 0 | Oct | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2021-10-15 13:08 | 2021-10-15 18:23 | 200 | 005:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C21101500069 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 315 | 2021-10-15 | 63000 | keep | 0 | Oct | 2021 | 0.042909 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-15 13:08 | 2021-10-15 13:55 | 75 | 000:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CAMION IMPACTO POSTE DE TELEFONO Y CRUZO LINEAS | A21101500046 | New_Event |  |  | Include | Wildlife | 47 | 2021-10-15 | 3525 | keep | 0 | Oct | 2021 | 0.0024009 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-10-15 13:11 | 2021-10-16 10:06 | 10 | 020:55 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21101500056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1255 | 2021-10-15 | 12550 | keep | 0 | Oct | 2021 | 0.0085477 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-15 13:12 | 2021-10-15 15:50 | 40 | 002:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21101500047 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2021-10-15 | 6320 | keep | 0 | Oct | 2021 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-15 13:12 | 2021-10-18 17:45 | 75 | 076:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21101500047 | New_Event | Wire Down | Include | Include | Equipment | 4593 | 2021-10-15 | 344475 | keep | 0 | Oct | 2021 | 0.23462 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 1565 | keep | 0 | Oct | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 976 | keep | 0 | Oct | 2021 | 0.00066475 | 0.00066475 | Momentary | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 548 | keep | 0 | Oct | 2021 | 0.00037324 | 0.00037324 | Momentary | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 315 | keep | 0 | Oct | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 870 | keep | 0 | Oct | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2906 | keep | 0 | Oct | 2021 | 0.0019793 | 0.0019793 | Momentary | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-10-15 13:16 | 2021-10-15 13:17 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2343 | keep | 0 | Oct | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 1565 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 29735 | keep | 0 | Oct | 2021 | 0.020252 | 0.0010659 | Sustained | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 976 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 18544 | keep | 0 | Oct | 2021 | 0.01263 | 0.00066475 | Sustained | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 548 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 10412 | keep | 0 | Oct | 2021 | 0.0070916 | 0.00037324 | Sustained | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 315 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 5985 | keep | 0 | Oct | 2021 | 0.0040764 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 870 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 16530 | keep | 0 | Oct | 2021 | 0.011259 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 2906 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 55214 | keep | 0 | Oct | 2021 | 0.037606 | 0.0019793 | Sustained | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-10-15 13:18 | 2021-10-15 13:37 | 2343 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2021-10-15 | 44517 | keep | 0 | Oct | 2021 | 0.03032 | 0.0015958 | Sustained | FALSE | TRUE | Not_TMED_Event | 2343
UTUADO | 2021-10-15 13:18 | 2021-10-15 13:20 | 934 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-15 | 1868 | keep | 0 | Oct | 2021 | 0.0012723 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
BARRANQUITAS | 2021-10-15 13:21 | 2021-10-15 13:22 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18400 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2410 | keep | 0 | Oct | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | TRUE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-10-15 13:21 | 2021-10-15 13:22 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18400 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2826 | keep | 0 | Oct | 2021 | 0.0019248 | 0.0019248 | Momentary | FALSE | TRUE | Not_TMED_Event | 2826
CAGUAS | 2021-10-15 13:25 | 2021-10-15 13:26 | 125 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101500172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 125 | keep | 0 | Oct | 2021 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2021-10-15 13:27 | 2021-10-15 13:28 | 1105 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21101500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-15 | 1105 | keep | 0 | Oct | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
CAGUAS | 2021-10-15 13:28 | 2021-10-15 16:52 | 95 | 003:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | C21101500173 | New_Event | Bad Weather | Include | Include | Weather | 204 | 2021-10-15 | 19380 | keep | 0 | Oct | 2021 | 0.0132 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-10-15 13:32 | 2021-10-16 09:56 | 300 | 020:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE Y SE ABRIO BREAKER 1901-05 QUE LLEVA EL 1901-04 PARA CERRAR PUENTE ABIERTO DEL TRONCAL | S21101500130 | New_Event | Wire Down | Include | Include | Equipment | 1224 | 2021-10-15 | 367200 | keep | 0 | Oct | 2021 | 0.2501 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-10-15 13:35 | 2021-10-15 14:22 | 9 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21101500190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-10-15 | 423 | keep | 0 | Oct | 2021 | 0.0002881 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2021-10-15 13:35 | 2021-10-15 16:27 | 80 | 002:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN BANCO DE TRANSFORMADOR | C21101500189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-10-15 | 13760 | keep | 0 | Oct | 2021 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-15 13:35 | 2021-10-15 16:05 | 14 | 002:30 | P | ESTRUCTURA AVERIADA | SE ABRE TRANSFORMADOR PARA PODER PASAR LINEA DE POSTE PARTIDO A POSTE EXISTENTE Y ASI ELIMINAR POSTE PARTIDO | P21101500022 | New_Event | Defective Pole | Include | Include | Equipment | 150 | 2021-10-15 | 2100 | keep | 0 | Oct | 2021 | 0.0014303 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
YAUCO | 2021-10-15 13:36 | 2021-10-16 16:43 | 80 | 027:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21101500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1627 | 2021-10-15 | 130160 | keep | 0 | Oct | 2021 | 0.088651 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-15 13:38 | 2021-10-15 17:21 | 2178 | 003:43 | T | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZO AISLADOR ROTO Y CERRO INTERRUPTOR | C21101500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 223 | 2021-10-15 | 485694 | keep | 0 | Oct | 2021 | 0.3308 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
ARECIBO | 2021-10-15 13:39 | 2021-10-15 18:01 | 7 | 004:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500051 | New_Event | Bad Weather | Include | Include | Weather | 262 | 2021-10-15 | 1834 | keep | 0 | Oct | 2021 | 0.0012491 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-15 13:44 | 2021-10-15 17:10 | 60 | 003:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-10-15 | 12360 | keep | 0 | Oct | 2021 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-15 13:46 | 2021-10-15 14:44 | 315 | 000:58 | T | DESGANCHE | DISPARO DEL 3603-01 LLEVANDO LA CARGA DEL 3604-06. SE ABRIO AMARRE 3603-01 Y 3604-06, TRANSFIRIENDO CARGA DEL 3604-06 AL 3603-03. | C21101500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-10-15 | 18270 | keep | 0 | Oct | 2021 | 0.012444 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2021-10-15 13:46 | 2021-10-15 14:43 | 2906 | 000:57 | T | DESGANCHE | DISPARO DEL 3603-01 LLEVANDO LA CARGA DEL 3604-06. SE ABRIO AMARRE 3603-01 Y 3604-06, TRANSFIRIENDO CARGA DEL 3604-06 AL 3603-03. | C21101500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-10-15 | 165642 | keep | 0 | Oct | 2021 | 0.11282 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
SAN JUAN | 2021-10-15 13:55 | 2021-10-15 13:56 | 36 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1620-04 LLEVANDO LA CARGA DEL 1620-01 | S21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 36 | keep | 0 | Oct | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-15 13:55 | 2021-10-15 13:56 | 172 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1620-01 | S21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 172 | keep | 0 | Oct | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BARRANQUITAS | 2021-10-15 13:55 | 2021-10-15 13:56 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 6500 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2635 | keep | 0 | Oct | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-10-15 13:55 | 2021-10-15 13:56 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 6500 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-10-15 13:55 | 2021-10-15 13:56 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 6500 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:23 | 137 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-15 | 3562 | keep | 0 | Oct | 2021 | 0.0024261 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:23 | 457 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-15 | 11882 | keep | 0 | Oct | 2021 | 0.0080928 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:23 | 1225 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-15 | 31850 | keep | 0 | Oct | 2021 | 0.021693 | 0.00083434 | Sustained | FALSE | TRUE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:23 | 1452 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-15 | 37752 | keep | 0 | Oct | 2021 | 0.025713 | 0.00098895 | Sustained | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:23 | 616 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-15 | 16016 | keep | 0 | Oct | 2021 | 0.010908 | 0.00041955 | Sustained | FALSE | TRUE | Not_TMED_Event | 616
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 16:37 | 3500 | 002:40 | P | LINEA DE TRANSMISION 38KV | EN DISPARO LINEA 3600 ABRIO INTERRUPTOR DE LA ALTA DE LA PORTATIL#22. LLEVA 40% 1204-3 Y 80% 1204-2 | S21101500281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 160 | 2021-10-15 | 560000 | keep | 0 | Oct | 2021 | 0.38141 | 0.0023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 3500
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 16:37 | 600 | 002:40 | P | LINEA DE TRANSMISION 38KV | EN DISPARO LINEA 3600 ABRIO INTERRUPTOR DE LA ALTA DE LA PORTATIL#22. LLEVA 40% 1204-3 Y 80% 1204-2 | S21101500281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 160 | 2021-10-15 | 96000 | keep | 0 | Oct | 2021 | 0.065385 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 108 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 3132 | keep | 0 | Oct | 2021 | 0.0021332 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 1368 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 39672 | keep | 0 | Oct | 2021 | 0.02702 | 0.00093174 | Sustained | FALSE | TRUE | Not_TMED_Event | 1368
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 2064 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 59856 | keep | 0 | Oct | 2021 | 0.040768 | 0.0014058 | Sustained | FALSE | TRUE | Not_TMED_Event | 2064
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 1681 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CARGA POR EL 1303-04 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 48749 | keep | 0 | Oct | 2021 | 0.033203 | 0.0011449 | Sustained | FALSE | TRUE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 2435 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 70615 | keep | 0 | Oct | 2021 | 0.048096 | 0.0016585 | Sustained | FALSE | TRUE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 726 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA EL 1346-04 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 21054 | keep | 0 | Oct | 2021 | 0.01434 | 0.00049448 | Sustained | FALSE | TRUE | Not_TMED_Event | 726
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 225 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 LLEVA LA CARGA DEL 1346-06 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 6525 | keep | 0 | Oct | 2021 | 0.0044441 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 870 | 000:29 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 25230 | keep | 0 | Oct | 2021 | 0.017184 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 3932 | 000:29 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CARGA POR EL 1303-03 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 114028 | keep | 0 | Oct | 2021 | 0.077664 | 0.0026781 | Sustained | FALSE | TRUE | Not_TMED_Event | 3932
SAN JUAN | 2021-10-15 13:57 | 2021-10-15 14:26 | 1598 | 000:29 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CARGA POR EL 1303-04 | S21101500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 29 | 2021-10-15 | 46342 | keep | 0 | Oct | 2021 | 0.031563 | 0.0010884 | Sustained | FALSE | TRUE | Not_TMED_Event | 1598
CAGUAS | 2021-10-15 13:58 | 2021-10-15 18:56 | 1510 | 004:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO INTERRUPTOR | C21101500209 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2021-10-15 | 449980 | keep | 0 | Oct | 2021 | 0.30648 | 0.0010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1510
AGUADILLA | 2021-10-15 14:00 | 2021-10-15 15:35 | 20 | 001:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CLIENTE CRUZO LINEAS CON RAMAS | M21101500076 | New_Event |  |  | Include | Wildlife | 95 | 2021-10-15 | 1900 | keep | 0 | Oct | 2021 | 0.0012941 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-10-15 14:02 | 2021-10-15 14:28 | 5 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21101500054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-10-15 | 130 | keep | 0 | Oct | 2021 | 8.8542e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-10-15 14:08 | 2021-10-15 14:09 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 6500 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2635 | keep | 0 | Oct | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-10-15 14:08 | 2021-10-15 14:09 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 6500 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-10-15 14:08 | 2021-10-15 14:09 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 6500 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-15 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
BAYAMON | 2021-10-15 14:10 | 2021-10-15 14:11 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 478 | keep | 0 | Oct | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-10-15 14:11 | 2021-10-15 15:43 | 478 | 001:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 92 | 2021-10-15 | 43976 | keep | 0 | Oct | 2021 | 0.029952 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-10-15 14:11 | 2021-10-15 15:43 | 679 | 001:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 92 | 2021-10-15 | 62468 | keep | 0 | Oct | 2021 | 0.042547 | 0.00046246 | Sustained | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2021-10-15 14:11 | 2021-10-15 15:43 | 949 | 001:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 92 | 2021-10-15 | 87308 | keep | 0 | Oct | 2021 | 0.059465 | 0.00064636 | Sustained | FALSE | FALSE | Not_TMED_Event | 949
BAYAMON | 2021-10-15 14:11 | 2021-10-15 15:43 | 67 | 001:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 92 | 2021-10-15 | 6164 | keep | 0 | Oct | 2021 | 0.0041983 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2021-10-15 14:11 | 2021-10-15 15:43 | 637 | 001:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 92 | 2021-10-15 | 58604 | keep | 0 | Oct | 2021 | 0.039915 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 959 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 137137 | keep | 0 | Oct | 2021 | 0.093403 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1382 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 197626 | keep | 0 | Oct | 2021 | 0.1346 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 663 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 94809 | keep | 0 | Oct | 2021 | 0.064574 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1715 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 245245 | keep | 0 | Oct | 2021 | 0.16704 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1498 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 214214 | keep | 0 | Oct | 2021 | 0.1459 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1221 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 174603 | keep | 0 | Oct | 2021 | 0.11892 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1100 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 157300 | keep | 0 | Oct | 2021 | 0.10714 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1514 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 216502 | keep | 0 | Oct | 2021 | 0.14746 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 1105 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 158015 | keep | 0 | Oct | 2021 | 0.10762 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 4176 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 597168 | keep | 0 | Oct | 2021 | 0.40673 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 252 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 36036 | keep | 0 | Oct | 2021 | 0.024544 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 2147 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 307021 | keep | 0 | Oct | 2021 | 0.20911 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-10-15 14:12 | 2021-10-15 16:35 | 2858 | 002:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV BAYAMON PUEBLO | B21101500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 143 | 2021-10-15 | 408694 | keep | 0 | Oct | 2021 | 0.27836 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
VEGA BAJA | 2021-10-15 14:19 | 2021-10-15 14:25 | 10 | 000:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-10-15 | 60 | keep | 0 | Oct | 2021 | 4.0866e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-15 14:20 | 2021-10-15 14:23 | 2704 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21101500074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-15 | 8112 | keep | 0 | Oct | 2021 | 0.005525 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
ARECIBO | 2021-10-15 14:21 | 2021-10-15 15:42 | 6 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101500055 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2021-10-15 | 486 | keep | 0 | Oct | 2021 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-10-15 14:22 | 2021-10-16 11:44 | 1 | 021:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | C21101500033 | New_Event | Bad Weather | Include | Include | Weather | 1282 | 2021-10-15 | 1282 | keep | 0 | Oct | 2021 | 0.00087316 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-15 14:26 | 2021-10-15 14:35 | 2435 | 000:09 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR SCADA LUEGO DE FUERTES LLUVIAS Y TRUENOS | S21101500104 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-10-15 | 21915 | keep | 0 | Oct | 2021 | 0.014926 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-10-15 14:26 | 2021-10-15 16:06 | 2234 | 001:40 | T | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE CERRO POR SCADA NO RTU EN SUBESTACION | B21101500204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-10-15 | 223400 | keep | 0 | Oct | 2021 | 0.15216 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
BARRANQUITAS | 2021-10-15 14:26 | 2021-10-15 14:27 | 2362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 2362 | keep | 0 | Oct | 2021 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
VEGA BAJA | 2021-10-15 14:27 | 2021-10-15 14:40 | 325 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | B21101500182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-10-15 | 4225 | keep | 0 | Oct | 2021 | 0.0028776 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
YAUCO | 2021-10-15 14:28 | 2021-10-15 16:38 | 96 | 002:10 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LINEA PRIMARIA | P21101500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-10-15 | 12480 | keep | 0 | Oct | 2021 | 0.0085001 | 6.5385e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 96
SAN JUAN | 2021-10-15 14:29 | 2021-10-15 16:51 | 2566 | 002:22 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES QUEMADOS EN SU-14 Y SE CERRO INTERRUPTOR | S21101500195 | New_Event | Switch Failure | Include | Include | Equipment | 142 | 2021-10-15 | 364372 | keep | 0 | Oct | 2021 | 0.24817 | 0.0017477 | Sustained | FALSE | FALSE | Not_TMED_Event | 2566
SAN JUAN | 2021-10-15 14:29 | 2021-10-15 14:33 | 2782 | 000:04 | T | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETES QUEMADOS EN EL SU-14 DEL 1111-01 QUE PASA JUNTO AL 1118-10 | S21101500195 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2021-10-15 | 11128 | keep | 0 | Oct | 2021 | 0.0075792 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
GUAYAMA | 2021-10-15 14:36 | 2021-10-15 20:50 | 8 | 006:14 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 2400 VOLTS | P21101500038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 374 | 2021-10-15 | 2992 | keep | 0 | Oct | 2021 | 0.0020378 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-10-15 14:36 | 2021-10-15 14:37 | 1604 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21101500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-15 | 1604 | keep | 0 | Oct | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-10-15 14:37 | 2021-10-15 20:50 | 502 | 006:13 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | C21101500235 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 373 | 2021-10-15 | 187246 | keep | 0 | Oct | 2021 | 0.12753 | 0.00034191 | Sustained | FALSE | TRUE | Not_TMED_Event | 502
BAYAMON | 2021-10-15 14:39 | 2021-10-17 15:57 | 10 | 049:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR 25 KVA | B21101500206 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2958 | 2021-10-15 | 29580 | keep | 0 | Oct | 2021 | 0.020147 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-15 14:40 | 2021-10-15 17:13 | 15 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500057 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-10-15 | 2295 | keep | 0 | Oct | 2021 | 0.0015631 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 99 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 3267 | keep | 0 | Oct | 2021 | 0.0022251 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 52 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 1716 | keep | 0 | Oct | 2021 | 0.0011688 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 32 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 1056 | keep | 0 | Oct | 2021 | 0.00071924 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 129 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 4257 | keep | 0 | Oct | 2021 | 0.0028994 | 8.7861e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 129
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 146 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 4818 | keep | 0 | Oct | 2021 | 0.0032815 | 9.944e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 146
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 69 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 2277 | keep | 0 | Oct | 2021 | 0.0015509 | 4.6996e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 69
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 15 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 495 | keep | 0 | Oct | 2021 | 0.00033714 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 132 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 4356 | keep | 0 | Oct | 2021 | 0.0029669 | 8.9905e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 132
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 1157 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 38181 | keep | 0 | Oct | 2021 | 0.026005 | 0.00078803 | Sustained | FALSE | TRUE | Not_TMED_Event | 1157
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 376 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 12408 | keep | 0 | Oct | 2021 | 0.008451 | 0.00025609 | Sustained | FALSE | TRUE | Not_TMED_Event | 376
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 1943 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 64119 | keep | 0 | Oct | 2021 | 0.043671 | 0.0013234 | Sustained | FALSE | TRUE | Not_TMED_Event | 1943
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 5 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 165 | keep | 0 | Oct | 2021 | 0.00011238 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 1024 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 33792 | keep | 0 | Oct | 2021 | 0.023016 | 0.00069744 | Sustained | FALSE | TRUE | Not_TMED_Event | 1024
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 19:09 | 1827 | 004:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 SE ENERGIZO A TRAVES DE LINEA 6000 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 268 | 2021-10-15 | 489636 | keep | 0 | Oct | 2021 | 0.33349 | 0.0012444 | Sustained | FALSE | TRUE | Not_TMED_Event | 1827
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 18:45 | 1047 | 004:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 SE ENERGIZO A TRAVES DE LINEA 6000 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 244 | 2021-10-15 | 255468 | keep | 0 | Oct | 2021 | 0.174 | 0.00071311 | Sustained | FALSE | TRUE | Not_TMED_Event | 1047
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 18:45 | 4882 | 004:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 SE ENERGIZO A TRAVES DE LINEA 6000 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 244 | 2021-10-15 | 1191208 | keep | 0 | Oct | 2021 | 0.81133 | 0.0033251 | Sustained | FALSE | TRUE | Not_TMED_Event | 4882
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 1485 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 49005 | keep | 0 | Oct | 2021 | 0.033377 | 0.0010114 | Sustained | FALSE | TRUE | Not_TMED_Event | 1485
AGUADILLA | 2021-10-15 14:41 | 2021-10-15 15:14 | 543 | 000:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 | M21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-15 | 17919 | keep | 0 | Oct | 2021 | 0.012205 | 0.00036983 | Sustained | FALSE | TRUE | Not_TMED_Event | 543
BARRANQUITAS | 2021-10-15 14:44 | 2021-10-15 14:53 | 1834 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21101500228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-10-15 | 16506 | keep | 0 | Oct | 2021 | 0.011242 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 1565 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 6260 | keep | 0 | Oct | 2021 | 0.0042637 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 976 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 3904 | keep | 0 | Oct | 2021 | 0.002659 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 548 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 2192 | keep | 0 | Oct | 2021 | 0.001493 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 315 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 1260 | keep | 0 | Oct | 2021 | 0.00085818 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 870 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 3480 | keep | 0 | Oct | 2021 | 0.0023702 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 2906 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 11624 | keep | 0 | Oct | 2021 | 0.0079171 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:44 | 2021-10-15 14:48 | 2343 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-15 | 9372 | keep | 0 | Oct | 2021 | 0.0063832 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 14:48 | 2021-10-17 12:45 | 21 | 045:57 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | C21101500231 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2757 | 2021-10-15 | 57897 | keep | 0 | Oct | 2021 | 0.039433 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CAGUAS | 2021-10-15 14:48 | 2021-10-15 14:58 | 315 | 000:10 | T | DESGANCHE | DISPARO DEL 3603-01 LLEVANDO LA CARGA DEL 3604-06. SE ABRIO AMARRE 3603-01 Y 3604-06, TRANSFIRIENDO CARGA DEL 3604-06 AL 3603-03. | C21101500000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 10 | 2021-10-15 | 3150 | keep | 0 | Oct | 2021 | 0.0021455 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-15 14:49 | 2021-10-15 17:40 | 37 | 002:51 | P | DESGANCHE | 1 X 65 1 X 80 EN CORTE DE LINEA | P21101500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-10-15 | 6327 | keep | 0 | Oct | 2021 | 0.0043093 | 2.5201e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 37
BARRANQUITAS | 2021-10-15 14:49 | 2021-10-15 17:52 | 328 | 003:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21101500223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-10-15 | 60024 | keep | 0 | Oct | 2021 | 0.040882 | 0.0002234 | Sustained | FALSE | TRUE | Not_TMED_Event | 328
BAYAMON | 2021-10-15 14:50 | 2021-10-15 14:51 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1709 01 | B21101500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 6136 | keep | 0 | Oct | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
ARECIBO | 2021-10-15 14:51 | 2021-10-15 15:35 | 15 | 000:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500059 | New_Event | Bad Weather | Include | Include | Weather | 44 | 2021-10-15 | 660 | keep | 0 | Oct | 2021 | 0.00044952 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-15 14:53 | 2021-10-15 16:52 | 271 | 001:59 | T | DESGANCHE | SE ABRIERON MACHETES EN AVE KENNEDY | S21101500217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-10-15 | 32249 | keep | 0 | Oct | 2021 | 0.021965 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
GUAYAMA | 2021-10-15 14:54 | 2021-10-15 16:53 | 11 | 001:59 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 2400VOLTS QUEMADO | P21101500041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 119 | 2021-10-15 | 1309 | keep | 0 | Oct | 2021 | 0.00089155 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-10-15 14:56 | 2021-10-15 14:57 | 1017 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101500240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 1017 | keep | 0 | Oct | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 1565 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 205015 | keep | 0 | Oct | 2021 | 0.13963 | 0.0010659 | Sustained | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 976 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 127856 | keep | 0 | Oct | 2021 | 0.087082 | 0.00066475 | Sustained | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 548 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 71788 | keep | 0 | Oct | 2021 | 0.048894 | 0.00037324 | Sustained | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 315 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 41265 | keep | 0 | Oct | 2021 | 0.028105 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 870 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 113970 | keep | 0 | Oct | 2021 | 0.077624 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 2906 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 380686 | keep | 0 | Oct | 2021 | 0.25928 | 0.0019793 | Sustained | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-10-15 14:58 | 2021-10-15 17:09 | 2343 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-15 | 306933 | keep | 0 | Oct | 2021 | 0.20905 | 0.0015958 | Sustained | FALSE | TRUE | Not_TMED_Event | 2343
BAYAMON | 2021-10-15 15:00 | 2021-10-15 18:05 | 10 | 003:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA Y CONEXIONES | S21101500231 | New_Event | Secondary Wire Down | Include | Include | Equipment | 185 | 2021-10-15 | 1850 | keep | 0 | Oct | 2021 | 0.00126 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-15 15:00 | 2021-10-15 19:08 | 15 | 004:08 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR ENEREDADERA | C21101500243 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 248 | 2021-10-15 | 3720 | keep | 0 | Oct | 2021 | 0.0025337 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-10-15 15:00 | 2021-10-16 13:46 | 55 | 022:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21101500242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1366 | 2021-10-15 | 75130 | keep | 0 | Oct | 2021 | 0.051171 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
ARECIBO | 2021-10-15 15:02 | 2021-10-15 16:16 | 25 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500060 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2021-10-15 | 1850 | keep | 0 | Oct | 2021 | 0.00126 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-15 15:07 | 2021-10-15 16:10 | 16 | 001:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BARRA EN PEDESTAL | R21101400199 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 63 | 2021-10-15 | 1008 | keep | 0 | Oct | 2021 | 0.00068654 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2021-10-15 15:11 | 2021-10-15 15:12 | 2782 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETES QUEMADOS EN EL SU-14 DEL 1111-01 QUE PASA JUNTO AL 1118-10 | S21101500195 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-10-15 | 2782 | keep | 0 | Oct | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
FAJARDO | 2021-10-15 15:14 | 2021-10-15 16:17 | 8 | 001:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21101500076 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 63 | 2021-10-15 | 504 | keep | 0 | Oct | 2021 | 0.00034327 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-10-15 15:17 | 2021-10-15 16:55 | 20 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BAJANTE SECUNDARIO | R21101500092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2021-10-15 | 1960 | keep | 0 | Oct | 2021 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-15 15:19 | 2021-10-15 16:28 | 7 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO TRANSFORMADOR | C21101500259 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-10-15 | 483 | keep | 0 | Oct | 2021 | 0.00032897 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-10-15 15:21 | 2021-10-15 19:05 | 19 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | R21101500095 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-10-15 | 4256 | keep | 0 | Oct | 2021 | 0.0028987 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
FAJARDO | 2021-10-15 15:25 | 2021-10-15 18:00 | 130 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y BAJANTE PRIMARIO | R21101500096 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2021-10-15 | 20150 | keep | 0 | Oct | 2021 | 0.013724 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-10-15 15:26 | 2021-10-16 01:18 | 80 | 009:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA | B21101500156 | New_Event | Cutout Failure | Include | Include | Equipment | 592 | 2021-10-15 | 47360 | keep | 0 | Oct | 2021 | 0.032257 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-15 15:30 | 2021-10-15 20:46 | 30 | 005:16 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTES DE LINEA | B21101500161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 316 | 2021-10-15 | 9480 | keep | 0 | Oct | 2021 | 0.0064568 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-15 15:37 | 2021-10-15 16:26 | 1 | 000:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21101500098 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 49 | 2021-10-15 | 49 | keep | 0 | Oct | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-15 15:39 | 2021-10-15 23:51 | 5 | 008:12 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101500065 | New_Event | Bad Weather | Include | Include | Weather | 492 | 2021-10-15 | 2460 | keep | 0 | Oct | 2021 | 0.0016755 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-15 15:40 | 2021-10-15 15:41 | 2782 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETES QUEMADOS EN EL SU-14 DEL 1111-01 QUE PASA JUNTO AL 1118-10 | S21101500195 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-10-15 | 2782 | keep | 0 | Oct | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2021-10-15 15:46 | 2021-10-15 18:14 | 7 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA LLUVIAS | R21101500099 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2021-10-15 | 1036 | keep | 0 | Oct | 2021 | 0.00070561 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
HUMACAO | 2021-10-15 15:52 | 2021-10-15 15:54 | 2450 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21101500292 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-15 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
AGUADILLA | 2021-10-15 15:52 | 2021-10-15 22:45 | 20 | 006:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101500143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2021-10-15 | 8260 | keep | 0 | Oct | 2021 | 0.0056258 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-15 15:55 | 2021-10-15 16:52 | 2 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101500140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-10-15 | 114 | keep | 0 | Oct | 2021 | 7.7645e-05 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
ARECIBO | 2021-10-15 15:56 | 2021-10-15 21:32 | 40 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A21101500066 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2021-10-15 | 13440 | keep | 0 | Oct | 2021 | 0.0091539 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-15 16:00 | 2021-10-15 16:01 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211015000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 3718 | keep | 0 | Oct | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2021-10-15 16:06 | 2021-10-16 13:56 | 25 | 021:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21101500168 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1310 | 2021-10-15 | 32750 | keep | 0 | Oct | 2021 | 0.022306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-15 16:08 | 2021-10-15 20:51 | 15 | 004:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA Y SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | A21101500067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 283 | 2021-10-15 | 4245 | keep | 0 | Oct | 2021 | 0.0028913 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-10-15 16:13 | 2021-10-15 17:51 | 64 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P21101500056 | New_Event |  |  | Include | Wildlife | 98 | 2021-10-15 | 6272 | keep | 0 | Oct | 2021 | 0.0042718 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
BAYAMON | 2021-10-15 16:35 | 2021-10-15 18:48 | 30 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B21101400107 | Partial_restoration | Wire Down | Include | Include | Equipment | 133 | 2021-10-15 | 3990 | keep | 0 | Oct | 2021 | 0.0027176 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-15 16:43 | 2021-10-16 12:46 | 60 | 020:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21101500220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1203 | 2021-10-15 | 72180 | keep | 0 | Oct | 2021 | 0.049161 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-10-15 16:50 | 2021-10-15 18:53 | 30 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500074 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2021-10-15 | 3690 | keep | 0 | Oct | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-15 16:51 | 2021-10-15 21:05 | 1500 | 004:14 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES QUEMADOS EN SU-14 Y SE CERRO EN MH-42 | S21101500195 | Partial_restoration | Switch Failure | Include | Include | Equipment | 254 | 2021-10-15 | 381000 | keep | 0 | Oct | 2021 | 0.2595 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-15 16:53 | 2021-10-15 16:55 | 2450 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21101500350 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-15 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-10-15 16:55 | 2021-10-15 20:43 | 77 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21101500394 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2021-10-15 | 17556 | keep | 0 | Oct | 2021 | 0.011957 | 5.2444e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 77
HUMACAO | 2021-10-15 17:02 | 2021-10-15 20:15 | 11 | 003:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21101500362 | New_Event |  |  | Include | Wildlife | 193 | 2021-10-15 | 2123 | keep | 0 | Oct | 2021 | 0.001446 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-10-15 17:09 | 2021-10-15 17:12 | 315 | 000:03 | T | DESGANCHE | DISPARO DEL 3603-01 LLEVANDO LA CARGA DEL 3604-06. SE ABRIO AMARRE 3603-01 Y 3604-06, TRANSFIRIENDO CARGA DEL 3604-06 AL 3603-03. | C21101500000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-10-15 | 945 | keep | 0 | Oct | 2021 | 0.00064364 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 3130 | keep | 0 | Oct | 2021 | 0.0021318 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 976 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 1952 | keep | 0 | Oct | 2021 | 0.0013295 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 548 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 1096 | keep | 0 | Oct | 2021 | 0.00074648 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 870 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 2906 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 5812 | keep | 0 | Oct | 2021 | 0.0039585 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-15 17:12 | 2021-10-15 17:14 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21101500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-15 | 4686 | keep | 0 | Oct | 2021 | 0.0031916 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-15 17:12 | 2021-10-15 18:00 | 80 | 000:48 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR RAMAS QUEMANDOSE SOBRE LAS LINEAS | M21101500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-10-15 | 3840 | keep | 0 | Oct | 2021 | 0.0026154 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-15 17:14 | 2021-10-15 20:20 | 88 | 003:06 | P | DESGANCHE | SE TRANSFIRIO PARTE DE LA CARGA AL 3602-02 SE SECCIONALIZO DESGANCHE CRITICO Y PUENTE ABIERTO | C21101500202 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-10-15 | 16368 | keep | 0 | Oct | 2021 | 0.011148 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
VEGA BAJA | 2021-10-15 17:37 | 2021-10-15 18:35 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B21101400100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-10-15 | 580 | keep | 0 | Oct | 2021 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-15 17:42 | 2021-10-15 17:43 | 5668 | 000:01 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA NORMALIZAR LAS CARGAS DEL 1646-01 MACHETES INCOMODOS PARA ABRIR CON CARGA | R21101500114 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-10-15 | 5668 | keep | 0 | Oct | 2021 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2021-10-15 17:42 | 2021-10-15 17:43 | 61 | 000:01 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA NORMALIZAR LAS CARGAS DEL 1646-01 MACHETES INCOMODOS PARA ABRIR CON CARGA | R21101500114 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-10-15 | 61 | keep | 0 | Oct | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
ARECIBO | 2021-10-15 17:47 | 2021-10-16 14:20 | 50 | 020:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A21101500079 | New_Event | Cutout Failure | Include | Include | Equipment | 1233 | 2021-10-15 | 61650 | keep | 0 | Oct | 2021 | 0.04199 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-10-15 17:48 | 2021-10-16 09:08 | 12 | 015:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21101500402 | New_Event | Bad Weather | Include | Include | Weather | 920 | 2021-10-15 | 11040 | keep | 0 | Oct | 2021 | 0.0075193 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-15 17:49 | 2021-10-15 18:20 | 30 | 000:31 | P | DESGANCHE | SE RETIRO RAMA SOBRE TRES FASES Y SE CERRARON MACHETES HACIA AMELIA INDUSTRIAL PARK | S21101500217 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 31 | 2021-10-15 | 930 | keep | 0 | Oct | 2021 | 0.00063342 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-10-15 17:50 | 2021-10-15 17:51 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211015000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 1475 | keep | 0 | Oct | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
FAJARDO | 2021-10-15 17:58 | 2021-10-15 18:19 | 1 | 000:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN BANCO DE TRANSFORMADORES LLUVIAS | R21101500118 | New_Event | Bad Weather | Include | Include | Weather | 21 | 2021-10-15 | 21 | keep | 0 | Oct | 2021 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-10-15 18:01 | 2021-10-15 18:02 | 1394 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R21101500096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-15 | 1394 | keep | 0 | Oct | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
BAYAMON | 2021-10-15 18:05 | 2021-10-16 12:26 | 60 | 018:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101500242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1101 | 2021-10-15 | 66060 | keep | 0 | Oct | 2021 | 0.044993 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-15 18:19 | 2021-10-16 17:38 | 10 | 023:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101500247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1399 | 2021-10-15 | 13990 | keep | 0 | Oct | 2021 | 0.0095285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-15 18:20 | 2021-10-15 23:02 | 164 | 004:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21101500305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2021-10-15 | 46248 | keep | 0 | Oct | 2021 | 0.031499 | 0.0001117 | Sustained | FALSE | TRUE | Not_TMED_Event | 164
ARECIBO | 2021-10-15 18:22 | 2021-10-16 12:30 | 25 | 018:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21101600081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1088 | 2021-10-15 | 27200 | keep | 0 | Oct | 2021 | 0.018526 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-15 18:26 | 2021-10-15 23:30 | 40 | 005:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101500190 | New_Event | Bad Weather | Include | Include | Weather | 304 | 2021-10-15 | 12160 | keep | 0 | Oct | 2021 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-15 18:26 | 2021-10-17 17:46 | 20 | 047:20 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE RETIRO PARARRAYO AVERIADO Y SE REALIZO DESGANCHE | B21101500250 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2840 | 2021-10-15 | 56800 | keep | 0 | Oct | 2021 | 0.038686 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-10-15 18:28 | 2021-10-16 10:33 | 8 | 016:05 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21101500429 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 965 | 2021-10-15 | 7720 | keep | 0 | Oct | 2021 | 0.0052581 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-15 18:29 | 2021-10-16 09:35 | 20 | 015:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21101500252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 906 | 2021-10-15 | 18120 | keep | 0 | Oct | 2021 | 0.012341 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-15 18:30 | 2021-10-15 19:31 | 130 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101500082 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2021-10-15 | 7930 | keep | 0 | Oct | 2021 | 0.0054011 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
SAN JUAN | 2021-10-15 18:33 | 2021-10-15 18:34 | 5290 | 000:01 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR PARA CORTAR PARTE DE POSTE QUE ESTA PEGADO Y QUEMANDO EL 13KV PERO NO ERA EL CORRECTO | S21101500000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-10-15 | 5290 | keep | 0 | Oct | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
UTUADO | 2021-10-15 18:38 | 2021-10-16 12:25 | 40 | 017:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101500085 | New_Event | Bad Weather | Include | Include | Weather | 1067 | 2021-10-15 | 42680 | keep | 0 | Oct | 2021 | 0.029069 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-15 18:38 | 2021-10-17 18:09 | 10 | 047:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR 25 KVA | B21101500255 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2851 | 2021-10-15 | 28510 | keep | 0 | Oct | 2021 | 0.019418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-15 18:46 | 2021-10-16 13:05 | 90 | 018:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21101500199 | New_Event | Bad Weather | Include | Include | Weather | 1099 | 2021-10-15 | 98910 | keep | 0 | Oct | 2021 | 0.067367 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-10-15 18:49 | 2021-10-16 10:11 | 30 | 015:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101500260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 922 | 2021-10-15 | 27660 | keep | 0 | Oct | 2021 | 0.018839 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-10-15 18:54 | 2021-10-16 01:19 | 10 | 006:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21101500440 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2021-10-15 | 3850 | keep | 0 | Oct | 2021 | 0.0026222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-15 18:56 | 2021-10-16 09:20 | 50 | 014:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-10 | S21101500314 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 864 | 2021-10-15 | 43200 | keep | 0 | Oct | 2021 | 0.029423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-10-15 19:02 | 2021-10-16 13:59 | 10 | 018:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | C21101500442 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1137 | 2021-10-15 | 11370 | keep | 0 | Oct | 2021 | 0.0077441 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-15 19:10 | 2021-10-15 22:48 | 130 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21101500444 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-10-15 | 28340 | keep | 0 | Oct | 2021 | 0.019302 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
YAUCO | 2021-10-15 19:12 | 2021-10-16 11:09 | 47 | 015:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101500074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 957 | 2021-10-15 | 44979 | keep | 0 | Oct | 2021 | 0.030635 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
VEGA BAJA | 2021-10-15 19:37 | 2021-10-15 22:17 | 158 | 002:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO NEUTRAL | B21101500273 | New_Event | Wire Down | Include | Include | Equipment | 160 | 2021-10-15 | 25280 | keep | 0 | Oct | 2021 | 0.017218 | 0.00010761 | Sustained | FALSE | TRUE | Not_TMED_Event | 158
BAYAMON | 2021-10-15 19:40 | 2021-10-17 10:50 | 7 | 039:10 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21101500275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2350 | 2021-10-15 | 16450 | keep | 0 | Oct | 2021 | 0.011204 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-10-15 19:50 | 2021-10-15 20:08 | 12 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21101500020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2021-10-15 | 216 | keep | 0 | Oct | 2021 | 0.00014712 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-10-15 19:57 | 2021-10-15 21:50 | 35 | 001:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA POR SITUACION DE PELIGRO PARA REPARAR DOS AISLADORES PARTIDOS | S21101500271 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2021-10-15 | 3955 | keep | 0 | Oct | 2021 | 0.0026937 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-10-15 19:57 | 2021-10-16 00:14 | 20 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101500092 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-10-15 | 5140 | keep | 0 | Oct | 2021 | 0.0035008 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-15 20:08 | 2021-10-16 11:59 | 4 | 015:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P21101500077 | New_Event | Wire Down | Include | Include | Equipment | 951 | 2021-10-15 | 3804 | keep | 0 | Oct | 2021 | 0.0025909 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
CANOVANAS | 2021-10-15 20:12 | 2021-10-15 22:37 | 300 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN CORTE DE LINEA LLUVIAS | R21101500125 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-10-15 | 43500 | keep | 0 | Oct | 2021 | 0.029628 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
VEGA BAJA | 2021-10-15 20:19 | 2021-10-16 11:45 | 80 | 015:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA Y SE LLEVO LINEA A AISLADOR Y SE REMPLAZO AISLADOR | B21101600010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 926 | 2021-10-15 | 74080 | keep | 0 | Oct | 2021 | 0.050456 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-10-15 20:38 | 2021-10-16 09:51 | 15 | 013:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21101500210 | New_Event | Bad Weather | Include | Include | Weather | 793 | 2021-10-15 | 11895 | keep | 0 | Oct | 2021 | 0.0081016 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-15 20:40 | 2021-10-15 21:18 | 50 | 000:38 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR PELIGRO. ARBOL PEGADO A LINEAS CAUSANDO CHISPAS Y FUEGO. | S21101500329 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-10-15 | 1900 | keep | 0 | Oct | 2021 | 0.0012941 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-15 21:14 | 2021-10-17 10:16 | 34 | 037:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO GANCHO DE LA LINEA | C21101500462 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2222 | 2021-10-15 | 75548 | keep | 0 | Oct | 2021 | 0.051455 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
UTUADO | 2021-10-15 21:17 | 2021-10-16 14:40 | 300 | 017:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES | A21101500093 | New_Event | Wire Down | Include | Include | Equipment | 1043 | 2021-10-15 | 312900 | keep | 0 | Oct | 2021 | 0.21311 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-10-15 21:23 | 2021-10-16 19:24 | 40 | 022:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR A 8 KV Y SE LEVANTO 2 CONDUCTORES DE 38KV | B21101500290 | New_Event | Wire Down | Include | Include | Equipment | 1321 | 2021-10-15 | 52840 | keep | 0 | Oct | 2021 | 0.035989 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-15 21:45 | 2021-10-16 11:24 | 60 | 013:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21101500470 | New_Event | Bad Weather | Include | Include | Weather | 819 | 2021-10-15 | 49140 | keep | 0 | Oct | 2021 | 0.033469 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-10-15 21:49 | 2021-10-16 08:42 | 200 | 010:53 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101500080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2021-10-15 | 130600 | keep | 0 | Oct | 2021 | 0.088951 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-10-15 21:50 | 2021-10-16 11:05 | 50 | 013:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21101500471 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 795 | 2021-10-15 | 39750 | keep | 0 | Oct | 2021 | 0.027074 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-15 22:04 | 2021-10-16 13:29 | 20 | 015:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21101500095 | New_Event | Bad Weather | Include | Include | Weather | 925 | 2021-10-15 | 18500 | keep | 0 | Oct | 2021 | 0.0126 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-15 22:22 | 2021-10-16 11:27 | 70 | 013:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C21101500477 | New_Event | Cutout Failure | Include | Include | Equipment | 785 | 2021-10-15 | 54950 | keep | 0 | Oct | 2021 | 0.037426 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-10-15 23:09 | 2021-10-16 12:13 | 1 | 013:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21101500483 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 784 | 2021-10-15 | 784 | keep | 0 | Oct | 2021 | 0.00053398 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-10-15 23:12 | 2021-10-16 10:54 | 100 | 011:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 50 EN CORTES DE LINEAS REEMPLAZO AISLADOR ROTO | C21101500484 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 702 | 2021-10-15 | 70200 | keep | 0 | Oct | 2021 | 0.047813 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-10-16 00:01 | 2021-10-16 15:13 | 80 | 015:12 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA | C21101600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 912 | 2021-10-16 | 72960 | keep | 0 | Oct | 2021 | 0.049693 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-10-16 01:19 | 2021-10-16 01:20 | 1131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101600000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 1131 | keep | 0 | Oct | 2021 | 0.00077032 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-16 01:20 | 2021-10-16 17:32 | 10 | 016:12 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21101500440 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 972 | 2021-10-16 | 9720 | keep | 0 | Oct | 2021 | 0.0066202 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-16 01:34 | 2021-10-16 01:35 | 1228 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21101600003 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-16 | 1228 | keep | 0 | Oct | 2021 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2021-10-16 01:35 | 2021-10-16 10:12 | 95 | 008:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21101600004 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 517 | 2021-10-16 | 49115 | keep | 0 | Oct | 2021 | 0.033452 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CAGUAS | 2021-10-16 02:06 | 2021-10-16 02:07 | 1702 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21101600000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-16 | 1702 | keep | 0 | Oct | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-10-16 02:07 | 2021-10-16 05:22 | 100 | 003:15 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C21101500010 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 195 | 2021-10-16 | 19500 | keep | 0 | Oct | 2021 | 0.013281 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-16 02:21 | 2021-10-16 02:22 | 10211 | 000:01 | T | DESGANCHE | RECERRO CARGA POR EL 1206-03 | S21101600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-16 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-16 02:21 | 2021-10-16 02:22 | 4133 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1204-05 | S21101600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-16 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-10-16 02:25 | 2021-10-16 12:56 | 10 | 010:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN AEREO PROVISIONAL | B21101600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 631 | 2021-10-16 | 6310 | keep | 0 | Oct | 2021 | 0.0042977 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-16 03:29 | 2021-10-16 16:46 | 80 | 013:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21101600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 797 | 2021-10-16 | 63760 | keep | 0 | Oct | 2021 | 0.043427 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-10-16 03:34 | 2021-10-16 17:56 | 50 | 014:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21101600008 | New_Event | Bad Weather | Include | Include | Weather | 862 | 2021-10-16 | 43100 | keep | 0 | Oct | 2021 | 0.029355 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-16 03:51 | 2021-10-16 11:25 | 200 | 007:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A21101600003 | New_Event | Cutout Failure | Include | Include | Equipment | 454 | 2021-10-16 | 90800 | keep | 0 | Oct | 2021 | 0.061843 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-16 04:40 | 2021-10-16 10:48 | 25 | 006:08 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M21101600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2021-10-16 | 9200 | keep | 0 | Oct | 2021 | 0.0062661 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-10-16 05:12 | 2021-10-16 09:09 | 30 | 003:57 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-10-16 | 7110 | keep | 0 | Oct | 2021 | 0.0048426 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-16 05:21 | 2021-10-16 09:30 | 300 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | M21101600006 | New_Event | Wire Down | Include | Include | Equipment | 249 | 2021-10-16 | 74700 | keep | 0 | Oct | 2021 | 0.050878 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-10-16 05:22 | 2021-10-16 05:23 | 1702 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21101600000 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-16 | 1702 | keep | 0 | Oct | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 05:23 | 2021-10-16 06:38 | 100 | 001:15 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C21101500010 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 75 | 2021-10-16 | 7500 | keep | 0 | Oct | 2021 | 0.0051082 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-16 05:28 | 2021-10-16 11:28 | 130 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 50 EN CORTES DE LINEAS MAL TIEMPO | C21101600012 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-10-16 | 46800 | keep | 0 | Oct | 2021 | 0.031875 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
HUMACAO | 2021-10-16 05:40 | 2021-10-16 05:41 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-10-16 05:40 | 2021-10-16 09:13 | 3025 | 003:33 | T | PARARRAYOS DEFECTUOSO | PARARRAYO AVERIADO EN BARRA DE INSPECCION DEL 2604-02. SE TRANSFIRIO CARGA AL 2604-03 | C21101600015 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 213 | 2021-10-16 | 644325 | keep | 0 | Oct | 2021 | 0.43885 | 0.0020603 | Sustained | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-10-16 05:40 | 2021-10-16 05:41 | 1593 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-10-16 05:41 | 2021-10-16 10:16 | 1 | 004:35 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE TRANSFORMADOR | C21101600056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 275 | 2021-10-16 | 275 | keep | 0 | Oct | 2021 | 0.0001873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-10-16 06:08 | 2021-10-16 12:06 | 70 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA NO FUNDIO FUSIBLE | R21101600008 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2021-10-16 | 25060 | keep | 0 | Oct | 2021 | 0.017068 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-10-16 06:09 | 2021-10-16 10:28 | 45 | 004:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21101600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2021-10-16 | 11655 | keep | 0 | Oct | 2021 | 0.0079382 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-10-16 06:11 | 2021-10-16 12:56 | 12 | 006:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE Y NEUTRAL SECUNDARIO EN VARIOS PUNTOS | R21101600014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 405 | 2021-10-16 | 4860 | keep | 0 | Oct | 2021 | 0.0033101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-10-16 06:16 | 2021-10-16 17:10 | 40 | 010:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 654 | 2021-10-16 | 26160 | keep | 0 | Oct | 2021 | 0.017817 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-16 06:22 | 2021-10-16 16:00 | 20 | 009:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 578 | 2021-10-16 | 11560 | keep | 0 | Oct | 2021 | 0.0078735 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-16 06:33 | 2021-10-16 13:28 | 210 | 006:55 | P | DESGANCHE | 2 X 50 Y 2 X 65 EN CORTES DE LINEAS | C21101600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2021-10-16 | 87150 | keep | 0 | Oct | 2021 | 0.059357 | 0.00014303 | Sustained | FALSE | TRUE | Not_TMED_Event | 210
CAGUAS | 2021-10-16 06:38 | 2021-10-16 06:39 | 1702 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21101600000 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-16 | 1702 | keep | 0 | Oct | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 06:39 | 2021-10-16 09:52 | 95 | 003:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21101600025 | New_Event |  |  | Include | Wildlife | 193 | 2021-10-16 | 18335 | keep | 0 | Oct | 2021 | 0.012488 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CAGUAS | 2021-10-16 06:39 | 2021-10-16 13:10 | 100 | 006:31 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C21101500010 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 391 | 2021-10-16 | 39100 | keep | 0 | Oct | 2021 | 0.026631 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-16 06:47 | 2021-10-16 06:48 | 676 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 676 | keep | 0 | Oct | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CANOVANAS | 2021-10-16 07:05 | 2021-10-16 09:40 | 90 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR IGUANA | R21101600010 | New_Event |  |  | Include | Wildlife | 155 | 2021-10-16 | 13950 | keep | 0 | Oct | 2021 | 0.0095013 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-16 07:10 | 2021-10-16 11:43 | 110 | 004:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R21101600011 | New_Event | Cutout Failure | Include | Include | Equipment | 273 | 2021-10-16 | 30030 | keep | 0 | Oct | 2021 | 0.020453 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
CAGUAS | 2021-10-16 07:17 | 2021-10-16 09:21 | 90 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21101600032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-10-16 | 11160 | keep | 0 | Oct | 2021 | 0.007601 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-16 07:19 | 2021-10-16 07:20 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
VEGA BAJA | 2021-10-16 07:25 | 2021-10-16 12:36 | 30 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-10-16 | 9330 | keep | 0 | Oct | 2021 | 0.0063546 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-16 07:34 | 2021-10-16 15:14 | 10 | 007:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 460 | 2021-10-16 | 4600 | keep | 0 | Oct | 2021 | 0.003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-16 07:37 | 2021-10-16 14:19 | 80 | 006:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE | C21101600037 | New_Event |  |  | Include | Wildlife | 402 | 2021-10-16 | 32160 | keep | 0 | Oct | 2021 | 0.021904 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-10-16 07:42 | 2021-10-16 08:52 | 150 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21101600003 | New_Event |  |  | Include | Wildlife | 70 | 2021-10-16 | 10500 | keep | 0 | Oct | 2021 | 0.0071515 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-16 07:43 | 2021-10-16 07:44 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 1097 | keep | 0 | Oct | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
ARECIBO | 2021-10-16 07:43 | 2021-10-16 10:38 | 100 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101600008 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2021-10-16 | 17500 | keep | 0 | Oct | 2021 | 0.011919 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-16 07:51 | 2021-10-16 13:36 | 20 | 005:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR CRUCE DE FASE PRIMARIA POR AVE | P21101600006 | New_Event |  |  | Include | Wildlife | 345 | 2021-10-16 | 6900 | keep | 0 | Oct | 2021 | 0.0046996 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-16 08:15 | 2021-10-16 11:47 | 22 | 003:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75KVA POR IGUAL CAPACIDAD | S21101500024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 212 | 2021-10-16 | 4664 | keep | 0 | Oct | 2021 | 0.0031766 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2021-10-16 08:18 | 2021-10-16 09:50 | 15 | 001:32 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO DOS PARARRAYOS AVERIADOS | P21101600010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 92 | 2021-10-16 | 1380 | keep | 0 | Oct | 2021 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-16 08:25 | 2021-10-16 08:26 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1303-04 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 225 | keep | 0 | Oct | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-16 08:25 | 2021-10-16 08:26 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1303-04 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 870 | keep | 0 | Oct | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2021-10-16 08:26 | 2021-10-16 12:19 | 658 | 003:53 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR POR CRUCE DE AVE EN MACHETES DE SALIDA EN SUBESTACION | P21101600004 | New_Event |  |  | Include | Wildlife | 233 | 2021-10-16 | 153314 | keep | 0 | Oct | 2021 | 0.10442 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
AGUADILLA | 2021-10-16 08:26 | 2021-10-16 18:05 | 1 | 009:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21101600028 | New_Event | Bad Weather | Include | Include | Weather | 579 | 2021-10-16 | 579 | keep | 0 | Oct | 2021 | 0.00039435 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-16 08:44 | 2021-10-16 18:29 | 15 | 009:45 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE | A21101600012 | New_Event | Defective Pole | Include | Include | Equipment | 585 | 2021-10-16 | 8775 | keep | 0 | Oct | 2021 | 0.0059766 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-10-16 08:45 | 2021-10-16 13:27 | 50 | 004:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101600019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2021-10-16 | 14100 | keep | 0 | Oct | 2021 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-16 08:47 | 2021-10-16 11:00 | 20 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER T-22 | R21101600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-10-16 | 2660 | keep | 0 | Oct | 2021 | 0.0018117 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-10-16 08:55 | 2021-10-16 15:27 | 50 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21101600015 | New_Event | Bad Weather | Include | Include | Weather | 392 | 2021-10-16 | 19600 | keep | 0 | Oct | 2021 | 0.013349 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-16 09:00 | 2021-10-16 18:30 | 200 | 009:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | M21101600035 | New_Event | Wire Down | Include | Include | Equipment | 570 | 2021-10-16 | 114000 | keep | 0 | Oct | 2021 | 0.077645 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-16 09:02 | 2021-10-16 16:14 | 10 | 007:12 | P | NO SE REPORTO CAUSA | 1 X 18 NX EN TRANSFORMADOR | R21101600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 432 | 2021-10-16 | 4320 | keep | 0 | Oct | 2021 | 0.0029423 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-16 09:05 | 2021-10-16 13:15 | 40 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21101600015 | New_Event |  |  | Include | Wildlife | 250 | 2021-10-16 | 10000 | keep | 0 | Oct | 2021 | 0.006811 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-16 09:12 | 2021-10-17 10:56 | 2 | 025:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21101600059 | New_Event | Bad Weather | Include | Include | Weather | 1544 | 2021-10-16 | 3088 | keep | 0 | Oct | 2021 | 0.0021032 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
PONCE | 2021-10-16 09:21 | 2021-10-16 15:25 | 101 | 006:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN SU-1 AVE CRUZO FASE | P21101600016 | New_Event |  |  | Include | Wildlife | 364 | 2021-10-16 | 36764 | keep | 0 | Oct | 2021 | 0.02504 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
MAYAGÃœEZ | 2021-10-16 09:27 | 2021-10-16 09:51 | 1666 | 000:24 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR EN MANIOBRAS DE AMARRE PARA TRANSFERIRLO AL 6702-02(SPARE) LO TRATO DE CERRALO NO CERRO SE REPORTO A RELES | M21101600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2021-10-16 | 39984 | keep | 0 | Oct | 2021 | 0.027233 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
CAGUAS | 2021-10-16 09:29 | 2021-10-17 19:05 | 20 | 033:36 | P | DESGANCHE | DESGANCHO LEVANTO CONDUCTOR Y CERRO PUENTE | C21101600064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2016 | 2021-10-16 | 40320 | keep | 0 | Oct | 2021 | 0.027462 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-16 09:45 | 2021-10-16 13:33 | 10 | 003:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21101500050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 228 | 2021-10-16 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-16 09:46 | 2021-10-16 15:47 | 30 | 006:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21101600021 | New_Event | Bad Weather | Include | Include | Weather | 361 | 2021-10-16 | 10830 | keep | 0 | Oct | 2021 | 0.0073763 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-16 09:56 | 2021-10-16 11:05 | 1264 | 001:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BREAKER 1901-05 QUE LLEVA EL 1901-04 PARA CERRAR PUENTE ABIERTO DEL TRONCAL | S21101500130 | Additional_clients | Wire Down | Include | Include | Equipment | 69 | 2021-10-16 | 87216 | keep | 0 | Oct | 2021 | 0.059402 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-16 09:56 | 2021-10-16 11:05 | 620 | 001:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BREAKER 1901-05 QUE LLEVA EL 1901-04 PARA CERRAR PUENTE ABIERTO DEL TRONCAL | S21101500130 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2021-10-16 | 42780 | keep | 0 | Oct | 2021 | 0.029137 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
YAUCO | 2021-10-16 09:58 | 2021-10-16 14:23 | 70 | 004:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER AVE CRUZO FASE | P21101600019 | New_Event |  |  | Include | Wildlife | 265 | 2021-10-16 | 18550 | keep | 0 | Oct | 2021 | 0.012634 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2021-10-16 09:59 | 2021-10-16 17:11 | 10 | 007:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA Y PARARRAYOS | B21101600034 | New_Event | Cutout Failure | Include | Include | Equipment | 432 | 2021-10-16 | 4320 | keep | 0 | Oct | 2021 | 0.0029423 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-16 10:00 | 2021-10-16 15:52 | 20 | 005:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21101600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-10-16 | 7040 | keep | 0 | Oct | 2021 | 0.0047949 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-10-16 10:04 | 2021-10-16 14:53 | 700 | 004:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRRUPTOR PARA CERRAR PUENTE EN TRONCAL DEL ALIMENTADOR | P21101600046 | New_Event | Wire Down | Include | Include | Equipment | 289 | 2021-10-16 | 202300 | keep | 0 | Oct | 2021 | 0.13779 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
AGUADILLA | 2021-10-16 10:06 | 2021-10-16 17:30 | 250 | 007:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21101600053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2021-10-16 | 111000 | keep | 0 | Oct | 2021 | 0.075602 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-10-16 10:18 | 2021-10-16 10:19 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-16 10:18 | 2021-10-16 10:19 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
ARECIBO | 2021-10-16 10:25 | 2021-10-16 13:40 | 1 | 003:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21101600023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-10-16 | 195 | keep | 0 | Oct | 2021 | 0.00013281 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-16 10:30 | 2021-10-16 19:17 | 150 | 008:47 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | M21101600057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 527 | 2021-10-16 | 79050 | keep | 0 | Oct | 2021 | 0.053841 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-16 10:31 | 2021-10-18 10:41 | 51 | 048:10 | P | NO SE REPORTO CAUSA | 1 X 100 CORTE DE LINEA | S21101600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2890 | 2021-10-16 | 147390 | keep | 0 | Oct | 2021 | 0.10039 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
SAN JUAN | 2021-10-16 10:47 | 2021-10-16 10:48 | 2179 | 000:01 | T | DESGANCHE | RECIERRE | R21101600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-16 | 2179 | keep | 0 | Oct | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2021-10-16 10:48 | 2021-10-16 20:20 | 30 | 009:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y REMPLAZO CAJA | R21101600074 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 572 | 2021-10-16 | 17160 | keep | 0 | Oct | 2021 | 0.011688 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-16 11:05 | 2021-10-16 17:02 | 10 | 005:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101600019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 357 | 2021-10-16 | 3570 | keep | 0 | Oct | 2021 | 0.0024315 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-16 11:09 | 2021-10-16 16:32 | 5 | 005:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21101600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 323 | 2021-10-16 | 1615 | keep | 0 | Oct | 2021 | 0.0011 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-10-16 11:14 | 2021-10-16 11:15 | 671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 671 | keep | 0 | Oct | 2021 | 0.00045702 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
SAN JUAN | 2021-10-16 11:18 | 2021-10-16 11:19 | 755 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1424-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1348-07 Y UN 80% 1348-6 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 755 | keep | 0 | Oct | 2021 | 0.00051423 | 0.00051423 | Momentary | FALSE | FALSE | Not_TMED_Event | 755
SAN JUAN | 2021-10-16 11:18 | 2021-10-16 11:19 | 278 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1424-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1348-07 Y UN 80% 1348-6 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 278 | keep | 0 | Oct | 2021 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-10-16 11:18 | 2021-10-16 11:19 | 9 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1424-08 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1348-07 Y UN 80% 1348-6 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 9 | keep | 0 | Oct | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-10-16 11:24 | 2021-10-16 13:05 | 996 | 001:41 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR EN OPERACIONES DE CAMPO | S21101600000 | New_Event | Human Error | Include | Include | Other | 101 | 2021-10-16 | 100596 | keep | 0 | Oct | 2021 | 0.068515 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2021-10-16 11:25 | 2021-10-16 17:33 | 10 | 006:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21101600059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 368 | 2021-10-16 | 3680 | keep | 0 | Oct | 2021 | 0.0025064 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-16 11:29 | 2021-10-16 16:24 | 10 | 004:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR MISMA CAPACIDAD | S21101600060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 295 | 2021-10-16 | 2950 | keep | 0 | Oct | 2021 | 0.0020092 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-16 11:33 | 2021-10-16 18:55 | 99 | 007:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21101600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2021-10-16 | 43758 | keep | 0 | Oct | 2021 | 0.029803 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
HUMACAO | 2021-10-16 11:40 | 2021-10-16 13:26 | 50 | 001:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21101600094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-10-16 | 5300 | keep | 0 | Oct | 2021 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-16 11:40 | 2021-10-16 15:24 | 7 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y TOMA | C21101600093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2021-10-16 | 1568 | keep | 0 | Oct | 2021 | 0.001068 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-10-16 11:51 | 2021-10-16 11:52 | 1437 | 000:01 | T | DESGANCHE | RECIERRE | C21101600096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-16 | 1437 | keep | 0 | Oct | 2021 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-10-16 11:52 | 2021-10-17 16:01 | 25 | 028:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101600101 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1689 | 2021-10-16 | 42225 | keep | 0 | Oct | 2021 | 0.028759 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-16 12:07 | 2021-10-17 12:05 | 150 | 023:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | M21101600068 | New_Event | Wire Down | Include | Include | Equipment | 1438 | 2021-10-16 | 215700 | keep | 0 | Oct | 2021 | 0.14691 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-10-16 12:16 | 2021-10-16 18:10 | 30 | 005:54 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21101600056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 354 | 2021-10-16 | 10620 | keep | 0 | Oct | 2021 | 0.0072332 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-16 12:29 | 2021-10-16 19:30 | 50 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR MAL TIEMPO | A21101600031 | New_Event | Bad Weather | Include | Include | Weather | 421 | 2021-10-16 | 21050 | keep | 0 | Oct | 2021 | 0.014337 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-10-16 12:56 | 2021-10-16 13:08 | 3 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-16 | 36 | keep | 0 | Oct | 2021 | 2.4519e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-10-16 12:56 | 2021-10-16 13:08 | 3957 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-16 | 47484 | keep | 0 | Oct | 2021 | 0.032341 | 0.0026951 | Sustained | FALSE | TRUE | Not_TMED_Event | 3957
BAYAMON | 2021-10-16 12:56 | 2021-10-16 13:08 | 58 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-16 | 696 | keep | 0 | Oct | 2021 | 0.00047404 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
SAN JUAN | 2021-10-16 12:56 | 2021-10-16 13:08 | 386 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-16 | 4632 | keep | 0 | Oct | 2021 | 0.0031548 | 0.0002629 | Sustained | FALSE | TRUE | Not_TMED_Event | 386
SAN JUAN | 2021-10-16 13:03 | 2021-10-16 17:48 | 12 | 004:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE Y NEUTRAL SECUNDARIO EN VARIOS PUNTOS | R21101600014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 285 | 2021-10-16 | 3420 | keep | 0 | Oct | 2021 | 0.0023293 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-16 13:06 | 2021-10-16 18:06 | 10 | 005:00 | P | NO SE REPORTO CAUSA | 1 X 10 EN AEREO PROVISIONAL | B21101600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2021-10-16 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-16 13:33 | 2021-10-17 11:47 | 70 | 022:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO NEUTRAL PARTIDO | P21101600042 | New_Event | Wire Down | Include | Include | Equipment | 1334 | 2021-10-16 | 93380 | keep | 0 | Oct | 2021 | 0.063601 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-10-16 13:39 | 2021-10-16 13:40 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO EL 1206-02 | S21101600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-16 13:39 | 2021-10-16 13:40 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO EL 1206-02 | S21101600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CAGUAS | 2021-10-16 13:46 | 2021-10-16 17:36 | 315 | 003:50 | T | DESGANCHE | DESGANCHO CERRO PUENTE RETEZO LINEA Y REMPLAZO AISLADOR | C21101600454 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-10-16 | 72450 | keep | 0 | Oct | 2021 | 0.049345 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 19:16 | 3500 | 005:26 | P | DESGANCHE | SE REALIZO DESGANCHE DE ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR 1204-02. SOLO ESTA LLEVANDO 80% DEL 1204-02 | S21101500281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-10-16 | 1141000 | keep | 0 | Oct | 2021 | 0.77713 | 0.0023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 3500
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 17:56 | 600 | 004:06 | P | DESGANCHE | DISPARO BAJA DE LA PORTATIL #22 POR ARBOL SOBRE EL 1204-02. SE DIVIDIO SU CARGA Y SE TIRO POR EL 1204-01. LLEVA 40% 1204-3 Y 80% 1204-2 | S21101500281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-10-16 | 147600 | keep | 0 | Oct | 2021 | 0.10053 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 14:18 | 1825 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 51100 | keep | 0 | Oct | 2021 | 0.034804 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 14:18 | 47 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 1316 | keep | 0 | Oct | 2021 | 0.00089632 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 14:18 | 315 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 8820 | keep | 0 | Oct | 2021 | 0.0060073 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 14:18 | 2 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 56 | keep | 0 | Oct | 2021 | 3.8141e-05 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-10-16 13:50 | 2021-10-16 14:18 | 2391 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 66948 | keep | 0 | Oct | 2021 | 0.045598 | 0.0016285 | Sustained | FALSE | TRUE | Not_TMED_Event | 2391
CAGUAS | 2021-10-16 13:50 | 2021-10-16 14:18 | 2276 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 63728 | keep | 0 | Oct | 2021 | 0.043405 | 0.0015502 | Sustained | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-10-16 13:50 | 2021-10-16 14:18 | 777 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 21756 | keep | 0 | Oct | 2021 | 0.014818 | 0.00052921 | Sustained | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-10-16 13:50 | 2021-10-16 14:18 | 12 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 336 | keep | 0 | Oct | 2021 | 0.00022885 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-10-16 13:50 | 2021-10-16 14:18 | 1290 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-10-16 | 36120 | keep | 0 | Oct | 2021 | 0.024601 | 0.00087861 | Sustained | FALSE | TRUE | Not_TMED_Event | 1290
SAN JUAN | 2021-10-16 13:51 | 2021-10-16 18:12 | 100 | 004:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21101600065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-10-16 | 26100 | keep | 0 | Oct | 2021 | 0.017777 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-16 13:55 | 2021-10-16 16:50 | 35 | 002:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21101600085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-10-16 | 6125 | keep | 0 | Oct | 2021 | 0.0041717 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-10-16 14:06 | 2021-10-16 14:07 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 176 | keep | 0 | Oct | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2021-10-16 14:09 | 2021-10-16 15:37 | 300 | 001:28 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO EN TRONCAL | B21101600085 | New_Event | Defective Pole | Include | Include | Equipment | 88 | 2021-10-16 | 26400 | keep | 0 | Oct | 2021 | 0.017981 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-16 14:10 | 2021-10-16 15:44 | 1 | 001:34 | T | DESGANCHE | INTERRUPTOR 1346-01 QUE ESTA POR PORTATIL #19 LLEVANDO LA CARGA DEL 1346-01, 1346-03, 60% DEL 1346-02 Y 80% DEL 1908-05. SE IDENTIFICIO BAMBUA SOBRE EL 1908-03 Y SE CERRO 1346-01. | S21101600221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-10-16 | 94 | keep | 0 | Oct | 2021 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-16 14:10 | 2021-10-16 15:44 | 1844 | 001:34 | T | DESGANCHE | INTERRUPTOR 1346-01 QUE ESTA POR PORTATIL #19 LLEVANDO LA CARGA DEL 1346-01, 1346-03, 60% DEL 1346-02 Y 80% DEL 1908-05. SE IDENTIFICIO BAMBUA SOBRE EL 1908-03 Y SE CERRO 1346-01. | S21101600221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-10-16 | 173336 | keep | 0 | Oct | 2021 | 0.11806 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2021-10-16 14:10 | 2021-10-16 15:44 | 2422 | 001:34 | S | DESGANCHE | INTERRUPTOR 1346-01 QUE ESTA POR PORTATIL #19 LLEVANDO LA CARGA DEL 1346-01, 1346-03, 60% DEL 1346-02 Y 80% DEL 1908-05. SE IDENTIFICIO BAMBUA SOBRE EL 1908-03 Y SE CERRO 1346-01. | S21101600221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-10-16 | 227668 | keep | 0 | Oct | 2021 | 0.15506 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
SAN JUAN | 2021-10-16 14:10 | 2021-10-16 15:44 | 3165 | 001:34 | P | DESGANCHE | 80% DE SU CARGA A TRAVES DE LA PORTATIL #19 1346-00 AFECTANDOSE POR BAMBUA SOBRE LINEA | S21101600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-10-16 | 297510 | keep | 0 | Oct | 2021 | 0.20263 | 0.0021557 | Sustained | FALSE | TRUE | Not_TMED_Event | 3165
SAN JUAN | 2021-10-16 14:18 | 2021-10-16 16:38 | 200 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA Y 1 X 80 EN OTRO CORTE DE LINEA. FUERTES LLUVIAS Y RAYOS | S21101600059 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-10-16 | 28000 | keep | 0 | Oct | 2021 | 0.019071 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-10-16 14:18 | 2021-10-16 17:13 | 1 | 002:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21101400059 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 175 | 2021-10-16 | 175 | keep | 0 | Oct | 2021 | 0.00011919 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
FAJARDO | 2021-10-16 14:19 | 2021-10-16 15:29 | 6 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | R21101600070 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2021-10-16 | 420 | keep | 0 | Oct | 2021 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-10-16 14:20 | 2021-10-16 14:21 | 2468 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 2468 | keep | 0 | Oct | 2021 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
CANOVANAS | 2021-10-16 14:28 | 2021-10-16 14:29 | 635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 635 | keep | 0 | Oct | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
ARECIBO | 2021-10-16 14:30 | 2021-10-16 16:45 | 9 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONECTORES | A21101600021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2021-10-16 | 1215 | keep | 0 | Oct | 2021 | 0.00082753 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-10-16 14:34 | 2021-10-16 19:42 | 30 | 005:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101600090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2021-10-16 | 9240 | keep | 0 | Oct | 2021 | 0.0062933 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-16 14:35 | 2021-10-16 18:16 | 60 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA FUERTES LLUVIAS Y RAYOS | S21101600189 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2021-10-16 | 13260 | keep | 0 | Oct | 2021 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-16 14:39 | 2021-10-16 20:32 | 50 | 005:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101600192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2021-10-16 | 17650 | keep | 0 | Oct | 2021 | 0.012021 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-16 14:43 | 2021-10-16 18:39 | 30 | 003:56 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA DESGANCHE | A21101600040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2021-10-16 | 7080 | keep | 0 | Oct | 2021 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-16 14:49 | 2021-10-16 20:46 | 30 | 005:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA | C21101600131 | New_Event | Wire Down | Include | Include | Equipment | 357 | 2021-10-16 | 10710 | keep | 0 | Oct | 2021 | 0.0072945 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-10-16 14:53 | 2021-10-16 15:32 | 2309 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRRUPTOR PARA CERRAR PUENTE EN TRONCAL DEL ALIMENTADOR | P21101600046 | Additional_clients | Wire Down | Include | Include | Equipment | 39 | 2021-10-16 | 90051 | keep | 0 | Oct | 2021 | 0.061333 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-16 15:01 | 2021-10-16 16:33 | 934 | 001:32 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 92 | 2021-10-16 | 85928 | keep | 0 | Oct | 2021 | 0.058525 | 0.00063614 | Sustained | FALSE | TRUE | Not_TMED_Event | 934
UTUADO | 2021-10-16 15:01 | 2021-10-16 16:33 | 4 | 001:32 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 92 | 2021-10-16 | 368 | keep | 0 | Oct | 2021 | 0.00025064 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-10-16 15:01 | 2021-10-16 16:33 | 1479 | 001:32 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 92 | 2021-10-16 | 136068 | keep | 0 | Oct | 2021 | 0.092675 | 0.0010073 | Sustained | FALSE | TRUE | Not_TMED_Event | 1479
UTUADO | 2021-10-16 15:01 | 2021-10-16 16:33 | 1841 | 001:32 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 92 | 2021-10-16 | 169372 | keep | 0 | Oct | 2021 | 0.11536 | 0.0012539 | Sustained | FALSE | TRUE | Not_TMED_Event | 1841
UTUADO | 2021-10-16 15:01 | 2021-10-16 16:33 | 1950 | 001:32 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A21101600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 92 | 2021-10-16 | 179400 | keep | 0 | Oct | 2021 | 0.12219 | 0.0013281 | Sustained | FALSE | TRUE | Not_TMED_Event | 1950
ARECIBO | 2021-10-16 15:04 | 2021-10-16 20:50 | 150 | 005:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21101600043 | New_Event | Bad Weather | Include | Include | Weather | 346 | 2021-10-16 | 51900 | keep | 0 | Oct | 2021 | 0.035349 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-16 15:06 | 2021-10-16 17:18 | 50 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PERSONAS DESGANCHANDO | R21101600075 | New_Event |  |  | Include | Wildlife | 132 | 2021-10-16 | 6600 | keep | 0 | Oct | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-16 15:14 | 2021-10-16 18:45 | 40 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CONVERTIDOR SE REPARARO BAJANTES DE SALIDA | A21101600049 | New_Event | Wire Down | Include | Include | Equipment | 211 | 2021-10-16 | 8440 | keep | 0 | Oct | 2021 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-16 15:15 | 2021-10-16 17:50 | 40 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE SOLTARON LINEAS CRUZADAS | M21101600091 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2021-10-16 | 6200 | keep | 0 | Oct | 2021 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-16 15:22 | 2021-10-16 17:44 | 200 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21101600049 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-10-16 | 28400 | keep | 0 | Oct | 2021 | 0.019343 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-16 15:29 | 2021-10-16 17:40 | 20 | 002:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZARON AISLADORES | A21101600055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2021-10-16 | 2620 | keep | 0 | Oct | 2021 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-16 15:31 | 2021-10-16 19:00 | 40 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESGANCHO PARA REPARAR LINEA PRIMARIA Y SE INSTALO CAJA PRIMARIA | A21101600056 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2021-10-16 | 8360 | keep | 0 | Oct | 2021 | 0.005694 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-16 15:37 | 2021-10-16 20:34 | 2700 | 004:57 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO EN TRONCAL | B21101600097 | Additional_clients | Defective Pole | Include | Include | Equipment | 297 | 2021-10-16 | 801900 | keep | 0 | Oct | 2021 | 0.54617 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-16 15:40 | 2021-10-16 15:41 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211016000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 527 | keep | 0 | Oct | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2021-10-16 15:50 | 2021-10-16 18:02 | 1058 | 002:12 | P | NO SE REPORTO CAUSA | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO AUTORIZADO POR LUIS MIRANDA. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-10-16 | 139656 | keep | 0 | Oct | 2021 | 0.095119 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2021-10-16 15:50 | 2021-10-16 18:02 | 300 | 002:12 | P | NO SE REPORTO CAUSA | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO AUTORIZADO POR LUIS MIRANDA. 20% DE SU CARGA POR PORTATIL | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-10-16 | 39600 | keep | 0 | Oct | 2021 | 0.026971 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-16 15:50 | 2021-10-16 18:02 | 1290 | 002:12 | S | NO SE REPORTO CAUSA | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO AUTORIZADO POR LUIS MIRANDA. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-10-16 | 170280 | keep | 0 | Oct | 2021 | 0.11598 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
MAYAGÃœEZ | 2021-10-16 16:16 | 2021-10-17 14:35 | 10 | 022:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21101600111 | New_Event | Bad Weather | Include | Include | Weather | 1339 | 2021-10-16 | 13390 | keep | 0 | Oct | 2021 | 0.0091199 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-16 16:33 | 2021-10-16 18:14 | 10 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES Y SECUNDARIA | S21101600024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-10-16 | 1010 | keep | 0 | Oct | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-16 16:45 | 2021-10-16 18:10 | 600 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO MACHETES DEL 1303-01 PARA REEMPALZAR CAJA QUEMADA YA QUE FUE A ESCALERA Y NO OFRECIA SEGURIDAD Y EL TRABAJO ERA COMPLICADO. EL GOI AFECTO LA CARGA TOTAL DEL 1346-06 | S21101600064 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2021-10-16 | 51000 | keep | 0 | Oct | 2021 | 0.034736 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-10-16 16:45 | 2021-10-16 18:10 | 1598 | 001:25 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO MACHETES DEL 1303-01 PARA REEMPLAZAR CAJA QUEMADA YA QUE FUE A ESCALERA Y NO OFRECIA SEGURIDAD Y EL TRABAJO ERA COMPLICADO. EL GOI AFECTO LA CARGA TOTAL DEL 1346-06. CARGA POR EL 1303-01 | S21101600064 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2021-10-16 | 135830 | keep | 0 | Oct | 2021 | 0.092513 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2021-10-16 16:53 | 2021-10-16 20:30 | 179 | 003:37 | T | DESGANCHE | SE RETIRO RAMA CRUZANDO FASES | M21101600123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-10-16 | 38843 | keep | 0 | Oct | 2021 | 0.026456 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
VEGA BAJA | 2021-10-16 16:55 | 2021-10-17 11:12 | 4 | 018:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21101600108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1097 | 2021-10-16 | 4388 | keep | 0 | Oct | 2021 | 0.0029886 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-10-16 17:04 | 2021-10-16 20:28 | 15 | 003:24 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | A21101600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-10-16 | 3060 | keep | 0 | Oct | 2021 | 0.0020842 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-16 17:13 | 2021-10-16 17:17 | 1825 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-16 | 7300 | keep | 0 | Oct | 2021 | 0.004972 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-16 17:13 | 2021-10-16 17:17 | 47 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-16 | 188 | keep | 0 | Oct | 2021 | 0.00012805 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-16 17:13 | 2021-10-16 17:17 | 315 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-16 | 1260 | keep | 0 | Oct | 2021 | 0.00085818 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-16 17:13 | 2021-10-16 17:17 | 2 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-16 | 8 | keep | 0 | Oct | 2021 | 5.4488e-06 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-16 17:13 | 2021-10-16 17:17 | 2391 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-16 | 9564 | keep | 0 | Oct | 2021 | 0.006514 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 17:13 | 2021-10-16 17:18 | 2276 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-16 | 11380 | keep | 0 | Oct | 2021 | 0.0077509 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 17:13 | 2021-10-16 17:18 | 777 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-16 | 3885 | keep | 0 | Oct | 2021 | 0.0026461 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 17:13 | 2021-10-16 17:18 | 12 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-16 | 60 | keep | 0 | Oct | 2021 | 4.0866e-05 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 17:13 | 2021-10-16 17:18 | 1290 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-16 | 6450 | keep | 0 | Oct | 2021 | 0.0043931 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 17:18 | 2021-10-26 14:44 | 1 | 237:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21101400059 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 14246 | 2021-10-16 | 14246 | keep | 0 | Oct | 2021 | 0.0097029 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-16 17:36 | 2021-10-16 18:17 | 14 | 000:41 | P | DESGANCHE | DESGANCHO CERRO PUENTE RETEZO LINEA Y REMPLAZO AISLADOR | C21101500454 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-10-16 | 574 | keep | 0 | Oct | 2021 | 0.00039095 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-10-16 17:36 | 2021-10-17 14:15 | 4 | 020:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21101600074 | New_Event | Bad Weather | Include | Include | Weather | 1239 | 2021-10-16 | 4956 | keep | 0 | Oct | 2021 | 0.0033755 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-10-16 17:37 | 2021-10-17 10:21 | 25 | 016:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | B21101600115 | New_Event |  |  | Include | Wildlife | 1004 | 2021-10-16 | 25100 | keep | 0 | Oct | 2021 | 0.017095 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-10-16 17:38 | 2021-10-17 12:25 | 8 | 018:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA | A21101600075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1127 | 2021-10-16 | 9016 | keep | 0 | Oct | 2021 | 0.0061408 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-16 17:41 | 2021-10-16 17:52 | 1 | 000:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21101600110 | New_Event | Cutout Failure | Include | Include | Equipment | 11 | 2021-10-16 | 11 | keep | 0 | Oct | 2021 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-10-16 17:42 | 2021-10-17 16:20 | 10 | 022:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA | A21101600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1358 | 2021-10-16 | 13580 | keep | 0 | Oct | 2021 | 0.0092493 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-10-16 17:43 | 2021-10-17 09:25 | 1 | 015:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21101600085 | New_Event |  |  | Include | Wildlife | 942 | 2021-10-16 | 942 | keep | 0 | Oct | 2021 | 0.00064159 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-16 17:47 | 2021-10-16 17:48 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101600060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 732 | keep | 0 | Oct | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
ARECIBO | 2021-10-16 18:03 | 2021-10-16 21:41 | 1 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21101600080 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-10-16 | 218 | keep | 0 | Oct | 2021 | 0.00014848 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 574 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 58548 | keep | 0 | Oct | 2021 | 0.039877 | 0.00039095 | Sustained | FALSE | TRUE | Not_TMED_Event | 574
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 2493 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 254286 | keep | 0 | Oct | 2021 | 0.17319 | 0.001698 | Sustained | FALSE | TRUE | Not_TMED_Event | 2493
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 1415 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 144330 | keep | 0 | Oct | 2021 | 0.098303 | 0.00096375 | Sustained | FALSE | TRUE | Not_TMED_Event | 1415
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 1428 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 145656 | keep | 0 | Oct | 2021 | 0.099206 | 0.0009726 | Sustained | FALSE | TRUE | Not_TMED_Event | 1428
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 1036 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 105672 | keep | 0 | Oct | 2021 | 0.071973 | 0.00070561 | Sustained | FALSE | TRUE | Not_TMED_Event | 1036
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 382 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 38964 | keep | 0 | Oct | 2021 | 0.026538 | 0.00026018 | Sustained | FALSE | TRUE | Not_TMED_Event | 382
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 39 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 3978 | keep | 0 | Oct | 2021 | 0.0027094 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 2366 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 241332 | keep | 0 | Oct | 2021 | 0.16437 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-10-16 18:09 | 2021-10-16 19:51 | 1337 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 136374 | keep | 0 | Oct | 2021 | 0.092884 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
AGUADILLA | 2021-10-16 18:09 | 2021-10-16 19:51 | 709 | 001:42 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21101600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-10-16 | 72318 | keep | 0 | Oct | 2021 | 0.049255 | 0.0004829 | Sustained | FALSE | TRUE | Not_TMED_Event | 709
CAGUAS | 2021-10-16 18:36 | 2021-10-17 17:13 | 100 | 022:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA Y CERRO PUENTE | C21101600164 | New_Event | Wire Down | Include | Include | Equipment | 1357 | 2021-10-16 | 135700 | keep | 0 | Oct | 2021 | 0.092425 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-16 18:36 | 2021-10-17 12:13 | 125 | 017:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21101600164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1057 | 2021-10-16 | 132125 | keep | 0 | Oct | 2021 | 0.08999 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
HUMACAO | 2021-10-16 19:06 | 2021-10-17 10:21 | 1 | 015:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21101600168 | New_Event | Bad Weather | Include | Include | Weather | 915 | 2021-10-16 | 915 | keep | 0 | Oct | 2021 | 0.0006232 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-10-16 19:23 | 2021-10-17 08:58 | 100 | 013:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21101600088 | New_Event |  |  | Include | Wildlife | 815 | 2021-10-16 | 81500 | keep | 0 | Oct | 2021 | 0.055509 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-16 19:25 | 2021-10-17 00:05 | 60 | 004:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | M21101600236 | New_Event | Cutout Failure | Include | Include | Equipment | 280 | 2021-10-16 | 16800 | keep | 0 | Oct | 2021 | 0.011442 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-16 19:29 | 2021-10-16 19:41 | 3500 | 000:12 | P | DESGANCHE | SE ABRIO ALIMENTADOR POR AISLADOR PARTIDO EN LA SALIDA. SE RELAIZO GOI Y SE CERRO INTERRUPTOR. SOLO ESTA LLEVANDO 80% DEL 1204-02 | S21101500281 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 12 | 2021-10-16 | 42000 | keep | 0 | Oct | 2021 | 0.028606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-16 19:44 | 2021-10-17 09:49 | 200 | 014:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21101600085 | New_Event | Bad Weather | Include | Include | Weather | 845 | 2021-10-16 | 169000 | keep | 0 | Oct | 2021 | 0.11511 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-16 20:15 | 2021-10-16 20:16 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 Y SE CERRO POR CONTROL | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 922 | keep | 0 | Oct | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-10-16 20:15 | 2021-10-16 20:16 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 Y SE CERRO POR CONTROL | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-16 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
UTUADO | 2021-10-16 20:28 | 2021-10-16 21:20 | 50 | 000:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21101600087 | New_Event | Bad Weather | Include | Include | Weather | 52 | 2021-10-16 | 2600 | keep | 0 | Oct | 2021 | 0.0017708 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-16 20:35 | 2021-10-17 11:50 | 1 | 015:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21101600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 915 | 2021-10-16 | 915 | keep | 0 | Oct | 2021 | 0.0006232 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-16 20:36 | 2021-10-17 12:54 | 65 | 016:18 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21101600462 | New_Event | Vegetation Contact | Include | Include | Vegetation | 978 | 2021-10-16 | 63570 | keep | 0 | Oct | 2021 | 0.043297 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
FAJARDO | 2021-10-16 20:42 | 2021-10-17 12:49 | 10 | 016:07 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | R21101600090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 967 | 2021-10-16 | 9670 | keep | 0 | Oct | 2021 | 0.0065862 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-10-16 20:57 | 2021-10-17 11:28 | 4 | 014:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL | R21101600091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 871 | 2021-10-16 | 3484 | keep | 0 | Oct | 2021 | 0.0023729 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-16 21:23 | 2021-10-16 21:25 | 315 | 000:02 | T | DESCONECTIVO DEFECTUOSO | MACHETE AVERIADO EN OPERACIONES PARA AMARRAR LA CARGA 4KV CONTRA EL 1343-03 DESPUES DEL CONVERTIDOR QUEMADO DEL 1908-03. SE ABRIO AMARRE NUEVAMENTE Y SE CERRO INTERRUPTOR | S21101600000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-10-16 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2021-10-16 21:29 | 2021-10-17 10:59 | 433 | 013:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21101600193 | New_Event | Cutout Failure | Include | Include | Equipment | 810 | 2021-10-16 | 350730 | keep | 0 | Oct | 2021 | 0.23888 | 0.00029491 | Sustained | FALSE | TRUE | Not_TMED_Event | 433
BAYAMON | 2021-10-16 22:21 | 2021-10-16 22:26 | 2422 | 000:05 | P | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF CARGA POR EL 1907-04 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-16 | 12110 | keep | 0 | Oct | 2021 | 0.0082481 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2021-10-16 22:21 | 2021-10-16 22:26 | 2466 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF LLEVA PARTE 1346-03 | S21101600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-16 | 12330 | keep | 0 | Oct | 2021 | 0.0083979 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
PONCE | 2021-10-16 22:30 | 2021-10-16 23:30 | 371 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PRIMARIO PARTIDO POR ACCIDENTE DE AUTO SE ABREN MACHETES PARA ELIMINAR POSTE PRIMARIO | P21101600070 | New_Event |  |  | Include | Wildlife | 60 | 2021-10-16 | 22260 | keep | 0 | Oct | 2021 | 0.015161 | 0.00025269 | Sustained | FALSE | FALSE | Not_TMED_Event | 371
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 574 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 574 | keep | 0 | Oct | 2021 | 0.00039095 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 2493 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 2493 | keep | 0 | Oct | 2021 | 0.001698 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 1415 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 1415 | keep | 0 | Oct | 2021 | 0.00096375 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 1428 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 1428 | keep | 0 | Oct | 2021 | 0.0009726 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 1036 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 1036 | keep | 0 | Oct | 2021 | 0.00070561 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 382 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 382 | keep | 0 | Oct | 2021 | 0.00026018 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 39 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 39 | keep | 0 | Oct | 2021 | 2.6563e-05 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 2366 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 2366 | keep | 0 | Oct | 2021 | 0.0016115 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-16 23:21 | 2021-10-16 23:22 | 1337 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 1337 | keep | 0 | Oct | 2021 | 0.00091062 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-16 23:21 | 2021-10-16 23:22 | 709 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21101600000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-16 | 709 | keep | 0 | Oct | 2021 | 0.0004829 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-17 00:45 | 2021-10-19 22:51 | 1 | 070:06 | P | ESTRUCTURA AVERIADA | REEMPLAZO POSTE PRIMARIAO ROTO Y CERRO PUENTE | C21101700004 | New_Event | Defective Pole | Include | Include | Equipment | 4206 | 2021-10-17 | 4206 | keep | 0 | Oct | 2021 | 0.0028647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-17 00:55 | 2021-10-17 02:19 | 1 | 001:24 | T | NO SE REPORTO CAUSA | DISPARO BKR.1 LLEVA CARGA 1346-2,3 PARTE DEK 1529-15 Y PARTE DEL 1908-3 SE CERRO LOCALMENTE | S2110170000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-10-17 | 84 | keep | 0 | Oct | 2021 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-17 00:55 | 2021-10-17 02:19 | 1844 | 001:24 | T | NO SE REPORTO CAUSA | DISPARO BKR.1 LLEVA CARGA 1346-2,3 PARTE DEK 1529-15 Y PARTE DEL 1908-3 SE CERRO LOCALMENTE | S2110170000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-10-17 | 154896 | keep | 0 | Oct | 2021 | 0.1055 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2021-10-17 00:55 | 2021-10-17 02:19 | 2422 | 001:24 | P | NO SE REPORTO CAUSA | DISPARO BKR.1 LLEVA CARGA 1346-2,3 PARTE DEK 1529-15 Y PARTE DEL 1908-3 SE CERRO LOCALMENTE | S21101700000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-10-17 | 203448 | keep | 0 | Oct | 2021 | 0.13857 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-17 00:55 | 2021-10-17 02:19 | 260 | 001:24 | P | NO SE REPORTO CAUSA | DISPARO BKR.1 LLEVA CARGA 1346-2,3 PARTE DEK 1529-15 Y PARTE DEL 1908-3 SE CERRO LOCALMENTE | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-10-17 | 21840 | keep | 0 | Oct | 2021 | 0.014875 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
SAN JUAN | 2021-10-17 00:55 | 2021-10-17 02:19 | 3000 | 001:24 | P | NO SE REPORTO CAUSA | DISPARO BKR.1 LLEVA CARGA 1346-2,3 PARTE DEK 1529-15 Y PARTE DEL 1908-3 SE CERRO LOCALMENTE | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-10-17 | 252000 | keep | 0 | Oct | 2021 | 0.17164 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
GUAYAMA | 2021-10-17 01:01 | 2021-10-17 03:09 | 1676 | 002:08 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR POR POSTE PRIMARIO PARTIDO EN ACCIDENTE DE AUTO | P21101700001 | New_Event |  |  | Include | Wildlife | 128 | 2021-10-17 | 214528 | keep | 0 | Oct | 2021 | 0.14611 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
SAN JUAN | 2021-10-17 01:30 | 2021-10-17 01:31 | 4133 | 000:01 | T | DESGANCHE | RECERRO CARGA POR EL 1206-03 | S21101700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-17 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-17 01:30 | 2021-10-17 01:31 | 4133 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1204-05 | S21101700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-17 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-17 01:31 | 2021-10-17 18:09 | 80 | 016:38 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101700091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 998 | 2021-10-17 | 79840 | keep | 0 | Oct | 2021 | 0.054379 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-10-17 01:31 | 2021-10-17 01:32 | 2937 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21101700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-17 | 2937 | keep | 0 | Oct | 2021 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
BARRANQUITAS | 2021-10-17 01:32 | 2021-10-17 10:43 | 47 | 009:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21101700016 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 551 | 2021-10-17 | 25897 | keep | 0 | Oct | 2021 | 0.017638 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
BAYAMON | 2021-10-17 02:37 | 2021-10-17 10:03 | 60 | 007:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21101700003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 446 | 2021-10-17 | 26760 | keep | 0 | Oct | 2021 | 0.018226 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-17 02:44 | 2021-10-17 12:42 | 500 | 009:58 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO Y AL CERRAR DISPARO ALIMENTADOR | S21101700030 | New_Event | Switch Failure | Include | Include | Equipment | 598 | 2021-10-17 | 299000 | keep | 0 | Oct | 2021 | 0.20365 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-10-17 03:13 | 2021-10-17 08:56 | 1 | 005:43 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R21101700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2021-10-17 | 343 | keep | 0 | Oct | 2021 | 0.00023362 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-17 03:20 | 2021-10-17 10:00 | 50 | 006:40 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN SU SE AJUSTA BASE DE FUSIBLE | B21101700005 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 400 | 2021-10-17 | 20000 | keep | 0 | Oct | 2021 | 0.013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-10-17 03:55 | 2021-10-17 03:56 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA 1346-5 Y PARTE 1348-8 | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 922 | keep | 0 | Oct | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-10-17 03:55 | 2021-10-17 03:56 | 600 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1401-08 | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-10-17 03:55 | 2021-10-17 03:56 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA 1346-5 Y PARTE 1348-8 | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2021-10-17 04:04 | 2021-10-17 10:47 | 40 | 006:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE | C21101700012 | New_Event | Cutout Failure | Include | Include | Equipment | 403 | 2021-10-17 | 16120 | keep | 0 | Oct | 2021 | 0.010979 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-17 04:29 | 2021-10-17 12:42 | 60 | 008:13 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN RISER SE DEJO T-29 AVERIADO FUERA PARA REMPLAZO | B21101700006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 493 | 2021-10-17 | 29580 | keep | 0 | Oct | 2021 | 0.020147 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-10-17 04:53 | 2021-10-17 10:17 | 197 | 005:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21101700014 | New_Event | Bad Weather | Include | Include | Weather | 324 | 2021-10-17 | 63828 | keep | 0 | Oct | 2021 | 0.043473 | 0.00013418 | Sustained | FALSE | TRUE | Not_TMED_Event | 197
PONCE | 2021-10-17 05:57 | 2021-10-17 05:58 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL 10 CON CARGA INTERRUPTORES 5018-01 5018-03 Y 5018-05 | P21101700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 1979 | keep | 0 | Oct | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-10-17 05:57 | 2021-10-17 05:58 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL 10 CON CARGA INTERRUPTORES 5018-01 5018-03 Y 5018-05 | P21101700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 5069 | keep | 0 | Oct | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-10-17 05:57 | 2021-10-17 05:58 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL 10 CON CARGA INTERRUPTORES 5018-01 5018-03 Y 5018-05 | P21101700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 5063 | keep | 0 | Oct | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
YAUCO | 2021-10-17 06:01 | 2021-10-17 06:02 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZO UNA OPERACION Y QUEDO EN SERVICIO | P21101700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 3973 | keep | 0 | Oct | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
MAYAGÃœEZ | 2021-10-17 06:32 | 2021-10-17 13:31 | 40 | 006:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21101700002 | New_Event | Bad Weather | Include | Include | Weather | 419 | 2021-10-17 | 16760 | keep | 0 | Oct | 2021 | 0.011415 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-17 06:32 | 2021-10-17 09:20 | 10 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21101700002 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2021-10-17 | 1680 | keep | 0 | Oct | 2021 | 0.0011442 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-17 06:54 | 2021-10-17 09:52 | 60 | 002:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21101700003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 178 | 2021-10-17 | 10680 | keep | 0 | Oct | 2021 | 0.0072741 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-17 07:02 | 2021-10-17 07:03 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 2697 | keep | 0 | Oct | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
SAN JUAN | 2021-10-17 07:05 | 2021-10-17 13:06 | 207 | 006:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA REMPLAZO 4 AISLADORES | R21101700005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 361 | 2021-10-17 | 74727 | keep | 0 | Oct | 2021 | 0.050896 | 0.00014099 | Sustained | FALSE | TRUE | Not_TMED_Event | 207
ARECIBO | 2021-10-17 07:16 | 2021-10-17 11:00 | 70 | 003:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA 100 AMP EN CORTE DE LINEA | A21101700006 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2021-10-17 | 15680 | keep | 0 | Oct | 2021 | 0.01068 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-10-17 07:18 | 2021-10-17 07:19 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 1533 | keep | 0 | Oct | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
SAN JUAN | 2021-10-17 07:41 | 2021-10-17 07:43 | 3718 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21101700111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-17 | 7436 | keep | 0 | Oct | 2021 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2021-10-17 07:42 | 2021-10-17 07:43 | 2201 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | A21101700000 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-17 | 2201 | keep | 0 | Oct | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
BARRANQUITAS | 2021-10-17 07:42 | 2021-10-17 07:43 | 3296 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21101700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 3296 | keep | 0 | Oct | 2021 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
ARECIBO | 2021-10-17 07:43 | 2021-10-17 09:40 | 20 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO FASES | A21101700009 | 1st_after_momentary |  |  | Include | Wildlife | 117 | 2021-10-17 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-10-17 07:50 | 2021-10-17 11:10 | 60 | 003:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21101700010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-10-17 | 12000 | keep | 0 | Oct | 2021 | 0.0081731 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-17 08:08 | 2021-10-17 10:00 | 100 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101700009 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2021-10-17 | 11200 | keep | 0 | Oct | 2021 | 0.0076283 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-17 08:17 | 2021-10-17 18:33 | 80 | 010:16 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S21101700139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 616 | 2021-10-17 | 49280 | keep | 0 | Oct | 2021 | 0.033564 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-10-17 08:23 | 2021-10-17 13:10 | 10 | 004:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21101700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-10-17 | 2870 | keep | 0 | Oct | 2021 | 0.0019547 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-10-17 08:45 | 2021-10-17 13:00 | 3 | 004:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE RETIRAN PISTOLAS PRIMARIAS A TRANSFORMADOR SUMERGIBLE PARA CONECTAR RESTABLECER CARGAS SECUNDARIAS DE OTRO TRANSFORMADOR TRANSFERIDAS | P21100500089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 255 | 2021-10-17 | 765 | keep | 0 | Oct | 2021 | 0.00052104 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-17 08:54 | 2021-10-17 09:04 | 199 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-10-17 | 1990 | keep | 0 | Oct | 2021 | 0.0013554 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2021-10-17 09:16 | 2021-10-17 17:55 | 2 | 008:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA ABIERTA | S21101700187 | New_Event | Secondary Wire Down | Include | Include | Equipment | 519 | 2021-10-17 | 1038 | keep | 0 | Oct | 2021 | 0.00070698 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-10-17 09:21 | 2021-10-18 13:08 | 7 | 027:47 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | C21101700035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1667 | 2021-10-17 | 11669 | keep | 0 | Oct | 2021 | 0.0079477 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-17 09:32 | 2021-10-18 10:53 | 250 | 025:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21101700023 | New_Event | Bad Weather | Include | Include | Weather | 1521 | 2021-10-17 | 380250 | keep | 0 | Oct | 2021 | 0.25899 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-10-17 09:37 | 2021-10-17 15:42 | 100 | 006:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21101700197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2021-10-17 | 36500 | keep | 0 | Oct | 2021 | 0.02486 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-17 09:39 | 2021-10-19 14:34 | 10 | 052:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | B21101700095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3175 | 2021-10-17 | 31750 | keep | 0 | Oct | 2021 | 0.021625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-17 09:40 | 2021-10-17 17:55 | 400 | 008:15 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | M21101700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2021-10-17 | 198000 | keep | 0 | Oct | 2021 | 0.13486 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CANOVANAS | 2021-10-17 09:58 | 2021-10-17 18:54 | 40 | 008:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21101700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2021-10-17 | 21440 | keep | 0 | Oct | 2021 | 0.014603 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-17 10:00 | 2021-10-17 14:17 | 80 | 004:17 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | M21101700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2021-10-17 | 20560 | keep | 0 | Oct | 2021 | 0.014003 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-10-17 10:04 | 2021-10-17 11:45 | 60 | 001:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-10-17 | 6060 | keep | 0 | Oct | 2021 | 0.0041274 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-10-17 10:05 | 2021-10-17 15:00 | 150 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | P21101700015 | New_Event | Wire Down | Include | Include | Equipment | 295 | 2021-10-17 | 44250 | keep | 0 | Oct | 2021 | 0.030138 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-17 10:21 | 2021-10-17 15:46 | 2 | 005:25 | P | NO SE REPORTO CAUSA | 2 X 50 EN SU-2 | S21101700226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2021-10-17 | 650 | keep | 0 | Oct | 2021 | 0.00044271 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-10-17 10:21 | 2021-10-17 15:08 | 40 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN AEREO PROVISIONAL | S21101700165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2021-10-17 | 11480 | keep | 0 | Oct | 2021 | 0.007819 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-10-17 10:39 | 2021-10-17 15:17 | 1 | 004:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO | C21101700048 | New_Event | Bad Weather | Include | Include | Weather | 278 | 2021-10-17 | 278 | keep | 0 | Oct | 2021 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-17 10:47 | 2021-10-17 10:48 | 3025 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR CARGA POR EL 2604-03 EN SERVICIO | C21101700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-17 | 3025 | keep | 0 | Oct | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-10-17 10:47 | 2021-10-17 10:48 | 1593 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 2604-02 EN SERVICIO | C21101700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-17 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-10-17 10:48 | 2021-10-17 14:24 | 40 | 003:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE | C21101700012 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 216 | 2021-10-17 | 8640 | keep | 0 | Oct | 2021 | 0.0058847 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-17 11:11 | 2021-10-17 16:46 | 50 | 005:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | M21101700038 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2021-10-17 | 16750 | keep | 0 | Oct | 2021 | 0.011408 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-10-17 11:19 | 2021-10-17 13:55 | 51 | 002:36 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE PODRIDO PARTIDO | C21101700012 | New_Event | Defective Pole | Include | Include | Equipment | 156 | 2021-10-17 | 7956 | keep | 0 | Oct | 2021 | 0.0054188 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
BAYAMON | 2021-10-17 11:35 | 2021-10-17 15:25 | 3 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21101700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2021-10-17 | 690 | keep | 0 | Oct | 2021 | 0.00046996 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-17 11:37 | 2021-10-17 14:20 | 20 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-10-17 | 3260 | keep | 0 | Oct | 2021 | 0.0022204 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-10-17 11:38 | 2021-10-17 17:09 | 5 | 005:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN CORTE DE LINEA CRUCE POR CULEBRA | R21101700011 | New_Event |  |  | Include | Wildlife | 331 | 2021-10-17 | 1655 | keep | 0 | Oct | 2021 | 0.0011272 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
AGUADILLA | 2021-10-17 11:43 | 2021-10-17 17:25 | 25 | 005:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X LO MISMO | M21101700037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 342 | 2021-10-17 | 8550 | keep | 0 | Oct | 2021 | 0.0058234 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-10-17 11:47 | 2021-10-17 17:25 | 10 | 005:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21101700023 | New_Event | Bad Weather | Include | Include | Weather | 338 | 2021-10-17 | 3380 | keep | 0 | Oct | 2021 | 0.0023021 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-17 11:49 | 2021-10-17 16:00 | 10 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21101700042 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2021-10-17 | 2510 | keep | 0 | Oct | 2021 | 0.0017095 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-17 11:56 | 2021-10-17 15:51 | 100 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21101700060 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2021-10-17 | 23500 | keep | 0 | Oct | 2021 | 0.016006 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-17 12:02 | 2021-10-17 12:03 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO TIENE LA CARGA DEL 5018-02 | P21101700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 3744 | keep | 0 | Oct | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-10-17 12:02 | 2021-10-17 12:03 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 5004-06 CON CARGA DE ALIMENTADOR 5018-02 | P21101700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 3114 | keep | 0 | Oct | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2021-10-17 12:41 | 2021-10-17 14:03 | 10 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER HACIA TRANSFORMADOR TIPO PM | B21101700032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-10-17 | 820 | keep | 0 | Oct | 2021 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-17 12:42 | 2021-10-18 17:51 | 30 | 029:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM 29 AVERIADO DE 100KVA X 100KVA | B21101700046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1749 | 2021-10-17 | 52470 | keep | 0 | Oct | 2021 | 0.035737 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-17 12:42 | 2021-10-17 12:49 | 3957 | 000:07 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO Y AL CERRAR DISPARO ALIMENTADOR SE SECCIONALIZO NUEVAMENTE Y SE CERRO POR SCADA | S21101700030 | New_Event | Switch Failure | Include | Include | Equipment | 7 | 2021-10-17 | 27699 | keep | 0 | Oct | 2021 | 0.018866 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
CAGUAS | 2021-10-17 12:46 | 2021-10-17 12:48 | 40 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101700067 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-10-17 | 80 | keep | 0 | Oct | 2021 | 5.4488e-05 | 2.7244e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-17 12:48 | 2021-10-17 13:33 | 1565 | 000:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA SE SECCIONALIZO | C21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2021-10-17 | 70425 | keep | 0 | Oct | 2021 | 0.047966 | 0.0010659 | Sustained | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-10-17 12:48 | 2021-10-17 13:33 | 976 | 000:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA SE SECCIONALIZO | C21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2021-10-17 | 43920 | keep | 0 | Oct | 2021 | 0.029914 | 0.00066475 | Sustained | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-10-17 12:48 | 2021-10-17 13:33 | 548 | 000:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A CIDRA SE SECCIONALIZO | C21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2021-10-17 | 24660 | keep | 0 | Oct | 2021 | 0.016796 | 0.00037324 | Sustained | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-10-17 12:48 | 2021-10-17 14:08 | 315 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-10-17 | 25200 | keep | 0 | Oct | 2021 | 0.017164 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-10-17 12:48 | 2021-10-17 14:08 | 870 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-10-17 | 69600 | keep | 0 | Oct | 2021 | 0.047404 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-10-17 12:48 | 2021-10-17 14:08 | 2906 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-10-17 | 232480 | keep | 0 | Oct | 2021 | 0.15834 | 0.0019793 | Sustained | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-10-17 12:48 | 2021-10-17 14:08 | 2343 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21101500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-10-17 | 187440 | keep | 0 | Oct | 2021 | 0.12766 | 0.0015958 | Sustained | FALSE | TRUE | Not_TMED_Event | 2343
SAN JUAN | 2021-10-17 12:49 | 2021-10-17 13:15 | 350 | 000:26 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES Y SE CONTINUA PATRULLANDO TRAMO RESTANTE | S21101700030 | Partial_restoration | Switch Failure | Include | Include | Equipment | 26 | 2021-10-17 | 9100 | keep | 0 | Oct | 2021 | 0.006198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-17 13:03 | 2021-10-17 13:04 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 651 | keep | 0 | Oct | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
MAYAGÃœEZ | 2021-10-17 13:11 | 2021-10-17 13:12 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21101700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 3458 | keep | 0 | Oct | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2021-10-17 13:15 | 2021-10-17 13:59 | 350 | 000:44 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES Y SE CONTINUA PATRULLANDO TRAMO RESTANTE | S21101700030 | Partial_restoration | Switch Failure | Include | Include | Equipment | 44 | 2021-10-17 | 15400 | keep | 0 | Oct | 2021 | 0.010489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-17 13:24 | 2021-10-17 14:45 | 100 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA DESACRGAS ELECTRICAS | C21101700138 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2021-10-17 | 8100 | keep | 0 | Oct | 2021 | 0.0055169 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-17 13:34 | 2021-10-17 16:31 | 600 | 002:57 | P | DESGANCHE | SE RETIRO BAMBUAS Y SE CERRO INTERRUPTOR 1204-01 (SPARE) QUE LLEVA LA CARGA DEL 1204-03 | S21101700348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-10-17 | 106200 | keep | 0 | Oct | 2021 | 0.072332 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-10-17 13:34 | 2021-10-17 13:35 | 641 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR LLEVA EL 1206-02 | S21101700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-17 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-17 13:34 | 2021-10-17 13:35 | 733 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR LLEVA EL 1206-02 | S21101700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-17 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-10-17 13:34 | 2021-10-17 13:35 | 1061 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR | S21101700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-17 | 1061 | keep | 0 | Oct | 2021 | 0.00072264 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
SAN JUAN | 2021-10-17 13:34 | 2021-10-17 13:35 | 1208 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR | S21101700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-17 | 1208 | keep | 0 | Oct | 2021 | 0.00082276 | 0.00082276 | Momentary | FALSE | FALSE | Not_TMED_Event | 1208
PONCE | 2021-10-17 13:44 | 2021-10-17 17:00 | 70 | 003:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101700021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-10-17 | 13720 | keep | 0 | Oct | 2021 | 0.0093446 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-17 13:46 | 2021-10-17 13:47 | 281 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 281 | keep | 0 | Oct | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-10-17 13:46 | 2021-10-17 13:47 | 1252 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 1252 | keep | 0 | Oct | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-10-17 13:46 | 2021-10-17 13:47 | 595 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 595 | keep | 0 | Oct | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-10-17 13:46 | 2021-10-17 13:47 | 51 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 51 | keep | 0 | Oct | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-10-17 13:46 | 2021-10-17 13:47 | 721 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 721 | keep | 0 | Oct | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-10-17 13:46 | 2021-10-17 13:47 | 1382 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 1382 | keep | 0 | Oct | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-10-17 13:46 | 2021-10-17 13:47 | 654 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-17 | 654 | keep | 0 | Oct | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
SAN JUAN | 2021-10-17 13:47 | 2021-10-17 13:48 | 108 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR | S21101701000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-17 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-10-17 13:54 | 2021-10-17 16:08 | 81 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21101700019 | New_Event |  |  | Include | Wildlife | 134 | 2021-10-17 | 10854 | keep | 0 | Oct | 2021 | 0.0073926 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
SAN JUAN | 2021-10-17 13:59 | 2021-10-17 14:03 | 3000 | 000:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR AL CERRAR MACHETES EN CARRETERA 1 FRENTE CAR AUTO SE DEJO MACHETES ABIERTOS | S21101700318 | Additional_clients | Switch Failure | Include | Include | Equipment | 4 | 2021-10-17 | 12000 | keep | 0 | Oct | 2021 | 0.0081731 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-17 14:02 | 2021-10-18 17:34 | 6 | 027:32 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21101700190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1652 | 2021-10-17 | 9912 | keep | 0 | Oct | 2021 | 0.006751 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-17 14:03 | 2021-10-17 15:45 | 300 | 001:42 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES EN CARRETERA 1 FRENTE CAR AUTO ABRIENDO MACHETES EN CARRETERA 842 FRENTE CONDOMINIO CAMELOT POR MACHETES QUEMADOS EN CARRETERA 842 | S21101700318 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 102 | 2021-10-17 | 30600 | keep | 0 | Oct | 2021 | 0.020842 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-17 14:04 | 2021-10-17 17:34 | 60 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101700373 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-10-17 | 12600 | keep | 0 | Oct | 2021 | 0.0085818 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-17 14:06 | 2021-10-17 14:08 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES PARA CERRAR EL 0803B | C21101700000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-17 | 3130 | keep | 0 | Oct | 2021 | 0.0021318 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-17 14:06 | 2021-10-17 14:08 | 976 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES PARA CERRAR EL 0803B | C21101700000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-17 | 1952 | keep | 0 | Oct | 2021 | 0.0013295 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-17 14:06 | 2021-10-17 14:08 | 548 | 000:02 | S | LINEA DE TRANSMISION 38KV | PERSONAL REALIZANDO OPERACIONES PARA CERRAR EL 0803B | C21101700000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-17 | 1096 | keep | 0 | Oct | 2021 | 0.00074648 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-17 14:08 | 2021-10-17 14:10 | 850 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA PARTE DE LA CARGA POR 1708 03 | B21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-17 | 1700 | keep | 0 | Oct | 2021 | 0.0011579 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
BAYAMON | 2021-10-17 14:08 | 2021-10-17 14:10 | 1498 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA PARTE DE LA CARGA DE 1708 02 | B21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-17 | 2996 | keep | 0 | Oct | 2021 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
CAGUAS | 2021-10-17 14:08 | 2021-10-17 15:14 | 40 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C21101700067 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 66 | 2021-10-17 | 2640 | keep | 0 | Oct | 2021 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-10-17 14:14 | 2021-10-17 18:35 | 40 | 004:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101700198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-10-17 | 10440 | keep | 0 | Oct | 2021 | 0.0071106 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 1405 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 4215 | keep | 0 | Oct | 2021 | 0.0028708 | 0.00095694 | Momentary | FALSE | TRUE | Not_TMED_Event | 1405
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 669 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 2007 | keep | 0 | Oct | 2021 | 0.001367 | 0.00045565 | Momentary | FALSE | TRUE | Not_TMED_Event | 669
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 1527 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 4581 | keep | 0 | Oct | 2021 | 0.0031201 | 0.00104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1527
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 1054 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 3162 | keep | 0 | Oct | 2021 | 0.0021536 | 0.00071787 | Momentary | FALSE | TRUE | Not_TMED_Event | 1054
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 932 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 2796 | keep | 0 | Oct | 2021 | 0.0019043 | 0.00063478 | Momentary | FALSE | TRUE | Not_TMED_Event | 932
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 705 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 2115 | keep | 0 | Oct | 2021 | 0.0014405 | 0.00048017 | Momentary | FALSE | TRUE | Not_TMED_Event | 705
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 1521 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 4563 | keep | 0 | Oct | 2021 | 0.0031078 | 0.0010359 | Momentary | FALSE | TRUE | Not_TMED_Event | 1521
UTUADO | 2021-10-17 14:16 | 2021-10-17 14:19 | 882 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 POR DESCARGAS ELECTRICAS | A21101700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-17 | 2646 | keep | 0 | Oct | 2021 | 0.0018022 | 0.00060073 | Momentary | FALSE | TRUE | Not_TMED_Event | 882
UTUADO | 2021-10-17 14:19 | 2021-10-17 16:09 | 705 | 001:50 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR PORTATIL POR DESCARGAS ELECTRICAS | A21101700031 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-10-17 | 77550 | keep | 0 | Oct | 2021 | 0.052819 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2021-10-17 14:19 | 2021-10-17 16:09 | 1521 | 001:50 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR PORTATIL POR DESCARGAS ELECTRICAS | A21101700031 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-10-17 | 167310 | keep | 0 | Oct | 2021 | 0.11395 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2021-10-17 14:19 | 2021-10-17 16:09 | 882 | 001:50 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR PORTATIL POR DESCARGAS ELECTRICAS | A21101700031 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-10-17 | 97020 | keep | 0 | Oct | 2021 | 0.06608 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
CAGUAS | 2021-10-17 14:22 | 2021-10-17 16:27 | 85 | 002:05 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21101700201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-10-17 | 10625 | keep | 0 | Oct | 2021 | 0.0072366 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
PONCE | 2021-10-17 14:26 | 2021-10-17 16:17 | 300 | 001:51 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21101700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-10-17 | 33300 | keep | 0 | Oct | 2021 | 0.02268 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-10-17 14:29 | 2021-10-17 17:13 | 55 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21101700204 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2021-10-17 | 9020 | keep | 0 | Oct | 2021 | 0.0061435 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-10-17 14:48 | 2021-10-17 16:30 | 50 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21101700395 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-10-17 | 5100 | keep | 0 | Oct | 2021 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-17 15:03 | 2021-10-17 16:17 | 20 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101700040 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2021-10-17 | 1480 | keep | 0 | Oct | 2021 | 0.001008 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-17 15:10 | 2021-10-17 16:10 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA Y REALIZAR DESGANCHE | B21101700023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-10-17 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-10-17 15:12 | 2021-10-17 16:15 | 1 | 001:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA REPORTAN MUCHO DESGANCHE | A21101700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2021-10-17 | 63 | keep | 0 | Oct | 2021 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-10-17 15:15 | 2021-10-18 09:19 | 150 | 018:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1X80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P21101700034 | New_Event | Bad Weather | Include | Include | Weather | 1084 | 2021-10-17 | 162600 | keep | 0 | Oct | 2021 | 0.11075 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-17 15:24 | 2021-10-17 16:50 | 10 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21101600096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-10-17 | 860 | keep | 0 | Oct | 2021 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-17 15:32 | 2021-10-17 16:00 | 8 | 000:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21101700055 | New_Event | Bad Weather | Include | Include | Weather | 28 | 2021-10-17 | 224 | keep | 0 | Oct | 2021 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-17 15:35 | 2021-10-17 16:55 | 10 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21101700056 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-10-17 | 800 | keep | 0 | Oct | 2021 | 0.00054488 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-17 15:39 | 2021-10-17 21:45 | 80 | 006:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21101700058 | New_Event | Bad Weather | Include | Include | Weather | 366 | 2021-10-17 | 29280 | keep | 0 | Oct | 2021 | 0.019942 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-17 15:40 | 2021-10-18 17:26 | 15 | 025:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21101700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1546 | 2021-10-17 | 23190 | keep | 0 | Oct | 2021 | 0.015795 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-10-17 15:43 | 2021-10-17 16:53 | 1 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C21101700219 | New_Event |  |  | Include | Wildlife | 70 | 2021-10-17 | 70 | keep | 0 | Oct | 2021 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-17 15:45 | 2021-10-17 16:12 | 300 | 000:27 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES EN CARRETERA 842 FRENTE CONDOMINIO CAMELOT ABRIENDO MACHETES EN CARRETERA 842 FRENTE URBANIZACION LA CAMPINA POR MACHETES QUEMADOS EN CARRETERA 842 | S21101700318 | Partial_restoration | Switch Failure | Include | Include | Equipment | 27 | 2021-10-17 | 8100 | keep | 0 | Oct | 2021 | 0.0055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-17 15:58 | 2021-10-18 14:22 | 7 | 022:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21101700222 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1344 | 2021-10-17 | 9408 | keep | 0 | Oct | 2021 | 0.0064077 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-17 16:12 | 2021-10-17 17:48 | 300 | 001:36 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES EN CARRETERA 842 FRENTE URBANIZACION LA CAMPINA REMPLAZANDO MACHETES QUEMADOS EN CARRETERA 842 FRENTE GARAJE DE GASOLINA | S21101700318 | Partial_restoration | Switch Failure | Include | Include | Equipment | 96 | 2021-10-17 | 28800 | keep | 0 | Oct | 2021 | 0.019616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-17 16:15 | 2021-10-17 16:28 | 100 | 000:13 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101700051 | New_Event | Bad Weather | Include | Include | Weather | 13 | 2021-10-17 | 1300 | keep | 0 | Oct | 2021 | 0.00088542 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-17 16:27 | 2021-10-17 16:28 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | M21101700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 4304 | keep | 0 | Oct | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2021-10-17 16:32 | 2021-10-17 16:33 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE DE LA CARGA 9405 05 | B21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 3597 | keep | 0 | Oct | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-10-17 16:32 | 2021-10-17 16:33 | 400 | 000:01 | P | NO SE REPORTO CAUSA | RECCIERRE DE INTERRUPTOR PARTE DE SU CARGA POR EL 1719-15 | B21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 400 | keep | 0 | Oct | 2021 | 0.00027244 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2021-10-17 16:33 | 2021-10-17 18:32 | 200 | 001:59 | P | NO SE REPORTO CAUSA | 3 X 200 EN CORTE DE LINEA | B21101700058 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-10-17 | 23800 | keep | 0 | Oct | 2021 | 0.01621 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-17 16:38 | 2021-10-18 15:04 | 10 | 022:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER | S21101700442 | New_Event | Cutout Failure | Include | Include | Equipment | 1346 | 2021-10-17 | 13460 | keep | 0 | Oct | 2021 | 0.0091675 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-17 16:53 | 2021-10-17 17:15 | 450 | 000:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21101700065 | New_Event | Bad Weather | Include | Include | Weather | 22 | 2021-10-17 | 9900 | keep | 0 | Oct | 2021 | 0.0067428 | 0.00030649 | Sustained | FALSE | TRUE | Not_TMED_Event | 450
UTUADO | 2021-10-17 17:00 | 2021-10-18 10:15 | 15 | 017:15 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101700053 | New_Event | Bad Weather | Include | Include | Weather | 1035 | 2021-10-17 | 15525 | keep | 0 | Oct | 2021 | 0.010574 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-17 17:02 | 2021-10-18 11:08 | 30 | 018:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21101700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1086 | 2021-10-17 | 32580 | keep | 0 | Oct | 2021 | 0.02219 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-17 17:03 | 2021-10-17 19:48 | 140 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21101700066 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2021-10-17 | 23100 | keep | 0 | Oct | 2021 | 0.015733 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
CAGUAS | 2021-10-17 17:15 | 2021-10-18 14:54 | 10 | 021:39 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADFO DE 50 KVA X 50 KVA | C21101700234 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1299 | 2021-10-17 | 12990 | keep | 0 | Oct | 2021 | 0.0088474 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-17 17:43 | 2021-10-17 17:53 | 20 | 000:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21101700071 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-10-17 | 200 | keep | 0 | Oct | 2021 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-10-17 17:45 | 2021-10-17 19:20 | 10 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA AVERIADA | A21101700055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-10-17 | 950 | keep | 0 | Oct | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-10-17 17:48 | 2021-10-17 17:51 | 1588 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA 1711 03 | B21101700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-17 | 4764 | keep | 0 | Oct | 2021 | 0.0032447 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-10-17 17:48 | 2021-10-17 17:51 | 13 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1711 01 | B21101700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-17 | 39 | keep | 0 | Oct | 2021 | 2.6563e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-10-17 18:07 | 2021-10-18 13:12 | 15 | 019:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR IGUAL | B21101700085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1145 | 2021-10-17 | 17175 | keep | 0 | Oct | 2021 | 0.011698 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-17 18:54 | 2021-10-18 16:52 | 10 | 021:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | S21101700478 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1318 | 2021-10-17 | 13180 | keep | 0 | Oct | 2021 | 0.0089768 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-17 19:00 | 2021-10-17 20:05 | 40 | 001:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101700061 | New_Event | Bad Weather | Include | Include | Weather | 65 | 2021-10-17 | 2600 | keep | 0 | Oct | 2021 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-17 19:02 | 2021-10-18 11:02 | 60 | 016:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21101700241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 960 | 2021-10-17 | 57600 | keep | 0 | Oct | 2021 | 0.039231 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-17 19:02 | 2021-10-18 13:11 | 10 | 018:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21101700241 | New_Event | Bad Weather | Include | Include | Weather | 1089 | 2021-10-17 | 10890 | keep | 0 | Oct | 2021 | 0.0074171 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-17 19:06 | 2021-10-18 14:15 | 20 | 019:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21101700065 | New_Event | Bad Weather | Include | Include | Weather | 1149 | 2021-10-17 | 22980 | keep | 0 | Oct | 2021 | 0.015652 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-17 19:26 | 2021-10-18 13:58 | 50 | 018:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 15KVA POR 15KVA | B21101700090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1112 | 2021-10-17 | 55600 | keep | 0 | Oct | 2021 | 0.037869 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-17 20:01 | 2021-10-18 09:35 | 5 | 013:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO Y REGULO TRANSFORMADOR | C21101700243 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 814 | 2021-10-17 | 4070 | keep | 0 | Oct | 2021 | 0.0027721 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-17 20:16 | 2021-10-18 17:36 | 5 | 021:20 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21101700246 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1280 | 2021-10-17 | 6400 | keep | 0 | Oct | 2021 | 0.004359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-17 20:19 | 2021-10-18 14:43 | 5 | 018:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21101700251 | New_Event | Bad Weather | Include | Include | Weather | 1104 | 2021-10-17 | 5520 | keep | 0 | Oct | 2021 | 0.0037596 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-17 20:20 | 2021-10-18 20:01 | 15 | 023:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21101700093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1421 | 2021-10-17 | 21315 | keep | 0 | Oct | 2021 | 0.014518 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-10-17 20:25 | 2021-10-17 20:26 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-17 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CAGUAS | 2021-10-17 21:05 | 2021-10-18 14:55 | 30 | 017:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21101700258 | New_Event | Wire Down | Include | Include | Equipment | 1070 | 2021-10-17 | 32100 | keep | 0 | Oct | 2021 | 0.021863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-10-17 21:31 | 2021-10-18 08:50 | 370 | 011:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO NADA | R21101700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 679 | 2021-10-17 | 251230 | keep | 0 | Oct | 2021 | 0.17111 | 0.00025201 | Sustained | FALSE | TRUE | Not_TMED_Event | 370
SAN JUAN | 2021-10-17 21:48 | 2021-10-18 | 108 | 002:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA LEVANTER PRIMARIA | S21101700573 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2021-10-17 | 14256 | keep | 0 | Oct | 2021 | 0.0097097 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-10-17 21:48 | 2021-10-18 | 1368 | 002:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA LEVANTER PRIMARIA EN 1205-1 | S21101700522 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2021-10-17 | 180576 | keep | 0 | Oct | 2021 | 0.12299 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
CAGUAS | 2021-10-17 22:10 | 2021-10-18 16:26 | 40 | 018:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101700264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1096 | 2021-10-17 | 43840 | keep | 0 | Oct | 2021 | 0.029859 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-17 22:39 | 2021-10-18 10:25 | 1 | 011:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER CRUCE POR AVE | R21101700032 | New_Event |  |  | Include | Wildlife | 706 | 2021-10-17 | 706 | keep | 0 | Oct | 2021 | 0.00048085 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 00:09 | 2021-10-18 00:10 | 4291 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21101800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 4291 | keep | 0 | Oct | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-10-18 00:09 | 2021-10-18 00:58 | 108 | 000:49 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTPR PARA REMPLAZAR MACHETE QUEMADO CARR.181 | S21101800003 | New_Event | Switch Failure | Include | Include | Equipment | 49 | 2021-10-18 | 5292 | keep | 0 | Oct | 2021 | 0.0036044 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-10-18 00:36 | 2021-10-18 17:01 | 45 | 016:25 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 985 | 2021-10-18 | 44325 | keep | 0 | Oct | 2021 | 0.03019 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-18 00:55 | 2021-10-18 15:30 | 300 | 014:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A21101800001 | New_Event | Wire Down | Include | Include | Equipment | 875 | 2021-10-18 | 262500 | keep | 0 | Oct | 2021 | 0.17879 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-10-18 02:40 | 2021-10-18 11:47 | 36 | 009:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2021-10-18 | 19692 | keep | 0 | Oct | 2021 | 0.013412 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
SAN JUAN | 2021-10-18 02:56 | 2021-10-18 10:00 | 41 | 007:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101800021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2021-10-18 | 17384 | keep | 0 | Oct | 2021 | 0.01184 | 2.7925e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 41
PONCE | 2021-10-18 03:22 | 2021-10-18 04:47 | 974 | 001:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P21101800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2021-10-18 | 82790 | keep | 0 | Oct | 2021 | 0.056388 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
SAN JUAN | 2021-10-18 03:31 | 2021-10-18 03:32 | 10211 | 000:01 | T | DESGANCHE | RECERRO CARGA POR EL 1206-03 | S21101800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-18 03:31 | 2021-10-18 03:32 | 4133 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1204-5 | S21101800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-18 03:32 | 2021-10-18 03:43 | 125 | 000:11 | P | DESGANCHE | 2 X 150 EN SU-4 SE REMPLAZO CAJA Y SE LLEVO PUENTE A CAJA POR DESGANCHE | S21101700485 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 11 | 2021-10-18 | 1375 | keep | 0 | Oct | 2021 | 0.00093651 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-10-18 03:43 | 2021-10-18 03:44 | 10211 | 000:01 | T | DESGANCHE | RECERRO CARGA POR EL 1206-03 | S21101800000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 10211 | keep | 0 | Oct | 2021 | 0.0069547 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-18 03:43 | 2021-10-18 03:44 | 4133 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1204-5 | S21101800000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 4133 | keep | 0 | Oct | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-18 03:44 | 2021-10-18 13:21 | 125 | 009:37 | P | DESGANCHE | 2 X 150 EN SU-4 SE REMPLAZO CAJA Y SE LLEVO PUENTE A CAJA POR DESGANCHE | S21101700485 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 577 | 2021-10-18 | 72125 | keep | 0 | Oct | 2021 | 0.049124 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-10-18 04:05 | 2021-10-18 18:41 | 15 | 014:36 | P | DESCONECTIVO DEFECTUOSO | SE ESTABLECIO GOI PARA REMPLAZAR MACHETES QUEMADOS EN TRAMO QUE DA A ACUEDUCTOS DE LA REPRESA CARRAIZO | S21101800000 | New_Event | Switch Failure | Include | Include | Equipment | 876 | 2021-10-18 | 13140 | keep | 0 | Oct | 2021 | 0.0089496 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-18 04:47 | 2021-10-18 13:14 | 50 | 008:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 507 | 2021-10-18 | 25350 | keep | 0 | Oct | 2021 | 0.017266 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-18 05:10 | 2021-10-18 10:29 | 50 | 005:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21101800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2021-10-18 | 15950 | keep | 0 | Oct | 2021 | 0.010863 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-10-18 05:24 | 2021-10-18 09:05 | 40 | 003:41 | P | DESGANCHE | 1X20 EN CORTE DE LINEA POR DESGANCHE | P21101800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-10-18 | 8840 | keep | 0 | Oct | 2021 | 0.0060209 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-18 06:08 | 2021-10-18 12:20 | 60 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 Y 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO ALAMBRE PARTIDO SE DEJO CORTE DE LINEA ABIERTO UN CLIENTE SIN SERVICIO | M21101800004 | New_Event | Wire Down | Include | Include | Equipment | 372 | 2021-10-18 | 22320 | keep | 0 | Oct | 2021 | 0.015202 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-18 06:15 | 2021-10-18 09:50 | 15 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | M21101800005 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2021-10-18 | 3225 | keep | 0 | Oct | 2021 | 0.0021965 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-18 06:27 | 2021-10-18 11:19 | 70 | 004:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101800003 | New_Event | Bad Weather | Include | Include | Weather | 292 | 2021-10-18 | 20440 | keep | 0 | Oct | 2021 | 0.013922 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-10-18 06:33 | 2021-10-18 11:09 | 22 | 004:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21101800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2021-10-18 | 6072 | keep | 0 | Oct | 2021 | 0.0041356 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
MAYAGÃœEZ | 2021-10-18 06:52 | 2021-10-18 09:50 | 20 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101800006 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-10-18 | 3560 | keep | 0 | Oct | 2021 | 0.0024247 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-18 07:09 | 2021-10-18 12:21 | 150 | 005:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTE DE LINEA POR CRUCE DE FASES POR GLOBO DE HELIO | P21101800011 | New_Event |  |  | Include | Wildlife | 312 | 2021-10-18 | 46800 | keep | 0 | Oct | 2021 | 0.031875 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BARRANQUITAS | 2021-10-18 07:09 | 2021-10-18 10:34 | 15 | 003:25 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21101800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-10-18 | 3075 | keep | 0 | Oct | 2021 | 0.0020944 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-18 07:17 | 2021-10-18 10:50 | 1 | 003:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21101800009 | New_Event | Bad Weather | Include | Include | Weather | 213 | 2021-10-18 | 213 | keep | 0 | Oct | 2021 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 07:21 | 2021-10-18 16:48 | 50 | 009:27 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DE RISER SU 1 PARA INSTALAR PUENTE DE FASE A FASE EN SU 1 Y ENERGIZAR CARGAS MONOFASICAS POR AVERIA DE CABLE SOTERRADO | S21101800049 | New_Event | UG Cable Fault | Include | Include | Equipment | 567 | 2021-10-18 | 28350 | keep | 0 | Oct | 2021 | 0.019309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2021-10-18 07:31 | 2021-10-18 10:46 | 60 | 003:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21101800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-10-18 | 11700 | keep | 0 | Oct | 2021 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-10-18 07:33 | 2021-10-18 20:11 | 4 | 012:38 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR DESGANCHO | C21101800014 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 758 | 2021-10-18 | 3032 | keep | 0 | Oct | 2021 | 0.0020651 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-10-18 07:46 | 2021-10-19 16:44 | 11 | 032:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | C21101800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1978 | 2021-10-18 | 21758 | keep | 0 | Oct | 2021 | 0.014819 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-10-18 07:46 | 2021-10-18 18:20 | 6 | 010:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 5 EN TRANSFORMADOR MAL TIEMPO | A21101800007 | New_Event | Bad Weather | Include | Include | Weather | 634 | 2021-10-18 | 3804 | keep | 0 | Oct | 2021 | 0.0025909 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-18 07:53 | 2021-10-18 07:54 | 1514 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21101800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 1514 | keep | 0 | Oct | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
UTUADO | 2021-10-18 07:54 | 2021-10-18 12:50 | 40 | 004:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 15 Y 1 X 25 EN DOS CORTES DE LINEA DISTINTOS SE REPARO LINEAS PRIMARIAS ROTAS | A21101800011 | New_Event | Wire Down | Include | Include | Equipment | 296 | 2021-10-18 | 11840 | keep | 0 | Oct | 2021 | 0.0080642 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-18 08:13 | 2021-10-18 14:01 | 7 | 005:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21101800006 | New_Event |  |  | Include | Wildlife | 348 | 2021-10-18 | 2436 | keep | 0 | Oct | 2021 | 0.0016591 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-10-18 08:13 | 2021-10-18 09:30 | 652 | 001:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA | B21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 77 | 2021-10-18 | 50204 | keep | 0 | Oct | 2021 | 0.034194 | 0.00044407 | Sustained | FALSE | TRUE | Not_TMED_Event | 652
VEGA BAJA | 2021-10-18 08:13 | 2021-10-18 09:30 | 2704 | 001:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA | B21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 77 | 2021-10-18 | 208208 | keep | 0 | Oct | 2021 | 0.14181 | 0.0018417 | Sustained | FALSE | TRUE | Not_TMED_Event | 2704
ARECIBO | 2021-10-18 08:17 | 2021-10-18 21:40 | 10 | 013:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO NEUTRAL SECUNDARIO | A21101800014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 803 | 2021-10-18 | 8030 | keep | 0 | Oct | 2021 | 0.0054692 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-18 08:27 | 2021-10-18 20:21 | 10 | 011:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | S21101800067 | New_Event | Cutout Failure | Include | Include | Equipment | 714 | 2021-10-18 | 7140 | keep | 0 | Oct | 2021 | 0.004863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-18 08:29 | 2021-10-18 16:56 | 50 | 008:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21101800025 | New_Event | Bad Weather | Include | Include | Weather | 507 | 2021-10-18 | 25350 | keep | 0 | Oct | 2021 | 0.017266 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-18 08:44 | 2021-10-18 11:57 | 9 | 003:13 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21101800027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 193 | 2021-10-18 | 1737 | keep | 0 | Oct | 2021 | 0.0011831 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2021-10-18 08:50 | 2021-10-18 08:58 | 23 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101800018 | New_Event | Bad Weather | Include | Include | Weather | 8 | 2021-10-18 | 184 | keep | 0 | Oct | 2021 | 0.00012532 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
CANOVANAS | 2021-10-18 08:53 | 2021-10-18 08:54 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R21101800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 1894 | keep | 0 | Oct | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
BAYAMON | 2021-10-18 09:00 | 2021-10-18 14:28 | 5 | 005:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21101800031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 328 | 2021-10-18 | 1640 | keep | 0 | Oct | 2021 | 0.001117 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-18 09:01 | 2021-10-18 19:43 | 60 | 010:42 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE DE EMERGENCIA. ARBOL ELECTRIFICADO | B21101800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 642 | 2021-10-18 | 38520 | keep | 0 | Oct | 2021 | 0.026236 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-10-18 09:10 | 2021-10-18 14:08 | 4 | 004:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REMPLAZO 3 PARARRAYOS Y LOS 3 BAJANTES PRIMARIOS DE LINEA A CAJA | C21101800033 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2021-10-18 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-10-18 09:13 | 2021-10-19 09:52 | 10 | 024:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | S21101800242 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1479 | 2021-10-18 | 14790 | keep | 0 | Oct | 2021 | 0.010073 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-18 09:16 | 2021-10-18 16:09 | 75 | 006:53 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21101800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2021-10-18 | 30975 | keep | 0 | Oct | 2021 | 0.021097 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-10-18 09:16 | 2021-10-18 17:22 | 75 | 008:06 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21101800034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 486 | 2021-10-18 | 36450 | keep | 0 | Oct | 2021 | 0.024826 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-10-18 09:20 | 2021-10-18 10:55 | 10 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M21101700080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-10-18 | 950 | keep | 0 | Oct | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-18 09:23 | 2021-10-18 09:24 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2021-10-18 09:24 | 2021-10-18 20:51 | 30 | 011:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 80 EN CORTE DE LINEA SE REPARO CONEXIONES SECUNDARIAS Y SE REMPLAZO TRAMO | S21101700194 | New_Event | Secondary Wire Down | Include | Include | Equipment | 687 | 2021-10-18 | 20610 | keep | 0 | Oct | 2021 | 0.014037 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-18 09:25 | 2021-10-18 14:20 | 2 | 004:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | A21101800022 | New_Event | Bad Weather | Include | Include | Weather | 295 | 2021-10-18 | 590 | keep | 0 | Oct | 2021 | 0.00040185 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
UTUADO | 2021-10-18 09:40 | 2021-10-18 10:39 | 15 | 000:59 | P | DESGANCHE | 1 X 15 EN DOS TRANSFORMADORES SE REALIZO DESGANCHE | A21101800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-10-18 | 885 | keep | 0 | Oct | 2021 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-10-18 09:49 | 2021-10-18 10:35 | 25 | 000:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN DOS TRANSFORMADORES LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101800026 | New_Event | Bad Weather | Include | Include | Weather | 46 | 2021-10-18 | 1150 | keep | 0 | Oct | 2021 | 0.00078326 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-10-18 09:55 | 2021-10-19 20:47 | 100 | 034:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101800104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2092 | 2021-10-18 | 209200 | keep | 0 | Oct | 2021 | 0.14249 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-18 09:55 | 2021-10-18 14:55 | 40 | 005:00 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 20 EN CORTES DE LINEA | C21101800045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2021-10-18 | 12000 | keep | 0 | Oct | 2021 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-18 09:55 | 2021-10-18 16:45 | 50 | 006:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101800041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 410 | 2021-10-18 | 20500 | keep | 0 | Oct | 2021 | 0.013962 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-18 10:03 | 2021-10-18 10:23 | 1588 | 000:20 | S | NO SE REPORTO CAUSA | OPERO INTERRUPTOR DE ALTA DEL TRANSFORMADOR LLEVA 1711-03 | B21101800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-18 | 31760 | keep | 0 | Oct | 2021 | 0.021632 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-10-18 10:03 | 2021-10-18 10:23 | 723 | 000:20 | S | NO SE REPORTO CAUSA | OPERO INTERRUPTOR DE ALTA DEL TRANSFORMADOR LLEVA 1711-05 | B21101800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-18 | 14460 | keep | 0 | Oct | 2021 | 0.0098486 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-10-18 10:03 | 2021-10-18 10:23 | 13 | 000:20 | S | NO SE REPORTO CAUSA | OPERO INTERRUPTOR DE ALTA DEL TRANSFORMADOR CARGA POR 1711-01 | B21101800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-18 | 260 | keep | 0 | Oct | 2021 | 0.00017708 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-10-18 10:03 | 2021-10-18 10:23 | 1976 | 000:20 | S | NO SE REPORTO CAUSA | OPERO INTERRUPTOR DE ALTA DEL TRANSFORMADOR CARGA POR 1711-02 | B21101800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-18 | 39520 | keep | 0 | Oct | 2021 | 0.026917 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-10-18 10:10 | 2021-10-18 15:57 | 1 | 005:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 15 EN MONTURA TRANSFORMADORES SE REMPLAZARON 3 CAJAS PRIMARIAS CARGA POR EL 1116-05 | S21101800111 | New_Event | Cutout Failure | Include | Include | Equipment | 347 | 2021-10-18 | 347 | keep | 0 | Oct | 2021 | 0.00023634 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-18 10:15 | 2021-10-18 16:00 | 100 | 005:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PERSONAL PRIVADO LIMPIANDO SOLAR TOCO TENZOR Y CRUZO LAS LINEAS | M21101800048 | New_Event |  |  | Include | Wildlife | 345 | 2021-10-18 | 34500 | keep | 0 | Oct | 2021 | 0.023498 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-18 10:30 | 2021-10-18 13:20 | 1 | 002:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 25KVA POR LA MISMA CAPACIDAD WR5955233 FID:33954041 MARCA:HOWARD #SERIE:1571600918 VOLTAJES 4160/7200 120/240 | A21101800030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 170 | 2021-10-18 | 170 | keep | 0 | Oct | 2021 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-18 10:33 | 2021-10-18 13:10 | 16 | 002:37 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR LA MISMA CAPACIDAD EN EL FID:19498208 MARCA:EATON #SERIE:205593818 VOLTAJES 2400/4200 120/240 | M21101800042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 157 | 2021-10-18 | 2512 | keep | 0 | Oct | 2021 | 0.0017109 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2021-10-18 10:45 | 2021-10-18 11:58 | 7 | 001:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | R21101800019 | New_Event | Bad Weather | Include | Include | Weather | 73 | 2021-10-18 | 511 | keep | 0 | Oct | 2021 | 0.00034804 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
AGUADILLA | 2021-10-18 10:45 | 2021-10-18 13:45 | 1 | 003:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA CON ESCAPE DE ACEITE POR LO MISMO | M21101800040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 180 | 2021-10-18 | 180 | keep | 0 | Oct | 2021 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-18 10:46 | 2021-10-21 16:15 | 1 | 077:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21101800034 | New_Event | Bad Weather | Include | Include | Weather | 4649 | 2021-10-18 | 4649 | keep | 0 | Oct | 2021 | 0.0031664 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-10-18 10:47 | 2021-10-18 13:42 | 29 | 002:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMDOR CRUCE POR AVE | R21101800021 | New_Event |  |  | Include | Wildlife | 175 | 2021-10-18 | 5075 | keep | 0 | Oct | 2021 | 0.0034566 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
CAGUAS | 2021-10-18 10:50 | 2021-10-18 11:15 | 7 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIIO TRANSFORMADOR PARA REPARAR BAJANTE Y TOMA | C21101800034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-10-18 | 175 | keep | 0 | Oct | 2021 | 0.00011919 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-18 10:51 | 2021-10-18 15:34 | 15 | 004:43 | P | DESGANCHE | 1 X 50 EN RISER SE REALIZO DESGANCHE | S21101800124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-10-18 | 4245 | keep | 0 | Oct | 2021 | 0.0028913 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-18 10:56 | 2021-10-18 13:48 | 20 | 002:52 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA REMPLAZO 2 PARARRAYOS | C21101800058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 172 | 2021-10-18 | 3440 | keep | 0 | Oct | 2021 | 0.002343 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-18 11:06 | 2021-10-18 15:45 | 60 | 004:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21101800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2021-10-18 | 16740 | keep | 0 | Oct | 2021 | 0.011402 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-18 11:18 | 2021-10-18 16:05 | 12 | 004:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CAJA DE CORTE DE LINEA | M21101800053 | New_Event | Wire Down | Include | Include | Equipment | 287 | 2021-10-18 | 3444 | keep | 0 | Oct | 2021 | 0.0023457 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BARRANQUITAS | 2021-10-18 11:19 | 2021-10-18 19:09 | 15 | 007:50 | P | ESTRUCTURA AVERIADA | REMPLAZO POSTE PARTIDO Y TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C21101700054 | New_Event | Defective Pole | Include | Include | Equipment | 470 | 2021-10-18 | 7050 | keep | 0 | Oct | 2021 | 0.0048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-18 11:21 | 2021-10-19 14:23 | 1655 | 027:02 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA Y AISLADOR PODRIDO | C21101800062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1622 | 2021-10-18 | 2684410 | keep | 0 | Oct | 2021 | 1.8283 | 0.0011272 | Sustained | FALSE | TRUE | Not_TMED_Event | 1655
CAGUAS | 2021-10-18 11:22 | 2021-10-18 16:57 | 40 | 005:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21101800064 | New_Event | Bad Weather | Include | Include | Weather | 335 | 2021-10-18 | 13400 | keep | 0 | Oct | 2021 | 0.0091267 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-18 11:23 | 2021-10-18 12:21 | 21 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21101800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-10-18 | 1218 | keep | 0 | Oct | 2021 | 0.00082957 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
HUMACAO | 2021-10-18 11:37 | 2021-10-18 11:38 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 12650 | C21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2450 | keep | 0 | Oct | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-10-18 11:37 | 2021-10-18 11:38 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 12650 | C21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 640 | keep | 0 | Oct | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
HUMACAO | 2021-10-18 11:38 | 2021-10-18 11:39 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO JUNTO CON LA LINEA 12600 SE CERRO POR SCADA | C21101800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 2450 | keep | 0 | Oct | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | TRUE | Not_TMED_Event | 2450
VEGA BAJA | 2021-10-18 11:45 | 2021-10-18 17:10 | 30 | 005:25 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21101800066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2021-10-18 | 9750 | keep | 0 | Oct | 2021 | 0.0066407 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-18 11:56 | 2021-10-18 14:45 | 30 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | S21101800134 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2021-10-18 | 5070 | keep | 0 | Oct | 2021 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-18 11:59 | 2021-10-19 10:27 | 30 | 022:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21101800135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1348 | 2021-10-18 | 40440 | keep | 0 | Oct | 2021 | 0.027543 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-10-18 12:01 | 2021-10-18 18:41 | 150 | 006:40 | P | DESGANCHE | 1 X 100 EN CL Y 1 X 10 EN TRANSFORMADOR | C21101800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2021-10-18 | 60000 | keep | 0 | Oct | 2021 | 0.040866 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-10-18 12:05 | 2021-10-18 15:55 | 2 | 003:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO CONECTORES | A21101800048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 230 | 2021-10-18 | 460 | keep | 0 | Oct | 2021 | 0.0003133 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-10-18 12:09 | 2021-10-18 19:51 | 45 | 007:42 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | C21101800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 462 | 2021-10-18 | 20790 | keep | 0 | Oct | 2021 | 0.01416 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-10-18 12:10 | 2021-10-18 19:00 | 50 | 006:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | P21101800086 | New_Event | Bad Weather | Include | Include | Weather | 410 | 2021-10-18 | 20500 | keep | 0 | Oct | 2021 | 0.013962 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-18 12:20 | 2021-10-18 14:25 | 1 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO SE CERO CORTE DE LINEA ABIERTO UN CLIENTE | M21101800004 | New_Event | Wire Down | Include | Include | Equipment | 125 | 2021-10-18 | 125 | keep | 0 | Oct | 2021 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 12:27 | 2021-10-18 14:40 | 1 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN SU 50 Y 1 X 20 EN BANCO DE TRANSFORMADORES SE DESPEGO NEUTRAL DE LA CAJA | R21101800029 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2021-10-18 | 133 | keep | 0 | Oct | 2021 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 12:31 | 2021-10-18 13:42 | 7 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR LAGARTIJO | R21101800030 | New_Event |  |  | Include | Wildlife | 71 | 2021-10-18 | 497 | keep | 0 | Oct | 2021 | 0.0003385 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-10-18 12:54 | 2021-10-18 18:38 | 60 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21101800078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2021-10-18 | 20640 | keep | 0 | Oct | 2021 | 0.014058 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1339 | keep | 0 | Oct | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 470 | keep | 0 | Oct | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | TRUE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2483 | keep | 0 | Oct | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | TRUE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2190 | keep | 0 | Oct | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | TRUE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 3006 | keep | 0 | Oct | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 179 | keep | 0 | Oct | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | TRUE | Not_TMED_Event | 179
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 107 | keep | 0 | Oct | 2021 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1666 | keep | 0 | Oct | 2021 | 0.0011347 | 0.0011347 | Momentary | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 4387 | keep | 0 | Oct | 2021 | 0.002988 | 0.002988 | Momentary | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 3147 | keep | 0 | Oct | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-10-18 12:55 | 2021-10-18 12:56 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21101800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 4304 | keep | 0 | Oct | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2021-10-18 12:56 | 2021-10-18 16:16 | 50 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21101800058 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-10-18 | 10000 | keep | 0 | Oct | 2021 | 0.006811 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-18 13:00 | 2021-10-18 20:14 | 50 | 007:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21101800135 | New_Event | Bad Weather | Include | Include | Weather | 434 | 2021-10-18 | 21700 | keep | 0 | Oct | 2021 | 0.01478 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-18 13:02 | 2021-10-18 13:03 | 671 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21101800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-18 | 671 | keep | 0 | Oct | 2021 | 0.00045702 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
MAYAGÃœEZ | 2021-10-18 13:03 | 2021-10-18 20:04 | 12 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21101800203 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 421 | 2021-10-18 | 5052 | keep | 0 | Oct | 2021 | 0.0034409 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
PONCE | 2021-10-18 13:04 | 2021-10-19 11:00 | 1 | 021:56 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21101800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1316 | 2021-10-18 | 1316 | keep | 0 | Oct | 2021 | 0.00089632 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:22 | 591 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-18 | 7092 | keep | 0 | Oct | 2021 | 0.0048303 | 0.00040253 | Sustained | FALSE | TRUE | Not_TMED_Event | 591
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 1924 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 19240 | keep | 0 | Oct | 2021 | 0.013104 | 0.0013104 | Sustained | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 968 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 9680 | keep | 0 | Oct | 2021 | 0.006593 | 0.0006593 | Sustained | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 680 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 6800 | keep | 0 | Oct | 2021 | 0.0046314 | 0.00046314 | Sustained | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2246 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 22460 | keep | 0 | Oct | 2021 | 0.015297 | 0.0015297 | Sustained | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:22 | 2011 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-18 | 24132 | keep | 0 | Oct | 2021 | 0.016436 | 0.0013697 | Sustained | FALSE | TRUE | Not_TMED_Event | 2011
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:22 | 339 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-18 | 4068 | keep | 0 | Oct | 2021 | 0.0027707 | 0.00023089 | Sustained | FALSE | TRUE | Not_TMED_Event | 339
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2470 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 24700 | keep | 0 | Oct | 2021 | 0.016823 | 0.0016823 | Sustained | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 1182 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 11820 | keep | 0 | Oct | 2021 | 0.0080505 | 0.00080505 | Sustained | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2340 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 23400 | keep | 0 | Oct | 2021 | 0.015938 | 0.0015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 1637 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 16370 | keep | 0 | Oct | 2021 | 0.01115 | 0.001115 | Sustained | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 1475 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 14750 | keep | 0 | Oct | 2021 | 0.010046 | 0.0010046 | Sustained | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 661 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 6610 | keep | 0 | Oct | 2021 | 0.004502 | 0.0004502 | Sustained | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 1569 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 15690 | keep | 0 | Oct | 2021 | 0.010686 | 0.0010686 | Sustained | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2309 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 23090 | keep | 0 | Oct | 2021 | 0.015726 | 0.0015726 | Sustained | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2179 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 21790 | keep | 0 | Oct | 2021 | 0.014841 | 0.0014841 | Sustained | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2440 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 24400 | keep | 0 | Oct | 2021 | 0.016619 | 0.0016619 | Sustained | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 1352 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 13520 | keep | 0 | Oct | 2021 | 0.0092084 | 0.00092084 | Sustained | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 3973 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 39730 | keep | 0 | Oct | 2021 | 0.02706 | 0.002706 | Sustained | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-10-18 13:10 | 2021-10-18 13:20 | 2484 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21101800057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-18 | 24840 | keep | 0 | Oct | 2021 | 0.016918 | 0.0016918 | Sustained | FALSE | TRUE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-10-18 13:10 | 2021-10-18 13:12 | 281 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 562 | keep | 0 | Oct | 2021 | 0.00038278 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-10-18 13:10 | 2021-10-18 13:12 | 1252 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 2504 | keep | 0 | Oct | 2021 | 0.0017055 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-10-18 13:10 | 2021-10-18 13:12 | 595 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 1190 | keep | 0 | Oct | 2021 | 0.0008105 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-10-18 13:10 | 2021-10-18 13:12 | 51 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 102 | keep | 0 | Oct | 2021 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-10-18 13:10 | 2021-10-18 13:12 | 721 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 1442 | keep | 0 | Oct | 2021 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2021-10-18 13:10 | 2021-10-18 13:12 | 1382 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | A21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 2764 | keep | 0 | Oct | 2021 | 0.0018825 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2021-10-18 13:10 | 2021-10-18 13:12 | 654 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | A21101800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-18 | 1308 | keep | 0 | Oct | 2021 | 0.00089087 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2021-10-18 13:12 | 2021-10-18 13:16 | 16 | 000:04 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR LA MISMA CAPACIDAD EN EL FID:19498208 MARCA:EATON #SERIE:205593818 VOLTAJES 2400/4200 120/240 | M21101800042 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 4 | 2021-10-18 | 64 | keep | 0 | Oct | 2021 | 4.359e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-18 13:13 | 2021-10-18 17:38 | 6 | 004:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21101800079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 265 | 2021-10-18 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-18 13:16 | 2021-10-18 13:22 | 281 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 1686 | keep | 0 | Oct | 2021 | 0.0011483 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-10-18 13:16 | 2021-10-18 13:22 | 1252 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 7512 | keep | 0 | Oct | 2021 | 0.0051164 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-10-18 13:16 | 2021-10-18 13:22 | 595 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 3570 | keep | 0 | Oct | 2021 | 0.0024315 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-10-18 13:16 | 2021-10-18 13:22 | 51 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 306 | keep | 0 | Oct | 2021 | 0.00020842 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-10-18 13:16 | 2021-10-18 13:22 | 721 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA YAUCO 38KV | M21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 4326 | keep | 0 | Oct | 2021 | 0.0029464 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2021-10-18 13:16 | 2021-10-18 13:22 | 1382 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV DE YAUCO 1 | A21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 8292 | keep | 0 | Oct | 2021 | 0.0056476 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2021-10-18 13:16 | 2021-10-18 13:22 | 654 | 000:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV DE YAUCO 1 | A21101800000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2021-10-18 | 3924 | keep | 0 | Oct | 2021 | 0.0026726 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
YAUCO | 2021-10-18 13:22 | 2021-10-18 17:03 | 50 | 003:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLASO CAJA QUEMADA | P21101700069 | New_Event | Cutout Failure | Include | Include | Equipment | 221 | 2021-10-18 | 11050 | keep | 0 | Oct | 2021 | 0.0075261 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-18 13:22 | 2021-10-19 13:54 | 16 | 024:32 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR LA MISMA CAPACIDAD EN EL FID:19498208 MARCA:EATON #SERIE:205593818 VOLTAJES 2400/4200 120/240 | M21101800042 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 1472 | 2021-10-18 | 23552 | keep | 0 | Oct | 2021 | 0.016041 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-10-18 13:23 | 2021-10-18 16:16 | 50 | 002:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA | M21101800065 | New_Event | Wire Down | Include | Include | Equipment | 173 | 2021-10-18 | 8650 | keep | 0 | Oct | 2021 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-18 13:29 | 2021-10-20 13:45 | 1 | 048:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15 KVA AVERIADO POR TRANSFORMADOR DE 15 KVA NUEVO | M21101800067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2896 | 2021-10-18 | 2896 | keep | 0 | Oct | 2021 | 0.0019725 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-18 13:39 | 2021-10-18 13:40 | 2833 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21101800065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 2833 | keep | 0 | Oct | 2021 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
CANOVANAS | 2021-10-18 13:42 | 2021-10-18 14:06 | 7 | 000:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21101800036 | New_Event |  |  | Include | Wildlife | 24 | 2021-10-18 | 168 | keep | 0 | Oct | 2021 | 0.00011442 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CANOVANAS | 2021-10-18 13:54 | 2021-10-18 16:31 | 7 | 002:37 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | R21101800037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 157 | 2021-10-18 | 1099 | keep | 0 | Oct | 2021 | 0.00074852 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-18 13:58 | 2021-10-18 16:23 | 15 | 002:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 15KVA POR IGUAL | B21101800034 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 145 | 2021-10-18 | 2175 | keep | 0 | Oct | 2021 | 0.0014814 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-18 14:06 | 2021-10-19 19:57 | 10 | 029:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 50 KVA POR 50 KVA | S21101800157 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1791 | 2021-10-18 | 17910 | keep | 0 | Oct | 2021 | 0.012198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-18 14:19 | 2021-10-18 17:41 | 195 | 003:22 | P | DESGANCHE | 2 X 80 Y 1 X 100 EN CORTES DE LINEA | C21101800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-10-18 | 39390 | keep | 0 | Oct | 2021 | 0.026828 | 0.00013281 | Sustained | FALSE | TRUE | Not_TMED_Event | 195
FAJARDO | 2021-10-18 14:26 | 2021-10-18 15:17 | 40 | 000:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESPEGO STRESS CONE DEL POSTE | R21101800039 | New_Event | Wire Down | Include | Include | Equipment | 51 | 2021-10-18 | 2040 | keep | 0 | Oct | 2021 | 0.0013894 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-10-18 14:27 | 2021-10-18 14:28 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1569 | keep | 0 | Oct | 2021 | 0.0010686 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
YAUCO | 2021-10-18 14:27 | 2021-10-18 14:28 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2309 | keep | 0 | Oct | 2021 | 0.0015726 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
YAUCO | 2021-10-18 14:27 | 2021-10-18 14:28 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2179 | keep | 0 | Oct | 2021 | 0.0014841 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
YAUCO | 2021-10-18 14:27 | 2021-10-18 14:28 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2440 | keep | 0 | Oct | 2021 | 0.0016619 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-18 14:29 | 2021-10-18 17:52 | 2999 | 003:23 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PATRULLO Y NO SE ENCONTRO CAUSA ALGUNA. | M21101800075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-10-18 | 608797 | keep | 0 | Oct | 2021 | 0.41465 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
BARRANQUITAS | 2021-10-18 14:31 | 2021-10-18 17:32 | 4 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21101800086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-10-18 | 724 | keep | 0 | Oct | 2021 | 0.00049311 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-18 14:42 | 2021-10-18 17:35 | 350 | 002:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21101800086 | New_Event | Bad Weather | Include | Include | Weather | 173 | 2021-10-18 | 60550 | keep | 0 | Oct | 2021 | 0.04124 | 0.00023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 350
CAGUAS | 2021-10-18 14:51 | 2021-10-18 14:52 | 554 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21101800113 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-18 | 554 | keep | 0 | Oct | 2021 | 0.00037733 | 0.00037733 | Momentary | FALSE | FALSE | Not_TMED_Event | 554
CAGUAS | 2021-10-18 14:52 | 2021-10-18 15:49 | 200 | 000:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | C21101800117 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 57 | 2021-10-18 | 11400 | keep | 0 | Oct | 2021 | 0.0077645 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-10-18 14:57 | 2021-10-19 00:07 | 80 | 009:10 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO PUENTE Y MACHETE | S21101800170 | New_Event | Switch Failure | Include | Include | Equipment | 550 | 2021-10-18 | 44000 | keep | 0 | Oct | 2021 | 0.029968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-10-18 14:59 | 2021-10-19 10:26 | 26 | 019:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMP0 | C21101800100 | New_Event | Bad Weather | Include | Include | Weather | 1167 | 2021-10-18 | 30342 | keep | 0 | Oct | 2021 | 0.020666 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
UTUADO | 2021-10-18 15:06 | 2021-10-18 19:00 | 10 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21101800077 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2021-10-18 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-18 15:15 | 2021-10-18 18:43 | 5 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21101800104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-10-18 | 1040 | keep | 0 | Oct | 2021 | 0.00070834 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-10-18 15:20 | 2021-10-18 19:00 | 15 | 003:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | M21101800112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 220 | 2021-10-18 | 3300 | keep | 0 | Oct | 2021 | 0.0022476 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-18 15:21 | 2021-10-18 15:22 | 638 | 000:01 | T | DESGANCHE | RECIERRE | C21101800111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 638 | keep | 0 | Oct | 2021 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2021-10-18 15:22 | 2021-10-19 11:08 | 120 | 019:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21101800122 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1186 | 2021-10-18 | 142320 | keep | 0 | Oct | 2021 | 0.096934 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
YAUCO | 2021-10-18 15:30 | 2021-10-19 09:54 | 15 | 018:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGA ELECTRICA | P21101800101 | New_Event | Bad Weather | Include | Include | Weather | 1104 | 2021-10-18 | 16560 | keep | 0 | Oct | 2021 | 0.011279 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-10-18 15:36 | 2021-10-18 16:51 | 40 | 001:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21101800118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-10-18 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-10-18 15:39 | 2021-10-19 11:54 | 2 | 020:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA AVERIADA | P21101800107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1215 | 2021-10-18 | 2430 | keep | 0 | Oct | 2021 | 0.0016551 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CAGUAS | 2021-10-18 15:49 | 2021-10-18 16:36 | 554 | 000:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A SOLICITUD EL SUPERVISOR RAUL SUAREZ POR CONDUCTOR VIVO EN EL SUELO | C21101800124 | Additional_clients | Wire Down | Include | Include | Equipment | 47 | 2021-10-18 | 26038 | keep | 0 | Oct | 2021 | 0.017734 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-18 15:50 | 2021-10-18 15:55 | 6 | 000:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21101800080 | New_Event | Bad Weather | Include | Include | Weather | 5 | 2021-10-18 | 30 | keep | 0 | Oct | 2021 | 2.0433e-05 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-10-18 15:58 | 2021-10-18 18:50 | 100 | 002:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA DESCARGA ELECTRICA | P21101800115 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2021-10-18 | 17200 | keep | 0 | Oct | 2021 | 0.011715 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-18 16:02 | 2021-10-18 19:30 | 80 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21101800082 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2021-10-18 | 16640 | keep | 0 | Oct | 2021 | 0.011333 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-18 16:12 | 2021-10-19 12:58 | 300 | 020:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | A21101800085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1246 | 2021-10-18 | 373800 | keep | 0 | Oct | 2021 | 0.25459 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-10-18 16:22 | 2021-10-18 19:05 | 10 | 002:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21101800129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 163 | 2021-10-18 | 1630 | keep | 0 | Oct | 2021 | 0.0011102 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-18 16:29 | 2021-10-19 18:29 | 10 | 025:60 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21101800107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1560 | 2021-10-18 | 15600 | keep | 0 | Oct | 2021 | 0.010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-18 16:34 | 2021-10-18 23:20 | 12 | 006:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN PROVISIONAL | S21101800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 406 | 2021-10-18 | 4872 | keep | 0 | Oct | 2021 | 0.0033183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-10-18 16:36 | 2021-10-18 18:30 | 200 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y CERRO PUENTE | C21101800117 | Partial_restoration | Wire Down | Include | Include | Equipment | 114 | 2021-10-18 | 22800 | keep | 0 | Oct | 2021 | 0.015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-18 16:37 | 2021-10-19 09:44 | 1 | 017:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21101800136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1027 | 2021-10-18 | 1027 | keep | 0 | Oct | 2021 | 0.00069949 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 16:40 | 2021-10-18 18:10 | 5 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTES SECUNDARIOS | R21101800053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2021-10-18 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-18 16:48 | 2021-10-18 17:08 | 150 | 000:20 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DE RISER SU 1 PARA INSTALAR PUENTE DE FASE A FASE EN SU 1 Y ENERGIZAR CARGAS MONOFASICAS POR AVERIA DE CABLE SOTERRADO | S21101800049 | New_Event | UG Cable Fault | Include | Include | Equipment | 20 | 2021-10-18 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-10-18 16:51 | 2021-10-19 17:21 | 12 | 024:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR CARGA POR EL 1303-04 | S21101800191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1470 | 2021-10-18 | 17640 | keep | 0 | Oct | 2021 | 0.012015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-18 16:54 | 2021-10-18 19:05 | 150 | 002:11 | P | DESCONECTIVO DEFECTUOSO | 1 X 100 EN CORTE DE LINEA 2 X 80 FUSIBLES TIPO SMU EN SU SE REMPLAZO MACHETE AVERIADO Y SE REPARO TERMINACION | S21101700446 | New_Event | Switch Failure | Include | Include | Equipment | 131 | 2021-10-18 | 19650 | keep | 0 | Oct | 2021 | 0.013384 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-10-18 17:02 | 2021-10-18 19:54 | 55 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21101800141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-10-18 | 9460 | keep | 0 | Oct | 2021 | 0.0064432 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2021-10-18 17:24 | 2021-10-18 22:19 | 1 | 004:55 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRE RISER A SU-3 Y SE CERRO N/O EN SU-3 A SU-4 FASE C PARA DAR SERVICIO HAY QUE LIMPIAR SERVIDUMBRE PARA LLEGAR A RISER | B21101800110 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 295 | 2021-10-18 | 295 | keep | 0 | Oct | 2021 | 0.00020092 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 17:27 | 2021-10-18 18:45 | 30 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21101800198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-18 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-10-18 17:29 | 2021-10-18 18:45 | 4 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21101800097 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2021-10-18 | 304 | keep | 0 | Oct | 2021 | 0.00020705 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-10-18 17:42 | 2021-10-19 10:00 | 8 | 016:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21101800099 | New_Event | Bad Weather | Include | Include | Weather | 978 | 2021-10-18 | 7824 | keep | 0 | Oct | 2021 | 0.0053289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-18 17:50 | 2021-10-18 18:37 | 3 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21101800152 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2021-10-18 | 141 | keep | 0 | Oct | 2021 | 9.6034e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-10-18 17:52 | 2021-10-18 23:16 | 2999 | 005:24 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO TRONCAL ALIMENTADOR | M21101800075 | New_Event | Switch Failure | Include | Include | Equipment | 324 | 2021-10-18 | 971676 | keep | 0 | Oct | 2021 | 0.6618 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-10-18 17:52 | 2021-10-18 23:16 | 1597 | 005:24 | S | DESCONECTIVO DEFECTUOSO | SE REEMPAZO MACHETE QUEMADO TRONCAL ALIMENTADOR | M21101800075 | New_Event | Switch Failure | Include | Include | Equipment | 324 | 2021-10-18 | 517428 | keep | 0 | Oct | 2021 | 0.35242 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
VEGA BAJA | 2021-10-18 18:02 | 2021-10-18 20:52 | 10 | 002:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 X 37.5 CON PROBLEMAS DE ALTO VOLTAJE | B21101800128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 170 | 2021-10-18 | 1700 | keep | 0 | Oct | 2021 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-18 18:06 | 2021-10-18 18:07 | 1067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21101800084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-18 | 1067 | keep | 0 | Oct | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
YAUCO | 2021-10-18 18:07 | 2021-10-19 13:17 | 12 | 019:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P21101800128 | New_Event | Bad Weather | Include | Include | Weather | 1150 | 2021-10-18 | 13800 | keep | 0 | Oct | 2021 | 0.0093991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-10-18 18:08 | 2021-10-18 18:09 | 50 | 000:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P21101800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 50 | keep | 0 | Oct | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-18 18:17 | 2021-10-18 21:30 | 100 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEAS MAL TIEMPO | P21101800132 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-10-18 | 19300 | keep | 0 | Oct | 2021 | 0.013145 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-18 18:47 | 2021-10-19 19:55 | 2 | 025:08 | P | TRANSFORMADOR AVERIADO | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C21101800155 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1508 | 2021-10-18 | 3016 | keep | 0 | Oct | 2021 | 0.0020542 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-10-18 18:50 | 2021-10-18 18:51 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1352 | keep | 0 | Oct | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-10-18 18:50 | 2021-10-18 18:51 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 3973 | keep | 0 | Oct | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-10-18 18:50 | 2021-10-18 18:51 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2484 | keep | 0 | Oct | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
YAUCO | 2021-10-18 18:51 | 2021-10-19 08:48 | 100 | 013:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA DESCARGA ELECTRICA | P21101800115 | Partial_restoration | Bad Weather | Include | Include | Weather | 837 | 2021-10-18 | 83700 | keep | 0 | Oct | 2021 | 0.057008 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1924 | keep | 0 | Oct | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 968 | keep | 0 | Oct | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 680 | keep | 0 | Oct | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2246 | keep | 0 | Oct | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2470 | keep | 0 | Oct | 2021 | 0.0016823 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1182 | keep | 0 | Oct | 2021 | 0.00080505 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-10-18 18:52 | 2021-10-18 18:53 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1637 | keep | 0 | Oct | 2021 | 0.001115 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-10-18 18:55 | 2021-10-18 18:56 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 1924 | keep | 0 | Oct | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-10-18 18:55 | 2021-10-18 18:56 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 968 | keep | 0 | Oct | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-10-18 18:55 | 2021-10-18 18:56 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 680 | keep | 0 | Oct | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-10-18 18:55 | 2021-10-18 18:56 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2246 | keep | 0 | Oct | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
SAN JUAN | 2021-10-18 19:00 | 2021-10-18 23:15 | 178 | 004:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA | S21101800206 | New_Event | Cutout Failure | Include | Include | Equipment | 255 | 2021-10-18 | 45390 | keep | 0 | Oct | 2021 | 0.030915 | 0.00012123 | Sustained | FALSE | TRUE | Not_TMED_Event | 178
MAYAGÃœEZ | 2021-10-18 19:08 | 2021-10-18 21:02 | 100 | 001:54 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LINEA PRIMARIA | M21101800188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-10-18 | 11400 | keep | 0 | Oct | 2021 | 0.0077645 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-18 19:11 | 2021-10-18 21:22 | 30 | 002:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO PRIMARIO | S21101800213 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2021-10-18 | 3930 | keep | 0 | Oct | 2021 | 0.0026767 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-10-18 19:15 | 2021-10-18 19:16 | 65 | 000:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHARON Y REMPLAZO AISLADOR | C21101700266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 65 | keep | 0 | Oct | 2021 | 4.4271e-05 | 4.4271e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 65
UTUADO | 2021-10-18 19:53 | 2021-10-19 14:46 | 60 | 018:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101800108 | New_Event | Bad Weather | Include | Include | Weather | 1133 | 2021-10-18 | 67980 | keep | 0 | Oct | 2021 | 0.046301 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-10-18 20:07 | 2021-10-18 20:08 | 2011 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 2011 | keep | 0 | Oct | 2021 | 0.0013697 | 0.0013697 | Momentary | FALSE | TRUE | Not_TMED_Event | 2011
YAUCO | 2021-10-18 20:07 | 2021-10-18 20:08 | 339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P211018000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-18 | 339 | keep | 0 | Oct | 2021 | 0.00023089 | 0.00023089 | Momentary | FALSE | TRUE | Not_TMED_Event | 339
SAN JUAN | 2021-10-18 20:08 | 2021-10-18 20:38 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | S21101700304 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-10-18 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-18 20:22 | 2021-10-19 11:59 | 100 | 015:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CONVERTIDOR SE REMPLAZO CAJA | B21101800119 | New_Event | Cutout Failure | Include | Include | Equipment | 937 | 2021-10-18 | 93700 | keep | 0 | Oct | 2021 | 0.063819 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-10-18 20:26 | 2021-10-19 17:55 | 6 | 021:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CREO UN PROVISIONAL SECUNDARIO AEREO DESDE T-58 HASTA PEDESTAL SECUNDARIO | P21101800143 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1289 | 2021-10-18 | 7734 | keep | 0 | Oct | 2021 | 0.0052676 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-18 20:55 | 2021-10-19 10:06 | 300 | 013:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN TRONCAL DE ALIMENTADOR | A21101800115 | New_Event | Wire Down | Include | Include | Equipment | 791 | 2021-10-18 | 237300 | keep | 0 | Oct | 2021 | 0.16162 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-10-18 21:10 | 2021-10-18 21:11 | 100 | 000:01 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | P21101800086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 100 | keep | 0 | Oct | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-18 21:17 | 2021-10-19 17:24 | 1 | 020:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21101800161 | New_Event | Bad Weather | Include | Include | Weather | 1207 | 2021-10-18 | 1207 | keep | 0 | Oct | 2021 | 0.00082208 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-18 21:22 | 2021-10-18 21:50 | 108 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO PRIMARIO | S21101800213 | Additional_clients | Wire Down | Include | Include | Equipment | 28 | 2021-10-18 | 3024 | keep | 0 | Oct | 2021 | 0.0020596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-18 21:32 | 2021-10-19 11:18 | 120 | 013:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101800163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 826 | 2021-10-18 | 99120 | keep | 0 | Oct | 2021 | 0.06751 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-10-18 21:32 | 2021-10-19 16:35 | 10 | 019:03 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21101800124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1143 | 2021-10-18 | 11430 | keep | 0 | Oct | 2021 | 0.0077849 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-18 21:37 | 2021-10-18 21:38 | 50 | 000:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21101800106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-18 | 50 | keep | 0 | Oct | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-10-18 22:41 | 2021-10-19 13:58 | 99 | 015:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21101800165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 917 | 2021-10-18 | 90783 | keep | 0 | Oct | 2021 | 0.061832 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
CANOVANAS | 2021-10-19 01:24 | 2021-10-19 10:52 | 200 | 009:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 100 EN CORTE DE LINEA CRUCE POR REPTIL | R21101900001 | New_Event |  |  | Include | Wildlife | 568 | 2021-10-19 | 113600 | keep | 0 | Oct | 2021 | 0.077372 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-19 02:12 | 2021-10-20 11:38 | 15 | 033:26 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21101900009 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2006 | 2021-10-19 | 30090 | keep | 0 | Oct | 2021 | 0.020494 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-19 02:13 | 2021-10-19 02:14 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA INSTALAR PUENTE PORTATIL PARA DAR SERVICIO PARA REPARARLO MANANANA | S21101900007 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-10-19 | 271 | keep | 0 | Oct | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2021-10-19 02:47 | 2021-10-19 20:32 | 100 | 017:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21101900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1065 | 2021-10-19 | 106500 | keep | 0 | Oct | 2021 | 0.072537 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-19 04:19 | 2021-10-19 10:40 | 100 | 006:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | S21101900010 | New_Event | Cutout Failure | Include | Include | Equipment | 381 | 2021-10-19 | 38100 | keep | 0 | Oct | 2021 | 0.02595 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-19 05:11 | 2021-10-19 05:13 | 199 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | S21101900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-19 | 398 | keep | 0 | Oct | 2021 | 0.00027108 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
BARRANQUITAS | 2021-10-19 05:45 | 2021-10-19 09:57 | 89 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21101900002 | New_Event | Bad Weather | Include | Include | Weather | 252 | 2021-10-19 | 22428 | keep | 0 | Oct | 2021 | 0.015276 | 6.0617e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 89
ARECIBO | 2021-10-19 06:04 | 2021-10-19 06:05 | 2697 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR | A21101900000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-10-19 | 2697 | keep | 0 | Oct | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-10-19 06:05 | 2021-10-19 12:25 | 1 | 006:20 | P | OTRAS CAUSAS | 1 X 65 EN RISER CT AVERIADO | A21101900033 | 1st_after_momentary | Other Causes | Include | Include | Other | 380 | 2021-10-19 | 380 | keep | 0 | Oct | 2021 | 0.00025882 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-19 06:18 | 2021-10-19 06:19 | 1615 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21101900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-19 | 1615 | keep | 0 | Oct | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2021-10-19 06:19 | 2021-10-19 10:30 | 200 | 004:11 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21100900007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-10-19 | 50200 | keep | 0 | Oct | 2021 | 0.034191 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-10-19 06:24 | 2021-10-19 12:21 | 21 | 005:57 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21101900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-10-19 | 7497 | keep | 0 | Oct | 2021 | 0.0051062 | 1.4303e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 21
ARECIBO | 2021-10-19 06:35 | 2021-10-19 16:23 | 50 | 009:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101900012 | New_Event | Bad Weather | Include | Include | Weather | 588 | 2021-10-19 | 29400 | keep | 0 | Oct | 2021 | 0.020024 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-19 06:41 | 2021-10-19 10:27 | 70 | 003:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | M21101900008 | New_Event | Wire Down | Include | Include | Equipment | 226 | 2021-10-19 | 15820 | keep | 0 | Oct | 2021 | 0.010775 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-19 06:43 | 2021-10-19 08:50 | 70 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21101900009 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2021-10-19 | 8890 | keep | 0 | Oct | 2021 | 0.0060549 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
YAUCO | 2021-10-19 07:07 | 2021-10-19 13:04 | 7 | 005:57 | P | ESTRUCTURA AVERIADA | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR POSTE DE MADERA 35 PIES | P21101900012 | New_Event | Defective Pole | Include | Include | Equipment | 357 | 2021-10-19 | 2499 | keep | 0 | Oct | 2021 | 0.0017021 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-10-19 07:11 | 2021-10-19 07:12 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21101900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 732 | keep | 0 | Oct | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
GUAYAMA | 2021-10-19 07:22 | 2021-10-19 07:23 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21101900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 1945 | keep | 0 | Oct | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
YAUCO | 2021-10-19 07:25 | 2021-10-19 09:11 | 100 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGA ELECTRICA | P21101900015 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-10-19 | 10600 | keep | 0 | Oct | 2021 | 0.0072196 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-19 07:40 | 2021-10-19 07:41 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21101900018 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 732 | keep | 0 | Oct | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
VEGA BAJA | 2021-10-19 07:45 | 2021-10-19 17:11 | 10 | 009:26 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B21101900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 566 | 2021-10-19 | 5660 | keep | 0 | Oct | 2021 | 0.003855 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-19 07:48 | 2021-10-19 09:34 | 10 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-10-19 | 1060 | keep | 0 | Oct | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-19 07:52 | 2021-10-19 14:59 | 25 | 007:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101900034 | New_Event | Bad Weather | Include | Include | Weather | 427 | 2021-10-19 | 10675 | keep | 0 | Oct | 2021 | 0.0072707 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-10-19 08:01 | 2021-10-19 09:23 | 1 | 001:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN MONTURA DE TRANSFORMADORES DESCARGA ELECTRICA | P21101900020 | New_Event | Bad Weather | Include | Include | Weather | 82 | 2021-10-19 | 82 | keep | 0 | Oct | 2021 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-19 08:02 | 2021-10-19 11:50 | 169 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21101900010 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2021-10-19 | 38532 | keep | 0 | Oct | 2021 | 0.026244 | 0.00011511 | Sustained | FALSE | TRUE | Not_TMED_Event | 169
CAGUAS | 2021-10-19 08:12 | 2021-10-19 13:03 | 6 | 004:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21101900011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 291 | 2021-10-19 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-19 08:14 | 2021-10-20 15:48 | 15 | 031:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 50KVA | S21101900030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1894 | 2021-10-19 | 28410 | keep | 0 | Oct | 2021 | 0.01935 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-10-19 08:23 | 2021-10-19 08:24 | 5630 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | C21101900014 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-19 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-10-19 08:24 | 2021-10-19 11:52 | 1 | 003:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | C21101900020 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 208 | 2021-10-19 | 208 | keep | 0 | Oct | 2021 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-10-19 08:24 | 2021-10-19 11:41 | 10 | 003:17 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR SE DESCONECTO TOMA A CLIENTE CON DEFECTO INTERIOR | P21101900024 | New_Event | Other Causes | Include | Include | Other | 197 | 2021-10-19 | 1970 | keep | 0 | Oct | 2021 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-19 08:24 | 2021-10-20 13:24 | 15 | 028:60 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21101900020 | New_Event | Bad Weather | Include | Include | Weather | 1740 | 2021-10-19 | 26100 | keep | 0 | Oct | 2021 | 0.017777 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-10-19 08:28 | 2021-10-19 11:48 | 90 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 SMU EN SU-11 SWITCH UNIT CONTAMINADO CON COMEJEN | P21101900026 | New_Event |  |  | Include | Wildlife | 200 | 2021-10-19 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2021-10-19 08:30 | 2021-10-19 09:40 | 30 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 35 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21101900036 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2021-10-19 | 2100 | keep | 0 | Oct | 2021 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-19 08:31 | 2021-10-19 08:32 | 776 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21101900047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 776 | keep | 0 | Oct | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
BAYAMON | 2021-10-19 08:32 | 2021-10-19 09:06 | 12 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21101800004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-10-19 | 408 | keep | 0 | Oct | 2021 | 0.00027789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-10-19 08:37 | 2021-10-19 11:15 | 40 | 002:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21101900038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-10-19 | 6320 | keep | 0 | Oct | 2021 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-10-19 08:41 | 2021-10-19 21:35 | 15 | 012:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21101900023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 774 | 2021-10-19 | 11610 | keep | 0 | Oct | 2021 | 0.0079075 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-19 08:49 | 2021-10-20 14:00 | 200 | 029:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | M21101900024 | New_Event | Wire Down | Include | Include | Equipment | 1751 | 2021-10-19 | 350200 | keep | 0 | Oct | 2021 | 0.23852 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-19 08:55 | 2021-10-19 18:59 | 12 | 010:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE REGULO TRANSFORMADOR QUEDO 125V | S21101800076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 604 | 2021-10-19 | 7248 | keep | 0 | Oct | 2021 | 0.0049366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-19 09:00 | 2021-10-19 11:25 | 7 | 002:25 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 37.5 KVA X 37.5 KVA | R21101900003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2021-10-19 | 1015 | keep | 0 | Oct | 2021 | 0.00069131 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-10-19 09:03 | 2021-10-19 16:29 | 45 | 007:26 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21101800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2021-10-19 | 20070 | keep | 0 | Oct | 2021 | 0.01367 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-19 09:15 | 2021-10-19 14:33 | 20 | 005:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101900040 | New_Event | Bad Weather | Include | Include | Weather | 318 | 2021-10-19 | 6360 | keep | 0 | Oct | 2021 | 0.0043318 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-19 09:16 | 2021-10-19 17:40 | 40 | 008:24 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA QUE PERSONAL REALIZARA DESGANCHE | M21101900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 504 | 2021-10-19 | 20160 | keep | 0 | Oct | 2021 | 0.013731 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-19 09:16 | 2021-10-19 19:16 | 1 | 010:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101900042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 600 | 2021-10-19 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-19 09:17 | 2021-10-19 15:00 | 60 | 005:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M21101900077 | New_Event | Cutout Failure | Include | Include | Equipment | 343 | 2021-10-19 | 20580 | keep | 0 | Oct | 2021 | 0.014017 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-19 09:21 | 2021-10-19 11:10 | 80 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21101900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-10-19 | 8720 | keep | 0 | Oct | 2021 | 0.0059392 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-19 09:25 | 2021-10-19 09:46 | 1 | 000:21 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER Y 1 X 40 EN TRANSCLOSURE | B21101900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-10-19 | 21 | keep | 0 | Oct | 2021 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-19 09:26 | 2021-10-19 11:25 | 30 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21101800048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-10-19 | 3570 | keep | 0 | Oct | 2021 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-19 09:28 | 2021-10-19 15:32 | 20 | 006:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | S21101800091 | New_Event | Wire Down | Include | Include | Equipment | 364 | 2021-10-19 | 7280 | keep | 0 | Oct | 2021 | 0.0049584 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-19 09:31 | 2021-10-19 10:15 | 10 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA EN TRANSFORMADOR PARA REPARAR BARRA EN PEDESTAL | C21101900070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-10-19 | 440 | keep | 0 | Oct | 2021 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-19 09:41 | 2021-10-19 11:49 | 10 | 002:08 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 75 KVA X 75 KVA | R21101900007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 128 | 2021-10-19 | 1280 | keep | 0 | Oct | 2021 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-19 09:48 | 2021-10-19 18:00 | 100 | 008:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR BAMBU | P21101900033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 492 | 2021-10-19 | 49200 | keep | 0 | Oct | 2021 | 0.03351 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-19 09:57 | 2021-10-20 14:56 | 35 | 028:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA RAYOS | B12101900048 | New_Event | Bad Weather | Include | Include | Weather | 1739 | 2021-10-19 | 60865 | keep | 0 | Oct | 2021 | 0.041455 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-10-19 10:06 | 2021-10-19 11:19 | 11 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA PARA REPARAR SECUNDARIA | C21101800057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2021-10-19 | 803 | keep | 0 | Oct | 2021 | 0.00054692 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2021-10-19 10:06 | 2021-10-19 15:58 | 1 | 005:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | C21101900024 | New_Event | Bad Weather | Include | Include | Weather | 352 | 2021-10-19 | 352 | keep | 0 | Oct | 2021 | 0.00023975 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-19 10:06 | 2021-10-19 11:29 | 1720 | 001:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL DE ALIMENTADOR AUTORIZADO POR A SOTO | A21101900047 | Additional_clients | Wire Down | Include | Include | Equipment | 83 | 2021-10-19 | 142760 | keep | 0 | Oct | 2021 | 0.097233 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-10-19 10:25 | 2021-10-19 14:50 | 2 | 004:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA LIMPIEZA DE CONECTORES SECUNDARIOS | M21101900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 265 | 2021-10-19 | 530 | keep | 0 | Oct | 2021 | 0.00036098 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-10-19 10:25 | 2021-10-19 14:11 | 20 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21101900051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2021-10-19 | 4520 | keep | 0 | Oct | 2021 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-19 10:32 | 2021-10-19 16:57 | 15 | 006:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M21101900048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 385 | 2021-10-19 | 5775 | keep | 0 | Oct | 2021 | 0.0039333 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-19 10:42 | 2021-10-20 16:33 | 80 | 029:51 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21101900056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1791 | 2021-10-19 | 143280 | keep | 0 | Oct | 2021 | 0.097587 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-10-19 10:50 | 2021-10-19 10:51 | 817 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 817 | keep | 0 | Oct | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
AGUADILLA | 2021-10-19 11:00 | 2021-10-19 14:30 | 30 | 003:30 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA REALIZAR TRABAJOS EN LINEA 6000 | M21101900052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 210 | 2021-10-19 | 6300 | keep | 0 | Oct | 2021 | 0.0042909 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-19 11:01 | 2021-10-19 12:06 | 10 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN SECUNDARIA | C21101900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-10-19 | 650 | keep | 0 | Oct | 2021 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-19 11:33 | 2021-10-21 04:06 | 8 | 040:33 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | S21101900269 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2433 | 2021-10-19 | 19464 | keep | 0 | Oct | 2021 | 0.013257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-10-19 11:36 | 2021-10-19 14:54 | 1 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGA ELECTRICA | P21101900038 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-10-19 | 198 | keep | 0 | Oct | 2021 | 0.00013486 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-19 11:37 | 2021-10-19 15:20 | 527 | 003:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SU CARGA ESTA POR EL 6404-04 | M21101900068 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-10-19 | 117521 | keep | 0 | Oct | 2021 | 0.080043 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2021-10-19 11:37 | 2021-10-19 15:20 | 671 | 003:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR LINEAM PRIMARIA | M21101900068 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-10-19 | 149633 | keep | 0 | Oct | 2021 | 0.10191 | 0.00045702 | Sustained | FALSE | TRUE | Not_TMED_Event | 671
GUAYAMA | 2021-10-19 11:43 | 2021-10-19 16:16 | 5 | 004:33 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA AVERIADA POR RAMA DE ARBOL | P21101900039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 273 | 2021-10-19 | 1365 | keep | 0 | Oct | 2021 | 0.0009297 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
HUMACAO | 2021-10-19 11:52 | 2021-10-19 11:53 | 5630 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | C21101900045 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-19 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-10-19 11:53 | 2021-10-19 13:56 | 1 | 002:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | C21101900020 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2021-10-19 | 123 | keep | 0 | Oct | 2021 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-19 11:53 | 2021-10-19 13:56 | 64 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMLAZO AISLADOR ROTO Y SE LEVANTO CONDUCTOR PRIMARIO CERRARON CORTE DE LINEA | C21101900074 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 123 | 2021-10-19 | 7872 | keep | 0 | Oct | 2021 | 0.0053616 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
UTUADO | 2021-10-19 12:03 | 2021-10-19 14:00 | 30 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101190064 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-10-19 | 3510 | keep | 0 | Oct | 2021 | 0.0023906 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-19 12:33 | 2021-10-19 14:07 | 40 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R21101900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2021-10-19 | 3760 | keep | 0 | Oct | 2021 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-19 12:39 | 2021-10-19 16:40 | 34 | 004:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE CERRO PUENTE DE CAJA A TRANSFORMADOR | C21101900049 | New_Event | Wire Down | Include | Include | Equipment | 241 | 2021-10-19 | 8194 | keep | 0 | Oct | 2021 | 0.0055809 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
PONCE | 2021-10-19 12:39 | 2021-10-19 15:24 | 60 | 002:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR BAMBU | P21101900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-10-19 | 9900 | keep | 0 | Oct | 2021 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-10-19 12:55 | 2021-10-19 16:59 | 85 | 004:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A LINEA | C21101900054 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2021-10-19 | 20740 | keep | 0 | Oct | 2021 | 0.014126 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
AGUADILLA | 2021-10-19 12:56 | 2021-10-19 15:25 | 10 | 002:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO CONECTORES SECUNDARIOS | M21101900078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 149 | 2021-10-19 | 1490 | keep | 0 | Oct | 2021 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-19 12:58 | 2021-10-19 18:58 | 51 | 006:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21101900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 360 | 2021-10-19 | 18360 | keep | 0 | Oct | 2021 | 0.012505 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
BAYAMON | 2021-10-19 13:00 | 2021-10-19 21:25 | 30 | 008:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101900069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 505 | 2021-10-19 | 15150 | keep | 0 | Oct | 2021 | 0.010319 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-10-19 13:03 | 2021-10-19 14:12 | 10 | 001:09 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50 KVA X 50 KVA | R21101900020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 69 | 2021-10-19 | 690 | keep | 0 | Oct | 2021 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-19 13:03 | 2021-10-19 14:38 | 10 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA Y TOMAS | B21101800009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-10-19 | 950 | keep | 0 | Oct | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-10-19 13:04 | 2021-10-19 16:38 | 7 | 003:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR REPTIL | R21101900021 | New_Event |  |  | Include | Wildlife | 214 | 2021-10-19 | 1498 | keep | 0 | Oct | 2021 | 0.0010203 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-19 13:20 | 2021-10-19 17:19 | 5 | 003:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA AVERIADO X 25 KVA NUEVO | A21101900064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 239 | 2021-10-19 | 1195 | keep | 0 | Oct | 2021 | 0.00081391 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-19 13:32 | 2021-10-19 17:25 | 5 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE RECONECTO NEUTRAL SECUNDARIO A TRANSFORMADOR | A21101900034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2021-10-19 | 1165 | keep | 0 | Oct | 2021 | 0.00079348 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-10-19 13:56 | 2021-10-19 13:57 | 5630 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | C21101900064 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-10-19 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-19 13:57 | 2021-10-19 15:08 | 1 | 001:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | C21101900020 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 71 | 2021-10-19 | 71 | keep | 0 | Oct | 2021 | 4.8358e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-19 13:57 | 2021-10-19 17:46 | 64 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMLAZO AISLADOR ROTO Y SE LEVANTO CONDUCTOR PRIMARIO CERRARON CORTE DE LINEA | C21101900074 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 229 | 2021-10-19 | 14656 | keep | 0 | Oct | 2021 | 0.0099821 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
ARECIBO | 2021-10-19 13:59 | 2021-10-19 19:00 | 12 | 005:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | A21101900073 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2021-10-19 | 3612 | keep | 0 | Oct | 2021 | 0.0024601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-10-19 14:01 | 2021-10-19 15:40 | 15 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21101900092 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-10-19 | 1485 | keep | 0 | Oct | 2021 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-19 14:06 | 2021-10-19 15:20 | 20 | 001:14 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE DESGANCHO Y LEVANTARON SECUNDARIA | C21101900065 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 74 | 2021-10-19 | 1480 | keep | 0 | Oct | 2021 | 0.001008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-19 14:12 | 2021-10-19 15:10 | 50 | 000:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21101900096 | New_Event | Bad Weather | Include | Include | Weather | 58 | 2021-10-19 | 2900 | keep | 0 | Oct | 2021 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-19 14:26 | 2021-10-19 16:06 | 40 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN SU-1 | S21101800162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-10-19 | 4000 | keep | 0 | Oct | 2021 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-10-19 14:42 | 2021-10-20 14:20 | 45 | 023:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21101900047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1418 | 2021-10-19 | 63810 | keep | 0 | Oct | 2021 | 0.043461 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-10-19 14:43 | 2021-10-19 18:16 | 5 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | B21101800088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-10-19 | 1065 | keep | 0 | Oct | 2021 | 0.00072537 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-10-19 14:48 | 2021-10-19 18:03 | 8 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21101900025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2021-10-19 | 1560 | keep | 0 | Oct | 2021 | 0.0010625 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-10-19 14:50 | 2021-10-19 18:20 | 50 | 003:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA Y DESGANCHE | S21101900102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-10-19 | 10500 | keep | 0 | Oct | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-19 14:54 | 2021-10-21 18:16 | 7 | 051:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3082 | 2021-10-19 | 21574 | keep | 0 | Oct | 2021 | 0.014694 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-10-19 14:55 | 2021-10-19 17:58 | 65 | 003:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A RISER | C21101900083 | New_Event | Wire Down | Include | Include | Equipment | 183 | 2021-10-19 | 11895 | keep | 0 | Oct | 2021 | 0.0081016 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-10-19 15:00 | 2021-10-19 15:01 | 2888 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO LA CAUSA | A21101900079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 2888 | keep | 0 | Oct | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
BAYAMON | 2021-10-19 15:12 | 2021-10-19 15:51 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B21101900086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-10-19 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-10-19 15:16 | 2021-10-20 11:11 | 20 | 019:55 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S21101900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1195 | 2021-10-19 | 23900 | keep | 0 | Oct | 2021 | 0.016278 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-19 15:24 | 2021-10-19 15:25 | 1571 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21101900056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-19 | 1571 | keep | 0 | Oct | 2021 | 0.00107 | 0.00107 | Momentary | FALSE | TRUE | Not_TMED_Event | 1571
PONCE | 2021-10-19 15:24 | 2021-10-19 15:25 | 752 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21101900056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-19 | 752 | keep | 0 | Oct | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | TRUE | Not_TMED_Event | 752
PONCE | 2021-10-19 15:25 | 2021-10-19 20:02 | 60 | 004:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR BAMBU | P21101900059 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-10-19 | 16620 | keep | 0 | Oct | 2021 | 0.01132 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-19 15:27 | 2021-10-19 17:25 | 30 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101900081 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-10-19 | 3540 | keep | 0 | Oct | 2021 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-19 15:30 | 2021-10-19 15:32 | 837 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1401-07 | S21101900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-19 | 1674 | keep | 0 | Oct | 2021 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-10-19 15:30 | 2021-10-19 15:32 | 908 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1401-6 | S21101900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-19 | 1816 | keep | 0 | Oct | 2021 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2021-10-19 15:32 | 2021-10-19 15:43 | 4291 | 000:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN TRONCAL Y SE CERRO INTERRUPTOR | S21101900112 | New_Event | Wire Down | Include | Include | Equipment | 11 | 2021-10-19 | 47201 | keep | 0 | Oct | 2021 | 0.032148 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
ARECIBO | 2021-10-19 15:40 | 2021-10-19 17:46 | 5 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TRAMO DE LINEA SECUNARIA AVERIADA | A21101900000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-10-19 | 630 | keep | 0 | Oct | 2021 | 0.00042909 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
YAUCO | 2021-10-19 15:48 | 2021-10-20 09:08 | 1 | 017:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGA ELECTRICA | P21101900053 | New_Event | Bad Weather | Include | Include | Weather | 1040 | 2021-10-19 | 1040 | keep | 0 | Oct | 2021 | 0.00070834 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-19 15:49 | 2021-10-19 18:00 | 10 | 002:11 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21101900031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2021-10-19 | 1310 | keep | 0 | Oct | 2021 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-19 15:54 | 2021-10-19 17:13 | 15 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P21101900055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2021-10-19 | 1185 | keep | 0 | Oct | 2021 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-19 15:55 | 2021-10-20 17:50 | 60 | 025:55 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21101900170 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1555 | 2021-10-19 | 93300 | keep | 0 | Oct | 2021 | 0.063546 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-19 15:57 | 2021-10-19 18:50 | 10 | 002:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | A21101900083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 173 | 2021-10-19 | 1730 | keep | 0 | Oct | 2021 | 0.0011783 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-19 15:59 | 2021-10-21 12:47 | 1 | 044:48 | P | NO SE REPORTO CAUSA | 1 X 40 RISER | S21101900139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2688 | 2021-10-19 | 2688 | keep | 0 | Oct | 2021 | 0.0018308 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-10-19 16:00 | 2021-10-20 09:07 | 15 | 017:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P21101900057 | New_Event | Bad Weather | Include | Include | Weather | 1027 | 2021-10-19 | 15405 | keep | 0 | Oct | 2021 | 0.010492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-19 16:04 | 2021-10-19 18:17 | 668 | 002:13 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN CORTE DE LINEA SE DEJO ABIERTO DEL SU-1 AL SU-2 AVERIADO | C21101900094 | New_Event | UG Cable Fault | Include | Include | Equipment | 133 | 2021-10-19 | 88844 | keep | 0 | Oct | 2021 | 0.060511 | 0.00045497 | Sustained | FALSE | TRUE | Not_TMED_Event | 668
SAN JUAN | 2021-10-19 16:08 | 2021-10-19 18:37 | 12 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21101800186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-10-19 | 1788 | keep | 0 | Oct | 2021 | 0.0012178 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-10-19 16:13 | 2021-10-19 20:54 | 510 | 004:41 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21101900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-10-19 | 143310 | keep | 0 | Oct | 2021 | 0.097608 | 0.00034736 | Sustained | FALSE | TRUE | Not_TMED_Event | 510
VEGA BAJA | 2021-10-19 16:42 | 2021-10-19 18:21 | 10 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21101900100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-10-19 | 990 | keep | 0 | Oct | 2021 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-19 16:49 | 2021-10-20 12:37 | 15 | 019:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA POR 50KVA | B21101900101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1188 | 2021-10-19 | 17820 | keep | 0 | Oct | 2021 | 0.012137 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-19 16:59 | 2021-10-20 14:38 | 25 | 021:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESCRUZO LINEA PRIMARIA | S21101900160 | New_Event | Wire Down | Include | Include | Equipment | 1299 | 2021-10-19 | 32475 | keep | 0 | Oct | 2021 | 0.022119 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-19 17:05 | 2021-10-19 22:06 | 15 | 005:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SUELTO EN CAJA DE CORTE DE LINEA | M21101900118 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2021-10-19 | 4515 | keep | 0 | Oct | 2021 | 0.0030751 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-19 17:07 | 2021-10-20 15:23 | 1 | 022:16 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 15 KVA | C21101900112 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1336 | 2021-10-19 | 1336 | keep | 0 | Oct | 2021 | 0.00090994 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-19 17:15 | 2021-10-20 19:18 | 40 | 026:03 | P | CABLE SOTERRADO AVERIADO | 1 X 15 EN RISER REMPLAZO CONDUCTOR DEL T 21 HACIA RISER | C21101900115 | New_Event | UG Cable Fault | Include | Include | Equipment | 1563 | 2021-10-19 | 62520 | keep | 0 | Oct | 2021 | 0.042582 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-10-19 17:19 | 2021-10-19 19:15 | 3 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21101900088 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-10-19 | 348 | keep | 0 | Oct | 2021 | 0.00023702 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-10-19 17:27 | 2021-10-19 17:28 | 4304 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR | M21101900123 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-19 | 4304 | keep | 0 | Oct | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2021-10-19 17:28 | 2021-10-20 10:46 | 40 | 017:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101900129 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1038 | 2021-10-19 | 41520 | keep | 0 | Oct | 2021 | 0.028279 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-19 17:51 | 2021-10-19 21:48 | 100 | 003:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21101900133 | New_Event | Bad Weather | Include | Include | Weather | 237 | 2021-10-19 | 23700 | keep | 0 | Oct | 2021 | 0.016142 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-19 17:52 | 2021-10-19 20:33 | 150 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 80 CORTE DE LINEA 1 X 20 EN PROVISIONAL Y 1 X 12 EN PM | S21101900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-10-19 | 24150 | keep | 0 | Oct | 2021 | 0.016448 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-19 17:59 | 2021-10-19 19:51 | 100 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21101900177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-10-19 | 11200 | keep | 0 | Oct | 2021 | 0.0076283 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-19 18:02 | 2021-10-20 12:15 | 40 | 018:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | FIJO BAJANTE Y REMPLAZO CAJA AVERIADA | C21101900128 | New_Event | Cutout Failure | Include | Include | Equipment | 1093 | 2021-10-19 | 43720 | keep | 0 | Oct | 2021 | 0.029777 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-10-19 18:06 | 2021-10-19 19:43 | 8 | 001:37 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA PARA REEMPLAZAR BARRA EN PEDESTAL | C21101900058 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 97 | 2021-10-19 | 776 | keep | 0 | Oct | 2021 | 0.00052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-10-19 18:07 | 2021-10-19 18:08 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21101900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 2722 | keep | 0 | Oct | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
MAYAGÃœEZ | 2021-10-19 18:11 | 2021-10-20 12:36 | 50 | 018:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101900141 | New_Event | Bad Weather | Include | Include | Weather | 1105 | 2021-10-19 | 55250 | keep | 0 | Oct | 2021 | 0.037631 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-19 18:15 | 2021-10-19 18:16 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21101900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 1084 | keep | 0 | Oct | 2021 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
BAYAMON | 2021-10-19 18:15 | 2021-10-19 22:41 | 50 | 004:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21101900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-10-19 | 13300 | keep | 0 | Oct | 2021 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-19 18:17 | 2021-10-20 12:57 | 20 | 018:40 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU 1 AL SU 2 INSTALO PUENTE PORTATIL EN EL SU 1 HACIA SU 2 | C21101900134 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1120 | 2021-10-19 | 22400 | keep | 0 | Oct | 2021 | 0.015257 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-19 18:17 | 2021-10-19 19:05 | 6 | 000:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA AVERIADO POR UNO DE 25KVA NUEVO | A21101800102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 48 | 2021-10-19 | 288 | keep | 0 | Oct | 2021 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-19 18:19 | 2021-10-19 23:01 | 50 | 004:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER CAJA QUEMADA | S21101900180 | New_Event | Cutout Failure | Include | Include | Equipment | 282 | 2021-10-19 | 14100 | keep | 0 | Oct | 2021 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-19 18:19 | 2021-10-19 19:25 | 70 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21101900143 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2021-10-19 | 4620 | keep | 0 | Oct | 2021 | 0.0031467 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-19 18:22 | 2021-10-20 11:06 | 600 | 016:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21101900146 | New_Event | Wire Down | Include | Include | Equipment | 1004 | 2021-10-19 | 602400 | keep | 0 | Oct | 2021 | 0.41029 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
HUMACAO | 2021-10-19 18:26 | 2021-10-20 16:22 | 4 | 021:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REMPLAZO CAJA AVERIADA | C21101900135 | New_Event | Cutout Failure | Include | Include | Equipment | 1316 | 2021-10-19 | 5264 | keep | 0 | Oct | 2021 | 0.0035853 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-19 18:30 | 2021-10-20 15:25 | 10 | 020:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21101900148 | New_Event | Bad Weather | Include | Include | Weather | 1255 | 2021-10-19 | 12550 | keep | 0 | Oct | 2021 | 0.0085477 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-19 18:33 | 2021-10-20 10:06 | 50 | 015:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101900149 | New_Event | Bad Weather | Include | Include | Weather | 933 | 2021-10-19 | 46650 | keep | 0 | Oct | 2021 | 0.031773 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-19 18:40 | 2021-10-19 19:12 | 30 | 000:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21101900107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2021-10-19 | 960 | keep | 0 | Oct | 2021 | 0.00065385 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-10-19 19:11 | 2021-10-20 12:25 | 85 | 017:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | C21101900141 | New_Event | Bad Weather | Include | Include | Weather | 1034 | 2021-10-19 | 87890 | keep | 0 | Oct | 2021 | 0.059861 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
BARRANQUITAS | 2021-10-19 19:15 | 2021-10-19 20:26 | 10 | 001:11 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA | C21101900080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 71 | 2021-10-19 | 710 | keep | 0 | Oct | 2021 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-19 20:04 | 2021-10-20 11:57 | 40 | 015:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21101900151 | New_Event |  |  | Include | Wildlife | 953 | 2021-10-19 | 38120 | keep | 0 | Oct | 2021 | 0.025963 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-19 20:10 | 2021-10-19 21:31 | 30 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21101900127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-10-19 | 2430 | keep | 0 | Oct | 2021 | 0.0016551 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-19 20:13 | 2021-10-20 11:58 | 30 | 015:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101900168 | New_Event | Bad Weather | Include | Include | Weather | 945 | 2021-10-19 | 28350 | keep | 0 | Oct | 2021 | 0.019309 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-19 20:18 | 2021-10-20 09:18 | 12 | 013:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE REMPLAZO LINEA SECUNDARIA CRUZADA | P21101900076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 780 | 2021-10-19 | 9360 | keep | 0 | Oct | 2021 | 0.0063751 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BARRANQUITAS | 2021-10-19 20:29 | 2021-10-20 17:06 | 5 | 020:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21101900154 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1237 | 2021-10-19 | 6185 | keep | 0 | Oct | 2021 | 0.0042126 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-19 20:42 | 2021-10-20 10:57 | 7 | 014:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21101900155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2021-10-19 | 5985 | keep | 0 | Oct | 2021 | 0.0040764 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-19 21:25 | 2021-10-20 09:45 | 6 | 012:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21101900110 | New_Event | Bad Weather | Include | Include | Weather | 740 | 2021-10-19 | 4440 | keep | 0 | Oct | 2021 | 0.0030241 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-19 21:45 | 2021-10-19 21:46 | 320 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21101900135 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-19 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-10-19 21:46 | 2021-10-20 16:07 | 50 | 018:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO DISCO | B21101900141 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1101 | 2021-10-19 | 55050 | keep | 0 | Oct | 2021 | 0.037494 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-19 21:49 | 2021-10-19 22:49 | 80 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21101900181 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-10-19 | 4800 | keep | 0 | Oct | 2021 | 0.0032693 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-19 22:03 | 2021-10-20 14:31 | 30 | 016:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21101900254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 988 | 2021-10-19 | 29640 | keep | 0 | Oct | 2021 | 0.020188 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-19 22:27 | 2021-10-19 22:28 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA PARTE 9202-3 | B21101900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 308 | keep | 0 | Oct | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-10-19 22:27 | 2021-10-19 22:28 | 100 | 000:01 | P | NO SE REPORTO CAUSA | PARTE DE LA CARGA POR EL 9202-02 | B21101900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 100 | keep | 0 | Oct | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-19 22:37 | 2021-10-20 16:06 | 10 | 017:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21101900137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1049 | 2021-10-19 | 10490 | keep | 0 | Oct | 2021 | 0.0071447 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-19 22:40 | 2021-10-20 00:01 | 892 | 001:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO SALIDA TORNCAL | S21101900000 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2021-10-19 | 72252 | keep | 0 | Oct | 2021 | 0.049211 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
CAGUAS | 2021-10-19 22:59 | 2021-10-19 23:00 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21101900163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-19 | 1084 | keep | 0 | Oct | 2021 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
VEGA BAJA | 2021-10-19 23:13 | 2021-10-20 17:39 | 13 | 018:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 50KVA | B21101900139 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1106 | 2021-10-19 | 14378 | keep | 0 | Oct | 2021 | 0.0097928 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-10-20 00:39 | 2021-10-20 12:35 | 50 | 011:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21102000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 716 | 2021-10-20 | 35800 | keep | 0 | Oct | 2021 | 0.024383 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-20 00:47 | 2021-10-20 00:48 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
ARECIBO | 2021-10-20 00:57 | 2021-10-20 11:16 | 75 | 010:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A21102000003 | New_Event | Wire Down | Include | Include | Equipment | 619 | 2021-10-20 | 46425 | keep | 0 | Oct | 2021 | 0.03162 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
FAJARDO | 2021-10-20 01:14 | 2021-10-20 01:15 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2286 | keep | 0 | Oct | 2021 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
CANOVANAS | 2021-10-20 01:49 | 2021-10-20 01:50 | 2708 | 000:01 | T | DESGANCHE | RECIERRE | R21102000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-20 | 2708 | keep | 0 | Oct | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-10-20 01:50 | 2021-10-20 06:22 | 424 | 004:32 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R21102000020 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-10-20 | 115328 | keep | 0 | Oct | 2021 | 0.078549 | 0.00028878 | Sustained | FALSE | TRUE | Not_TMED_Event | 424
MAYAGÃœEZ | 2021-10-20 03:19 | 2021-10-20 11:15 | 40 | 007:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000005 | New_Event | Bad Weather | Include | Include | Weather | 476 | 2021-10-20 | 19040 | keep | 0 | Oct | 2021 | 0.012968 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-20 03:24 | 2021-10-20 10:31 | 100 | 007:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO CAUSA | C21102000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 427 | 2021-10-20 | 42700 | keep | 0 | Oct | 2021 | 0.029083 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-10-20 03:54 | 2021-10-20 11:14 | 125 | 007:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN RISER CRUCE POR RATA | R21102000001 | New_Event |  |  | Include | Wildlife | 440 | 2021-10-20 | 55000 | keep | 0 | Oct | 2021 | 0.03746 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2021-10-20 03:56 | 2021-10-20 10:09 | 60 | 006:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21102000007 | New_Event | Bad Weather | Include | Include | Weather | 373 | 2021-10-20 | 22380 | keep | 0 | Oct | 2021 | 0.015243 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-20 04:28 | 2021-10-20 14:26 | 1 | 009:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21102000008 | New_Event | Bad Weather | Include | Include | Weather | 598 | 2021-10-20 | 598 | keep | 0 | Oct | 2021 | 0.0004073 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-20 05:07 | 2021-10-20 11:22 | 780 | 006:15 | P | ESTRUCTURA AVERIADA | 2 X 140 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | R21102000003 | New_Event | Defective Pole | Include | Include | Equipment | 375 | 2021-10-20 | 292500 | keep | 0 | Oct | 2021 | 0.19922 | 0.00053125 | Sustained | FALSE | TRUE | Not_TMED_Event | 780
HUMACAO | 2021-10-20 05:56 | 2021-10-21 09:08 | 5 | 027:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102000041 | New_Event | Bad Weather | Include | Include | Weather | 1632 | 2021-10-20 | 8160 | keep | 0 | Oct | 2021 | 0.0055577 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-10-20 06:04 | 2021-10-20 06:05 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 1859 | keep | 0 | Oct | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2021-10-20 06:05 | 2021-10-21 18:48 | 36 | 036:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21102000017 | New_Event | Cutout Failure | Include | Include | Equipment | 2203 | 2021-10-20 | 79308 | keep | 0 | Oct | 2021 | 0.054016 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
VEGA BAJA | 2021-10-20 06:05 | 2021-10-20 18:38 | 60 | 012:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21102000016 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 753 | 2021-10-20 | 45180 | keep | 0 | Oct | 2021 | 0.030772 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-20 06:07 | 2021-10-20 06:08 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21102000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 3458 | keep | 0 | Oct | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2021-10-20 06:08 | 2021-10-20 10:45 | 35 | 004:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21102000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2021-10-20 | 9695 | keep | 0 | Oct | 2021 | 0.0066032 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-10-20 06:14 | 2021-10-20 13:36 | 125 | 007:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN CORTE DE LINEA REMPLAZO CAJA CRUCE POR AVE | C21102000014 | New_Event |  |  | Include | Wildlife | 442 | 2021-10-20 | 55250 | keep | 0 | Oct | 2021 | 0.037631 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-10-20 06:19 | 2021-10-21 11:59 | 8 | 029:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD EN EL FID:19435222 MARCA:HOWARD INDUSTRIES #SERIE:1638931018 VOLTAJES:4160/7200 120/240 | M21102000010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1780 | 2021-10-20 | 14240 | keep | 0 | Oct | 2021 | 0.0096988 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-10-20 06:21 | 2021-10-20 06:22 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2635 | keep | 0 | Oct | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
CANOVANAS | 2021-10-20 06:22 | 2021-10-20 06:23 | 2708 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R21102000034 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-20 | 2708 | keep | 0 | Oct | 2021 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-20 06:22 | 2021-10-20 13:53 | 65 | 007:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21102000049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 451 | 2021-10-20 | 29315 | keep | 0 | Oct | 2021 | 0.019966 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-10-20 06:23 | 2021-10-20 09:55 | 424 | 003:32 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R21102000020 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-10-20 | 89888 | keep | 0 | Oct | 2021 | 0.061222 | 0.00028878 | Sustained | FALSE | TRUE | Not_TMED_Event | 424
SAN JUAN | 2021-10-20 06:28 | 2021-10-20 12:50 | 1 | 006:22 | P | NO SE REPORTO CAUSA | 2 X 20 EN CORTE DE LINEA | S21102000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 382 | 2021-10-20 | 382 | keep | 0 | Oct | 2021 | 0.00026018 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-20 06:30 | 2021-10-20 11:45 | 217 | 005:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 Y 1 X 30 EN CORTES DE LINEA SE REEMPLAZO 4 DISCOS, 1 RIGIDO Y 1 CAJA PRIMARIA | R21102000017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 315 | 2021-10-20 | 68355 | keep | 0 | Oct | 2021 | 0.046556 | 0.0001478 | Sustained | FALSE | TRUE | Not_TMED_Event | 217
BAYAMON | 2021-10-20 06:32 | 2021-10-20 10:38 | 30 | 004:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | S21102000008 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2021-10-20 | 7380 | keep | 0 | Oct | 2021 | 0.0050265 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-20 06:54 | 2021-10-20 21:10 | 20 | 014:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOE AVERIADO DE 37.5 KVA POR 50 KVA | A21102000013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 856 | 2021-10-20 | 17120 | keep | 0 | Oct | 2021 | 0.01166 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-10-20 06:55 | 2021-10-20 10:46 | 12 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21102000001 | New_Event |  |  | Include | Wildlife | 231 | 2021-10-20 | 2772 | keep | 0 | Oct | 2021 | 0.001888 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-10-20 07:02 | 2021-10-20 20:14 | 100 | 013:12 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000013 | New_Event | Bad Weather | Include | Include | Weather | 792 | 2021-10-20 | 79200 | keep | 0 | Oct | 2021 | 0.053943 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-20 07:02 | 2021-10-20 14:06 | 575 | 007:04 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE 900 AMP. | A21102000014 | New_Event | Switch Failure | Include | Include | Equipment | 424 | 2021-10-20 | 243800 | keep | 0 | Oct | 2021 | 0.16605 | 0.00039163 | Sustained | FALSE | FALSE | Not_TMED_Event | 575
BAYAMON | 2021-10-20 07:08 | 2021-10-20 13:45 | 25 | 006:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102000067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 397 | 2021-10-20 | 9925 | keep | 0 | Oct | 2021 | 0.0067599 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-20 07:13 | 2021-10-20 18:04 | 25 | 010:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21102000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 651 | 2021-10-20 | 16275 | keep | 0 | Oct | 2021 | 0.011085 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-10-20 07:15 | 2021-10-21 18:12 | 30 | 034:57 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B21102000010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2097 | 2021-10-20 | 62910 | keep | 0 | Oct | 2021 | 0.042848 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-20 07:25 | 2021-10-20 22:13 | 20 | 014:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21102000016 | New_Event | Bad Weather | Include | Include | Weather | 888 | 2021-10-20 | 17760 | keep | 0 | Oct | 2021 | 0.012096 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-10-20 07:28 | 2021-10-20 12:42 | 75 | 005:14 | P | DESGANCHE | 1 X 50, 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE DESGANCHO | R21102000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-10-20 | 23550 | keep | 0 | Oct | 2021 | 0.01604 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
YAUCO | 2021-10-20 07:32 | 2021-10-20 10:42 | 12 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGA ELECTRICA | P21102000006 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-10-20 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-10-20 07:52 | 2021-10-20 15:11 | 12 | 007:19 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO | R21102000031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 439 | 2021-10-20 | 5268 | keep | 0 | Oct | 2021 | 0.003588 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-20 07:53 | 2021-10-20 16:46 | 25 | 008:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21101900028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 533 | 2021-10-20 | 13325 | keep | 0 | Oct | 2021 | 0.0090756 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-10-20 07:59 | 2021-10-20 08:00 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 7621 | keep | 0 | Oct | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
MAYAGÃœEZ | 2021-10-20 08:11 | 2021-10-20 14:37 | 10 | 006:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101200024 | New_Event | Bad Weather | Include | Include | Weather | 386 | 2021-10-20 | 3860 | keep | 0 | Oct | 2021 | 0.002629 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-20 08:20 | 2021-10-20 08:22 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE LLEVA LA CARGA DEL 1303-01 Y 1346-06, 1303-04 ESTA TRANSFERIDO | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-20 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-20 08:20 | 2021-10-20 08:22 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE LLEVA LA CARGA DEL 1303-01 Y 1346-06, 1303-04 ESTA TRANSFERIDO | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-20 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-20 08:20 | 2021-10-20 08:22 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 LLEVANDO LA CARGA DEL 1303-01 Y 1346-06 | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-20 | 3196 | keep | 0 | Oct | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-10-20 08:23 | 2021-10-21 10:44 | 15 | 026:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S21102000040 | New_Event | Cutout Failure | Include | Include | Equipment | 1581 | 2021-10-20 | 23715 | keep | 0 | Oct | 2021 | 0.016152 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-10-20 08:27 | 2021-10-21 12:30 | 6 | 028:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21102000014 | New_Event | Bad Weather | Include | Include | Weather | 1683 | 2021-10-20 | 10098 | keep | 0 | Oct | 2021 | 0.0068777 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
ARECIBO | 2021-10-20 08:49 | 2021-10-20 11:04 | 200 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS | A21102000023 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-10-20 | 27000 | keep | 0 | Oct | 2021 | 0.01839 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 108 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 324 | keep | 0 | Oct | 2021 | 0.00022067 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 1368 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 4104 | keep | 0 | Oct | 2021 | 0.0027952 | 0.00093174 | Momentary | FALSE | TRUE | Not_TMED_Event | 1368
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 2064 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 6192 | keep | 0 | Oct | 2021 | 0.0042173 | 0.0014058 | Momentary | FALSE | TRUE | Not_TMED_Event | 2064
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 1681 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 5043 | keep | 0 | Oct | 2021 | 0.0034348 | 0.0011449 | Momentary | FALSE | TRUE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 2435 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 7305 | keep | 0 | Oct | 2021 | 0.0049754 | 0.0016585 | Momentary | FALSE | TRUE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 726 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 2178 | keep | 0 | Oct | 2021 | 0.0014834 | 0.00049448 | Momentary | FALSE | TRUE | Not_TMED_Event | 726
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 225 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 675 | keep | 0 | Oct | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | TRUE | Not_TMED_Event | 225
SAN JUAN | 2021-10-20 09:19 | 2021-10-20 09:22 | 870 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 2610 | keep | 0 | Oct | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
HUMACAO | 2021-10-20 09:35 | 2021-10-20 13:28 | 6 | 003:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | R21102000049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2021-10-20 | 1398 | keep | 0 | Oct | 2021 | 0.00095217 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-10-20 09:36 | 2021-10-21 20:05 | 4 | 034:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE 50KVA | B21102000022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2069 | 2021-10-20 | 8276 | keep | 0 | Oct | 2021 | 0.0056367 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-10-20 09:45 | 2021-10-20 15:50 | 11 | 006:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21102000030 | New_Event | Bad Weather | Include | Include | Weather | 365 | 2021-10-20 | 4015 | keep | 0 | Oct | 2021 | 0.0027346 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
PONCE | 2021-10-20 10:05 | 2021-10-20 12:34 | 1 | 002:29 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 25 SMU EN SU-9A SWITCHING UNIT CONTAMINADO | P21102000017 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 149 | 2021-10-20 | 149 | keep | 0 | Oct | 2021 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-10-20 10:09 | 2021-10-20 14:36 | 150 | 004:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO | C21102000054 | New_Event | Bad Weather | Include | Include | Weather | 267 | 2021-10-20 | 40050 | keep | 0 | Oct | 2021 | 0.027278 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-20 10:11 | 2021-10-20 10:12 | 860 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECIERRO SE COLOCO RR EN OFF Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | P21102000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 860 | keep | 0 | Oct | 2021 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
CANOVANAS | 2021-10-20 10:29 | 2021-10-20 12:30 | 50 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21102000059 | New_Event |  |  | Include | Wildlife | 121 | 2021-10-20 | 6050 | keep | 0 | Oct | 2021 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-20 10:31 | 2021-10-20 11:47 | 15 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21101800140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-10-20 | 1140 | keep | 0 | Oct | 2021 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 108 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 1080 | keep | 0 | Oct | 2021 | 0.00073558 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 1368 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 13680 | keep | 0 | Oct | 2021 | 0.0093174 | 0.00093174 | Sustained | FALSE | TRUE | Not_TMED_Event | 1368
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 2064 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 20640 | keep | 0 | Oct | 2021 | 0.014058 | 0.0014058 | Sustained | FALSE | TRUE | Not_TMED_Event | 2064
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 1681 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 16810 | keep | 0 | Oct | 2021 | 0.011449 | 0.0011449 | Sustained | FALSE | TRUE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 2435 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 24350 | keep | 0 | Oct | 2021 | 0.016585 | 0.0016585 | Sustained | FALSE | TRUE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 726 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 7260 | keep | 0 | Oct | 2021 | 0.0049448 | 0.00049448 | Sustained | FALSE | TRUE | Not_TMED_Event | 726
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 225 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 2250 | keep | 0 | Oct | 2021 | 0.0015325 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
SAN JUAN | 2021-10-20 10:32 | 2021-10-20 10:42 | 870 | 000:10 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-10-20 | 8700 | keep | 0 | Oct | 2021 | 0.0059255 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
YAUCO | 2021-10-20 10:44 | 2021-10-20 12:00 | 28 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21102000036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-10-20 | 2128 | keep | 0 | Oct | 2021 | 0.0014494 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
BAYAMON | 2021-10-20 10:45 | 2021-10-20 10:49 | 1514 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 6056 | keep | 0 | Oct | 2021 | 0.0041247 | 0.0010312 | Momentary | FALSE | TRUE | Not_TMED_Event | 1514
BAYAMON | 2021-10-20 10:45 | 2021-10-20 10:49 | 1105 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 4420 | keep | 0 | Oct | 2021 | 0.0030104 | 0.00075261 | Momentary | FALSE | TRUE | Not_TMED_Event | 1105
SAN JUAN | 2021-10-20 11:03 | 2021-10-20 11:33 | 90 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | S21102000143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2021-10-20 | 2700 | keep | 0 | Oct | 2021 | 0.001839 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-10-20 11:04 | 2021-10-20 11:06 | 2888 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21102000044 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-10-20 | 5776 | keep | 0 | Oct | 2021 | 0.003934 | 0.001967 | Momentary | FALSE | TRUE | Not_TMED_Event | 2888
ARECIBO | 2021-10-20 11:06 | 2021-10-20 14:50 | 200 | 003:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS | A21102000023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 224 | 2021-10-20 | 44800 | keep | 0 | Oct | 2021 | 0.030513 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-10-20 11:28 | 2021-10-20 12:25 | 7 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | R21102000070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-10-20 | 399 | keep | 0 | Oct | 2021 | 0.00027176 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-20 11:35 | 2021-10-20 12:52 | 50 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000062 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-10-20 | 3850 | keep | 0 | Oct | 2021 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-20 11:49 | 2021-10-20 11:53 | 641 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 2564 | keep | 0 | Oct | 2021 | 0.0017463 | 0.00043658 | Momentary | FALSE | TRUE | Not_TMED_Event | 641
SAN JUAN | 2021-10-20 11:49 | 2021-10-20 11:53 | 733 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 2932 | keep | 0 | Oct | 2021 | 0.001997 | 0.00049924 | Momentary | FALSE | TRUE | Not_TMED_Event | 733
SAN JUAN | 2021-10-20 11:49 | 2021-10-20 11:53 | 4133 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 16532 | keep | 0 | Oct | 2021 | 0.01126 | 0.002815 | Momentary | FALSE | TRUE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-20 11:49 | 2021-10-20 11:53 | 1799 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21102000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 7196 | keep | 0 | Oct | 2021 | 0.0049012 | 0.0012253 | Momentary | FALSE | TRUE | Not_TMED_Event | 1799
CAGUAS | 2021-10-20 11:52 | 2021-10-21 07:41 | 53 | 019:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21102000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1189 | 2021-10-20 | 63017 | keep | 0 | Oct | 2021 | 0.042921 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
MAYAGÃœEZ | 2021-10-20 11:58 | 2021-10-20 11:59 | 4304 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA SE CERRO POR CONTROL SCADA | M21102000000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-10-20 | 4304 | keep | 0 | Oct | 2021 | 0.0029314 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-20 11:59 | 2021-10-20 13:19 | 30 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21101900168 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 80 | 2021-10-20 | 2400 | keep | 0 | Oct | 2021 | 0.0016346 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-20 12:11 | 2021-10-20 16:24 | 2 | 004:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21102000064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2021-10-20 | 506 | keep | 0 | Oct | 2021 | 0.00034463 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-10-20 12:13 | 2021-10-20 12:14 | 590 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 590 | keep | 0 | Oct | 2021 | 0.00040185 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
PONCE | 2021-10-20 12:27 | 2021-10-20 12:28 | 576 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21102000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 576 | keep | 0 | Oct | 2021 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2021-10-20 12:29 | 2021-10-20 12:30 | 23 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P21102000068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 23 | keep | 0 | Oct | 2021 | 1.5665e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2021-10-20 12:33 | 2021-10-20 15:05 | 20 | 002:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 18 NX MAL TIEMPO | R21102000077 | New_Event | Bad Weather | Include | Include | Weather | 152 | 2021-10-20 | 3040 | keep | 0 | Oct | 2021 | 0.0020705 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-20 12:33 | 2021-10-23 22:22 | 40 | 081:49 | P | CABLE SOTERRADO AVERIADO | 2 X 25 EN CORTE DE LINEA SE CONTRUYERON DOS AEREOS PROVISIONALES DE T-5 @ T-6 Y DE T-6 @ T-7 | B21102000037 | New_Event | UG Cable Fault | Include | Include | Equipment | 4909 | 2021-10-20 | 196360 | keep | 0 | Oct | 2021 | 0.13374 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-20 12:33 | 2021-10-20 12:34 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102000049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 3597 | keep | 0 | Oct | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
HUMACAO | 2021-10-20 12:33 | 2021-10-20 16:41 | 6 | 004:08 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21102000074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 248 | 2021-10-20 | 1488 | keep | 0 | Oct | 2021 | 0.0010135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-10-20 12:33 | 2021-10-21 15:43 | 2 | 027:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA EVENTO DEL DIA 20 | A21102000067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1630 | 2021-10-20 | 3260 | keep | 0 | Oct | 2021 | 0.0022204 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-10-20 12:35 | 2021-10-20 12:36 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102000043 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2402 | keep | 0 | Oct | 2021 | 0.001636 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-20 12:36 | 2021-10-20 12:37 | 4291 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | S21102000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-20 | 4291 | keep | 0 | Oct | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-10-20 12:36 | 2021-10-20 12:39 | 2435 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-20 | 7305 | keep | 0 | Oct | 2021 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-10-20 12:36 | 2021-10-20 13:08 | 50 | 000:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21102000002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 32 | 2021-10-20 | 1600 | keep | 0 | Oct | 2021 | 0.0010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-10-20 12:41 | 2021-10-20 17:12 | 4291 | 004:31 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. SE REEMPLAZO AISLADORES PIN POLE TOP | S21102000137 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 271 | 2021-10-20 | 1162861 | keep | 0 | Oct | 2021 | 0.79202 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2021-10-20 12:46 | 2021-10-20 15:57 | 100 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21102000146 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2021-10-20 | 19100 | keep | 0 | Oct | 2021 | 0.013009 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-20 12:51 | 2021-10-20 17:35 | 8 | 004:44 | P | ESTRUCTURA AVERIADA | ABRIO PUENTES PARA REMPLAZAR POSTE PRIMARIO | C21102000082 | New_Event | Defective Pole | Include | Include | Equipment | 284 | 2021-10-20 | 2272 | keep | 0 | Oct | 2021 | 0.0015474 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-20 12:52 | 2021-10-20 12:53 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 281 | keep | 0 | Oct | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-10-20 12:52 | 2021-10-20 12:53 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 1252 | keep | 0 | Oct | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-10-20 12:52 | 2021-10-20 12:53 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 595 | keep | 0 | Oct | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-10-20 12:52 | 2021-10-20 12:53 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 51 | keep | 0 | Oct | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-10-20 12:52 | 2021-10-20 12:53 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 721 | keep | 0 | Oct | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-10-20 12:52 | 2021-10-20 12:53 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 1382 | keep | 0 | Oct | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-10-20 12:52 | 2021-10-20 12:53 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 654 | keep | 0 | Oct | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
BAYAMON | 2021-10-20 12:53 | 2021-10-20 21:17 | 23 | 008:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL | B21102000048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 504 | 2021-10-20 | 11592 | keep | 0 | Oct | 2021 | 0.0078953 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2021-10-20 12:53 | 2021-10-20 15:30 | 50 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000062 | Partial_restoration | Bad Weather | Include | Include | Weather | 157 | 2021-10-20 | 7850 | keep | 0 | Oct | 2021 | 0.0053466 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-20 12:58 | 2021-10-20 12:59 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21102000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2435 | keep | 0 | Oct | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2021-10-20 13:01 | 2021-10-21 09:04 | 40 | 020:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21102000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1203 | 2021-10-20 | 48120 | keep | 0 | Oct | 2021 | 0.032774 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-20 13:10 | 2021-10-20 17:34 | 25 | 004:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21102000058 | New_Event | Bad Weather | Include | Include | Weather | 264 | 2021-10-20 | 6600 | keep | 0 | Oct | 2021 | 0.0044952 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-10-20 13:11 | 2021-10-20 15:45 | 216 | 002:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO DISCO | R21102000096 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 154 | 2021-10-20 | 33264 | keep | 0 | Oct | 2021 | 0.022656 | 0.00014712 | Sustained | FALSE | TRUE | Not_TMED_Event | 216
VEGA BAJA | 2021-10-20 13:12 | 2021-10-20 21:15 | 10 | 008:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-2 HACIA T-13 | B21102000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 483 | 2021-10-20 | 4830 | keep | 0 | Oct | 2021 | 0.0032897 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-20 13:18 | 2021-10-20 17:36 | 150 | 004:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA HOWEL | A21102000060 | New_Event | Cutout Failure | Include | Include | Equipment | 258 | 2021-10-20 | 38700 | keep | 0 | Oct | 2021 | 0.026358 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-10-20 13:24 | 2021-10-20 18:20 | 50 | 004:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21102000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-10-20 | 14800 | keep | 0 | Oct | 2021 | 0.01008 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-20 13:27 | 2021-10-20 15:27 | 300 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000094 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-10-20 | 36000 | keep | 0 | Oct | 2021 | 0.024519 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-10-20 13:28 | 2021-10-20 14:46 | 3 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21102000091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-10-20 | 234 | keep | 0 | Oct | 2021 | 0.00015938 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-10-20 13:29 | 2021-10-20 13:30 | 2722 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO | R21102000097 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-20 | 2722 | keep | 0 | Oct | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2021-10-20 13:30 | 2021-10-20 17:20 | 15 | 003:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21102000119 | 1st_after_momentary |  |  | Include | Wildlife | 230 | 2021-10-20 | 3450 | keep | 0 | Oct | 2021 | 0.0023498 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-10-20 13:38 | 2021-10-20 15:38 | 75 | 002:00 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN DISTINTOS CORTE DE LINEA Y SE REALIZO DESGANCHE | S21102000169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-10-20 | 9000 | keep | 0 | Oct | 2021 | 0.0061299 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-10-20 13:39 | 2021-10-20 13:40 | 1066 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 1066 | keep | 0 | Oct | 2021 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2021-10-20 13:44 | 2021-10-20 17:37 | 50 | 003:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21102000091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-10-20 | 11650 | keep | 0 | Oct | 2021 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-20 13:44 | 2021-10-20 19:53 | 36 | 006:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN T-56 Y 1 X 10 EN T-55 | B21102000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2021-10-20 | 13284 | keep | 0 | Oct | 2021 | 0.0090477 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 959 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 3836 | keep | 0 | Oct | 2021 | 0.0026127 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 1382 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 5528 | keep | 0 | Oct | 2021 | 0.0037651 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 663 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 2652 | keep | 0 | Oct | 2021 | 0.0018063 | 0.00045157 | Momentary | FALSE | TRUE | Not_TMED_Event | 663
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 1715 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 6860 | keep | 0 | Oct | 2021 | 0.0046723 | 0.0011681 | Momentary | FALSE | TRUE | Not_TMED_Event | 1715
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 1498 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 5992 | keep | 0 | Oct | 2021 | 0.0040811 | 0.0010203 | Momentary | FALSE | TRUE | Not_TMED_Event | 1498
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 1221 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 4884 | keep | 0 | Oct | 2021 | 0.0033265 | 0.00083162 | Momentary | FALSE | TRUE | Not_TMED_Event | 1221
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 1100 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 4400 | keep | 0 | Oct | 2021 | 0.0029968 | 0.0007492 | Momentary | FALSE | TRUE | Not_TMED_Event | 1100
UTUADO | 2021-10-20 13:45 | 2021-10-20 20:20 | 80 | 006:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21102000064 | New_Event | Bad Weather | Include | Include | Weather | 395 | 2021-10-20 | 31600 | keep | 0 | Oct | 2021 | 0.021523 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 4176 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 16704 | keep | 0 | Oct | 2021 | 0.011377 | 0.0028443 | Momentary | FALSE | TRUE | Not_TMED_Event | 4176
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 252 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 1008 | keep | 0 | Oct | 2021 | 0.00068654 | 0.00017164 | Momentary | FALSE | TRUE | Not_TMED_Event | 252
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 2147 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 8588 | keep | 0 | Oct | 2021 | 0.0058492 | 0.0014623 | Momentary | FALSE | TRUE | Not_TMED_Event | 2147
BAYAMON | 2021-10-20 13:45 | 2021-10-20 13:49 | 2858 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-10-20 | 11432 | keep | 0 | Oct | 2021 | 0.0077863 | 0.0019466 | Momentary | FALSE | TRUE | Not_TMED_Event | 2858
BAYAMON | 2021-10-20 13:47 | 2021-10-20 13:50 | 1983 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1801-02 | B21102000077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 5949 | keep | 0 | Oct | 2021 | 0.0040518 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-10-20 13:47 | 2021-10-20 13:50 | 186 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO Y SE CERRO POR CONTROL LINEA 9600 | B21102000077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-20 | 558 | keep | 0 | Oct | 2021 | 0.00038005 | 0.00012668 | Momentary | FALSE | TRUE | Not_TMED_Event | 186
UTUADO | 2021-10-20 13:47 | 2021-10-20 17:00 | 50 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21102000063 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-10-20 | 9650 | keep | 0 | Oct | 2021 | 0.0065726 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-20 13:49 | 2021-10-20 15:50 | 25 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102000067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2021-10-20 | 3025 | keep | 0 | Oct | 2021 | 0.0020603 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-20 13:50 | 2021-10-20 20:12 | 100 | 006:22 | P | LINEA DE TRANSMISION 38KV | 3 X 65 EN CORTE DE LINEA SE REPARO SE LA LINEA DE DISTRIBUCION QUE SE AVERIO CUANDO LA 9600 LE CAYO ENCIMA | B21102000104 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 382 | 2021-10-20 | 38200 | keep | 0 | Oct | 2021 | 0.026018 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-20 13:50 | 2021-10-20 19:09 | 100 | 005:19 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102000097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2021-10-20 | 31900 | keep | 0 | Oct | 2021 | 0.021727 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-20 13:50 | 2021-10-20 16:30 | 170 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000113 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-10-20 | 27200 | keep | 0 | Oct | 2021 | 0.018526 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
MAYAGÃœEZ | 2021-10-20 14:00 | 2021-10-20 14:01 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2200 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-20 | 974 | keep | 0 | Oct | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
MAYAGÃœEZ | 2021-10-20 14:03 | 2021-10-20 14:04 | 863 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21102000110 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-20 | 863 | keep | 0 | Oct | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
ARECIBO | 2021-10-20 14:03 | 2021-10-20 22:48 | 20 | 008:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | A21102000069 | New_Event | Bad Weather | Include | Include | Weather | 525 | 2021-10-20 | 10500 | keep | 0 | Oct | 2021 | 0.0071515 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-20 14:04 | 2021-10-20 17:51 | 60 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21102000177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2021-10-20 | 13620 | keep | 0 | Oct | 2021 | 0.0092765 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-20 14:08 | 2021-10-20 20:01 | 25 | 005:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21102000180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 353 | 2021-10-20 | 8825 | keep | 0 | Oct | 2021 | 0.0060107 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-20 14:10 | 2021-10-20 18:00 | 140 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000115 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-10-20 | 32200 | keep | 0 | Oct | 2021 | 0.021931 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
CANOVANAS | 2021-10-20 14:18 | 2021-10-20 18:01 | 275 | 003:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE SE CERRO PUENTE | R21102000106 | New_Event |  |  | Include | Wildlife | 223 | 2021-10-20 | 61325 | keep | 0 | Oct | 2021 | 0.041768 | 0.0001873 | Sustained | TRUE | TRUE | Not_TMED_Event | 275
ARECIBO | 2021-10-20 14:20 | 2021-10-20 18:35 | 100 | 004:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A21102000074 | New_Event | Cutout Failure | Include | Include | Equipment | 255 | 2021-10-20 | 25500 | keep | 0 | Oct | 2021 | 0.017368 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-20 14:24 | 2021-10-20 14:25 | 2174 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | A21101200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-20 | 2174 | keep | 0 | Oct | 2021 | 0.0014807 | 0.0014807 | Momentary | FALSE | FALSE | Not_TMED_Event | 2174
MAYAGÃœEZ | 2021-10-20 14:24 | 2021-10-20 14:25 | 2225 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | A21101200119 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-20 | 2225 | keep | 0 | Oct | 2021 | 0.0015154 | 0.0015154 | Momentary | FALSE | FALSE | Not_TMED_Event | 2225
CANOVANAS | 2021-10-20 14:26 | 2021-10-20 16:56 | 45 | 002:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA ENREDADERA | R21102000108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-10-20 | 6750 | keep | 0 | Oct | 2021 | 0.0045974 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-10-20 14:28 | 2021-10-21 10:00 | 80 | 019:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21102000078 | New_Event | Bad Weather | Include | Include | Weather | 1172 | 2021-10-20 | 93760 | keep | 0 | Oct | 2021 | 0.06386 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-10-20 14:28 | 2021-10-20 16:07 | 80 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21102000078 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-10-20 | 7920 | keep | 0 | Oct | 2021 | 0.0053943 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-20 14:31 | 2021-10-21 15:25 | 20 | 024:54 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21102000097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1494 | 2021-10-20 | 29880 | keep | 0 | Oct | 2021 | 0.020351 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-10-20 14:31 | 2021-10-20 17:29 | 45 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21102000111 | New_Event |  |  | Include | Wildlife | 178 | 2021-10-20 | 8010 | keep | 0 | Oct | 2021 | 0.0054556 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-10-20 14:38 | 2021-10-20 14:39 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 1261 | keep | 0 | Oct | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2021-10-20 14:43 | 2021-10-21 09:47 | 50 | 019:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102000127 | New_Event | Bad Weather | Include | Include | Weather | 1144 | 2021-10-20 | 57200 | keep | 0 | Oct | 2021 | 0.038959 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-20 14:44 | 2021-10-20 14:45 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2956 | keep | 0 | Oct | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
MAYAGÃœEZ | 2021-10-20 14:44 | 2021-10-20 18:55 | 60 | 004:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102000128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-10-20 | 15060 | keep | 0 | Oct | 2021 | 0.010257 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-20 14:53 | 2021-10-20 18:14 | 300 | 003:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000135 | New_Event | Bad Weather | Include | Include | Weather | 201 | 2021-10-20 | 60300 | keep | 0 | Oct | 2021 | 0.04107 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-10-20 15:02 | 2021-10-20 15:59 | 50 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21102000088 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-10-20 | 2850 | keep | 0 | Oct | 2021 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-20 15:05 | 2021-10-20 15:06 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21102000199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 922 | keep | 0 | Oct | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-10-20 15:05 | 2021-10-20 15:06 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21102000199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-10-20 15:13 | 2021-10-20 15:14 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA DEL 1336-09 | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 5290 | keep | 0 | Oct | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-10-20 15:13 | 2021-10-20 15:14 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA DEL 1336-09 | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 207 | keep | 0 | Oct | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2021-10-20 15:13 | 2021-10-20 16:20 | 1 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER POR DESCARGAS ELECTRICAS | A21102000090 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-10-20 | 67 | keep | 0 | Oct | 2021 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-10-20 15:16 | 2021-10-20 17:13 | 80 | 001:57 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21102000104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-10-20 | 9360 | keep | 0 | Oct | 2021 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-20 15:18 | 2021-10-20 17:27 | 45 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000144 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-10-20 | 5805 | keep | 0 | Oct | 2021 | 0.0039538 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-10-20 15:22 | 2021-10-20 18:40 | 6 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21102000092 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-10-20 | 1188 | keep | 0 | Oct | 2021 | 0.00080914 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-20 15:23 | 2021-10-20 16:50 | 60 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21101200093 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2021-10-20 | 5220 | keep | 0 | Oct | 2021 | 0.0035553 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-10-20 15:31 | 2021-10-20 19:17 | 154 | 003:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 226 | 2021-10-20 | 34804 | keep | 0 | Oct | 2021 | 0.023705 | 0.00010489 | Sustained | FALSE | TRUE | Not_TMED_Event | 154
AGUADILLA | 2021-10-20 15:31 | 2021-10-20 19:17 | 1261 | 003:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 226 | 2021-10-20 | 284986 | keep | 0 | Oct | 2021 | 0.1941 | 0.00085886 | Sustained | FALSE | TRUE | Not_TMED_Event | 1261
AGUADILLA | 2021-10-20 15:31 | 2021-10-20 19:17 | 3894 | 003:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 226 | 2021-10-20 | 880044 | keep | 0 | Oct | 2021 | 0.59939 | 0.0026522 | Sustained | FALSE | TRUE | Not_TMED_Event | 3894
AGUADILLA | 2021-10-20 15:31 | 2021-10-20 19:17 | 997 | 003:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 226 | 2021-10-20 | 225322 | keep | 0 | Oct | 2021 | 0.15347 | 0.00067905 | Sustained | FALSE | TRUE | Not_TMED_Event | 997
AGUADILLA | 2021-10-20 15:31 | 2021-10-20 19:17 | 1497 | 003:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 | M21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 226 | 2021-10-20 | 338322 | keep | 0 | Oct | 2021 | 0.23043 | 0.0010196 | Sustained | FALSE | TRUE | Not_TMED_Event | 1497
MAYAGÃœEZ | 2021-10-20 15:33 | 2021-10-20 18:45 | 35 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000155 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-10-20 | 6720 | keep | 0 | Oct | 2021 | 0.004577 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-10-20 15:34 | 2021-10-20 15:35 | 225 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 QUE LLEVA LA CARGA DEL 1303-01 Y 1346-06, 1303-04 ESTA TRANSFERIDO | S21102000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-20 | 225 | keep | 0 | Oct | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-20 15:34 | 2021-10-20 15:36 | 225 | 000:02 | T | DESGANCHE | DISPARO INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S21102000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-20 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-20 15:34 | 2021-10-20 15:36 | 870 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S21102000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-20 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-10-20 15:34 | 2021-10-20 15:35 | 1598 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR 1303-04 LLEVANDO LA CARGA DEL 1303-01 Y 1346-06 | S21102000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-20 | 1598 | keep | 0 | Oct | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-10-20 15:36 | 2021-10-20 19:53 | 15 | 004:17 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR | S21101900090 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 257 | 2021-10-20 | 3855 | keep | 0 | Oct | 2021 | 0.0026256 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-20 15:42 | 2021-10-21 12:23 | 8 | 020:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 37.5 KVA | A21102000096 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1241 | 2021-10-20 | 9928 | keep | 0 | Oct | 2021 | 0.0067619 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-20 15:47 | 2021-10-20 20:30 | 50 | 004:43 | P | PARARRAYOS DEFECTUOSO | 3 X 80 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSOS | M21102000177 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 283 | 2021-10-20 | 14150 | keep | 0 | Oct | 2021 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-20 15:48 | 2021-10-20 15:52 | 15 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFORMADOR | S21101800181 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-10-20 | 60 | keep | 0 | Oct | 2021 | 4.0866e-05 | 1.0216e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-20 15:48 | 2021-10-20 20:57 | 60 | 005:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000348 | New_Event | Bad Weather | Include | Include | Weather | 309 | 2021-10-20 | 18540 | keep | 0 | Oct | 2021 | 0.012628 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-20 15:50 | 2021-10-21 17:39 | 55 | 025:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN RISER | S21102000219 | New_Event | Cutout Failure | Include | Include | Equipment | 1549 | 2021-10-20 | 85195 | keep | 0 | Oct | 2021 | 0.058026 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2021-10-20 15:50 | 2021-10-20 21:33 | 150 | 005:43 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | B21102000111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2021-10-20 | 51450 | keep | 0 | Oct | 2021 | 0.035042 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-10-20 15:51 | 2021-10-20 19:25 | 12 | 003:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21102000098 | New_Event | Bad Weather | Include | Include | Weather | 214 | 2021-10-20 | 2568 | keep | 0 | Oct | 2021 | 0.0017491 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
VEGA BAJA | 2021-10-20 15:55 | 2021-10-20 18:36 | 6 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21102000113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-10-20 | 966 | keep | 0 | Oct | 2021 | 0.00065794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:58 | 998 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON CARGA POR EL 1652-05 | S21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-20 | 1996 | keep | 0 | Oct | 2021 | 0.0013595 | 0.00067973 | Momentary | FALSE | TRUE | Not_TMED_Event | 998
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:59 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04. ADEMAS LLEVA LA CARGA DEL 1620-01 | S21102000223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-20 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:59 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04. ADEMAS LLEVA LA CARGA DEL 1620-01 | S21102000223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-20 | 516 | keep | 0 | Oct | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:58 | 614 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON | R21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-20 | 1228 | keep | 0 | Oct | 2021 | 0.00083639 | 0.00041819 | Momentary | FALSE | TRUE | Not_TMED_Event | 614
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:58 | 770 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON | R21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-20 | 1540 | keep | 0 | Oct | 2021 | 0.0010489 | 0.00052444 | Momentary | FALSE | TRUE | Not_TMED_Event | 770
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:58 | 1271 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON | R21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-20 | 2542 | keep | 0 | Oct | 2021 | 0.0017313 | 0.00086567 | Momentary | FALSE | TRUE | Not_TMED_Event | 1271
SAN JUAN | 2021-10-20 15:56 | 2021-10-20 15:58 | 247 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON LLEVANDO LA CARGA DEL 1301-03 | R21102000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-20 | 494 | keep | 0 | Oct | 2021 | 0.00033646 | 0.00016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 247
MAYAGÃœEZ | 2021-10-20 16:03 | 2021-10-21 11:00 | 50 | 018:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102000202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1137 | 2021-10-20 | 56850 | keep | 0 | Oct | 2021 | 0.03872 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-20 16:10 | 2021-10-20 17:35 | 300 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJAS PRIMARIAS | M21102000094 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2021-10-20 | 25500 | keep | 0 | Oct | 2021 | 0.017368 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-20 16:11 | 2021-10-20 20:20 | 45 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000208 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-10-20 | 11205 | keep | 0 | Oct | 2021 | 0.0076317 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-10-20 16:13 | 2021-10-20 18:24 | 36 | 002:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | S21102000122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-10-20 | 4716 | keep | 0 | Oct | 2021 | 0.003212 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
UTUADO | 2021-10-20 16:17 | 2021-10-21 17:00 | 40 | 024:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES PRIMARIOS | A21102000102 | New_Event | Wire Down | Include | Include | Equipment | 1483 | 2021-10-20 | 59320 | keep | 0 | Oct | 2021 | 0.040403 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-20 16:20 | 2021-10-20 18:13 | 100 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTE DE LINEA | B21102000119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2021-10-20 | 11300 | keep | 0 | Oct | 2021 | 0.0076964 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-20 16:20 | 2021-10-20 16:45 | 5 | 000:25 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR RAMAS CRUZANDO LAS LINEAS | M21102000215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-10-20 | 125 | keep | 0 | Oct | 2021 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-10-20 16:20 | 2021-10-21 14:09 | 5 | 021:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A TRANSFORMADOR | M21102000218 | New_Event | Wire Down | Include | Include | Equipment | 1309 | 2021-10-20 | 6545 | keep | 0 | Oct | 2021 | 0.0044578 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-20 16:28 | 2021-10-20 19:07 | 1 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | A21102000104 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2021-10-20 | 159 | keep | 0 | Oct | 2021 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-20 16:41 | 2021-10-20 22:10 | 100 | 005:29 | P | DESGANCHE | 1 X 30 , 1 X 50 Y 1 X 65 EN DISTINTOS CORTES DE LINEAS SE REALIZO DESGANCHE | B21102000120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 329 | 2021-10-20 | 32900 | keep | 0 | Oct | 2021 | 0.022408 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-20 16:51 | 2021-10-21 10:21 | 2 | 017:30 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | M21102000248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1050 | 2021-10-20 | 2100 | keep | 0 | Oct | 2021 | 0.0014303 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-10-20 16:57 | 2021-10-20 20:17 | 55 | 003:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | S21102000236 | New_Event | Cutout Failure | Include | Include | Equipment | 200 | 2021-10-20 | 11000 | keep | 0 | Oct | 2021 | 0.007492 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2021-10-20 17:07 | 2021-10-20 18:27 | 15 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R21102000089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-10-20 | 1200 | keep | 0 | Oct | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-10-20 17:16 | 2021-10-20 19:41 | 15 | 002:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLASO CAJA QUEMADA | P21102000130 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2021-10-20 | 2175 | keep | 0 | Oct | 2021 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-20 17:18 | 2021-10-20 17:19 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1620-01 | S21102000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 36 | keep | 0 | Oct | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-20 17:18 | 2021-10-20 17:19 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1620-01 | S21102000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 172 | keep | 0 | Oct | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
UTUADO | 2021-10-20 17:18 | 2021-10-20 18:11 | 35 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21102000111 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-10-20 | 1855 | keep | 0 | Oct | 2021 | 0.0012634 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-10-20 17:27 | 2021-10-20 19:59 | 40 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA RETEZO LINEAS Y REMPLAZO PARARRAYO | C21102000118 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2021-10-20 | 6080 | keep | 0 | Oct | 2021 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-20 17:28 | 2021-10-20 18:17 | 300 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000277 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-10-20 | 14700 | keep | 0 | Oct | 2021 | 0.010012 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-10-20 17:33 | 2021-10-20 20:06 | 2 | 002:33 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO LOCAL | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-10-20 | 306 | keep | 0 | Oct | 2021 | 0.00020842 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-10-20 17:40 | 2021-10-20 18:18 | 4 | 000:38 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21102000118 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 38 | 2021-10-20 | 152 | keep | 0 | Oct | 2021 | 0.00010353 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-20 17:41 | 2021-10-20 17:53 | 4291 | 000:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | PERSONAL DE DESPACHO INDICA REALIZANDO PRUEBA EN CORTE DE LINEA CON FUSIBLE OCASIONO ABRIERA PUENTE DE LINEA A CAJA | S21102000000 | New_Event | Wire Down | Include | Include | Equipment | 12 | 2021-10-20 | 51492 | keep | 0 | Oct | 2021 | 0.035071 | 0.0029226 | Sustained | FALSE | TRUE | Not_TMED_Event | 4291
CAGUAS | 2021-10-20 17:41 | 2021-10-20 17:42 | 20 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA | C21102000090 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-20 | 20 | keep | 0 | Oct | 2021 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-10-20 17:42 | 2021-10-20 19:23 | 9 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 NX MAL TIEMPO | R21102000133 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-10-20 | 909 | keep | 0 | Oct | 2021 | 0.00061912 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-10-20 17:46 | 2021-10-20 17:47 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 863 | keep | 0 | Oct | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2021-10-20 17:53 | 2021-10-20 19:20 | 85 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA Y SE CERRO PUENTE DE LINEA A CAJA | S21102000068 | Partial_restoration | Wire Down | Include | Include | Equipment | 87 | 2021-10-20 | 7395 | keep | 0 | Oct | 2021 | 0.0050367 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-10-20 17:56 | 2021-10-21 15:44 | 20 | 021:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21102000136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1308 | 2021-10-20 | 26160 | keep | 0 | Oct | 2021 | 0.017817 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-10-20 18:07 | 2021-10-20 19:05 | 40 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21102000123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2021-10-20 | 2320 | keep | 0 | Oct | 2021 | 0.0015801 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-10-20 18:09 | 2021-10-20 18:10 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2021-10-20 18:16 | 2021-10-20 18:17 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2203 | keep | 0 | Oct | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
MAYAGÃœEZ | 2021-10-20 18:25 | 2021-10-20 22:17 | 300 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA POR RAYOS | M21102000306 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2021-10-20 | 69600 | keep | 0 | Oct | 2021 | 0.047404 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-20 18:35 | 2021-10-20 20:07 | 400 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21102000310 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2021-10-20 | 36800 | keep | 0 | Oct | 2021 | 0.025064 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
BAYAMON | 2021-10-20 18:37 | 2021-10-23 10:52 | 10 | 064:15 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA SE LEVANTO CONDUCTOR Y SE REPARO LINEA SECUNDARIA | S21102000276 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 3855 | 2021-10-20 | 38550 | keep | 0 | Oct | 2021 | 0.026256 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-20 18:53 | 2021-10-21 18:34 | 8 | 023:41 | P | TRANSFORMADOR AVERIADO | REMPLAZAR TRANSFORMADOR AVERIADO 15 KVA X 25 KVA | C21102000128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1421 | 2021-10-20 | 11368 | keep | 0 | Oct | 2021 | 0.0077427 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-20 19:12 | 2021-10-21 10:47 | 60 | 015:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102000324 | New_Event | Bad Weather | Include | Include | Weather | 935 | 2021-10-20 | 56100 | keep | 0 | Oct | 2021 | 0.038209 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-10-20 19:17 | 2021-10-20 19:52 | 40 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21102000057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-10-20 | 1400 | keep | 0 | Oct | 2021 | 0.00095353 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-20 19:28 | 2021-10-20 20:32 | 20 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21102000329 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-10-20 | 1280 | keep | 0 | Oct | 2021 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-10-20 19:30 | 2021-10-20 19:31 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21102000294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 922 | keep | 0 | Oct | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-10-20 19:30 | 2021-10-20 19:31 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21102000294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
ARECIBO | 2021-10-20 19:33 | 2021-10-21 16:10 | 4 | 020:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21102100119 | New_Event | Bad Weather | Include | Include | Weather | 1237 | 2021-10-20 | 4948 | keep | 0 | Oct | 2021 | 0.0033701 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-10-20 19:45 | 2021-10-21 09:25 | 100 | 013:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102000336 | New_Event | Bad Weather | Include | Include | Weather | 820 | 2021-10-20 | 82000 | keep | 0 | Oct | 2021 | 0.05585 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-10-20 19:46 | 2021-10-20 21:37 | 135 | 001:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R21102000137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-10-20 | 14985 | keep | 0 | Oct | 2021 | 0.010206 | 9.1948e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 135
PONCE | 2021-10-20 19:48 | 2021-10-21 17:55 | 10 | 022:07 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR DE 37.5KVA A 4.16KV QUEMADO POR UNO DE IGUAL CAPACIDAD | P21102000143 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1327 | 2021-10-20 | 13270 | keep | 0 | Oct | 2021 | 0.0090381 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-20 19:49 | 2021-10-21 10:08 | 40 | 014:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102000340 | New_Event | Bad Weather | Include | Include | Weather | 859 | 2021-10-20 | 34360 | keep | 0 | Oct | 2021 | 0.023402 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-20 19:50 | 2021-10-20 21:10 | 15 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 11 X 15 EN TRANSFORMADOR MAL TIEMPO | A21102000121 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-10-20 | 1200 | keep | 0 | Oct | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2021-10-20 19:52 | 2021-10-20 19:53 | 2340 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P21102000098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
ARECIBO | 2021-10-20 19:55 | 2021-10-21 09:16 | 50 | 013:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102000122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 801 | 2021-10-20 | 40050 | keep | 0 | Oct | 2021 | 0.027278 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-20 20:08 | 2021-10-20 23:26 | 20 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CONVERTIDOR POR MAL TIEMPO | M21102000346 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-10-20 | 3960 | keep | 0 | Oct | 2021 | 0.0026971 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-10-20 20:26 | 2021-10-20 22:35 | 50 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21102000147 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-10-20 | 6450 | keep | 0 | Oct | 2021 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-20 20:30 | 2021-10-21 20:30 | 45 | 024:00 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21102100300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1440 | 2021-10-20 | 64800 | keep | 0 | Oct | 2021 | 0.044135 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-10-20 20:36 | 2021-10-21 06:51 | 1 | 010:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN RISER SE REMPLAZO CAJA | B21102000137 | New_Event | Cutout Failure | Include | Include | Equipment | 615 | 2021-10-20 | 615 | keep | 0 | Oct | 2021 | 0.00041887 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-20 20:49 | 2021-10-21 18:36 | 95 | 021:47 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN RISER Y SE ELIMINO PARARRAYOS AVERIADO EN SU-4 | S21102000305 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1307 | 2021-10-20 | 124165 | keep | 0 | Oct | 2021 | 0.084568 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-10-20 20:50 | 2021-10-21 16:07 | 1 | 019:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21102000351 | New_Event | Bad Weather | Include | Include | Weather | 1157 | 2021-10-20 | 1157 | keep | 0 | Oct | 2021 | 0.00078803 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-20 21:22 | 2021-10-20 22:01 | 641 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO ALIMENTADOR 1206-01 LLEVANDO LA CARGA DEL 1206-02 PARA CERRAR PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | S21102000312 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-10-20 | 24999 | keep | 0 | Oct | 2021 | 0.017027 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-20 21:22 | 2021-10-20 22:01 | 733 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO ALIMENTADOR 1206-01 LLEVANDO LA CARGA DEL 1206-02 PARA CERRAR PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | S21102000312 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-10-20 | 28587 | keep | 0 | Oct | 2021 | 0.01947 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2021-10-20 21:41 | 2021-10-21 16:46 | 30 | 019:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102000139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1145 | 2021-10-20 | 34350 | keep | 0 | Oct | 2021 | 0.023396 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-20 21:47 | 2021-10-21 09:47 | 50 | 012:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21102000140 | New_Event | Bad Weather | Include | Include | Weather | 720 | 2021-10-20 | 36000 | keep | 0 | Oct | 2021 | 0.024519 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-20 22:21 | 2021-10-21 19:26 | 10 | 021:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21102100356 | New_Event | Bad Weather | Include | Include | Weather | 1265 | 2021-10-20 | 12650 | keep | 0 | Oct | 2021 | 0.0086159 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-10-20 22:40 | 2021-10-21 06:08 | 60 | 007:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA RETIRO ARBOL DE LA LINEA LEVANTARON Y LIGARON CONDUCTOR PRIMARIO | C21102000142 | New_Event | Wire Down | Include | Include | Equipment | 448 | 2021-10-20 | 26880 | keep | 0 | Oct | 2021 | 0.018308 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-20 22:51 | 2021-10-21 17:01 | 55 | 018:10 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO Y SE LEVANTO LINEA PRIMARIA | S21102000336 | New_Event | Defective Pole | Include | Include | Equipment | 1090 | 2021-10-20 | 59950 | keep | 0 | Oct | 2021 | 0.040832 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
PONCE | 2021-10-20 23:00 | 2021-10-21 14:50 | 100 | 015:50 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO PARTIDO | P21102100162 | New_Event | Defective Pole | Include | Include | Equipment | 950 | 2021-10-20 | 95000 | keep | 0 | Oct | 2021 | 0.064704 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-20 23:09 | 2021-10-20 23:10 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 2926 | keep | 0 | Oct | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2021-10-20 23:09 | 2021-10-20 23:10 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 325 | keep | 0 | Oct | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CANOVANAS | 2021-10-20 23:12 | 2021-10-21 09:49 | 150 | 010:37 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | R21102000152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 637 | 2021-10-20 | 95550 | keep | 0 | Oct | 2021 | 0.065079 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-10-20 23:44 | 2021-10-20 23:45 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2604-03 LLEVANDO LA CARGA DEL 2604-02 | C21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 3025 | keep | 0 | Oct | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-10-20 23:44 | 2021-10-20 23:45 | 1593 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2604-03 LLEVANDO LA CARGA DEL 2604-02 | C21102000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-20 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
CAGUAS | 2021-10-20 23:48 | 2021-10-21 10:57 | 50 | 011:09 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA POSTE INCLINADO | C21102000156 | New_Event | Defective Pole | Include | Include | Equipment | 669 | 2021-10-20 | 33450 | keep | 0 | Oct | 2021 | 0.022783 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-21 | 2021-10-21 14:13 | 200 | 014:13 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100001 | New_Event | Bad Weather | Include | Include | Weather | 853 | 2021-10-21 | 170600 | keep | 0 | Oct | 2021 | 0.11619 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-10-21 00:07 | 2021-10-21 10:23 | 103 | 010:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P21102100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 616 | 2021-10-21 | 63448 | keep | 0 | Oct | 2021 | 0.043214 | 7.0153e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 103
CAGUAS | 2021-10-21 01:04 | 2021-10-21 09:25 | 142 | 008:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21102100003 | New_Event | Bad Weather | Include | Include | Weather | 501 | 2021-10-21 | 71142 | keep | 0 | Oct | 2021 | 0.048454 | 9.6716e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 142
HUMACAO | 2021-10-21 01:41 | 2021-10-21 01:42 | 2126 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECERRO | C21102100007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-21 | 2126 | keep | 0 | Oct | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-10-21 01:42 | 2021-10-21 02:10 | 851 | 000:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y PARARRAYO | C21102100010 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2021-10-21 | 23828 | keep | 0 | Oct | 2021 | 0.016229 | 0.00057961 | Sustained | FALSE | FALSE | Not_TMED_Event | 851
CAGUAS | 2021-10-21 01:44 | 2021-10-21 01:45 | 436 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 80% DE SU CARGA PR EL 3015-07 | C21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 436 | keep | 0 | Oct | 2021 | 0.00029696 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
AGUADILLA | 2021-10-21 01:50 | 2021-10-21 17:10 | 20 | 015:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21102000002 | New_Event | Bad Weather | Include | Include | Weather | 920 | 2021-10-21 | 18400 | keep | 0 | Oct | 2021 | 0.012532 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-10-21 02:10 | 2021-10-21 02:11 | 2126 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECERRO | C21102100008 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-10-21 | 2126 | keep | 0 | Oct | 2021 | 0.001448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-21 02:11 | 2021-10-21 03:18 | 851 | 001:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y PARARRAYO | C21102100010 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2021-10-21 | 57017 | keep | 0 | Oct | 2021 | 0.038834 | 0.00057961 | Sustained | FALSE | FALSE | Not_TMED_Event | 851
SAN JUAN | 2021-10-21 02:27 | 2021-10-21 10:06 | 40 | 007:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN RISER | R21102100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 459 | 2021-10-21 | 18360 | keep | 0 | Oct | 2021 | 0.012505 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-21 03:03 | 2021-10-21 10:55 | 10 | 007:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21102100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2021-10-21 | 4720 | keep | 0 | Oct | 2021 | 0.0032148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-21 03:13 | 2021-10-21 03:14 | 2354 | 000:01 | T | DESGANCHE | RECIERRE | C21102100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-21 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-10-21 03:14 | 2021-10-21 16:12 | 6 | 012:58 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 40 AMP EN SU 5 | C21102100097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 778 | 2021-10-21 | 4668 | keep | 0 | Oct | 2021 | 0.0031794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-21 03:18 | 2021-10-21 10:19 | 100 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21102100002 | New_Event | Bad Weather | Include | Include | Weather | 421 | 2021-10-21 | 42100 | keep | 0 | Oct | 2021 | 0.028674 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-21 03:18 | 2021-10-21 10:12 | 2126 | 006:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y PARARRAYO | C21102100010 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 414 | 2021-10-21 | 880164 | keep | 0 | Oct | 2021 | 0.59948 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-21 03:47 | 2021-10-21 03:48 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO LA CARGA DEL 1206-02 | S21102100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-21 03:47 | 2021-10-21 03:48 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO LA CARGA DEL 1206-02 | S21102100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
GUAYAMA | 2021-10-21 03:49 | 2021-10-21 13:25 | 391 | 009:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 140 EN CORTE DE LINEA SE REEMPLAZARON TRES CAJAS PRIMARIAS QUEMADAS | P21102100007 | New_Event | Cutout Failure | Include | Include | Equipment | 576 | 2021-10-21 | 225216 | keep | 0 | Oct | 2021 | 0.15339 | 0.00026631 | Sustained | FALSE | TRUE | Not_TMED_Event | 391
HUMACAO | 2021-10-21 03:55 | 2021-10-21 09:29 | 221 | 005:34 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80 EN CORTE DE LINEA MAL TIEMPO | C21102100017 | New_Event | Bad Weather | Include | Include | Weather | 334 | 2021-10-21 | 73814 | keep | 0 | Oct | 2021 | 0.050274 | 0.00015052 | Sustained | FALSE | TRUE | Not_TMED_Event | 221
BAYAMON | 2021-10-21 04:06 | 2021-10-21 04:53 | 353 | 000:47 | T | TRANSFORMADOR AVERIADO | DISPARO 1531-05 Y SE CERRO POR SCADA. PROBLEMAS CON EL RTU EN SUBESTACION | S21102100012 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 47 | 2021-10-21 | 16591 | keep | 0 | Oct | 2021 | 0.0113 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-21 04:11 | 2021-10-21 04:12 | 546 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO Y SE CERRO POR SCADA | S21102100000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-21 | 546 | keep | 0 | Oct | 2021 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
SAN JUAN | 2021-10-21 04:12 | 2021-10-21 22:46 | 300 | 018:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO EN SU-1 HACIA MH-4 PARA ESTABLECER GOI Y REPARAR 3 PISTOLAS AVERIADAS | S21102100064 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1114 | 2021-10-21 | 334200 | keep | 0 | Oct | 2021 | 0.22762 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-10-21 04:13 | 2021-10-21 04:14 | 4188 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | R21102100000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-10-21 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-10-21 04:14 | 2021-10-21 11:53 | 20 | 007:39 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21102100012 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 459 | 2021-10-21 | 9180 | keep | 0 | Oct | 2021 | 0.0062525 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-10-21 04:35 | 2021-10-21 14:32 | 50 | 009:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REMPLAZO AISLACION | C21102100025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 597 | 2021-10-21 | 29850 | keep | 0 | Oct | 2021 | 0.020331 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-21 04:48 | 2021-10-21 09:35 | 40 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21102100028 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2021-10-21 | 11480 | keep | 0 | Oct | 2021 | 0.007819 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-21 04:53 | 2021-10-21 10:15 | 8 | 005:22 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | S21101900269 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 322 | 2021-10-21 | 2576 | keep | 0 | Oct | 2021 | 0.0017545 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-21 04:59 | 2021-10-21 14:42 | 100 | 009:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA SE REMPLAZO CAJAS PRIMARIAS AVERIADAS | A21102100003 | New_Event | Wire Down | Include | Include | Equipment | 583 | 2021-10-21 | 58300 | keep | 0 | Oct | 2021 | 0.039708 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-10-21 05:02 | 2021-10-21 05:03 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21102100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 1615 | keep | 0 | Oct | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-10-21 06:15 | 2021-10-21 14:45 | 90 | 008:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y 1 X 80 EN OTRO CORTE DE LINEA Y SE REEMPLAZO CAJA | S21102100028 | New_Event | Cutout Failure | Include | Include | Equipment | 510 | 2021-10-21 | 45900 | keep | 0 | Oct | 2021 | 0.031262 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-10-21 06:24 | 2021-10-21 10:56 | 50 | 004:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21102100049 | New_Event | Bad Weather | Include | Include | Weather | 272 | 2021-10-21 | 13600 | keep | 0 | Oct | 2021 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-21 06:30 | 2021-10-21 06:33 | 2720 | 000:03 | T | CABLE SOTERRADO AVERIADO | SE CERRO POR SCADA | S21102100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2021-10-21 | 8160 | keep | 0 | Oct | 2021 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-10-21 06:33 | 2021-10-23 19:34 | 1 | 061:01 | P | CABLE SOTERRADO AVERIADO | SE ALAMBRO TRAMO SOTERRADO AVERIADO | S21102100185 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 3661 | 2021-10-21 | 3661 | keep | 0 | Oct | 2021 | 0.0024935 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-21 06:45 | 2021-10-21 06:46 | 619 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21102100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-21 | 619 | keep | 0 | Oct | 2021 | 0.0004216 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2021-10-21 06:46 | 2021-10-21 18:32 | 125 | 011:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102100070 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 706 | 2021-10-21 | 88250 | keep | 0 | Oct | 2021 | 0.060107 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
ARECIBO | 2021-10-21 06:49 | 2021-10-21 13:40 | 10 | 006:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA | A21102100007 | New_Event | Cutout Failure | Include | Include | Equipment | 411 | 2021-10-21 | 4110 | keep | 0 | Oct | 2021 | 0.0027993 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-21 06:51 | 2021-10-21 06:52 | 5961 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B21102100000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-21 | 5961 | keep | 0 | Oct | 2021 | 0.00406 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-21 06:52 | 2021-10-21 10:37 | 1 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN RISER SE REMPLAZO CAJA | B21102000137 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 225 | 2021-10-21 | 225 | keep | 0 | Oct | 2021 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-21 06:53 | 2021-10-21 11:22 | 150 | 004:29 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE DESGANCHO Y CERRO PUENTE | R21102100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2021-10-21 | 40350 | keep | 0 | Oct | 2021 | 0.027482 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-10-21 07:06 | 2021-10-22 12:10 | 15 | 029:04 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21102100008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1744 | 2021-10-21 | 26160 | keep | 0 | Oct | 2021 | 0.017817 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-10-21 07:10 | 2021-10-21 10:23 | 80 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21102100064 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2021-10-21 | 15440 | keep | 0 | Oct | 2021 | 0.010516 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-21 07:11 | 2021-10-21 15:07 | 90 | 007:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA PRINCIPAL Y 1 X 80 EN SU-4 | S21102100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2021-10-21 | 42840 | keep | 0 | Oct | 2021 | 0.029178 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
PONCE | 2021-10-21 07:18 | 2021-10-21 09:31 | 87 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P21102100017 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-10-21 | 11571 | keep | 0 | Oct | 2021 | 0.007881 | 5.9255e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 87
BAYAMON | 2021-10-21 07:23 | 2021-10-21 07:24 | 573 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1704-04 LLEVANDO LA CARGA DEL 1704-05 Y SE CERRO POR CONTROL | B21102100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 573 | keep | 0 | Oct | 2021 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-10-21 07:23 | 2021-10-21 07:24 | 1313 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1704-04 LLEVANDO LA CARGA DEL 1704-05 Y SE CERRO POR CONTROL | B21102100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 1313 | keep | 0 | Oct | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2021-10-21 07:25 | 2021-10-21 13:53 | 12 | 006:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA | B21102100012 | New_Event | Wire Down | Include | Include | Equipment | 388 | 2021-10-21 | 4656 | keep | 0 | Oct | 2021 | 0.0031712 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
AGUADILLA | 2021-10-21 07:31 | 2021-10-21 12:58 | 40 | 005:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA EN CORTE DE LINEA DE 100AMP INFORMO EL JOURNEYMAN QUE NO TENIA LA MARCA DE LA CAJA | M21102100010 | New_Event | Cutout Failure | Include | Include | Equipment | 327 | 2021-10-21 | 13080 | keep | 0 | Oct | 2021 | 0.0089087 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-10-21 07:38 | 2021-10-21 14:16 | 20 | 006:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE DESGANCHO Y RETEZO LINEAS | R21102100009 | New_Event | Wire Down | Include | Include | Equipment | 398 | 2021-10-21 | 7960 | keep | 0 | Oct | 2021 | 0.0054215 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-10-21 07:39 | 2021-10-21 13:47 | 5 | 006:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100073 | New_Event | Bad Weather | Include | Include | Weather | 368 | 2021-10-21 | 1840 | keep | 0 | Oct | 2021 | 0.0012532 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-21 07:43 | 2021-10-21 10:00 | 20 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102100012 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-10-21 | 2740 | keep | 0 | Oct | 2021 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-21 07:47 | 2021-10-21 14:55 | 70 | 007:08 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | P21102100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2021-10-21 | 29960 | keep | 0 | Oct | 2021 | 0.020406 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-10-21 08:04 | 2021-10-21 16:52 | 40 | 008:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21102100078 | New_Event | Bad Weather | Include | Include | Weather | 528 | 2021-10-21 | 21120 | keep | 0 | Oct | 2021 | 0.014385 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-10-21 08:07 | 2021-10-21 11:33 | 65 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21102100026 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2021-10-21 | 13390 | keep | 0 | Oct | 2021 | 0.0091199 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
UTUADO | 2021-10-21 08:09 | 2021-10-21 11:17 | 100 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 25 EN CORTES DE LINEA DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A21102100013 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-10-21 | 18800 | keep | 0 | Oct | 2021 | 0.012805 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-21 08:10 | 2021-10-21 11:00 | 80 | 002:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21102100014 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-10-21 | 13600 | keep | 0 | Oct | 2021 | 0.0092629 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-10-21 08:12 | 2021-10-21 16:31 | 36 | 008:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21102100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 499 | 2021-10-21 | 17964 | keep | 0 | Oct | 2021 | 0.012235 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
HUMACAO | 2021-10-21 08:19 | 2021-10-21 15:24 | 28 | 007:05 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA QUE PERSONAL CONTRATISTA DESGANCHARA | C21102100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2021-10-21 | 11900 | keep | 0 | Oct | 2021 | 0.008105 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
ARECIBO | 2021-10-21 08:34 | 2021-10-21 17:12 | 7 | 008:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21102100015 | New_Event | Bad Weather | Include | Include | Weather | 518 | 2021-10-21 | 3626 | keep | 0 | Oct | 2021 | 0.0024697 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-21 08:42 | 2021-10-22 18:25 | 12 | 033:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR UNO DE 25KVA | B21102100018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2023 | 2021-10-21 | 24276 | keep | 0 | Oct | 2021 | 0.016534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-10-21 08:47 | 2021-10-21 08:48 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 5630 | keep | 0 | Oct | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2021-10-21 08:48 | 2021-10-21 11:43 | 51 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21102100046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2021-10-21 | 8925 | keep | 0 | Oct | 2021 | 0.0060788 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
HUMACAO | 2021-10-21 08:48 | 2021-10-21 18:21 | 1 | 009:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | C21102100194 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 573 | 2021-10-21 | 573 | keep | 0 | Oct | 2021 | 0.00039027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-10-21 09:00 | 2021-10-21 16:50 | 1 | 007:50 | P | ESTRUCTURA AVERIADA | 3 X 40 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO PARTIDO | P21102100048 | New_Event | Defective Pole | Include | Include | Equipment | 470 | 2021-10-21 | 470 | keep | 0 | Oct | 2021 | 0.00032011 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-21 09:01 | 2021-10-21 15:27 | 6 | 006:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21102100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 386 | 2021-10-21 | 2316 | keep | 0 | Oct | 2021 | 0.0015774 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-10-21 09:05 | 2021-10-21 19:10 | 1 | 010:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21102000033 | New_Event | Wire Down | Include | Include | Equipment | 605 | 2021-10-21 | 605 | keep | 0 | Oct | 2021 | 0.00041206 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-10-21 09:18 | 2021-10-21 09:19 | 7 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21102100006 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-21 | 7 | keep | 0 | Oct | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-21 09:21 | 2021-10-21 15:12 | 100 | 005:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21102100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2021-10-21 | 35100 | keep | 0 | Oct | 2021 | 0.023906 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-10-21 09:23 | 2021-10-21 14:23 | 25 | 005:00 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 25 EN CORTE DE LINEA | B21102100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 300 | 2021-10-21 | 7500 | keep | 0 | Oct | 2021 | 0.0051082 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-21 09:31 | 2021-10-21 10:38 | 15 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | S21102100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-10-21 | 1005 | keep | 0 | Oct | 2021 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-10-21 09:42 | 2021-10-21 14:06 | 10 | 004:24 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A21102100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2021-10-21 | 2640 | keep | 0 | Oct | 2021 | 0.0017981 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-21 09:48 | 2021-10-21 12:05 | 40 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21102100102 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-10-21 | 5480 | keep | 0 | Oct | 2021 | 0.0037324 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-21 09:50 | 2021-10-21 13:53 | 13 | 004:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-10-21 | 3159 | keep | 0 | Oct | 2021 | 0.0021516 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
ARECIBO | 2021-10-21 09:55 | 2021-10-21 10:29 | 10 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21102000124 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-10-21 | 340 | keep | 0 | Oct | 2021 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-21 10:03 | 2021-10-21 13:35 | 50 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21102100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-10-21 | 10600 | keep | 0 | Oct | 2021 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-21 10:07 | 2021-10-21 13:39 | 150 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 65 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102100041 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-10-21 | 31800 | keep | 0 | Oct | 2021 | 0.021659 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-21 10:10 | 2021-10-21 15:05 | 50 | 004:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2021-10-21 | 14750 | keep | 0 | Oct | 2021 | 0.010046 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-21 10:10 | 2021-10-21 13:10 | 3894 | 003:00 | T | LINEA DE TRANSMISION 38KV | SE ABRIO EL INTERRUPTOR AUTORIZADO POR LUIS FENEQUE PARA TRABAJOS EN LINEA 5600 SOBRE EL TRONCAL DEL ALIMENTADOR | M21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2021-10-21 | 700920 | keep | 0 | Oct | 2021 | 0.47739 | 0.0026522 | Sustained | FALSE | TRUE | Not_TMED_Event | 3894
HUMACAO | 2021-10-21 10:12 | 2021-10-21 11:48 | 851 | 001:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y PARARRAYO | C21102100010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 96 | 2021-10-21 | 81696 | keep | 0 | Oct | 2021 | 0.055643 | 0.00057961 | Sustained | FALSE | FALSE | Not_TMED_Event | 851
UTUADO | 2021-10-21 10:13 | 2021-10-21 16:10 | 100 | 005:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A21102100022 | New_Event | Wire Down | Include | Include | Equipment | 357 | 2021-10-21 | 35700 | keep | 0 | Oct | 2021 | 0.024315 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-10-21 10:14 | 2021-10-21 16:56 | 100 | 006:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZARON DISCOS | S21102100063 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 402 | 2021-10-21 | 40200 | keep | 0 | Oct | 2021 | 0.02738 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-21 10:22 | 2021-10-21 11:58 | 1 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21102100022 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2021-10-21 | 96 | keep | 0 | Oct | 2021 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-21 10:30 | 2021-10-21 20:35 | 25 | 010:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR IGUAL CAPACIDAD | S21102100067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 605 | 2021-10-21 | 15125 | keep | 0 | Oct | 2021 | 0.010302 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-10-21 10:31 | 2021-10-21 13:47 | 25 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2021-10-21 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-21 10:36 | 2021-10-21 19:35 | 45 | 008:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102100072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 539 | 2021-10-21 | 24255 | keep | 0 | Oct | 2021 | 0.01652 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-10-21 10:41 | 2021-10-21 16:07 | 30 | 005:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-10-21 | 9780 | keep | 0 | Oct | 2021 | 0.0066611 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-21 11:05 | 2021-10-21 17:23 | 4 | 006:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA | A21102100026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 378 | 2021-10-21 | 1512 | keep | 0 | Oct | 2021 | 0.0010298 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-21 11:14 | 2021-10-21 15:24 | 13 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21102100054 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2021-10-21 | 3250 | keep | 0 | Oct | 2021 | 0.0022136 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2021-10-21 11:19 | 2021-10-21 15:30 | 250 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | A21102100029 | New_Event | Wire Down | Include | Include | Equipment | 251 | 2021-10-21 | 62750 | keep | 0 | Oct | 2021 | 0.042739 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
HUMACAO | 2021-10-21 11:21 | 2021-10-21 14:44 | 20 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA Y 2 X 10 EN TRANSFORMADORES MAL TIEMPO | C21102100134 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-10-21 | 4060 | keep | 0 | Oct | 2021 | 0.0027652 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-10-21 11:29 | 2021-10-21 15:20 | 40 | 003:51 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA ELIMINAR POSTE Y RETEZAR LINEA | C21102100139 | New_Event | Defective Pole | Include | Include | Equipment | 231 | 2021-10-21 | 9240 | keep | 0 | Oct | 2021 | 0.0062933 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-21 11:30 | 2021-10-21 20:17 | 20 | 008:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21102100041 | New_Event | Cutout Failure | Include | Include | Equipment | 527 | 2021-10-21 | 10540 | keep | 0 | Oct | 2021 | 0.0071787 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-21 11:31 | 2021-10-21 16:05 | 50 | 004:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102100140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2021-10-21 | 13700 | keep | 0 | Oct | 2021 | 0.009331 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-21 11:32 | 2021-10-21 12:32 | 1 | 001:00 | P | NO SE REPORTO CAUSA | 2 X 10 EN RISER | B21102100042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2021-10-21 | 60 | keep | 0 | Oct | 2021 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-21 11:44 | 2021-10-22 13:00 | 34 | 025:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21102100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1516 | 2021-10-21 | 51544 | keep | 0 | Oct | 2021 | 0.035106 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
CANOVANAS | 2021-10-21 11:46 | 2021-10-21 14:16 | 3 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21102100024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2021-10-21 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-21 12:13 | 2021-10-21 12:15 | 959 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 1918 | keep | 0 | Oct | 2021 | 0.0013063 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-10-21 12:13 | 2021-10-21 12:15 | 1297 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 2594 | keep | 0 | Oct | 2021 | 0.0017668 | 0.00088338 | Momentary | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-10-21 12:13 | 2021-10-21 12:15 | 451 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 902 | keep | 0 | Oct | 2021 | 0.00061435 | 0.00030717 | Momentary | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-10-21 12:13 | 2021-10-21 12:15 | 1264 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 2528 | keep | 0 | Oct | 2021 | 0.0017218 | 0.0008609 | Momentary | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-10-21 12:13 | 2021-10-21 12:15 | 620 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 1240 | keep | 0 | Oct | 2021 | 0.00084456 | 0.00042228 | Momentary | FALSE | TRUE | Not_TMED_Event | 620
CAGUAS | 2021-10-21 12:29 | 2021-10-21 15:21 | 8 | 002:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO | C21102100152 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2021-10-21 | 1376 | keep | 0 | Oct | 2021 | 0.00093719 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-21 12:33 | 2021-10-21 20:29 | 60 | 007:56 | P | CABLE SOTERRADO AVERIADO | 1 X 80 1 X 50 EN C/L Y 1 X 15 EN TRANSFORMADOR PROBO MALO DEL T-7 @ T-6 | B21102100037 | New_Event | UG Cable Fault | Include | Include | Equipment | 476 | 2021-10-21 | 28560 | keep | 0 | Oct | 2021 | 0.019452 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-10-21 12:34 | 2021-10-21 20:38 | 25 | 008:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102000131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 484 | 2021-10-21 | 12100 | keep | 0 | Oct | 2021 | 0.0082413 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-10-21 12:39 | 2021-10-21 16:12 | 15 | 003:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21102100154 | New_Event | Bad Weather | Include | Include | Weather | 213 | 2021-10-21 | 3195 | keep | 0 | Oct | 2021 | 0.0021761 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-10-21 12:44 | 2021-10-21 14:43 | 25 | 001:59 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA | R21102100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-10-21 | 2975 | keep | 0 | Oct | 2021 | 0.0020263 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-10-21 12:46 | 2021-10-22 14:20 | 2 | 025:34 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL | C21102100160 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1534 | 2021-10-21 | 3068 | keep | 0 | Oct | 2021 | 0.0020896 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-10-21 12:48 | 2021-10-21 17:58 | 50 | 005:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21102100162 | New_Event | Bad Weather | Include | Include | Weather | 310 | 2021-10-21 | 15500 | keep | 0 | Oct | 2021 | 0.010557 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-21 12:53 | 2021-10-21 16:24 | 10 | 003:31 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA | R21102100029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 211 | 2021-10-21 | 2110 | keep | 0 | Oct | 2021 | 0.0014371 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-21 12:59 | 2021-10-21 13:00 | 3 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 3 | keep | 0 | Oct | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-10-21 13:08 | 2021-10-21 13:09 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO LA CARGA DEL 1206-02 | S21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-21 13:08 | 2021-10-21 13:09 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO LA CARGA DEL 1206-02 | S21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-10-21 13:08 | 2021-10-21 13:13 | 36 | 000:05 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA 1620-04 QUE LLEVA LA CARGA DEL 1620-01 | S21102100104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-21 | 180 | keep | 0 | Oct | 2021 | 0.0001226 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-21 13:08 | 2021-10-21 13:13 | 172 | 000:05 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA 1620-04 LLEVA LA CARGA DEL 1620-01 | S21102100104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-10-21 | 860 | keep | 0 | Oct | 2021 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-10-21 13:09 | 2021-10-21 13:12 | 1615 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO | R21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-21 | 4845 | keep | 0 | Oct | 2021 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-10-21 13:14 | 2021-10-21 13:15 | 1132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 1132 | keep | 0 | Oct | 2021 | 0.000771 | 0.000771 | Momentary | FALSE | FALSE | Not_TMED_Event | 1132
SAN JUAN | 2021-10-21 13:16 | 2021-10-21 14:50 | 1066 | 001:34 | T | DESGANCHE | DISPARO DE INTERRUPTOR. SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21102100109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-10-21 | 100204 | keep | 0 | Oct | 2021 | 0.068248 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2021-10-21 13:19 | 2021-10-21 16:30 | 1310 | 003:11 | T | DESGANCHE | DISPARO DE INTERUPTOR. SE SECCIONALIZO LINEA Y SE DESGACHO EN VARIOS PUNTOS. ENTRO UN 50% | S21102100114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-10-21 | 250210 | keep | 0 | Oct | 2021 | 0.17042 | 0.00089224 | Sustained | FALSE | TRUE | Not_TMED_Event | 1310
BAYAMON | 2021-10-21 13:20 | 2021-10-21 16:35 | 25 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RELOCALIZARON LINEAS POR EMERGENCIA PROBLEMAS DE INVASION SERVIDUMBRE | B21102100000 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2021-10-21 | 4875 | keep | 0 | Oct | 2021 | 0.0033203 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-21 13:23 | 2021-10-21 13:24 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 271 | keep | 0 | Oct | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2021-10-21 13:26 | 2021-10-21 18:38 | 5 | 005:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100167 | New_Event | Bad Weather | Include | Include | Weather | 312 | 2021-10-21 | 1560 | keep | 0 | Oct | 2021 | 0.0010625 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-21 13:28 | 2021-10-21 13:29 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 58 | keep | 0 | Oct | 2021 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2021-10-21 13:30 | 2021-10-21 13:31 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 1498 | keep | 0 | Oct | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-10-21 13:31 | 2021-10-21 21:44 | 60 | 008:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21102100077 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 493 | 2021-10-21 | 29580 | keep | 0 | Oct | 2021 | 0.020147 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-21 13:44 | 2021-10-21 18:42 | 50 | 004:58 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA Y SE REALIZO PODA | S21102100124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2021-10-21 | 14900 | keep | 0 | Oct | 2021 | 0.010148 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-21 13:44 | 2021-10-21 18:33 | 125 | 004:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 100 EN SU-13 | S21102100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-10-21 | 36125 | keep | 0 | Oct | 2021 | 0.024605 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-10-21 13:44 | 2021-10-21 13:45 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 959 | keep | 0 | Oct | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BARRANQUITAS | 2021-10-21 13:44 | 2021-10-21 16:06 | 3 | 002:22 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR DESGANCHO | C21102100168 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 142 | 2021-10-21 | 426 | keep | 0 | Oct | 2021 | 0.00029015 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-10-21 13:45 | 2021-10-21 13:46 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 959 | keep | 0 | Oct | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
AGUADILLA | 2021-10-21 13:48 | 2021-10-21 14:30 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | M21102100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-10-21 | 420 | keep | 0 | Oct | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-21 14:00 | 2021-10-21 17:41 | 65 | 003:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21102100130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-10-21 | 14365 | keep | 0 | Oct | 2021 | 0.0097839 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-10-21 14:04 | 2021-10-22 15:25 | 8 | 025:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN SWITCHING UNIT MAL TIEMPO DESCARGAS ELECTRICAS | M21102100085 | New_Event | Bad Weather | Include | Include | Weather | 1521 | 2021-10-21 | 12168 | keep | 0 | Oct | 2021 | 0.0082876 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-10-21 14:18 | 2021-10-21 18:23 | 30 | 004:05 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO CRUZADO | M21102100117 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 245 | 2021-10-21 | 7350 | keep | 0 | Oct | 2021 | 0.0050061 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-21 14:39 | 2021-10-21 16:31 | 25 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102100190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-10-21 | 2800 | keep | 0 | Oct | 2021 | 0.0019071 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-10-21 14:42 | 2021-10-21 15:56 | 13 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21102100144 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-10-21 | 962 | keep | 0 | Oct | 2021 | 0.00065521 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-10-21 14:49 | 2021-10-21 18:55 | 10 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21102100050 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2021-10-21 | 2460 | keep | 0 | Oct | 2021 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-21 15:31 | 2021-10-21 17:27 | 10 | 001:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | C21102100181 | New_Event | Wire Down | Include | Include | Equipment | 116 | 2021-10-21 | 1160 | keep | 0 | Oct | 2021 | 0.00079007 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-21 15:31 | 2021-10-21 16:49 | 5 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21102100186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-21 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-10-21 15:31 | 2021-10-21 20:28 | 50 | 004:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21102100054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2021-10-21 | 14850 | keep | 0 | Oct | 2021 | 0.010114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-21 15:31 | 2021-10-22 13:24 | 7 | 021:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102100108 | New_Event | Bad Weather | Include | Include | Weather | 1313 | 2021-10-21 | 9191 | keep | 0 | Oct | 2021 | 0.0062599 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-21 15:31 | 2021-10-21 16:20 | 10 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 8 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21102100087 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-10-21 | 490 | keep | 0 | Oct | 2021 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-21 15:31 | 2021-10-21 23:32 | 40 | 008:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR UN PAJARO | M21102100097 | New_Event |  |  | Include | Wildlife | 481 | 2021-10-21 | 19240 | keep | 0 | Oct | 2021 | 0.013104 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-21 15:31 | 2021-10-21 17:14 | 20 | 001:43 | P | DESGANCHE | 3 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE EN LINEA PRIMARIA | M21102100097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-10-21 | 2060 | keep | 0 | Oct | 2021 | 0.0014031 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-10-21 15:31 | 2021-10-21 18:10 | 5 | 002:39 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21102100098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-10-21 | 795 | keep | 0 | Oct | 2021 | 0.00054147 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-21 15:32 | 2021-10-22 11:07 | 10 | 019:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | A21102100052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1175 | 2021-10-21 | 11750 | keep | 0 | Oct | 2021 | 0.0080029 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-21 15:45 | 2021-10-22 09:15 | 180 | 017:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 50 EN CORTE DE LINEA PERSONAL DE LIBERTY IMPACTO LINEA | C21102100195 | New_Event |  |  | Include | Wildlife | 1050 | 2021-10-21 | 189000 | keep | 0 | Oct | 2021 | 0.12873 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-10-21 15:47 | 2021-10-22 16:00 | 4 | 024:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES PRIMARIOS | M21102100175 | New_Event | Wire Down | Include | Include | Equipment | 1453 | 2021-10-21 | 5812 | keep | 0 | Oct | 2021 | 0.0039585 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
AGUADILLA | 2021-10-21 15:52 | 2021-10-21 17:53 | 10 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21102100183 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-10-21 | 1210 | keep | 0 | Oct | 2021 | 0.00082413 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-10-21 16:00 | 2021-10-21 16:01 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21102100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-21 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-10-21 16:01 | 2021-10-21 22:36 | 300 | 006:35 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA Y SE REPARO LINEAS PARTIDAS | A21102100058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 395 | 2021-10-21 | 118500 | keep | 0 | Oct | 2021 | 0.08071 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-10-21 16:05 | 2021-10-21 16:07 | 959 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S21102100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 1918 | keep | 0 | Oct | 2021 | 0.0013063 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-10-21 16:05 | 2021-10-21 16:07 | 1297 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S21102100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 2594 | keep | 0 | Oct | 2021 | 0.0017668 | 0.00088338 | Momentary | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-10-21 16:05 | 2021-10-21 16:07 | 451 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S21102100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 902 | keep | 0 | Oct | 2021 | 0.00061435 | 0.00030717 | Momentary | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-10-21 16:05 | 2021-10-21 16:07 | 1264 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S21102100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 2528 | keep | 0 | Oct | 2021 | 0.0017218 | 0.0008609 | Momentary | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-10-21 16:05 | 2021-10-21 16:07 | 620 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S21102100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-21 | 1240 | keep | 0 | Oct | 2021 | 0.00084456 | 0.00042228 | Momentary | FALSE | TRUE | Not_TMED_Event | 620
VEGA BAJA | 2021-10-21 16:07 | 2021-10-21 23:59 | 35 | 007:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21102100097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2021-10-21 | 16520 | keep | 0 | Oct | 2021 | 0.011252 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-21 16:10 | 2021-10-21 16:55 | 40 | 000:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21102100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-10-21 | 1800 | keep | 0 | Oct | 2021 | 0.001226 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-21 16:12 | 2021-10-21 18:32 | 1 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RAICER MAL TIEMPO | P21102100065 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-10-21 | 140 | keep | 0 | Oct | 2021 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-21 16:15 | 2021-10-21 16:16 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1706-02 QUE LLEVA 1706-03 | B21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 1382 | keep | 0 | Oct | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-10-21 16:15 | 2021-10-21 16:16 | 663 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1706-02 QUE LLEVA 1706-03 | B21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 663 | keep | 0 | Oct | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
HUMACAO | 2021-10-21 16:15 | 2021-10-21 17:45 | 5 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100202 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-10-21 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-21 16:22 | 2021-10-21 17:35 | 20 | 001:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-10-21 | 1460 | keep | 0 | Oct | 2021 | 0.0009944 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-21 16:30 | 2021-10-21 17:51 | 750 | 001:21 | P | DESGANCHE | DISPARO DE INTERUPTOR. SE SECCIONALIZO LINEA Y SE DESGACHO EN VARIOS PUNTOS | S21102100114 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-10-21 | 60750 | keep | 0 | Oct | 2021 | 0.041377 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-21 16:53 | 2021-10-21 17:20 | 9 | 000:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21102100130 | New_Event | Bad Weather | Include | Include | Weather | 27 | 2021-10-21 | 243 | keep | 0 | Oct | 2021 | 0.00016551 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
ARECIBO | 2021-10-21 16:53 | 2021-10-21 17:20 | 1 | 000:27 | P | PARARRAYOS DEFECTUOSO | 3 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A21102100069 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 27 | 2021-10-21 | 27 | keep | 0 | Oct | 2021 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-21 17:03 | 2021-10-21 18:47 | 65 | 001:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21102100208 | New_Event | Bad Weather | Include | Include | Weather | 104 | 2021-10-21 | 6760 | keep | 0 | Oct | 2021 | 0.0046042 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-10-21 17:08 | 2021-10-21 21:25 | 80 | 004:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21102100179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2021-10-21 | 20560 | keep | 0 | Oct | 2021 | 0.014003 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-10-21 17:10 | 2021-10-21 19:20 | 5 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100210 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-10-21 | 650 | keep | 0 | Oct | 2021 | 0.00044271 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-21 17:21 | 2021-10-21 18:36 | 8 | 001:15 | P | DESGANCHE | SECCIONALIZO POSTE SECUNDARIO PARTIDO POR RAMA | C21102100211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-10-21 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-21 17:27 | 2021-10-22 15:45 | 55 | 022:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 50 EN CORTE DE LINEA PRINCIPAL | S21102100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1338 | 2021-10-21 | 73590 | keep | 0 | Oct | 2021 | 0.050122 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
HUMACAO | 2021-10-21 17:32 | 2021-10-22 11:41 | 3 | 018:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100214 | New_Event | Bad Weather | Include | Include | Weather | 1089 | 2021-10-21 | 3267 | keep | 0 | Oct | 2021 | 0.0022251 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-10-21 17:34 | 2021-10-21 19:29 | 25 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | C21102100215 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-10-21 | 2875 | keep | 0 | Oct | 2021 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-21 17:35 | 2021-10-21 19:30 | 50 | 001:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102100071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-10-21 | 5750 | keep | 0 | Oct | 2021 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-21 17:43 | 2021-10-22 17:00 | 1 | 023:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA BANCO DE TRANSFORMADORES | C21102100219 | New_Event | Wire Down | Include | Include | Equipment | 1397 | 2021-10-21 | 1397 | keep | 0 | Oct | 2021 | 0.00095149 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-21 17:53 | 2021-10-21 21:20 | 5 | 003:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21102100072 | New_Event | Bad Weather | Include | Include | Weather | 207 | 2021-10-21 | 1035 | keep | 0 | Oct | 2021 | 0.00070493 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-21 18:13 | 2021-10-22 11:33 | 15 | 017:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102100073 | New_Event | Bad Weather | Include | Include | Weather | 1040 | 2021-10-21 | 15600 | keep | 0 | Oct | 2021 | 0.010625 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-10-21 18:24 | 2021-10-22 11:01 | 11 | 016:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100226 | New_Event | Bad Weather | Include | Include | Weather | 997 | 2021-10-21 | 10967 | keep | 0 | Oct | 2021 | 0.0074696 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-10-21 18:26 | 2021-10-22 10:22 | 12 | 015:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21102100229 | New_Event |  |  | Include | Wildlife | 956 | 2021-10-21 | 11472 | keep | 0 | Oct | 2021 | 0.0078135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-21 18:28 | 2021-10-21 18:33 | 2402 | 000:05 | T | ERROR HUMANO | DISPARO HACIENDO OPERACIONES DE VIA LIBRE D2021-00377 ENERGIZAR TRAMOS SOTERRADOS EN URB. RIVIERA VILLAGE | S21102100058 | New_Event | Human Error | Include | Include | Other | 5 | 2021-10-21 | 12010 | keep | 0 | Oct | 2021 | 0.00818 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
ARECIBO | 2021-10-21 18:32 | 2021-10-21 20:05 | 100 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102100075 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2021-10-21 | 9300 | keep | 0 | Oct | 2021 | 0.0063342 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-21 18:34 | 2021-10-22 09:52 | 8 | 015:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21102100230 | New_Event | Bad Weather | Include | Include | Weather | 918 | 2021-10-21 | 7344 | keep | 0 | Oct | 2021 | 0.005002 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-10-21 18:49 | 2021-10-22 12:08 | 1 | 017:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1039 | 2021-10-21 | 1039 | keep | 0 | Oct | 2021 | 0.00070766 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-21 18:55 | 2021-10-22 10:45 | 258 | 015:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 65 EN CORTES DE LINEA SE REEMPLAZO DISCO ROTO | C21102100231 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 950 | 2021-10-21 | 245100 | keep | 0 | Oct | 2021 | 0.16694 | 0.00017572 | Sustained | FALSE | TRUE | Not_TMED_Event | 258
BAYAMON | 2021-10-21 19:07 | 2021-10-21 21:06 | 60 | 001:59 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA 1 X 10 EN XMR | B21102100118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-10-21 | 7140 | keep | 0 | Oct | 2021 | 0.004863 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-21 19:13 | 2021-10-21 20:30 | 1 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21102100148 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-10-21 | 77 | keep | 0 | Oct | 2021 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-21 19:30 | 2021-10-21 20:30 | 5 | 001:00 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21102100148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-10-21 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-10-21 19:30 | 2021-10-21 21:06 | 20 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | M21102100151 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2021-10-21 | 1920 | keep | 0 | Oct | 2021 | 0.0013077 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-21 20:14 | 2021-10-21 21:52 | 50 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21102100124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2021-10-21 | 4900 | keep | 0 | Oct | 2021 | 0.0033374 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-21 20:58 | 2021-10-21 23:28 | 20 | 002:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA DEFECTUOSA | M21102200352 | New_Event | Cutout Failure | Include | Include | Equipment | 150 | 2021-10-21 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-21 20:59 | 2021-10-21 21:01 | 2900 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21102100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-21 | 5800 | keep | 0 | Oct | 2021 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
HUMACAO | 2021-10-21 21:07 | 2021-10-22 16:05 | 8 | 018:58 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO BUSHING SECUNDARIO | C21102100239 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1138 | 2021-10-21 | 9104 | keep | 0 | Oct | 2021 | 0.0062007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-10-21 21:12 | 2021-10-22 13:08 | 28 | 015:56 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C21102100240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2021-10-21 | 26768 | keep | 0 | Oct | 2021 | 0.018232 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
PONCE | 2021-10-21 21:17 | 2021-10-22 09:08 | 83 | 011:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21102100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 711 | 2021-10-21 | 59013 | keep | 0 | Oct | 2021 | 0.040193 | 5.6531e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 83
CAGUAS | 2021-10-21 22:52 | 2021-10-21 22:53 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21102100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-21 | 2900 | keep | 0 | Oct | 2021 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
SAN JUAN | 2021-10-21 23:06 | 2021-10-22 09:26 | 62 | 010:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21102100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 620 | 2021-10-21 | 38440 | keep | 0 | Oct | 2021 | 0.026181 | 4.2228e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 62
CAGUAS | 2021-10-21 23:07 | 2021-10-22 17:01 | 1 | 017:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21102100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1074 | 2021-10-21 | 1074 | keep | 0 | Oct | 2021 | 0.0007315 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 2231 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 13386 | keep | 0 | Oct | 2021 | 0.0091171 | 0.0015195 | Sustained | FALSE | TRUE | Not_TMED_Event | 2231
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 1923 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 11538 | keep | 0 | Oct | 2021 | 0.0078585 | 0.0013097 | Sustained | FALSE | TRUE | Not_TMED_Event | 1923
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 1066 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 6396 | keep | 0 | Oct | 2021 | 0.0043563 | 0.00072605 | Sustained | FALSE | TRUE | Not_TMED_Event | 1066
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 141 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 846 | keep | 0 | Oct | 2021 | 0.00057621 | 9.6034e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 141
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 2107 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 12642 | keep | 0 | Oct | 2021 | 0.0086104 | 0.0014351 | Sustained | FALSE | TRUE | Not_TMED_Event | 2107
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 308 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 1848 | keep | 0 | Oct | 2021 | 0.0012587 | 0.00020978 | Sustained | FALSE | TRUE | Not_TMED_Event | 308
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 2697 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 16182 | keep | 0 | Oct | 2021 | 0.011021 | 0.0018369 | Sustained | FALSE | TRUE | Not_TMED_Event | 2697
ARECIBO | 2021-10-21 23:47 | 2021-10-21 23:53 | 67 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A21102100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-21 | 402 | keep | 0 | Oct | 2021 | 0.0002738 | 4.5633e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 67
HUMACAO | 2021-10-22 00:14 | 2021-10-22 13:19 | 15 | 013:05 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA SE RETIRO PENCA | C21102200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 785 | 2021-10-22 | 11775 | keep | 0 | Oct | 2021 | 0.0080199 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-22 00:33 | 2021-10-22 10:16 | 4 | 009:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR ROEDOR CRUZO LINEAS | A21102200002 | New_Event |  |  | Include | Wildlife | 583 | 2021-10-22 | 2332 | keep | 0 | Oct | 2021 | 0.0015883 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-10-22 00:49 | 2021-10-22 16:35 | 50 | 015:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21102200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 946 | 2021-10-22 | 47300 | keep | 0 | Oct | 2021 | 0.032216 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-22 01:09 | 2021-10-22 10:20 | 6 | 009:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102200001 | New_Event | Bad Weather | Include | Include | Weather | 551 | 2021-10-22 | 3306 | keep | 0 | Oct | 2021 | 0.0022517 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-22 02:03 | 2021-10-22 05:41 | 2113 | 003:38 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR. SE ABRE RISER DE ENTRADA AL SOTERRADO EN EL TRONCAL PARA SECCIONALIZAR ALIMENTADOR | P21102200001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 218 | 2021-10-22 | 460634 | keep | 0 | Oct | 2021 | 0.31374 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
CAGUAS | 2021-10-22 02:15 | 2021-10-22 10:10 | 18 | 007:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21102200006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 475 | 2021-10-22 | 8550 | keep | 0 | Oct | 2021 | 0.0058234 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2021-10-22 02:52 | 2021-10-22 02:53 | 3699 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO | R21102200003 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-22 | 3699 | keep | 0 | Oct | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2021-10-22 02:53 | 2021-10-22 21:26 | 50 | 018:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA QUEMADA | R21102200054 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1113 | 2021-10-22 | 55650 | keep | 0 | Oct | 2021 | 0.037903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-22 03:33 | 2021-10-22 03:34 | 4028 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO Y SE CERRO POR SCADA | B21102200000 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-22 | 4028 | keep | 0 | Oct | 2021 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2021-10-22 03:34 | 2021-10-22 19:26 | 60 | 015:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO CAUSADO POR POSTE IMPACTADO POR VEHICULO | B21102200104 | 1st_after_momentary |  |  | Include | Wildlife | 952 | 2021-10-22 | 57120 | keep | 0 | Oct | 2021 | 0.038904 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-22 04:38 | 2021-10-22 12:13 | 60 | 007:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | B21102200007 | New_Event | Cutout Failure | Include | Include | Equipment | 455 | 2021-10-22 | 27300 | keep | 0 | Oct | 2021 | 0.018594 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-22 05:10 | 2021-10-22 14:23 | 23 | 009:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21102200007 | New_Event | Bad Weather | Include | Include | Weather | 553 | 2021-10-22 | 12719 | keep | 0 | Oct | 2021 | 0.0086629 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
FAJARDO | 2021-10-22 05:33 | 2021-10-22 05:34 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21102200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 1830 | keep | 0 | Oct | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
PONCE | 2021-10-22 05:41 | 2021-10-22 06:17 | 1900 | 000:36 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRE INTERRUPTOR PARA CERRAR RISER DE ENTRADA AL SOTERRADO EN TRONCAL DEL ALIMENTADOR | P21102200010 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 36 | 2021-10-22 | 68400 | keep | 0 | Oct | 2021 | 0.046587 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-10-22 05:46 | 2021-10-22 10:29 | 70 | 004:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21102200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-10-22 | 19810 | keep | 0 | Oct | 2021 | 0.013493 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-10-22 06:17 | 2021-10-22 06:23 | 2113 | 000:06 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL PROBAR SOTERRADO | P21102200012 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 6 | 2021-10-22 | 12678 | keep | 0 | Oct | 2021 | 0.0086349 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-22 06:23 | 2021-10-22 13:32 | 1900 | 007:09 | P | CABLE SOTERRADO AVERIADO | CABLE SOTERRADO AVERIADO SE ABRE RISER PARA SECCIONALIZAR AVERIA | P21102200022 | New_Event | UG Cable Fault | Include | Include | Equipment | 429 | 2021-10-22 | 815100 | keep | 0 | Oct | 2021 | 0.55516 | 0.0012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 1900
UTUADO | 2021-10-22 06:33 | 2021-10-22 15:30 | 30 | 008:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21102200005 | New_Event | Bad Weather | Include | Include | Weather | 537 | 2021-10-22 | 16110 | keep | 0 | Oct | 2021 | 0.010972 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-10-22 06:46 | 2021-10-22 11:45 | 70 | 004:59 | P | PARARRAYOS DEFECTUOSO | 2 X 100, 1 X 50 Y 1 X 40 EN CORTES DE LINEA Y 3 X 8 EN BANCO DE TRANSFORMADOR SE REEMPLAZARON PARARRAYOS | R21102200019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 299 | 2021-10-22 | 20930 | keep | 0 | Oct | 2021 | 0.014255 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-10-22 07:00 | 2021-10-22 07:01 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 1310 | keep | 0 | Oct | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-10-22 07:20 | 2021-10-22 17:35 | 1 | 010:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21102200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 615 | 2021-10-22 | 615 | keep | 0 | Oct | 2021 | 0.00041887 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-10-22 07:31 | 2021-10-22 07:34 | 200 | 000:03 | P | LINEA DE TRANSMISION 38KV | SE ABRIO MACHETES PARA TRABAJOS EN LINEA 5600 AUTORIZADO POR EL ING LUIS FENEQUE | M21102200232 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-22 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00013622 | Momentary | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 693 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 5544 | keep | 0 | Oct | 2021 | 0.003776 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 47 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 376 | keep | 0 | Oct | 2021 | 0.00025609 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 1256 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 10048 | keep | 0 | Oct | 2021 | 0.0068436 | 0.00085546 | Sustained | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 558 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 4464 | keep | 0 | Oct | 2021 | 0.0030404 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:57 | 1192 | 001:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 83 | 2021-10-22 | 98936 | keep | 0 | Oct | 2021 | 0.067385 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:57 | 3041 | 001:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 83 | 2021-10-22 | 252403 | keep | 0 | Oct | 2021 | 0.17191 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:57 | 390 | 001:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 83 | 2021-10-22 | 32370 | keep | 0 | Oct | 2021 | 0.022047 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:57 | 650 | 001:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 83 | 2021-10-22 | 53950 | keep | 0 | Oct | 2021 | 0.036745 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 569 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 4552 | keep | 0 | Oct | 2021 | 0.0031003 | 0.00038754 | Sustained | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 1245 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 9960 | keep | 0 | Oct | 2021 | 0.0067837 | 0.00084796 | Sustained | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 1155 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 9240 | keep | 0 | Oct | 2021 | 0.0062933 | 0.00078667 | Sustained | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 867 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 6936 | keep | 0 | Oct | 2021 | 0.0047241 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 257 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 2056 | keep | 0 | Oct | 2021 | 0.0014003 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 1336 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 10688 | keep | 0 | Oct | 2021 | 0.0072795 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 3315 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 26520 | keep | 0 | Oct | 2021 | 0.018063 | 0.0022578 | Sustained | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 07:42 | 1718 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2021-10-22 | 13744 | keep | 0 | Oct | 2021 | 0.009361 | 0.0011701 | Sustained | FALSE | FALSE | Not_TMED_Event | 1718
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:55 | 154 | 001:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 81 | 2021-10-22 | 12474 | keep | 0 | Oct | 2021 | 0.008496 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:55 | 1261 | 001:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 81 | 2021-10-22 | 102141 | keep | 0 | Oct | 2021 | 0.069568 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:55 | 3894 | 001:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 81 | 2021-10-22 | 315414 | keep | 0 | Oct | 2021 | 0.21483 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:55 | 997 | 001:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 81 | 2021-10-22 | 80757 | keep | 0 | Oct | 2021 | 0.055003 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2021-10-22 07:34 | 2021-10-22 08:55 | 1497 | 001:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DEL 38KV VICTORIA TC | M21102200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 81 | 2021-10-22 | 121257 | keep | 0 | Oct | 2021 | 0.082588 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
AGUADILLA | 2021-10-22 07:50 | 2021-10-22 08:10 | 40 | 000:20 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-10-22 | 800 | keep | 0 | Oct | 2021 | 0.00054488 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-10-22 07:54 | 2021-10-22 17:55 | 400 | 010:01 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21102200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 601 | 2021-10-22 | 240400 | keep | 0 | Oct | 2021 | 0.16374 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
SAN JUAN | 2021-10-22 08:02 | 2021-10-22 10:37 | 51 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A MACHETE | S21102200012 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2021-10-22 | 7905 | keep | 0 | Oct | 2021 | 0.0053841 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-10-22 08:04 | 2021-10-22 14:30 | 5 | 006:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102200068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2021-10-22 | 1930 | keep | 0 | Oct | 2021 | 0.0013145 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 574 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 95858 | keep | 0 | Oct | 2021 | 0.065288 | 0.00039095 | Sustained | FALSE | TRUE | Not_TMED_Event | 574
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 2493 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 416331 | keep | 0 | Oct | 2021 | 0.28356 | 0.001698 | Sustained | FALSE | TRUE | Not_TMED_Event | 2493
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 1415 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 236305 | keep | 0 | Oct | 2021 | 0.16095 | 0.00096375 | Sustained | FALSE | TRUE | Not_TMED_Event | 1415
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 1428 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 238476 | keep | 0 | Oct | 2021 | 0.16242 | 0.0009726 | Sustained | FALSE | TRUE | Not_TMED_Event | 1428
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 1036 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 173012 | keep | 0 | Oct | 2021 | 0.11784 | 0.00070561 | Sustained | FALSE | TRUE | Not_TMED_Event | 1036
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 382 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 63794 | keep | 0 | Oct | 2021 | 0.04345 | 0.00026018 | Sustained | FALSE | TRUE | Not_TMED_Event | 382
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 10:57 | 39 | 002:47 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES SOLICITO ABRIR LA LINEA 5600 POR POSIBLE PUENTE ABIERTO | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2021-10-22 | 6513 | keep | 0 | Oct | 2021 | 0.004436 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 14:55 | 2366 | 006:45 | S | PARARRAYOS DEFECTUOSO | SE ABRIO LINEA 5600 POR POSIBLE PUENTE ABIERTO Y SE ENCONTRÃ“ PARARRAYOS AVERIADO Y FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR 7303 | M21102200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 405 | 2021-10-22 | 958230 | keep | 0 | Oct | 2021 | 0.65265 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-10-22 08:10 | 2021-10-22 15:00 | 1337 | 006:50 | S | PARARRAYOS DEFECTUOSO | SE ABRIO LINEA 5600 POR POSIBLE PUENTE ABIERTO Y SE ENCONTRÃ“ PARARRAYOS AVERIADO Y FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR 7303 | M21102200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 410 | 2021-10-22 | 548170 | keep | 0 | Oct | 2021 | 0.37336 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
AGUADILLA | 2021-10-22 08:10 | 2021-10-22 14:55 | 709 | 006:45 | S | PARARRAYOS DEFECTUOSO | SE ABRIO LINEA 5600 POR POSIBLE PUENTE ABIERTO Y SE ENCONTRÃ“ PARARRAYOS AVERIADO Y FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR 7303 | M21102200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 405 | 2021-10-22 | 287145 | keep | 0 | Oct | 2021 | 0.19557 | 0.0004829 | Sustained | FALSE | TRUE | Not_TMED_Event | 709
CAGUAS | 2021-10-22 08:16 | 2021-10-22 08:17 | 2302 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | C21102100195 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-22 | 2302 | keep | 0 | Oct | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-10-22 08:17 | 2021-10-22 14:35 | 4 | 006:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA | C21102200047 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 378 | 2021-10-22 | 1512 | keep | 0 | Oct | 2021 | 0.0010298 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-10-22 08:28 | 2021-10-22 11:02 | 18 | 002:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | R21102200024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 154 | 2021-10-22 | 2772 | keep | 0 | Oct | 2021 | 0.001888 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
UTUADO | 2021-10-22 08:46 | 2021-10-22 16:20 | 1 | 007:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 5 KVA POR IGUAL CAPACIDAD | A21102200009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 454 | 2021-10-22 | 454 | keep | 0 | Oct | 2021 | 0.00030922 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-22 08:47 | 2021-10-22 08:48 | 3431 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DEL INTERRUPTOR | A21102200010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-10-22 | 3431 | keep | 0 | Oct | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-10-22 08:48 | 2021-10-22 11:42 | 1 | 002:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA | A21102200016 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 174 | 2021-10-22 | 174 | keep | 0 | Oct | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-22 08:52 | 2021-10-22 18:01 | 6 | 009:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21102200037 | New_Event | Bad Weather | Include | Include | Weather | 549 | 2021-10-22 | 3294 | keep | 0 | Oct | 2021 | 0.0022435 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-10-22 08:52 | 2021-10-22 12:39 | 125 | 003:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA | C21102200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-10-22 | 28375 | keep | 0 | Oct | 2021 | 0.019326 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
AGUADILLA | 2021-10-22 08:52 | 2021-10-22 10:03 | 30 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21102200126 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-10-22 | 2130 | keep | 0 | Oct | 2021 | 0.0014507 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-22 08:55 | 2021-10-22 15:06 | 200 | 006:11 | P | LINEA DE TRANSMISION 38KV | SE ABRIO MACHETES PARA TRABAJOS EN LINEA 5600 AUTORIZADO POR EL ING LUIS FENEQUE | M21102200232 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 371 | 2021-10-22 | 74200 | keep | 0 | Oct | 2021 | 0.050537 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-22 09:10 | 2021-10-22 12:31 | 100 | 003:21 | P | DESCONECTIVO DEFECTUOSO | SE REPARO MACHETE QUEMADO EN SU-4 | B21102200037 | New_Event | Switch Failure | Include | Include | Equipment | 201 | 2021-10-22 | 20100 | keep | 0 | Oct | 2021 | 0.01369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-22 09:34 | 2021-10-22 10:34 | 20 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR TIERRAS EN TRANSFORMADOR | M21102200149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-10-22 | 1200 | keep | 0 | Oct | 2021 | 0.00081731 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-22 09:39 | 2021-10-22 09:40 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21102200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 3941 | keep | 0 | Oct | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
ARECIBO | 2021-10-22 10:00 | 2021-10-22 12:04 | 100 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102200021 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2021-10-22 | 12400 | keep | 0 | Oct | 2021 | 0.0084456 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-22 10:02 | 2021-10-22 12:27 | 15 | 002:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21102000023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 145 | 2021-10-22 | 2175 | keep | 0 | Oct | 2021 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-22 10:07 | 2021-10-22 10:08 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 974 | keep | 0 | Oct | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
BAYAMON | 2021-10-22 10:08 | 2021-10-22 11:17 | 15 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21102000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-10-22 | 1035 | keep | 0 | Oct | 2021 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-10-22 10:10 | 2021-10-22 10:11 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBA AL SOTERRADO CARGA POR EL 5011-05 SE SECIONALIZA AVERIA | P21102200043 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-22 | 778 | keep | 0 | Oct | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-10-22 10:10 | 2021-10-22 10:11 | 11 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBA AL SOTERRADO CARGA POR EL 5011-05 | P21102200043 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-22 | 11 | keep | 0 | Oct | 2021 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-10-22 10:10 | 2021-10-22 10:11 | 113 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBA AL SOTERRADO LLEVA LA CARGA DEL 5004-08 Y 5004-10 SE SECIONALIZA AVERIA | P21102200043 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-10-22 | 113 | keep | 0 | Oct | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
CAGUAS | 2021-10-22 10:35 | 2021-10-22 16:42 | 50 | 006:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C21102200051 | New_Event | Bad Weather | Include | Include | Weather | 367 | 2021-10-22 | 18350 | keep | 0 | Oct | 2021 | 0.012498 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-22 10:41 | 2021-10-22 10:42 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1706-02 LLEVANDO LA CARGA DEL 1706-03 | B21102200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 1382 | keep | 0 | Oct | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-10-22 10:41 | 2021-10-22 10:42 | 663 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1706-02 LLEVANDO LA CARGA DEL 1706-03 | B21102200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 663 | keep | 0 | Oct | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
ARECIBO | 2021-10-22 10:44 | 2021-10-22 12:29 | 75 | 001:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR QUEMADO | A21102200030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2021-10-22 | 7875 | keep | 0 | Oct | 2021 | 0.0053636 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-10-22 10:46 | 2021-10-22 19:27 | 23 | 008:41 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21102200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2021-10-22 | 11983 | keep | 0 | Oct | 2021 | 0.0081616 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
CAGUAS | 2021-10-22 10:46 | 2021-10-22 15:15 | 1 | 004:29 | P | OTRAS CAUSAS | 1 X 8 EN GABINETE PRIVADO PROBLEMA DEL CLIENTE | C21102200052 | New_Event | Other Causes | Include | Include | Other | 269 | 2021-10-22 | 269 | keep | 0 | Oct | 2021 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-22 10:46 | 2021-10-22 10:47 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 974 | keep | 0 | Oct | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
CAGUAS | 2021-10-22 10:48 | 2021-10-22 11:29 | 4 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES EN BAJANTE SECUNDARIO | C21102100189 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-10-22 | 164 | keep | 0 | Oct | 2021 | 0.0001117 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-22 10:50 | 2021-10-22 10:51 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21102200186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-10-22 10:56 | 2021-10-22 17:37 | 15 | 006:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR IGUAL CAPACIDAD | S21102000095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 401 | 2021-10-22 | 6015 | keep | 0 | Oct | 2021 | 0.0040968 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-22 10:56 | 2021-10-22 17:26 | 25 | 006:30 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU-2 Y SE REPORTA AVERIA SOTERRADA DEL SU-2 AL T-10. SE CERRO N\O DEL T-13 AL T-12 | S21102100138 | New_Event | UG Cable Fault | Include | Include | Equipment | 390 | 2021-10-22 | 9750 | keep | 0 | Oct | 2021 | 0.0066407 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-10-22 10:57 | 2021-10-22 21:03 | 40 | 010:06 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 606 | 2021-10-22 | 24240 | keep | 0 | Oct | 2021 | 0.01651 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-22 11:01 | 2021-10-22 14:44 | 80 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21102200033 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-10-22 | 17840 | keep | 0 | Oct | 2021 | 0.012151 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:16 | 1935 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 3870 | keep | 0 | Oct | 2021 | 0.0026358 | 0.0013179 | Momentary | FALSE | TRUE | Not_TMED_Event | 1935
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:16 | 3 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 6 | keep | 0 | Oct | 2021 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:16 | 61 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 122 | keep | 0 | Oct | 2021 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 61
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:16 | 1501 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 3002 | keep | 0 | Oct | 2021 | 0.0020446 | 0.0010223 | Momentary | FALSE | TRUE | Not_TMED_Event | 1501
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:16 | 546 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 1092 | keep | 0 | Oct | 2021 | 0.00074376 | 0.00037188 | Momentary | FALSE | TRUE | Not_TMED_Event | 546
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:17 | 959 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-22 | 2877 | keep | 0 | Oct | 2021 | 0.0019595 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:17 | 1297 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-22 | 3891 | keep | 0 | Oct | 2021 | 0.0026501 | 0.00088338 | Momentary | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:17 | 451 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-22 | 1353 | keep | 0 | Oct | 2021 | 0.00092152 | 0.00030717 | Momentary | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:17 | 1264 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-22 | 3792 | keep | 0 | Oct | 2021 | 0.0025827 | 0.0008609 | Momentary | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-10-22 11:14 | 2021-10-22 11:17 | 620 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-22 | 1860 | keep | 0 | Oct | 2021 | 0.0012668 | 0.00042228 | Momentary | FALSE | TRUE | Not_TMED_Event | 620
HUMACAO | 2021-10-22 11:14 | 2021-10-22 16:46 | 34 | 005:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA SE PATRULLO | C21102200054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 332 | 2021-10-22 | 11288 | keep | 0 | Oct | 2021 | 0.0076882 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 959 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 22057 | keep | 0 | Oct | 2021 | 0.015023 | 0.00065317 | Sustained | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 1382 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 LLEVANDO LA CARGA DEL 1706-03 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 31786 | keep | 0 | Oct | 2021 | 0.021649 | 0.00094127 | Sustained | FALSE | TRUE | Not_TMED_Event | 1382
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 663 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 CARGA POR EL 1706-02 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 15249 | keep | 0 | Oct | 2021 | 0.010386 | 0.00045157 | Sustained | FALSE | TRUE | Not_TMED_Event | 663
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 1514 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 34822 | keep | 0 | Oct | 2021 | 0.023717 | 0.0010312 | Sustained | FALSE | TRUE | Not_TMED_Event | 1514
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 1105 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 25415 | keep | 0 | Oct | 2021 | 0.01731 | 0.00075261 | Sustained | FALSE | TRUE | Not_TMED_Event | 1105
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 4176 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 96048 | keep | 0 | Oct | 2021 | 0.065418 | 0.0028443 | Sustained | FALSE | TRUE | Not_TMED_Event | 4176
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 252 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 5796 | keep | 0 | Oct | 2021 | 0.0039476 | 0.00017164 | Sustained | FALSE | TRUE | Not_TMED_Event | 252
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 2147 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 49381 | keep | 0 | Oct | 2021 | 0.033633 | 0.0014623 | Sustained | FALSE | TRUE | Not_TMED_Event | 2147
BAYAMON | 2021-10-22 11:17 | 2021-10-22 11:40 | 2858 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-10-22 | 65734 | keep | 0 | Oct | 2021 | 0.044771 | 0.0019466 | Sustained | FALSE | TRUE | Not_TMED_Event | 2858
MAYAGÃœEZ | 2021-10-22 11:19 | 2021-10-22 13:05 | 400 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO Y SE REMPLAZO AISLADOR ROTO | M21102100138 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-10-22 | 42400 | keep | 0 | Oct | 2021 | 0.028878 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
UTUADO | 2021-10-22 11:24 | 2021-10-22 13:26 | 100 | 002:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-10-22 | 12200 | keep | 0 | Oct | 2021 | 0.0083094 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-22 11:35 | 2021-10-22 14:35 | 50 | 003:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON DOS CAJA QUEMADAS Y SE REEMPLAZO 2 FUSIBLES DE 50AMP | S21102100083 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2021-10-22 | 9000 | keep | 0 | Oct | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-22 11:40 | 2021-10-22 13:04 | 8 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C21102100173 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-10-22 | 672 | keep | 0 | Oct | 2021 | 0.0004577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-22 11:40 | 2021-10-22 11:55 | 1 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21102200200 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-10-22 | 15 | keep | 0 | Oct | 2021 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-22 11:40 | 2021-10-22 13:38 | 15 | 001:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21102000018 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 118 | 2021-10-22 | 1770 | keep | 0 | Oct | 2021 | 0.0012055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-22 11:45 | 2021-10-22 17:08 | 8 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE CERRO PUENTE ABIERTO | S21102200044 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2021-10-22 | 2584 | keep | 0 | Oct | 2021 | 0.00176 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-10-22 11:47 | 2021-10-23 18:06 | 30 | 030:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102200059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1819 | 2021-10-22 | 54570 | keep | 0 | Oct | 2021 | 0.037167 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-22 11:51 | 2021-10-22 17:57 | 55 | 006:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21102200043 | New_Event | Wire Down | Include | Include | Equipment | 366 | 2021-10-22 | 20130 | keep | 0 | Oct | 2021 | 0.01371 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
ARECIBO | 2021-10-22 11:53 | 2021-10-22 14:15 | 80 | 002:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21102200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-10-22 | 11360 | keep | 0 | Oct | 2021 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-22 12:05 | 2021-10-22 14:35 | 50 | 002:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102200212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-10-22 | 7500 | keep | 0 | Oct | 2021 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-22 12:12 | 2021-10-22 22:30 | 1 | 010:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN BANCO DE TRANSFORMADORES SE REEMPLAZO CAJA AVERIADA Y SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S21102200048 | New_Event | Cutout Failure | Include | Include | Equipment | 618 | 2021-10-22 | 618 | keep | 0 | Oct | 2021 | 0.00042092 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-22 12:23 | 2021-10-23 10:41 | 30 | 022:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZARON 2 AISLADORES | B21102200083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1338 | 2021-10-22 | 40140 | keep | 0 | Oct | 2021 | 0.027339 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-22 12:33 | 2021-10-24 15:40 | 20 | 051:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR UNO DE 75KVA | B21102200084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3067 | 2021-10-22 | 61340 | keep | 0 | Oct | 2021 | 0.041778 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-22 12:49 | 2021-10-22 22:20 | 45 | 009:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN AEREO PROVISIONAL SE REEMPALZO CAJA QUEMADA | B21102200092 | New_Event | Cutout Failure | Include | Include | Equipment | 571 | 2021-10-22 | 25695 | keep | 0 | Oct | 2021 | 0.017501 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-10-22 13:02 | 2021-10-22 17:52 | 218 | 004:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1113-04 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1110-03 Y 1110-01 SE ABRIO MACHETE DE AMARRE Y SE REPARO PUENTE SAFADO DE LINEA TRONCAL ADEMAS SE REALIZO DESGANCHE Y SE REEPLAZO DOS JUEGOS DE MACHETES | S21102200053 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2021-10-22 | 63220 | keep | 0 | Oct | 2021 | 0.043059 | 0.00014848 | Sustained | FALSE | TRUE | Not_TMED_Event | 218
SAN JUAN | 2021-10-22 13:02 | 2021-10-22 17:52 | 1526 | 004:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1113-04 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1110-03 Y 1110-01 SE ABRIO MACHETE DE AMARRE Y SE REPARO PUENTE SAFADO DE LINEA TRONCAL ADEMAS SE REALIZO DESGANCHE Y SE REEPLAZO DOS JUEGOS DE MACHETES | S21102200053 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2021-10-22 | 442540 | keep | 0 | Oct | 2021 | 0.30141 | 0.0010394 | Sustained | FALSE | TRUE | Not_TMED_Event | 1526
SAN JUAN | 2021-10-22 13:02 | 2021-10-22 14:01 | 553 | 000:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1113-04 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1110-3 Y 1. SE ABRIO AMARRE ENTRE 1110-3 Y SE CERRO POR SCADA. | S21102200053 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2021-10-22 | 32627 | keep | 0 | Oct | 2021 | 0.022222 | 0.00037665 | Sustained | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2021-10-22 13:27 | 2021-10-23 13:14 | 40 | 023:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21102200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1427 | 2021-10-22 | 57080 | keep | 0 | Oct | 2021 | 0.038877 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-22 13:32 | 2021-10-22 16:18 | 2113 | 002:46 | T | CABLE SOTERRADO AVERIADO | SE ABRE INTERRUPTOR PARA REALIZAR PRUEBAS AL SOTERRADO | P21102200059 | New_Event | UG Cable Fault | Include | Include | Equipment | 166 | 2021-10-22 | 350758 | keep | 0 | Oct | 2021 | 0.2389 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2021-10-22 13:33 | 2021-10-22 17:01 | 40 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21102200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-10-22 | 8320 | keep | 0 | Oct | 2021 | 0.0056667 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-10-22 13:39 | 2021-10-23 10:33 | 70 | 020:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21102200061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1254 | 2021-10-22 | 87780 | keep | 0 | Oct | 2021 | 0.059787 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-10-22 13:42 | 2021-10-22 15:55 | 50 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN SU LLUVIAS | C21102200000 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-10-22 | 6650 | keep | 0 | Oct | 2021 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-22 13:42 | 2021-10-22 17:35 | 100 | 003:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21102200068 | New_Event | Cutout Failure | Include | Include | Equipment | 233 | 2021-10-22 | 23300 | keep | 0 | Oct | 2021 | 0.01587 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-22 13:46 | 2021-10-22 19:57 | 25 | 006:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REPORTA DESGANCHE MASIVO | S21102200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2021-10-22 | 9275 | keep | 0 | Oct | 2021 | 0.0063172 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-22 14:11 | 2021-10-22 16:44 | 1 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA ZAFADA EN TRANSFORMADOR | A21102200055 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2021-10-22 | 153 | keep | 0 | Oct | 2021 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-22 14:19 | 2021-10-22 16:50 | 6 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21102200056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2021-10-22 | 906 | keep | 0 | Oct | 2021 | 0.00061707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-22 14:22 | 2021-10-23 19:27 | 36 | 029:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN C/L FUE OCASIONADO POR PERSONAS DESGANCHANDO | B21102200104 | New_Event |  |  | Include | Wildlife | 1745 | 2021-10-22 | 62820 | keep | 0 | Oct | 2021 | 0.042786 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2021-10-22 14:23 | 2021-10-22 14:24 | 2132 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | A21102200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-22 | 2132 | keep | 0 | Oct | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-10-22 14:24 | 2021-10-22 16:20 | 350 | 001:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21102200059 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-10-22 | 40600 | keep | 0 | Oct | 2021 | 0.027652 | 0.00023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 350
FAJARDO | 2021-10-22 14:34 | 2021-10-22 15:31 | 20 | 000:57 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DERRAME DE ACEITE DE 75 X 75KVA | R21102200042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 57 | 2021-10-22 | 1140 | keep | 0 | Oct | 2021 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-22 14:35 | 2021-10-22 15:28 | 390 | 000:53 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REALIZAR REEMPLAZO DE 2 CAJAS QUEMADAS EN AZOTEA DE LA CALLE FORTALEZA | S21102100077 | Additional_clients | Cutout Failure | Include | Include | Equipment | 53 | 2021-10-22 | 20670 | keep | 0 | Oct | 2021 | 0.014078 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-22 14:44 | 2021-10-22 15:21 | 6 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO EN PM Y SE REPARO EN PEDESTAL | B21102200118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-10-22 | 222 | keep | 0 | Oct | 2021 | 0.0001512 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-22 14:48 | 2021-10-22 16:31 | 50 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21102200119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-10-22 | 5150 | keep | 0 | Oct | 2021 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-22 14:48 | 2021-10-23 13:29 | 4 | 022:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR TOMA | C21102200076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1361 | 2021-10-22 | 5444 | keep | 0 | Oct | 2021 | 0.0037079 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-10-22 15:02 | 2021-10-22 15:03 | 2234 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21102200124 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-22 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-10-22 15:03 | 2021-10-22 16:41 | 20 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN RISER 2 X 20 EN TRANSFORMADOR SE RETEZO CONDUCTORES ENREDADOS | B21102200125 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2021-10-22 | 1960 | keep | 0 | Oct | 2021 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-22 15:03 | 2021-10-22 15:11 | 30 | 000:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21102200175 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 8 | 2021-10-22 | 240 | keep | 0 | Oct | 2021 | 0.00016346 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-22 15:11 | 2021-10-22 15:12 | 2234 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21102200128 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-22 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-22 15:12 | 2021-10-22 15:13 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 QUE A SU VEZ LLEVA LA CARGA DEL 1206-02 | S21102200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-22 15:12 | 2021-10-22 15:13 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-01 QUE A SU VEZ LLEVA LA CARGA DEL 1206-02 | S21102200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2021-10-22 15:12 | 2021-10-23 10:07 | 30 | 018:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21102200175 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1135 | 2021-10-22 | 34050 | keep | 0 | Oct | 2021 | 0.023191 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-22 15:53 | 2021-10-22 20:12 | 15 | 004:19 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B21102200137 | New_Event | Defective Pole | Include | Include | Equipment | 259 | 2021-10-22 | 3885 | keep | 0 | Oct | 2021 | 0.0026461 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-22 15:55 | 2021-10-22 18:56 | 65 | 003:01 | P | TRANSFORMADOR AVERIADO | 1 X 80 EN SU-1 AVERIA DE T-12@ T-13, T-13 FUERA | B21102200139 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2021-10-22 | 11765 | keep | 0 | Oct | 2021 | 0.0080131 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2021-10-22 16:15 | 2021-10-23 09:49 | 40 | 017:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21102200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1054 | 2021-10-22 | 42160 | keep | 0 | Oct | 2021 | 0.028715 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-22 16:15 | 2021-10-22 18:25 | 8 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21102200040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-10-22 | 1040 | keep | 0 | Oct | 2021 | 0.00070834 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-10-22 16:18 | 2021-10-23 15:42 | 1900 | 023:24 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CABLE SOTERRADO DESDE EL MH-10 AL MH-1 Y SE CORRIGIERON EMPALMES EN MH-13 AL MH-12 SE TRANSFIRIO 90 PORCIENTO DE LA CARGA AL 5011-05 | P21102200082 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1404 | 2021-10-22 | 2667600 | keep | 0 | Oct | 2021 | 1.8169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-22 16:20 | 2021-10-22 16:33 | 3 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21102200019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-10-22 | 39 | keep | 0 | Oct | 2021 | 2.6563e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
FAJARDO | 2021-10-22 16:24 | 2021-10-22 16:58 | 10 | 000:34 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR | R21102200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2021-10-22 | 340 | keep | 0 | Oct | 2021 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-22 16:35 | 2021-10-23 19:19 | 15 | 026:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21102200081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1604 | 2021-10-22 | 24060 | keep | 0 | Oct | 2021 | 0.016387 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-10-22 16:51 | 2021-10-22 17:55 | 88 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | P21102200083 | New_Event |  |  | Include | Wildlife | 64 | 2021-10-22 | 5632 | keep | 0 | Oct | 2021 | 0.0038359 | 5.9936e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 88
CAGUAS | 2021-10-22 16:53 | 2021-10-23 09:42 | 1 | 016:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21102200089 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1009 | 2021-10-22 | 1009 | keep | 0 | Oct | 2021 | 0.00068723 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 1138 | keep | 0 | Oct | 2021 | 0.00077509 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 1245 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 2490 | keep | 0 | Oct | 2021 | 0.0016959 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 1155 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 2310 | keep | 0 | Oct | 2021 | 0.0015733 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 867 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 1734 | keep | 0 | Oct | 2021 | 0.001181 | 0.00059051 | Momentary | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 257 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 514 | keep | 0 | Oct | 2021 | 0.00035008 | 0.00017504 | Momentary | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 1336 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 2672 | keep | 0 | Oct | 2021 | 0.0018199 | 0.00090994 | Momentary | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 3315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 6630 | keep | 0 | Oct | 2021 | 0.0045157 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-10-22 17:01 | 2021-10-22 17:03 | 1718 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 3436 | keep | 0 | Oct | 2021 | 0.0023402 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
BARRANQUITAS | 2021-10-22 17:24 | 2021-10-23 10:55 | 40 | 017:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y CERRO PUENTE | C21102200092 | New_Event | Wire Down | Include | Include | Equipment | 1051 | 2021-10-22 | 42040 | keep | 0 | Oct | 2021 | 0.028633 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-10-22 17:31 | 2021-10-22 17:32 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21102200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 1533 | keep | 0 | Oct | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
PONCE | 2021-10-22 17:36 | 2021-10-23 15:48 | 90 | 022:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21102200087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1332 | 2021-10-22 | 119880 | keep | 0 | Oct | 2021 | 0.08165 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BARRANQUITAS | 2021-10-22 17:47 | 2021-10-22 19:58 | 100 | 002:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21102200095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-10-22 | 13100 | keep | 0 | Oct | 2021 | 0.0089224 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-22 17:54 | 2021-10-22 19:09 | 4 | 001:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE Y SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | C21102200096 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 75 | 2021-10-22 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
CAGUAS | 2021-10-22 17:56 | 2021-10-22 19:20 | 4 | 001:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102200097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2021-10-22 | 336 | keep | 0 | Oct | 2021 | 0.00022885 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-10-22 17:56 | 2021-10-22 20:38 | 30 | 002:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21102200065 | New_Event | Wire Down | Include | Include | Equipment | 162 | 2021-10-22 | 4860 | keep | 0 | Oct | 2021 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-22 17:57 | 2021-10-22 20:57 | 50 | 003:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE LINEA | B21102110109 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2021-10-22 | 9000 | keep | 0 | Oct | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-22 18:07 | 2021-10-22 18:08 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21102200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 2782 | keep | 0 | Oct | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2021-10-22 18:19 | 2021-10-23 11:19 | 50 | 017:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21102200131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1020 | 2021-10-22 | 51000 | keep | 0 | Oct | 2021 | 0.034736 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-22 18:19 | 2021-10-23 09:17 | 50 | 014:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21102200049 | New_Event | Bad Weather | Include | Include | Weather | 898 | 2021-10-22 | 44900 | keep | 0 | Oct | 2021 | 0.030581 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-22 18:25 | 2021-10-22 18:26 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA | M21102200277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-22 | 4304 | keep | 0 | Oct | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BARRANQUITAS | 2021-10-22 18:25 | 2021-10-23 12:07 | 50 | 017:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21102200100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1062 | 2021-10-22 | 53100 | keep | 0 | Oct | 2021 | 0.036166 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-22 18:35 | 2021-10-23 00:29 | 10 | 005:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21102200066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 354 | 2021-10-22 | 3540 | keep | 0 | Oct | 2021 | 0.0024111 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-22 18:56 | 2021-10-23 19:13 | 20 | 024:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR UNO DE 100 KVA | B21102200139 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1457 | 2021-10-22 | 29140 | keep | 0 | Oct | 2021 | 0.019847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-22 19:00 | 2021-10-23 08:36 | 7 | 013:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21102200102 | New_Event | Bad Weather | Include | Include | Weather | 816 | 2021-10-22 | 5712 | keep | 0 | Oct | 2021 | 0.0038904 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-22 19:26 | 2021-10-23 01:28 | 130 | 006:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 140 EN RISER SE REEMPLAZO SU-1A IMPACTADO POR AUTO | B21102200144 | New_Event |  |  | Include | Wildlife | 362 | 2021-10-22 | 47060 | keep | 0 | Oct | 2021 | 0.032052 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-10-22 19:39 | 2021-10-23 15:59 | 20 | 020:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21102200168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1220 | 2021-10-22 | 24400 | keep | 0 | Oct | 2021 | 0.016619 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-22 19:54 | 2021-10-24 13:50 | 8 | 041:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21102200301 | New_Event | Bad Weather | Include | Include | Weather | 2516 | 2021-10-22 | 20128 | keep | 0 | Oct | 2021 | 0.013709 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 569 | keep | 0 | Oct | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 1245 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 1245 | keep | 0 | Oct | 2021 | 0.00084796 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 1155 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 1155 | keep | 0 | Oct | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 867 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 867 | keep | 0 | Oct | 2021 | 0.00059051 | 0.00059051 | Momentary | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 257 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 257 | keep | 0 | Oct | 2021 | 0.00017504 | 0.00017504 | Momentary | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 1336 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 1336 | keep | 0 | Oct | 2021 | 0.00090994 | 0.00090994 | Momentary | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 3315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 3315 | keep | 0 | Oct | 2021 | 0.0022578 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-10-22 20:02 | 2021-10-22 20:03 | 1718 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21102200000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-22 | 1718 | keep | 0 | Oct | 2021 | 0.0011701 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
VEGA BAJA | 2021-10-22 20:03 | 2021-10-24 12:46 | 20 | 040:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO CONDUCTOR PRIMARIO | B21102200170 | New_Event | Wire Down | Include | Include | Equipment | 2443 | 2021-10-22 | 48860 | keep | 0 | Oct | 2021 | 0.033278 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-10-22 20:44 | 2021-10-23 11:23 | 10 | 014:39 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21102200057 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 879 | 2021-10-22 | 8790 | keep | 0 | Oct | 2021 | 0.0059868 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-22 20:57 | 2021-10-23 12:11 | 8 | 015:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS SE REPARO LINEA SECUNDARIA Y SE TAPEO TRANSFORMADOR | A21102200070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 914 | 2021-10-22 | 7312 | keep | 0 | Oct | 2021 | 0.0049802 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
SAN JUAN | 2021-10-22 21:48 | 2021-10-22 21:49 | 55 | 000:01 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE Y TRANSFORMADOR DE 37.5KVA | S21022000006 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-10-22 | 55 | keep | 0 | Oct | 2021 | 3.746e-05 | 3.746e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-10-22 22:06 | 2021-10-23 15:47 | 6 | 017:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REGULAR TRANSFORMADOR BAJO TAP D AL B QUEDO 124/248V | C21102200107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1061 | 2021-10-22 | 6366 | keep | 0 | Oct | 2021 | 0.0043359 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-22 22:12 | 2021-10-22 22:19 | 2888 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21102200080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-10-22 | 20216 | keep | 0 | Oct | 2021 | 0.013769 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
HUMACAO | 2021-10-22 22:13 | 2021-10-22 22:15 | 1089 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 JUNCOS @ RIO BLANCO | C21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 2178 | keep | 0 | Oct | 2021 | 0.0014834 | 0.00074171 | Momentary | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-10-22 22:13 | 2021-10-22 22:15 | 3896 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 JUNCOS @ RIO BLANCO | C21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 7792 | keep | 0 | Oct | 2021 | 0.0053071 | 0.0026535 | Momentary | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-10-22 22:13 | 2021-10-22 22:15 | 1467 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 JUNCOS @ RIO BLANCO | C21102200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-22 | 2934 | keep | 0 | Oct | 2021 | 0.0019983 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
BAYAMON | 2021-10-22 22:46 | 2021-10-23 13:32 | 10 | 014:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21102200182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 886 | 2021-10-22 | 8860 | keep | 0 | Oct | 2021 | 0.0060345 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-10-22 23:05 | 2021-10-22 23:25 | 6 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 12 NX | S21102200156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-10-22 | 120 | keep | 0 | Oct | 2021 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-23 01:01 | 2021-10-23 12:49 | 7 | 011:48 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21102300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 708 | 2021-10-23 | 4956 | keep | 0 | Oct | 2021 | 0.0033755 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-10-23 01:31 | 2021-10-23 05:21 | 470 | 003:50 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR POR CABLES DE TELEFONO CRUZANDO CON LINEAS PRIMARIAS LLEVA 7003-02 | M21102300007 | New_Event |  |  | Include | Wildlife | 230 | 2021-10-23 | 108100 | keep | 0 | Oct | 2021 | 0.073626 | 0.00032011 | Sustained | FALSE | TRUE | Not_TMED_Event | 470
AGUADILLA | 2021-10-23 01:31 | 2021-10-23 05:21 | 1345 | 003:50 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR 7003-01 EL CUAL ESTA LLEVANDO LA CARGA DEL 7003-02 ESTO POR CABLES DE TELEFONO CRUZANDO CON LINEAS PRIMARIAS | M21102300007 | New_Event |  |  | Include | Wildlife | 230 | 2021-10-23 | 309350 | keep | 0 | Oct | 2021 | 0.2107 | 0.00091607 | Sustained | FALSE | TRUE | Not_TMED_Event | 1345
BAYAMON | 2021-10-23 02:11 | 2021-10-23 12:37 | 35 | 010:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA | S21102300003 | New_Event | Cutout Failure | Include | Include | Equipment | 626 | 2021-10-23 | 21910 | keep | 0 | Oct | 2021 | 0.014923 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-23 03:06 | 2021-10-23 14:17 | 36 | 011:11 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA, 1 X 25 EN PROVISIONAL AEREO, 1 X 50 EN SU Y 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21102300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 671 | 2021-10-23 | 24156 | keep | 0 | Oct | 2021 | 0.016453 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
CAGUAS | 2021-10-23 03:08 | 2021-10-23 13:37 | 50 | 010:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 629 | 2021-10-23 | 31450 | keep | 0 | Oct | 2021 | 0.02142 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-23 04:09 | 2021-10-23 04:10 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2604-03 LLEVANDO LA CARGA DEL 2604-02 | C21102300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 3025 | keep | 0 | Oct | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-10-23 04:09 | 2021-10-23 04:10 | 1593 | 000:01 | T | DESGANCHE | RECIERRE DEL 2604-03 LLEVANDO LA CARGA DEL 2604-02 | C21102300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-23 | 1593 | keep | 0 | Oct | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-10-23 04:11 | 2021-10-23 09:46 | 80 | 005:35 | P | DESGANCHE | 1 X 50 Y 1 X 25 EN CORTES DE LINEA | C21102300006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-10-23 | 26800 | keep | 0 | Oct | 2021 | 0.018253 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-23 04:14 | 2021-10-23 17:50 | 150 | 013:36 | P | CABLE SOTERRADO AVERIADO | 2 X 20 1 X 65 EN RISER Y 1 X 80 RBA EN SU 11 AVERIA NUEVA DEL T 27 AL T 28 Y AVERIA VIEJA DEL T 29 AL T 28 QUEDO FUERA EL T 28 | C21102300007 | New_Event | UG Cable Fault | Include | Include | Equipment | 816 | 2021-10-23 | 122400 | keep | 0 | Oct | 2021 | 0.083366 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-10-23 04:28 | 2021-10-23 06:26 | 2580 | 001:58 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2021-10-23 | 304440 | keep | 0 | Oct | 2021 | 0.20735 | 0.0017572 | Sustained | FALSE | TRUE | Not_TMED_Event | 2580
CANOVANAS | 2021-10-23 04:28 | 2021-10-23 06:26 | 500 | 001:58 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2021-10-23 | 59000 | keep | 0 | Oct | 2021 | 0.040185 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
BAYAMON | 2021-10-23 04:31 | 2021-10-23 12:40 | 80 | 008:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA Y SE HIZO DESGANCHE Y SE LEVANTO LINEA | S21102300005 | New_Event | Wire Down | Include | Include | Equipment | 489 | 2021-10-23 | 39120 | keep | 0 | Oct | 2021 | 0.026644 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-23 04:51 | 2021-10-23 04:52 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO LA CARGA DEL 1206-02 | S21102300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-23 04:51 | 2021-10-23 04:52 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-01 LLEVANDO LA CARGA DEL 1206-02 | S21102300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
HUMACAO | 2021-10-23 05:25 | 2021-10-23 14:50 | 40 | 009:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21102300011 | New_Event |  |  | Include | Wildlife | 565 | 2021-10-23 | 22600 | keep | 0 | Oct | 2021 | 0.015393 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-23 05:50 | 2021-10-23 18:10 | 40 | 012:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102300003 | New_Event | Bad Weather | Include | Include | Weather | 740 | 2021-10-23 | 29600 | keep | 0 | Oct | 2021 | 0.02016 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-23 05:57 | 2021-10-23 19:45 | 200 | 013:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21102300016 | New_Event | Wire Down | Include | Include | Equipment | 828 | 2021-10-23 | 165600 | keep | 0 | Oct | 2021 | 0.11279 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-10-23 05:59 | 2021-10-23 12:00 | 30 | 006:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21102300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2021-10-23 | 10830 | keep | 0 | Oct | 2021 | 0.0073763 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-23 06:38 | 2021-10-23 06:41 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF DE 1620-04 QUE LLEVA CARGA DEL 1620-01 SE PROBO QUEDO EN SERVICIO CARGA POR EL 1620-04 | S21102300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-23 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-23 06:38 | 2021-10-23 06:41 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 1620-1 SE PROBO QUEDO EN SERVICIO | S21102300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-23 | 516 | keep | 0 | Oct | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-10-23 06:39 | 2021-10-23 15:04 | 35 | 008:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 505 | 2021-10-23 | 17675 | keep | 0 | Oct | 2021 | 0.012038 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-10-23 06:43 | 2021-10-24 08:59 | 8 | 026:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21102300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1576 | 2021-10-23 | 12608 | keep | 0 | Oct | 2021 | 0.0085873 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2021-10-23 07:15 | 2021-10-23 14:00 | 125 | 006:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA EN EL SUELO SE ABRIO CORTE DE LINEA Y SE REPARO | P21102300014 | New_Event | Wire Down | Include | Include | Equipment | 405 | 2021-10-23 | 50625 | keep | 0 | Oct | 2021 | 0.03448 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
PONCE | 2021-10-23 07:17 | 2021-10-23 18:00 | 900 | 010:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO EN TRONCAL SE ABRE INTERRUPTOR PARA CORREGIR CONDICION | P21102300015 | New_Event | Wire Down | Include | Include | Equipment | 643 | 2021-10-23 | 578700 | keep | 0 | Oct | 2021 | 0.39415 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
HUMACAO | 2021-10-23 07:40 | 2021-10-23 13:38 | 45 | 005:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21102300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2021-10-23 | 16110 | keep | 0 | Oct | 2021 | 0.010972 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-10-23 07:49 | 2021-10-23 15:29 | 1 | 007:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER DESCARGAS ELECTRICAS | M21102300034 | New_Event | Bad Weather | Include | Include | Weather | 460 | 2021-10-23 | 460 | keep | 0 | Oct | 2021 | 0.0003133 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-23 08:13 | 2021-10-23 13:33 | 10 | 005:20 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE SECCIONALIZO AVERIA DE POSTE PARTIDO | B21102300013 | New_Event | Defective Pole | Include | Include | Equipment | 320 | 2021-10-23 | 3200 | keep | 0 | Oct | 2021 | 0.0021795 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-10-23 08:29 | 2021-10-23 20:07 | 3 | 011:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | R21102300049 | New_Event | Bad Weather | Include | Include | Weather | 698 | 2021-10-23 | 2094 | keep | 0 | Oct | 2021 | 0.0014262 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-10-23 08:30 | 2021-10-23 18:00 | 70 | 009:30 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21102300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 570 | 2021-10-23 | 39900 | keep | 0 | Oct | 2021 | 0.027176 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-10-23 08:34 | 2021-10-23 19:03 | 40 | 010:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102300010 | New_Event | Bad Weather | Include | Include | Weather | 629 | 2021-10-23 | 25160 | keep | 0 | Oct | 2021 | 0.017136 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-10-23 08:36 | 2021-10-23 13:52 | 50 | 005:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21102300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-10-23 | 15800 | keep | 0 | Oct | 2021 | 0.010761 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-23 09:02 | 2021-10-23 19:00 | 15 | 009:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA 100AMP | M21102300046 | New_Event | Cutout Failure | Include | Include | Equipment | 598 | 2021-10-23 | 8970 | keep | 0 | Oct | 2021 | 0.0061094 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-23 09:11 | 2021-10-23 20:34 | 60 | 011:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102300011 | New_Event | Bad Weather | Include | Include | Weather | 683 | 2021-10-23 | 40980 | keep | 0 | Oct | 2021 | 0.027911 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-10-23 09:14 | 2021-10-23 11:03 | 1 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21102300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-10-23 | 109 | keep | 0 | Oct | 2021 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-23 09:15 | 2021-10-23 09:20 | 10 | 000:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21102200319 | New_Event | Secondary Wire Down | Include | Include | Equipment | 5 | 2021-10-23 | 50 | keep | 0 | Oct | 2021 | 3.4055e-05 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-23 09:15 | 2021-10-24 15:07 | 1 | 029:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA | M21102300047 | New_Event | Cutout Failure | Include | Include | Equipment | 1792 | 2021-10-23 | 1792 | keep | 0 | Oct | 2021 | 0.0012205 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-10-23 09:17 | 2021-10-23 11:38 | 60 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21102300032 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2021-10-23 | 8460 | keep | 0 | Oct | 2021 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-10-23 09:30 | 2021-10-23 15:42 | 1 | 006:12 | P | CABLE SOTERRADO AVERIADO | SE ABRE DEL MH-10 AL MH-1 PARA REMPLAZAR CABLE SOTERRADO AVERIADO AVERIA SECCIONALIZADA | P21102300034 | New_Event | UG Cable Fault | Include | Include | Equipment | 372 | 2021-10-23 | 372 | keep | 0 | Oct | 2021 | 0.00025337 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-10-23 09:40 | 2021-10-23 16:52 | 1 | 007:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 15 KVA | A21102300013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 432 | 2021-10-23 | 432 | keep | 0 | Oct | 2021 | 0.00029423 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-23 09:50 | 2021-10-23 11:50 | 1666 | 002:00 | T | DESCONECTIVO DEFECTUOSO | CARGA POR 6702-04 | M21102300003 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2021-10-23 | 199920 | keep | 0 | Oct | 2021 | 0.13616 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-10-23 09:50 | 2021-10-23 11:50 | 4387 | 002:00 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON 2 MACHETES QUEMADOS DE 900AMP SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 6702-03 | M21102300003 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2021-10-23 | 526440 | keep | 0 | Oct | 2021 | 0.35856 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
YAUCO | 2021-10-23 10:03 | 2021-10-23 14:19 | 60 | 004:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21102300035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2021-10-23 | 15360 | keep | 0 | Oct | 2021 | 0.010462 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-23 10:17 | 2021-10-23 13:09 | 150 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO LINEA A CAJA | S21102300021 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2021-10-23 | 25800 | keep | 0 | Oct | 2021 | 0.017572 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-23 10:27 | 2021-10-23 13:00 | 60 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA 100AMP POLIMERO | A21102300015 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2021-10-23 | 9180 | keep | 0 | Oct | 2021 | 0.0062525 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-10-23 10:33 | 2021-10-23 10:34 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-10-23 10:33 | 2021-10-23 10:34 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1017 | keep | 0 | Oct | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-10-23 10:33 | 2021-10-23 10:34 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 828 | keep | 0 | Oct | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-10-23 10:33 | 2021-10-23 10:34 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 863 | keep | 0 | Oct | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-10-23 10:33 | 2021-10-23 10:34 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 309 | keep | 0 | Oct | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-10-23 10:33 | 2021-10-23 10:34 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 176 | keep | 0 | Oct | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
GUAYAMA | 2021-10-23 10:36 | 2021-10-23 14:28 | 150 | 003:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA DE 100 AMPERES | P21102300040 | New_Event | Cutout Failure | Include | Include | Equipment | 232 | 2021-10-23 | 34800 | keep | 0 | Oct | 2021 | 0.023702 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-10-23 10:41 | 2021-10-23 13:22 | 10 | 002:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 100 KVA | B21102300030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 161 | 2021-10-23 | 1610 | keep | 0 | Oct | 2021 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-23 10:55 | 2021-10-23 14:04 | 1246 | 003:09 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO EL INTERRUPTOR ELECTRICAMENTE | C21102300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2021-10-23 | 235494 | keep | 0 | Oct | 2021 | 0.16039 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
CAGUAS | 2021-10-23 10:59 | 2021-10-23 14:59 | 25 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21102300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-10-23 | 6000 | keep | 0 | Oct | 2021 | 0.0040866 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-23 11:06 | 2021-10-23 11:07 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-10-23 11:06 | 2021-10-23 11:07 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1017 | keep | 0 | Oct | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-10-23 11:06 | 2021-10-23 11:07 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 828 | keep | 0 | Oct | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-10-23 11:06 | 2021-10-23 11:07 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 863 | keep | 0 | Oct | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-10-23 11:06 | 2021-10-23 11:07 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 309 | keep | 0 | Oct | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-10-23 11:06 | 2021-10-23 11:07 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 176 | keep | 0 | Oct | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
SAN JUAN | 2021-10-23 11:10 | 2021-10-23 23:18 | 10 | 012:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 25KVA POR 37.5KVA | S21102300024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 728 | 2021-10-23 | 7280 | keep | 0 | Oct | 2021 | 0.0049584 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-23 11:11 | 2021-10-23 11:12 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-10-23 11:11 | 2021-10-23 11:12 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1017 | keep | 0 | Oct | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-10-23 11:11 | 2021-10-23 11:12 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 828 | keep | 0 | Oct | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-10-23 11:11 | 2021-10-23 11:12 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 863 | keep | 0 | Oct | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-10-23 11:11 | 2021-10-23 11:12 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 309 | keep | 0 | Oct | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-10-23 11:11 | 2021-10-23 11:12 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 176 | keep | 0 | Oct | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
ARECIBO | 2021-10-23 11:18 | 2021-10-24 11:56 | 12 | 024:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE AVERIADO | A21102300018 | New_Event | Cutout Failure | Include | Include | Equipment | 1478 | 2021-10-23 | 17736 | keep | 0 | Oct | 2021 | 0.01208 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-23 11:20 | 2021-10-23 12:37 | 12 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | S21102300025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-10-23 | 924 | keep | 0 | Oct | 2021 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-10-23 11:23 | 2021-10-23 15:41 | 607 | 004:18 | T | CABLE SOTERRADO AVERIADO | SE ABRE INTERRUPTOR 5007-04 CON CARGA DE EL ALIMENTADOR 5007-02 AUTORIZADO POR ALEXIS MARTINEZ PARA PODER DESENERGIZAR MH-13 Y PODER COMPLETAR TRABAJOS EN SOTERRADO | P21102300049 | New_Event | UG Cable Fault | Include | Include | Equipment | 258 | 2021-10-23 | 156606 | keep | 0 | Oct | 2021 | 0.10666 | 0.00041342 | Sustained | FALSE | FALSE | Not_TMED_Event | 607
PONCE | 2021-10-23 11:23 | 2021-10-23 15:41 | 462 | 004:18 | T | CABLE SOTERRADO AVERIADO | SE ABRE INTERRUPTOR 5007-04 AUTORIZADO POR ALEXIS MARTINEZ PARA PODER DESENERGIZAR MH-13 Y PODER COMPLETAR TRABAJOS EN SOTERRADO | P21102300049 | New_Event | UG Cable Fault | Include | Include | Equipment | 258 | 2021-10-23 | 119196 | keep | 0 | Oct | 2021 | 0.081184 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
YAUCO | 2021-10-23 11:24 | 2021-10-23 17:10 | 17 | 005:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA A 2.4KV POR TRANSFORMADOR DE 50 KVA A 2.4 KV POR FALTA DE DISPONIBILIDAD | P21102300050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 346 | 2021-10-23 | 5882 | keep | 0 | Oct | 2021 | 0.0040062 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
FAJARDO | 2021-10-23 11:27 | 2021-10-23 16:09 | 40 | 004:42 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21102300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2021-10-23 | 11280 | keep | 0 | Oct | 2021 | 0.0076828 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-10-23 11:30 | 2021-10-23 16:00 | 1 | 004:30 | P | OTRAS CAUSAS | 1 X 50 EN RISER PROBLEMA INTERNO DEL CLIENTE | A21102300032 | New_Event | Other Causes | Include | Include | Other | 270 | 2021-10-23 | 270 | keep | 0 | Oct | 2021 | 0.0001839 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-23 11:31 | 2021-10-23 15:39 | 100 | 004:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21102300064 | New_Event | Wire Down | Include | Include | Equipment | 248 | 2021-10-23 | 24800 | keep | 0 | Oct | 2021 | 0.016891 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-10-23 11:31 | 2021-10-23 11:55 | 20 | 000:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2021-10-23 | 480 | keep | 0 | Oct | 2021 | 0.00032693 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-10-23 11:37 | 2021-10-23 11:40 | 4035 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P211023000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-23 | 12105 | keep | 0 | Oct | 2021 | 0.0082447 | 0.0027482 | Momentary | FALSE | TRUE | Not_TMED_Event | 4035
PONCE | 2021-10-23 11:37 | 2021-10-23 11:40 | 3718 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P211023000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-10-23 | 11154 | keep | 0 | Oct | 2021 | 0.0075969 | 0.0025323 | Momentary | FALSE | TRUE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2021-10-23 11:50 | 2021-10-23 14:39 | 1666 | 002:49 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO DOS MACHETES QUEMADOS DE SALIDA DE INTERRUPTOR LEVA LA CARGA DEL 6702-04 | M21102300003 | New_Event | Switch Failure | Include | Include | Equipment | 169 | 2021-10-23 | 281554 | keep | 0 | Oct | 2021 | 0.19177 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-10-23 11:50 | 2021-10-23 14:39 | 4387 | 002:49 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO DOS MACHETES QUEMADOS DE SALIDA DE INTERRUPTOR | M21102300003 | New_Event | Switch Failure | Include | Include | Equipment | 169 | 2021-10-23 | 741403 | keep | 0 | Oct | 2021 | 0.50497 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
YAUCO | 2021-10-23 11:59 | 2021-10-23 15:08 | 30 | 003:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21102300061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-10-23 | 5670 | keep | 0 | Oct | 2021 | 0.0038618 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-23 12:02 | 2021-10-23 17:30 | 10 | 005:28 | P | DESGANCHE | 1 X 20 EN RISER SE RETIRO ENREDADERA | M21102300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-10-23 | 3280 | keep | 0 | Oct | 2021 | 0.002234 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-23 12:02 | 2021-10-23 16:06 | 50 | 004:04 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-10-23 | 12200 | keep | 0 | Oct | 2021 | 0.0083094 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-23 12:15 | 2021-10-23 12:27 | 200 | 000:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | R21102300022 | New_Event | Wire Down | Include | Include | Equipment | 12 | 2021-10-23 | 2400 | keep | 0 | Oct | 2021 | 0.0016346 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 12:25 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1617 | keep | 0 | Oct | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 12:25 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1017 | keep | 0 | Oct | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 12:25 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 828 | keep | 0 | Oct | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 12:25 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 863 | keep | 0 | Oct | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 12:25 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 309 | keep | 0 | Oct | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 12:25 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21102300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 176 | keep | 0 | Oct | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-10-23 12:24 | 2021-10-23 17:09 | 974 | 004:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2021-10-23 | 277590 | keep | 0 | Oct | 2021 | 0.18907 | 0.00066339 | Sustained | FALSE | TRUE | Not_TMED_Event | 974
HUMACAO | 2021-10-23 12:25 | 2021-10-23 15:46 | 1 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21102300054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2021-10-23 | 201 | keep | 0 | Oct | 2021 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-10-23 12:27 | 2021-10-23 12:28 | 2722 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21102300024 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-10-23 | 2722 | keep | 0 | Oct | 2021 | 0.0018539 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-23 12:28 | 2021-10-23 16:18 | 60 | 003:50 | P | DESGANCHE | 1 X 50 Y 2 X 40 EN CORTES DE LINEA SE REALIZO DESGANCHE | B21102300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-10-23 | 13800 | keep | 0 | Oct | 2021 | 0.0093991 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-10-23 12:28 | 2021-10-23 13:47 | 200 | 001:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | R21102300022 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 79 | 2021-10-23 | 15800 | keep | 0 | Oct | 2021 | 0.010761 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-23 12:42 | 2021-10-23 20:23 | 60 | 007:41 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | B21102300043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 461 | 2021-10-23 | 27660 | keep | 0 | Oct | 2021 | 0.018839 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-23 13:05 | 2021-10-23 15:18 | 10 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102300027 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-10-23 | 1330 | keep | 0 | Oct | 2021 | 0.00090586 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-23 13:06 | 2021-10-23 15:37 | 6 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21102300063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2021-10-23 | 906 | keep | 0 | Oct | 2021 | 0.00061707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-10-23 13:12 | 2021-10-24 13:22 | 4 | 024:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21102300064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1450 | 2021-10-23 | 5800 | keep | 0 | Oct | 2021 | 0.0039504 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-23 13:30 | 2021-10-23 17:19 | 30 | 003:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN SU CRUCE CON RATON | R21102300037 | New_Event |  |  | Include | Wildlife | 229 | 2021-10-23 | 6870 | keep | 0 | Oct | 2021 | 0.0046791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-10-23 13:37 | 2021-10-23 18:53 | 10 | 005:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CLIENTE CRUZA TOMA SECUNDARIA CON TAPA DE PULL OUT | P21102300079 | New_Event |  |  | Include | Wildlife | 316 | 2021-10-23 | 3160 | keep | 0 | Oct | 2021 | 0.0021523 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-23 13:41 | 2021-10-23 17:44 | 1339 | 004:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21102300098 | New_Event | Wire Down | Include | Include | Equipment | 243 | 2021-10-23 | 325377 | keep | 0 | Oct | 2021 | 0.22161 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 1717 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 20604 | keep | 0 | Oct | 2021 | 0.014033 | 0.0011694 | Sustained | FALSE | TRUE | Not_TMED_Event | 1717
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 974 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 11688 | keep | 0 | Oct | 2021 | 0.0079606 | 0.00066339 | Sustained | FALSE | TRUE | Not_TMED_Event | 974
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 1905 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 22860 | keep | 0 | Oct | 2021 | 0.01557 | 0.0012975 | Sustained | FALSE | TRUE | Not_TMED_Event | 1905
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 1262 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 15144 | keep | 0 | Oct | 2021 | 0.010315 | 0.00085954 | Sustained | FALSE | TRUE | Not_TMED_Event | 1262
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 200 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 2400 | keep | 0 | Oct | 2021 | 0.0016346 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 222 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 2664 | keep | 0 | Oct | 2021 | 0.0018144 | 0.0001512 | Sustained | FALSE | TRUE | Not_TMED_Event | 222
PONCE | 2021-10-23 13:42 | 2021-10-23 13:54 | 537 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21102300090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-23 | 6444 | keep | 0 | Oct | 2021 | 0.004389 | 0.00036575 | Sustained | FALSE | TRUE | Not_TMED_Event | 537
SAN JUAN | 2021-10-23 13:54 | 2021-10-23 23:19 | 35 | 009:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO ARBOL DE FLAMBOYAN | S21102300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 565 | 2021-10-23 | 19775 | keep | 0 | Oct | 2021 | 0.013469 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
AGUADILLA | 2021-10-23 13:54 | 2021-10-24 08:50 | 17 | 018:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | M21102300102 | New_Event | Bad Weather | Include | Include | Weather | 1136 | 2021-10-23 | 19312 | keep | 0 | Oct | 2021 | 0.013153 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2021-10-23 13:59 | 2021-10-23 17:38 | 6 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21102300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2021-10-23 | 1314 | keep | 0 | Oct | 2021 | 0.00089496 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-23 14:00 | 2021-10-23 16:58 | 25 | 002:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21102300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2021-10-23 | 4450 | keep | 0 | Oct | 2021 | 0.0030309 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-23 14:04 | 2021-10-23 17:56 | 35 | 003:52 | P | DESGANCHE | 1 X 65 EN CORTE DE DE LINEA Y SE REPORTA AVERIA POR DESGANCHE | S21102300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2021-10-23 | 8120 | keep | 0 | Oct | 2021 | 0.0055305 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BARRANQUITAS | 2021-10-23 14:10 | 2021-10-23 18:13 | 229 | 004:03 | S | DESCONECTIVO DEFECTUOSO | SE HIZO BY PASS AL WAVE TRAP DE COMUNICACION Y SE TRANSFIRIO LA CARGA DEL 9901-02 AL 9901-01 POR 2 MACHETES DE BARRA QUEMADOS | C21102300066 | New_Event | Switch Failure | Include | Include | Equipment | 243 | 2021-10-23 | 55647 | keep | 0 | Oct | 2021 | 0.037901 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
BARRANQUITAS | 2021-10-23 14:10 | 2021-10-23 18:13 | 1246 | 004:03 | S | DESCONECTIVO DEFECTUOSO | SE HIZO BY PASS AL WAVE TRAP DE COMUNICACION Y SE TRANSFIRIO LA CARGA DEL 9901-02 AL 9901-01 POR 2 MACHETES DE BARRA QUEMADOS | C21102300066 | New_Event | Switch Failure | Include | Include | Equipment | 243 | 2021-10-23 | 302778 | keep | 0 | Oct | 2021 | 0.20622 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
PONCE | 2021-10-23 14:38 | 2021-10-23 14:39 | 978 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21102300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 978 | keep | 0 | Oct | 2021 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
MAYAGÃœEZ | 2021-10-23 14:42 | 2021-10-24 00:23 | 10 | 009:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO PARTIDO | M21102300116 | New_Event | Wire Down | Include | Include | Equipment | 581 | 2021-10-23 | 5810 | keep | 0 | Oct | 2021 | 0.0039572 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-23 14:44 | 2021-10-23 18:13 | 20 | 003:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2021-10-23 | 4180 | keep | 0 | Oct | 2021 | 0.002847 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-23 14:54 | 2021-10-23 14:55 | 1604 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1604 | keep | 0 | Oct | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | TRUE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-10-23 14:54 | 2021-10-23 14:55 | 1131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 1131 | keep | 0 | Oct | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | TRUE | Not_TMED_Event | 1131
BARRANQUITAS | 2021-10-23 14:54 | 2021-10-23 14:55 | 2362 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C21102300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-23 | 2362 | keep | 0 | Oct | 2021 | 0.0016087 | 0.0016087 | Momentary | FALSE | TRUE | Not_TMED_Event | 2362
BAYAMON | 2021-10-23 14:59 | 2021-10-23 20:41 | 50 | 005:42 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN RISER SE REMPLAZO TRANSFORMADOR AVERIADO DE 100KVA POR UNO DE 100KVA | S21112300055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 342 | 2021-10-23 | 17100 | keep | 0 | Oct | 2021 | 0.011647 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-10-23 15:02 | 2021-10-23 15:19 | 25 | 000:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21102300099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2021-10-23 | 425 | keep | 0 | Oct | 2021 | 0.00028947 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-23 15:08 | 2021-10-23 19:10 | 230 | 004:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102300053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2021-10-23 | 55660 | keep | 0 | Oct | 2021 | 0.03791 | 0.00015665 | Sustained | FALSE | TRUE | Not_TMED_Event | 230
BAYAMON | 2021-10-23 15:16 | 2021-10-23 15:35 | 6 | 000:19 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21102300055 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 19 | 2021-10-23 | 114 | keep | 0 | Oct | 2021 | 7.7645e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-23 15:16 | 2021-10-23 22:07 | 90 | 006:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21102300053 | New_Event | Cutout Failure | Include | Include | Equipment | 411 | 2021-10-23 | 36990 | keep | 0 | Oct | 2021 | 0.025194 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
YAUCO | 2021-10-23 15:21 | 2021-10-24 16:57 | 1 | 025:36 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21102300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1536 | 2021-10-23 | 1536 | keep | 0 | Oct | 2021 | 0.0010462 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-23 15:42 | 2021-10-24 12:53 | 7 | 021:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21102300071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1271 | 2021-10-23 | 8897 | keep | 0 | Oct | 2021 | 0.0060597 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-23 15:49 | 2021-10-24 09:11 | 10 | 017:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102300035 | New_Event | Bad Weather | Include | Include | Weather | 1042 | 2021-10-23 | 10420 | keep | 0 | Oct | 2021 | 0.007097 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
GUAYAMA | 2021-10-23 15:52 | 2021-10-23 16:47 | 15 | 000:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21102300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-10-23 | 825 | keep | 0 | Oct | 2021 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-23 15:52 | 2021-10-23 17:28 | 100 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CAMION IMPACTO POSTE CRUZANDO MOMENTANEAMENTE LAS LINEAS | A21102300036 | New_Event |  |  | Include | Wildlife | 96 | 2021-10-23 | 9600 | keep | 0 | Oct | 2021 | 0.0065385 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-23 16:09 | 2021-10-24 16:33 | 43 | 024:24 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 100 X 100KVA | R21102300044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1464 | 2021-10-23 | 62952 | keep | 0 | Oct | 2021 | 0.042876 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
ARECIBO | 2021-10-23 16:32 | 2021-10-23 19:00 | 100 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102300037 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2021-10-23 | 14800 | keep | 0 | Oct | 2021 | 0.01008 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-23 16:33 | 2021-10-24 10:27 | 12 | 017:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTOR SECUNDARIO | S21102300060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1074 | 2021-10-23 | 12888 | keep | 0 | Oct | 2021 | 0.008778 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-23 16:35 | 2021-10-23 18:44 | 80 | 002:09 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21102300061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-10-23 | 10320 | keep | 0 | Oct | 2021 | 0.0070289 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-23 16:37 | 2021-10-24 10:41 | 6 | 018:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA LLUVIAS | R21102300045 | New_Event | Bad Weather | Include | Include | Weather | 1084 | 2021-10-23 | 6504 | keep | 0 | Oct | 2021 | 0.0044298 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
PONCE | 2021-10-23 16:49 | 2021-10-23 20:02 | 60 | 003:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | P21102300115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2021-10-23 | 11580 | keep | 0 | Oct | 2021 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-10-23 16:58 | 2021-10-23 18:25 | 50 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | R21102300047 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2021-10-23 | 4350 | keep | 0 | Oct | 2021 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-23 17:06 | 2021-10-24 15:25 | 56 | 022:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO IGUANA | S21102300065 | New_Event |  |  | Include | Wildlife | 1339 | 2021-10-23 | 74984 | keep | 0 | Oct | 2021 | 0.051071 | 3.8141e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 56
BAYAMON | 2021-10-23 17:17 | 2021-10-24 14:41 | 20 | 021:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21102300073 | New_Event | Cutout Failure | Include | Include | Equipment | 1284 | 2021-10-23 | 25680 | keep | 0 | Oct | 2021 | 0.017491 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-10-23 17:20 | 2021-10-24 10:24 | 6 | 017:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21102300128 | New_Event | Wire Down | Include | Include | Equipment | 1024 | 2021-10-23 | 6144 | keep | 0 | Oct | 2021 | 0.0041847 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-10-23 17:35 | 2021-10-23 17:36 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21102300125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 1475 | keep | 0 | Oct | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
MAYAGÃœEZ | 2021-10-23 17:36 | 2021-10-24 11:15 | 200 | 017:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21102300129 | New_Event | Bad Weather | Include | Include | Weather | 1059 | 2021-10-23 | 211800 | keep | 0 | Oct | 2021 | 0.14426 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-10-23 17:43 | 2021-10-23 17:44 | 4664 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21102300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-23 | 4664 | keep | 0 | Oct | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-10-23 17:44 | 2021-10-23 21:15 | 4 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE HACIENDO CONTACTO CON POSTE | M21102300131 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 211 | 2021-10-23 | 844 | keep | 0 | Oct | 2021 | 0.00057484 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-10-23 17:45 | 2021-10-23 17:46 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102300089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 1261 | keep | 0 | Oct | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
ARECIBO | 2021-10-23 17:48 | 2021-10-24 20:30 | 30 | 026:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21102400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1602 | 2021-10-23 | 48060 | keep | 0 | Oct | 2021 | 0.032733 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-10-23 18:00 | 2021-10-23 18:25 | 2689 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN TRONCAL PRIMARIO Y SE COLOCO INTERRUPTOR EN SERVICIO | P21102300127 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-10-23 | 67225 | keep | 0 | Oct | 2021 | 0.045787 | 0.0018315 | Sustained | FALSE | FALSE | Not_TMED_Event | 2689
SAN JUAN | 2021-10-23 18:01 | 2021-10-24 09:39 | 1 | 015:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA QUEMADA | R21102300051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 938 | 2021-10-23 | 938 | keep | 0 | Oct | 2021 | 0.00063887 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-10-23 18:13 | 2021-10-23 18:17 | 40 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y CERRO PUENTE | C21102200092 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-10-23 | 160 | keep | 0 | Oct | 2021 | 0.00010898 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-10-23 18:19 | 2021-10-23 22:47 | 80 | 004:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | M21102300133 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 268 | 2021-10-23 | 21440 | keep | 0 | Oct | 2021 | 0.014603 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-23 18:20 | 2021-10-24 10:33 | 71 | 016:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21102300137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 973 | 2021-10-23 | 69083 | keep | 0 | Oct | 2021 | 0.047052 | 4.8358e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 71
PONCE | 2021-10-23 18:21 | 2021-10-23 21:19 | 80 | 002:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21102300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2021-10-23 | 14240 | keep | 0 | Oct | 2021 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-10-23 18:25 | 2021-10-24 12:05 | 5 | 017:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21102300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1060 | 2021-10-23 | 5300 | keep | 0 | Oct | 2021 | 0.0036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-10-23 18:27 | 2021-10-23 22:08 | 150 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P21102300133 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2021-10-23 | 33150 | keep | 0 | Oct | 2021 | 0.022578 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-10-23 18:30 | 2021-10-24 09:58 | 10 | 015:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO CAJA AVERIADO | C21102300083 | New_Event | Cutout Failure | Include | Include | Equipment | 928 | 2021-10-23 | 9280 | keep | 0 | Oct | 2021 | 0.0063206 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-23 18:39 | 2021-10-24 16:56 | 20 | 022:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO TRAMO SECUNDARIO | C21102300085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1337 | 2021-10-23 | 26740 | keep | 0 | Oct | 2021 | 0.018212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-10-23 18:41 | 2021-10-24 13:50 | 90 | 019:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA DEL PISO | P21102300139 | New_Event | Wire Down | Include | Include | Equipment | 1149 | 2021-10-23 | 103410 | keep | 0 | Oct | 2021 | 0.070432 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-10-23 19:01 | 2021-10-24 14:00 | 20 | 018:59 | P | CABLE SOTERRADO AVERIADO | 1 X 25 RBA EN SU 19 HACIA EL T 48 QUEDO FUERA EL T 49 | C21102300086 | New_Event | UG Cable Fault | Include | Include | Equipment | 1139 | 2021-10-23 | 22780 | keep | 0 | Oct | 2021 | 0.015515 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-10-23 19:36 | 2021-10-24 09:33 | 50 | 013:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21102300087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 837 | 2021-10-23 | 41850 | keep | 0 | Oct | 2021 | 0.028504 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-23 19:46 | 2021-10-24 09:40 | 8 | 013:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21102300073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 834 | 2021-10-23 | 6672 | keep | 0 | Oct | 2021 | 0.0045443 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-23 20:28 | 2021-10-23 21:43 | 26 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102300079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-10-23 | 1950 | keep | 0 | Oct | 2021 | 0.0013281 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
YAUCO | 2021-10-23 20:47 | 2021-10-24 09:32 | 107 | 012:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21102300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 765 | 2021-10-23 | 81855 | keep | 0 | Oct | 2021 | 0.055751 | 7.2877e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 107
BAYAMON | 2021-10-23 20:48 | 2021-10-24 13:14 | 12 | 016:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S21102300060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 986 | 2021-10-23 | 11832 | keep | 0 | Oct | 2021 | 0.0080587 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-10-23 21:05 | 2021-10-24 10:58 | 1 | 013:53 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR PROBLEMA DEL CLIENTE | R21102300065 | New_Event | Other Causes | Include | Include | Other | 833 | 2021-10-23 | 833 | keep | 0 | Oct | 2021 | 0.00056735 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-23 21:32 | 2021-10-23 22:55 | 60 | 001:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A21102300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-10-23 | 4980 | keep | 0 | Oct | 2021 | 0.0033919 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-10-23 22:14 | 2021-10-24 10:06 | 10 | 011:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REAPARO BAJANTE DE LINEA A CAJA | C21102300093 | New_Event | Wire Down | Include | Include | Equipment | 712 | 2021-10-23 | 7120 | keep | 0 | Oct | 2021 | 0.0048494 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-23 22:40 | 2021-10-23 22:41 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21102300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 6285 | keep | 0 | Oct | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-10-23 22:47 | 2021-10-23 22:48 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21102300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 4381 | keep | 0 | Oct | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-10-23 22:48 | 2021-10-24 09:00 | 80 | 010:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | M21102300133 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 612 | 2021-10-23 | 48960 | keep | 0 | Oct | 2021 | 0.033346 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-10-23 22:58 | 2021-10-24 11:30 | 10 | 012:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21102300097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 752 | 2021-10-23 | 7520 | keep | 0 | Oct | 2021 | 0.0051218 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-10-23 22:58 | 2021-10-23 22:59 | 1067 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE REALIZO PRUEBA CON RR EN OFF Y QUEDO EN SERVICIO | P21102300156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-23 | 1067 | keep | 0 | Oct | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
ARECIBO | 2021-10-23 23:30 | 2021-10-24 16:05 | 12 | 016:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21102300042 | New_Event | Wire Down | Include | Include | Equipment | 995 | 2021-10-23 | 11940 | keep | 0 | Oct | 2021 | 0.0081323 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-24 00:32 | 2021-10-24 09:57 | 10 | 009:25 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21102400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 565 | 2021-10-24 | 5650 | keep | 0 | Oct | 2021 | 0.0038482 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-24 00:49 | 2021-10-24 16:03 | 36 | 015:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 914 | 2021-10-24 | 32904 | keep | 0 | Oct | 2021 | 0.022411 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
AGUADILLA | 2021-10-24 03:46 | 2021-10-24 04:50 | 1337 | 001:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUALMENTE | M21102400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2021-10-24 | 85568 | keep | 0 | Oct | 2021 | 0.05828 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
VEGA BAJA | 2021-10-24 04:51 | 2021-10-24 08:45 | 40 | 003:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21102400004 | New_Event | Cutout Failure | Include | Include | Equipment | 234 | 2021-10-24 | 9360 | keep | 0 | Oct | 2021 | 0.0063751 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-24 06:11 | 2021-10-24 17:37 | 7 | 011:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN RISER SE REMPLAZO SECUNDARIA | S21102400006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 686 | 2021-10-24 | 4802 | keep | 0 | Oct | 2021 | 0.0032706 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-10-24 06:52 | 2021-10-24 06:53 | 1250 | 000:01 | T | DESGANCHE | RECIERRE | C21102400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-24 | 1250 | keep | 0 | Oct | 2021 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
FAJARDO | 2021-10-24 06:53 | 2021-10-24 08:59 | 3 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | R21102400002 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-10-24 | 378 | keep | 0 | Oct | 2021 | 0.00025745 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-10-24 06:53 | 2021-10-24 10:31 | 15 | 003:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y REPARO BAJANTE DE LINEA A CAJA | C21102400006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-10-24 | 3270 | keep | 0 | Oct | 2021 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-24 07:25 | 2021-10-24 10:51 | 7 | 003:26 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 25 KVA | C21102300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 206 | 2021-10-24 | 1442 | keep | 0 | Oct | 2021 | 0.00098214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-10-24 07:44 | 2021-10-24 14:34 | 2 | 006:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21102400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2021-10-24 | 820 | keep | 0 | Oct | 2021 | 0.0005585 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CAGUAS | 2021-10-24 07:52 | 2021-10-24 11:29 | 40 | 003:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21102400010 | New_Event |  |  | Include | Wildlife | 217 | 2021-10-24 | 8680 | keep | 0 | Oct | 2021 | 0.0059119 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-24 07:54 | 2021-10-24 14:03 | 50 | 006:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-2 HACIA SU-3 | B21102400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2021-10-24 | 18450 | keep | 0 | Oct | 2021 | 0.012566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-24 08:01 | 2021-10-24 12:50 | 80 | 004:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21102400009 | New_Event | Bad Weather | Include | Include | Weather | 289 | 2021-10-24 | 23120 | keep | 0 | Oct | 2021 | 0.015747 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-10-24 08:04 | 2021-10-24 11:14 | 50 | 003:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21102400013 | New_Event |  |  | Include | Wildlife | 190 | 2021-10-24 | 9500 | keep | 0 | Oct | 2021 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-24 08:10 | 2021-10-24 18:24 | 30 | 010:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21102400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 614 | 2021-10-24 | 18420 | keep | 0 | Oct | 2021 | 0.012546 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-10-24 08:10 | 2021-10-24 10:45 | 100 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102400005 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-10-24 | 15500 | keep | 0 | Oct | 2021 | 0.010557 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-24 08:11 | 2021-10-24 10:56 | 100 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO PRIMARIA | S21102400009 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2021-10-24 | 16500 | keep | 0 | Oct | 2021 | 0.011238 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-24 08:33 | 2021-10-24 14:08 | 25 | 005:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21102400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-10-24 | 8375 | keep | 0 | Oct | 2021 | 0.0057042 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-10-24 08:33 | 2021-10-24 10:07 | 1 | 001:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 37.5 KVA | A21102400007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 94 | 2021-10-24 | 94 | keep | 0 | Oct | 2021 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-24 08:51 | 2021-10-24 11:11 | 20 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21102400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2021-10-24 | 2800 | keep | 0 | Oct | 2021 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-10-24 09:10 | 2021-10-24 10:14 | 15 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR BARRAS EN PEDESTAL | P21102400005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-10-24 | 960 | keep | 0 | Oct | 2021 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-24 09:13 | 2021-10-24 09:14 | 2203 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO FUERTES LLUVIAS | S21102400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-24 | 2203 | keep | 0 | Oct | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2021-10-24 09:14 | 2021-10-24 10:24 | 60 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102400010 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2021-10-24 | 4200 | keep | 0 | Oct | 2021 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-24 09:30 | 2021-10-24 11:12 | 30 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO DE LINEA A CAJA PRIMARIA EN CORTE DE LINEA | B21102300026 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-10-24 | 3060 | keep | 0 | Oct | 2021 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-24 09:37 | 2021-10-24 10:06 | 99 | 000:29 | T | OTRAS CAUSAS | DISPARO SE SECCIONALIZO AVERIA DE CLIENTE PRIVADO | R21102400000 | New_Event | Other Causes | Include | Include | Other | 29 | 2021-10-24 | 2871 | keep | 0 | Oct | 2021 | 0.0019554 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
MAYAGÃœEZ | 2021-10-24 09:41 | 2021-10-24 15:36 | 11 | 005:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE RETEZO LINEAS PRIMARIAS CRUZADAS | M21102400018 | New_Event | Wire Down | Include | Include | Equipment | 355 | 2021-10-24 | 3905 | keep | 0 | Oct | 2021 | 0.0026597 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
ARECIBO | 2021-10-24 09:45 | 2021-10-24 10:09 | 6 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21102400004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-10-24 | 144 | keep | 0 | Oct | 2021 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-24 10:06 | 2021-10-24 10:32 | 24 | 000:26 | P | OTRAS CAUSAS | AVERIA DEL CLIENTE DEL SU1 AL NT3 | R21102400000 | New_Event | Other Causes | Include | Include | Other | 26 | 2021-10-24 | 624 | keep | 0 | Oct | 2021 | 0.000425 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-10-24 10:13 | 2021-10-24 11:00 | 10 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | B21102400015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-10-24 | 470 | keep | 0 | Oct | 2021 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-24 10:26 | 2021-10-24 10:30 | 36 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1620-04 POR BARRA DE INSPECCION | S21102400020 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-10-24 | 144 | keep | 0 | Oct | 2021 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-24 10:26 | 2021-10-24 10:30 | 172 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1620-01 POR BARRA DE INSPECCION | S21102400020 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-10-24 | 688 | keep | 0 | Oct | 2021 | 0.00046859 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-10-24 10:28 | 2021-10-24 10:29 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 2203 | keep | 0 | Oct | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2021-10-24 10:34 | 2021-10-24 10:35 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1530-06 | S21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 1420 | keep | 0 | Oct | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-10-24 10:34 | 2021-10-24 10:35 | 437 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO LLEVA 1526-2 | S21102400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-24 | 437 | keep | 0 | Oct | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-10-24 10:35 | 2021-10-24 10:36 | 290 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | S21102400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-24 | 290 | keep | 0 | Oct | 2021 | 0.00019752 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2021-10-24 10:36 | 2021-10-24 16:27 | 200 | 005:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL | S21102400030 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 351 | 2021-10-24 | 70200 | keep | 0 | Oct | 2021 | 0.047813 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-24 10:37 | 2021-10-24 10:38 | 1420 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO CARGA POR EL 1530-06 | S21102400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-24 | 1420 | keep | 0 | Oct | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-10-24 10:37 | 2021-10-24 10:38 | 437 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO LLEVA 1526-2 | S21102400000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-10-24 | 437 | keep | 0 | Oct | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2021-10-24 10:39 | 2021-10-24 10:40 | 600 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
CAGUAS | 2021-10-24 10:43 | 2021-10-24 13:55 | 8 | 003:12 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO | C21102400019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 192 | 2021-10-24 | 1536 | keep | 0 | Oct | 2021 | 0.0010462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-24 10:45 | 2021-10-24 10:47 | 1408 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 1714 03 | B21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-24 | 2816 | keep | 0 | Oct | 2021 | 0.001918 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-10-24 10:45 | 2021-10-24 10:47 | 455 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1714 02 | B21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-24 | 910 | keep | 0 | Oct | 2021 | 0.0006198 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
FAJARDO | 2021-10-24 10:54 | 2021-10-24 14:36 | 3 | 003:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | R21102400008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 222 | 2021-10-24 | 666 | keep | 0 | Oct | 2021 | 0.00045361 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-10-24 10:54 | 2021-10-24 15:15 | 30 | 004:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-10-24 | 7830 | keep | 0 | Oct | 2021 | 0.005333 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-10-24 11:03 | 2021-10-24 14:11 | 30 | 003:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21102400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2021-10-24 | 5640 | keep | 0 | Oct | 2021 | 0.0038414 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-10-24 11:04 | 2021-10-24 14:27 | 40 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21102400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-10-24 | 8120 | keep | 0 | Oct | 2021 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-24 11:11 | 2021-10-24 15:32 | 63 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21102400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2021-10-24 | 16443 | keep | 0 | Oct | 2021 | 0.011199 | 4.2909e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 63
BAYAMON | 2021-10-24 11:22 | 2021-10-24 13:27 | 20 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21102400025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-10-24 | 2500 | keep | 0 | Oct | 2021 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-10-24 11:32 | 2021-10-24 13:50 | 25 | 002:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21102400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2021-10-24 | 3450 | keep | 0 | Oct | 2021 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-24 11:38 | 2021-10-24 11:39 | 225 | 000:01 | T | DESGANCHE | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1303-4 | S21102400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-24 | 225 | keep | 0 | Oct | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-24 11:38 | 2021-10-24 11:39 | 870 | 000:01 | T | DESGANCHE | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1303-4 | S21102400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-24 | 870 | keep | 0 | Oct | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-10-24 11:42 | 2021-10-24 12:18 | 40 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S21102400053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-10-24 | 1440 | keep | 0 | Oct | 2021 | 0.00098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-10-24 12:09 | 2021-10-24 15:12 | 225 | 003:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1303-4. SE REALIZO DESGANCHE EN EL 1303-05. | S21102400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-10-24 | 41175 | keep | 0 | Oct | 2021 | 0.028044 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-24 12:09 | 2021-10-24 15:12 | 870 | 003:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1303-4 | S21102300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-10-24 | 159210 | keep | 0 | Oct | 2021 | 0.10844 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-10-24 12:13 | 2021-10-24 14:39 | 1802 | 002:26 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ENTRO UN 40% EN SERVICIO | S21102400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-10-24 | 263092 | keep | 0 | Oct | 2021 | 0.17919 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
CANOVANAS | 2021-10-24 12:26 | 2021-10-24 17:16 | 7 | 004:50 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | R21102400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2021-10-24 | 2030 | keep | 0 | Oct | 2021 | 0.0013826 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-24 12:39 | 2021-10-24 12:41 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21102400033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-24 | 4468 | keep | 0 | Oct | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2021-10-24 12:41 | 2021-10-24 18:40 | 3 | 005:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 5 EN TRANSFORMADOR SE CORRIGIO LINEA SECUNDARIA CRUZADA | M21102400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 359 | 2021-10-24 | 1077 | keep | 0 | Oct | 2021 | 0.00073354 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CANOVANAS | 2021-10-24 13:08 | 2021-10-24 13:10 | 2580 | 000:02 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 11100 | R21102400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-24 | 5160 | keep | 0 | Oct | 2021 | 0.0035145 | 0.0017572 | Momentary | FALSE | TRUE | Not_TMED_Event | 2580
CANOVANAS | 2021-10-24 13:08 | 2021-10-24 13:10 | 500 | 000:02 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 11100 | R21102400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-24 | 1000 | keep | 0 | Oct | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-10-24 13:23 | 2021-10-24 13:24 | 1022 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21102400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-24 | 1022 | keep | 0 | Oct | 2021 | 0.00069608 | 0.00069608 | Momentary | FALSE | FALSE | Not_TMED_Event | 1022
ARECIBO | 2021-10-24 13:24 | 2021-10-24 13:29 | 120 | 000:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE PARTIDO | A21102400000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 5 | 2021-10-24 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 8.1731e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2021-10-24 13:27 | 2021-10-24 15:14 | 844 | 001:47 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-10-24 | 90308 | keep | 0 | Oct | 2021 | 0.061508 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
ARECIBO | 2021-10-24 13:29 | 2021-10-24 14:51 | 1022 | 001:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR DE EMERGENCIA POR ALAMBRE PARTIDO EN EL SUELO | A21102400000 | Additional_clients | Wire Down | Include | Include | Equipment | 82 | 2021-10-24 | 83804 | keep | 0 | Oct | 2021 | 0.057079 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-24 13:30 | 2021-10-24 15:50 | 30 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21102400021 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-10-24 | 4200 | keep | 0 | Oct | 2021 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-24 13:43 | 2021-10-24 13:45 | 3718 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21102400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-24 | 7436 | keep | 0 | Oct | 2021 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2021-10-24 14:00 | 2021-10-24 14:01 | 1709 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 1709 | keep | 0 | Oct | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
BAYAMON | 2021-10-24 14:01 | 2021-10-24 14:29 | 6 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21102000026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-10-24 | 168 | keep | 0 | Oct | 2021 | 0.00011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-10-24 14:01 | 2021-10-25 15:37 | 20 | 025:36 | P | CABLE SOTERRADO AVERIADO | 1 X 25 RBA EN SU 19 HACIA EL T 48 QUEDO FUERA EL T 49 | C21102300086 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1536 | 2021-10-24 | 30720 | keep | 0 | Oct | 2021 | 0.020923 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-24 14:18 | 2021-10-24 17:30 | 50 | 003:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21102400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-10-24 | 9600 | keep | 0 | Oct | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-24 14:27 | 2021-10-24 14:28 | 2888 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERURPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A21102400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 2888 | keep | 0 | Oct | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
AGUADILLA | 2021-10-24 14:36 | 2021-10-24 15:40 | 1 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO CONECTORES PRIMARIOS | M21102400044 | New_Event | Wire Down | Include | Include | Equipment | 64 | 2021-10-24 | 64 | keep | 0 | Oct | 2021 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-24 14:39 | 2021-10-24 17:59 | 750 | 003:20 | P | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA ENTRO UN 65% EN SERVICIO | S21102400000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-10-24 | 150000 | keep | 0 | Oct | 2021 | 0.10216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-24 14:39 | 2021-10-24 14:40 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 3941 | keep | 0 | Oct | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
ARECIBO | 2021-10-24 14:50 | 2021-10-25 13:12 | 10 | 022:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR Y 1 X 20 EN CORTE DE LINEA POR MAL TIEMPO | A21102400028 | New_Event | Bad Weather | Include | Include | Weather | 1342 | 2021-10-24 | 13420 | keep | 0 | Oct | 2021 | 0.0091403 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-24 14:51 | 2021-10-24 16:24 | 5 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | C21102400030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2021-10-24 | 465 | keep | 0 | Oct | 2021 | 0.00031671 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-24 14:51 | 2021-10-24 16:40 | 120 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO MACHETES | A21102400000 | Partial_restoration | Wire Down | Include | Include | Equipment | 109 | 2021-10-24 | 13080 | keep | 0 | Oct | 2021 | 0.0089087 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-10-24 14:57 | 2021-10-24 21:34 | 40 | 006:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | M21102400046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 397 | 2021-10-24 | 15880 | keep | 0 | Oct | 2021 | 0.010816 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-24 15:11 | 2021-10-24 19:13 | 2368 | 004:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21102400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2021-10-24 | 573056 | keep | 0 | Oct | 2021 | 0.39031 | 0.0016128 | Sustained | FALSE | TRUE | Not_TMED_Event | 2368
VEGA BAJA | 2021-10-24 15:11 | 2021-10-24 19:13 | 538 | 004:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21102400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2021-10-24 | 130196 | keep | 0 | Oct | 2021 | 0.088676 | 0.00036643 | Sustained | FALSE | TRUE | Not_TMED_Event | 538
VEGA BAJA | 2021-10-24 15:11 | 2021-10-24 19:13 | 1284 | 004:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21102400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2021-10-24 | 310728 | keep | 0 | Oct | 2021 | 0.21164 | 0.00087453 | Sustained | FALSE | TRUE | Not_TMED_Event | 1284
SAN JUAN | 2021-10-24 15:14 | 2021-10-24 18:54 | 150 | 003:40 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. SE REALIZARON OPERACIONES DE CAMPO Y ENTRO UN 100% EN SERVICIO | S21102400000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-10-24 | 33000 | keep | 0 | Oct | 2021 | 0.022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-24 15:24 | 2021-10-24 18:56 | 14 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CONECTORES QUEMADOS | A21102400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2021-10-24 | 2968 | keep | 0 | Oct | 2021 | 0.0020215 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2021-10-24 15:38 | 2021-10-26 11:51 | 40 | 044:13 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVICIONAL AEREO HQACIA EL T - 28 | C21102400032 | New_Event | UG Cable Fault | Include | Include | Equipment | 2653 | 2021-10-24 | 106120 | keep | 0 | Oct | 2021 | 0.072278 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-10-24 16:33 | 2021-10-25 09:53 | 5 | 017:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25 KVA | S21102400167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1040 | 2021-10-24 | 5200 | keep | 0 | Oct | 2021 | 0.0035417 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-10-24 16:42 | 2021-10-25 09:46 | 70 | 017:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C21102400034 | New_Event |  |  | Include | Wildlife | 1024 | 2021-10-24 | 71680 | keep | 0 | Oct | 2021 | 0.048821 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-24 17:10 | 2021-10-24 21:33 | 80 | 004:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO LINEA | M21102400052 | New_Event |  |  | Include | Wildlife | 263 | 2021-10-24 | 21040 | keep | 0 | Oct | 2021 | 0.01433 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-24 17:55 | 2021-10-24 18:25 | 50 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21102400180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2021-10-24 | 1500 | keep | 0 | Oct | 2021 | 0.0010216 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-24 17:59 | 2021-10-24 18:08 | 1802 | 000:09 | T | DESGANCHE | SE REALIZARON OPERACIONES DE CAMPO Y SE DISPARO INTERRUPTOR | S21102400000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 9 | 2021-10-24 | 16218 | keep | 0 | Oct | 2021 | 0.011046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-24 18:07 | 2021-10-24 20:15 | 1979 | 002:08 | S | ANIMAL U OBJETO EXTRAÃ‘O | LOCK OUT TRIP POR DISPARO LINEA 36900 AVE CRUZA EXTRUCTURA CON PARARRAYO 115KV | P21102400019 | New_Event |  |  | Include | Wildlife | 128 | 2021-10-24 | 253312 | keep | 0 | Oct | 2021 | 0.17253 | 0.0013479 | Sustained | FALSE | TRUE | Not_TMED_Event | 1979
PONCE | 2021-10-24 18:07 | 2021-10-24 20:15 | 3114 | 002:08 | S | ANIMAL U OBJETO EXTRAÃ‘O | LOCK OUT TRIP POR DISPARO LINEA 36900 AVE CRUZA EXTRUCTURA CON PARARRAYO 115KV | P21102400019 | New_Event |  |  | Include | Wildlife | 128 | 2021-10-24 | 398592 | keep | 0 | Oct | 2021 | 0.27148 | 0.0021209 | Sustained | FALSE | TRUE | Not_TMED_Event | 3114
PONCE | 2021-10-24 18:07 | 2021-10-24 20:15 | 5069 | 002:08 | S | ANIMAL U OBJETO EXTRAÃ‘O | LOCK OUT TRIP POR DISPARO LINEA 36900 AVE CRUZA EXTRUCTURA CON PARARRAYO 115KV | P21102400019 | New_Event |  |  | Include | Wildlife | 128 | 2021-10-24 | 648832 | keep | 0 | Oct | 2021 | 0.44192 | 0.0034525 | Sustained | FALSE | TRUE | Not_TMED_Event | 5069
PONCE | 2021-10-24 18:07 | 2021-10-24 20:15 | 2696 | 002:08 | S | ANIMAL U OBJETO EXTRAÃ‘O | LOCK OUT TRIP POR DISPARO LINEA 36900 AVE CRUZA EXTRUCTURA CON PARARRAYO 115KV | P21102400019 | New_Event |  |  | Include | Wildlife | 128 | 2021-10-24 | 345088 | keep | 0 | Oct | 2021 | 0.23504 | 0.0018362 | Sustained | FALSE | TRUE | Not_TMED_Event | 2696
PONCE | 2021-10-24 18:07 | 2021-10-24 20:15 | 5063 | 002:08 | S | ANIMAL U OBJETO EXTRAÃ‘O | LOCK OUT TRIP POR DISPARO LINEA 36900 AVE CRUZA EXTRUCTURA CON PARARRAYO 115KV | P21102400019 | New_Event |  |  | Include | Wildlife | 128 | 2021-10-24 | 648064 | keep | 0 | Oct | 2021 | 0.44139 | 0.0034484 | Sustained | FALSE | TRUE | Not_TMED_Event | 5063
BAYAMON | 2021-10-24 18:08 | 2021-10-24 18:29 | 950 | 000:21 | P | DESGANCHE | SE REALIZARON OPERACIONES DE CAMPO Y ENTRO UN 100% EN SERVICIO. SE DEJO SECCIONALIZADO PARCIAL DEL 1346-02 QUE ESTA POR EL 1529-15 Y SE ATENDERA MAÃ‘ANA | S21102400000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 21 | 2021-10-24 | 19950 | keep | 0 | Oct | 2021 | 0.013588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-24 18:15 | 2021-10-25 11:00 | 15 | 016:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO MASETILLA | A21102400039 | New_Event | Cutout Failure | Include | Include | Equipment | 1005 | 2021-10-24 | 15075 | keep | 0 | Oct | 2021 | 0.010268 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-10-24 18:17 | 2021-10-25 11:07 | 60 | 016:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | C21102400036 | New_Event | Wire Down | Include | Include | Equipment | 1010 | 2021-10-24 | 60600 | keep | 0 | Oct | 2021 | 0.041274 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-24 18:29 | 2021-10-25 15:52 | 950 | 021:23 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA SE REALIZARON OPERACIONES DE CAMPO Y ENTRO UN 100% | S21102400000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1283 | 2021-10-24 | 1218850 | keep | 0 | Oct | 2021 | 0.83015 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-10-24 18:54 | 2021-10-24 18:57 | 1681 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA ADEMAS LLEVA LA CARGA DEL 1303-01 Y 1346-06 CARGA POR EL 1303-04 | S21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-24 | 5043 | keep | 0 | Oct | 2021 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-24 18:54 | 2021-10-24 18:57 | 1598 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA ADEMAS LLEVA LA CARGA DEL 1303-01 Y CARGA POR EL 1303-04 | S21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-24 | 4794 | keep | 0 | Oct | 2021 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-10-24 19:00 | 2021-10-24 19:01 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 1533 | keep | 0 | Oct | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
UTUADO | 2021-10-24 19:07 | 2021-10-25 10:54 | 200 | 015:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | A21102400041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 947 | 2021-10-24 | 189400 | keep | 0 | Oct | 2021 | 0.129 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-10-24 19:16 | 2021-10-24 19:17 | 538 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21102400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 538 | keep | 0 | Oct | 2021 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2021-10-24 19:17 | 2021-10-25 10:11 | 40 | 014:54 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA PRINCIPAL Y 1 X 65 EN CORTE DE LINEA INTERMEDIO | B21102400155 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 894 | 2021-10-24 | 35760 | keep | 0 | Oct | 2021 | 0.024356 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-24 19:18 | 2021-10-24 23:41 | 400 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | S21102400019 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2021-10-24 | 105200 | keep | 0 | Oct | 2021 | 0.071651 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
BAYAMON | 2021-10-24 19:33 | 2021-10-25 11:32 | 30 | 015:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REMPLAZO AISLADOR | S21102400200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 959 | 2021-10-24 | 28770 | keep | 0 | Oct | 2021 | 0.019595 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-10-24 19:49 | 2021-10-24 23:50 | 300 | 004:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO DOS CAJAS PRIMARIAS AVERIADAS DE 200 AMP | P21102400042 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2021-10-24 | 72300 | keep | 0 | Oct | 2021 | 0.049243 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-10-24 20:24 | 2021-10-25 12:24 | 6 | 016:00 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | C21102400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 960 | 2021-10-24 | 5760 | keep | 0 | Oct | 2021 | 0.0039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-24 20:29 | 2021-10-24 21:33 | 6 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21102400136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-10-24 | 384 | keep | 0 | Oct | 2021 | 0.00026154 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-10-24 20:57 | 2021-10-24 20:58 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21102400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 1533 | keep | 0 | Oct | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
HUMACAO | 2021-10-24 21:10 | 2021-10-25 11:02 | 7 | 013:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21102400039 | New_Event | Bad Weather | Include | Include | Weather | 832 | 2021-10-24 | 5824 | keep | 0 | Oct | 2021 | 0.0039667 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-24 21:41 | 2021-10-25 17:08 | 25 | 019:27 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR Y 1 X 10 EN RISER SE REALIZO DESGANCHE | B21102400150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1167 | 2021-10-24 | 29175 | keep | 0 | Oct | 2021 | 0.019871 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-10-24 22:22 | 2021-10-25 15:18 | 1 | 016:56 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | S21102400214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1016 | 2021-10-24 | 1016 | keep | 0 | Oct | 2021 | 0.00069199 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-24 22:31 | 2021-10-24 22:55 | 40 | 000:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21102400154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2021-10-24 | 960 | keep | 0 | Oct | 2021 | 0.00065385 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-24 23:55 | 2021-10-24 23:56 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21102400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-24 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
BAYAMON | 2021-10-25 00:21 | 2021-10-25 11:07 | 50 | 010:46 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21102500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 646 | 2021-10-25 | 32300 | keep | 0 | Oct | 2021 | 0.021999 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-25 00:31 | 2021-10-25 10:28 | 15 | 009:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21102500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 597 | 2021-10-25 | 8955 | keep | 0 | Oct | 2021 | 0.0060992 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-25 02:41 | 2021-10-25 02:42 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO 50% DEL 9405-05 | B21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 3597 | keep | 0 | Oct | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
FAJARDO | 2021-10-25 02:41 | 2021-10-25 07:55 | 2286 | 005:14 | S | LINEA DE TRANSMISION 38KV | SE REEMPLAZO AISLADOR ROTO EN LA LINEA 3100 | R21102500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 314 | 2021-10-25 | 717804 | keep | 0 | Oct | 2021 | 0.48889 | 0.001557 | Sustained | FALSE | TRUE | Not_TMED_Event | 2286
FAJARDO | 2021-10-25 02:41 | 2021-10-25 07:55 | 693 | 005:14 | S | LINEA DE TRANSMISION 38KV | SE REEMPLAZO AISLADOR ROTO EN LA LINEA 3100 | R21102500004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 314 | 2021-10-25 | 217602 | keep | 0 | Oct | 2021 | 0.14821 | 0.000472 | Sustained | FALSE | TRUE | Not_TMED_Event | 693
BAYAMON | 2021-10-25 02:41 | 2021-10-25 02:42 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1719-15 LLEVANDO 50% DEL 9405-05 | B21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 1500 | keep | 0 | Oct | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
FAJARDO | 2021-10-25 02:48 | 2021-10-25 11:30 | 1001 | 008:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE DE MACHETE A LINEA | R21102500005 | New_Event | Wire Down | Include | Include | Equipment | 522 | 2021-10-25 | 522522 | keep | 0 | Oct | 2021 | 0.35589 | 0.00068178 | Sustained | FALSE | TRUE | Not_TMED_Event | 1001
BAYAMON | 2021-10-25 04:15 | 2021-10-25 10:45 | 5 | 006:30 | P | NO SE REPORTO CAUSA | SE REPUSO 3 X 125 FUSIBLES TIPO SMU EN SU 9 | B21102500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 390 | 2021-10-25 | 1950 | keep | 0 | Oct | 2021 | 0.0013281 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-25 04:29 | 2021-10-25 18:11 | 7 | 013:42 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 100 KVA | R21102500027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 822 | 2021-10-25 | 5754 | keep | 0 | Oct | 2021 | 0.003919 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-25 05:08 | 2021-10-25 05:09 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21102500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 990 | keep | 0 | Oct | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2021-10-25 05:09 | 2021-10-25 05:10 | 485 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1404-09 LLEVANDO LA CARGA DEL 1420-05 | S21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 485 | keep | 0 | Oct | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2021-10-25 05:09 | 2021-10-25 05:10 | 4 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1404-09 LLEVANDO LA CARGA DEL 1420-05 | S21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 4 | keep | 0 | Oct | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-25 05:09 | 2021-10-25 16:40 | 1 | 011:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 200AMP EN RISER | M21102500058 | New_Event | Cutout Failure | Include | Include | Equipment | 691 | 2021-10-25 | 691 | keep | 0 | Oct | 2021 | 0.00047064 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-10-25 05:22 | 2021-10-25 05:23 | 2635 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR EN SERVICIO | C21102500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-25 | 2635 | keep | 0 | Oct | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-10-25 05:23 | 2021-10-25 15:01 | 190 | 009:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIAS | C21102500006 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 578 | 2021-10-25 | 109820 | keep | 0 | Oct | 2021 | 0.074798 | 0.00012941 | Sustained | FALSE | TRUE | Not_TMED_Event | 190
FAJARDO | 2021-10-25 05:30 | 2021-10-25 10:00 | 5 | 004:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR REPTIL | R21102500030 | New_Event |  |  | Include | Wildlife | 270 | 2021-10-25 | 1350 | keep | 0 | Oct | 2021 | 0.00091948 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-25 05:31 | 2021-10-25 11:58 | 20 | 006:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO CULEBRA CRUZANDO LINEAS | B21102500008 | New_Event |  |  | Include | Wildlife | 387 | 2021-10-25 | 7740 | keep | 0 | Oct | 2021 | 0.0052717 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-25 05:40 | 2021-10-25 05:41 | 4381 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | M21102500010 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-25 | 4381 | keep | 0 | Oct | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-10-25 05:41 | 2021-10-25 17:15 | 1 | 011:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 100 AMP EN RISER | M21102500075 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 694 | 2021-10-25 | 694 | keep | 0 | Oct | 2021 | 0.00047268 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-25 05:57 | 2021-10-25 09:21 | 40 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21102500032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-10-25 | 8160 | keep | 0 | Oct | 2021 | 0.0055577 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-25 06:01 | 2021-10-25 18:03 | 10 | 012:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21102500010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 722 | 2021-10-25 | 7220 | keep | 0 | Oct | 2021 | 0.0049175 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-10-25 06:03 | 2021-10-25 06:52 | 3012 | 000:49 | T | NO SE REPORTO CAUSA | DISPARO NO RTU | C21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2021-10-25 | 147588 | keep | 0 | Oct | 2021 | 0.10052 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2021-10-25 06:08 | 2021-10-25 09:11 | 70 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | R21102500033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-10-25 | 12810 | keep | 0 | Oct | 2021 | 0.0087248 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-10-25 06:35 | 2021-10-25 08:14 | 12 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REMPLAZO BUSHING CAJA PRIMARIA | S21102500013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2021-10-25 | 1188 | keep | 0 | Oct | 2021 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-10-25 06:39 | 2021-10-26 11:40 | 10 | 029:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | P21102500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1741 | 2021-10-25 | 17410 | keep | 0 | Oct | 2021 | 0.011858 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-25 06:44 | 2021-10-25 16:06 | 100 | 009:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA | A21102500005 | New_Event | Bad Weather | Include | Include | Weather | 562 | 2021-10-25 | 56200 | keep | 0 | Oct | 2021 | 0.038278 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-25 06:53 | 2021-10-25 16:58 | 150 | 010:05 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA | S21102500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 605 | 2021-10-25 | 90750 | keep | 0 | Oct | 2021 | 0.061809 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-10-25 07:03 | 2021-10-25 16:36 | 60 | 009:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO | A21102500006 | New_Event | Bad Weather | Include | Include | Weather | 573 | 2021-10-25 | 34380 | keep | 0 | Oct | 2021 | 0.023416 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-10-25 07:14 | 2021-10-25 11:06 | 10 | 003:52 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21102500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2021-10-25 | 2320 | keep | 0 | Oct | 2021 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-25 07:15 | 2021-10-25 11:43 | 10 | 004:28 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21102500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2021-10-25 | 2680 | keep | 0 | Oct | 2021 | 0.0018253 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-25 07:17 | 2021-10-25 12:21 | 12 | 005:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21102500016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 304 | 2021-10-25 | 3648 | keep | 0 | Oct | 2021 | 0.0024846 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-10-25 07:23 | 2021-10-25 10:13 | 90 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | M21102500012 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2021-10-25 | 15300 | keep | 0 | Oct | 2021 | 0.010421 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
VEGA BAJA | 2021-10-25 07:54 | 2021-10-25 07:55 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 3332 | keep | 0 | Oct | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
ARECIBO | 2021-10-25 07:58 | 2021-10-25 16:37 | 6 | 008:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A21102500011 | New_Event | Wire Down | Include | Include | Equipment | 519 | 2021-10-25 | 3114 | keep | 0 | Oct | 2021 | 0.0021209 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-25 08:13 | 2021-10-25 11:34 | 100 | 003:21 | P | DESGANCHE | 1 X 40 Y 1 X 65 EN CORTE DE LINEA | R21102500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-10-25 | 20100 | keep | 0 | Oct | 2021 | 0.01369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 600 | 000:06 | P | LINEA DE TRANSMISION 115KV | DISPARO L-36200 20% DE LA CARGA POR EL 1303-02 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 3600 | keep | 0 | Oct | 2021 | 0.0024519 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 108 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 648 | keep | 0 | Oct | 2021 | 0.00044135 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 1368 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 8208 | keep | 0 | Oct | 2021 | 0.0055904 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 2064 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 12384 | keep | 0 | Oct | 2021 | 0.0084347 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 1681 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 LLEVA 1346-6 Y 1303-1 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 10086 | keep | 0 | Oct | 2021 | 0.0068695 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 2435 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 LLEVA 20% 1204-2 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 14610 | keep | 0 | Oct | 2021 | 0.0099508 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 726 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 4356 | keep | 0 | Oct | 2021 | 0.0029669 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 225 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 1350 | keep | 0 | Oct | 2021 | 0.00091948 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 870 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 5220 | keep | 0 | Oct | 2021 | 0.0035553 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 3932 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CARGA POR EL 1303-03 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 23592 | keep | 0 | Oct | 2021 | 0.016068 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-10-25 08:14 | 2021-10-25 08:20 | 1598 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 LLEVA 1346-6 Y 1303-1 CARGA POR EL 1303-04 | S21102500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-10-25 | 9588 | keep | 0 | Oct | 2021 | 0.0065303 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2021-10-25 08:18 | 2021-10-25 10:36 | 5 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21102500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-10-25 | 690 | keep | 0 | Oct | 2021 | 0.00046996 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-10-25 08:20 | 2021-10-25 13:49 | 12 | 005:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REMPLAZO BUSHING CAJA PRIMARIA | S21102500013 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 329 | 2021-10-25 | 3948 | keep | 0 | Oct | 2021 | 0.002689 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-25 08:20 | 2021-10-25 13:06 | 80 | 004:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21102500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-10-25 | 22880 | keep | 0 | Oct | 2021 | 0.015583 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-25 08:29 | 2021-10-25 16:10 | 20 | 007:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE INSTALO AISLADOR EN POSTE PARA SEPARAR PUENTE PRIMARIO DE POSTE | A21102500016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 461 | 2021-10-25 | 9220 | keep | 0 | Oct | 2021 | 0.0062797 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-10-25 08:30 | 2021-10-25 18:00 | 400 | 009:30 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA QUE PERSONAL PRIVADO REALIZARA DESGANCHE MASIVO EN EL AREA | A21102500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 570 | 2021-10-25 | 228000 | keep | 0 | Oct | 2021 | 0.15529 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
ARECIBO | 2021-10-25 08:32 | 2021-10-25 12:40 | 3 | 004:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21102500017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2021-10-25 | 744 | keep | 0 | Oct | 2021 | 0.00050674 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-25 08:42 | 2021-10-25 13:40 | 194 | 004:58 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21102500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2021-10-25 | 57812 | keep | 0 | Oct | 2021 | 0.039375 | 0.00013213 | Sustained | FALSE | TRUE | Not_TMED_Event | 194
SAN JUAN | 2021-10-25 08:44 | 2021-10-25 12:08 | 99 | 003:24 | T | OTRAS CAUSAS | SE CERRO EL INTERRUPTOR NO RTU LLEVA LA CARGA DEL 1647-07 PROA DE PLAZA CAROLINA | R21102500066 | New_Event | Other Causes | Include | Include | Other | 204 | 2021-10-25 | 20196 | keep | 0 | Oct | 2021 | 0.013755 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
SAN JUAN | 2021-10-25 08:44 | 2021-10-25 12:08 | 31 | 003:24 | T | OTRAS CAUSAS | CARGAS POR EL 1647-06 PROA DE PLAZA CAROLINA | R21102500066 | New_Event | Other Causes | Include | Include | Other | 204 | 2021-10-25 | 6324 | keep | 0 | Oct | 2021 | 0.0043072 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
ARECIBO | 2021-10-25 08:44 | 2021-10-25 13:07 | 30 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE ENCONTRO LINEA CRUZADA | A21102500018 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2021-10-25 | 7890 | keep | 0 | Oct | 2021 | 0.0053738 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-25 08:46 | 2021-10-25 12:01 | 5 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21102500019 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2021-10-25 | 975 | keep | 0 | Oct | 2021 | 0.00066407 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-25 09:03 | 2021-10-25 19:13 | 15 | 010:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | S21102500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 610 | 2021-10-25 | 9150 | keep | 0 | Oct | 2021 | 0.006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-10-25 09:05 | 2021-10-25 12:10 | 80 | 003:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21102500021 | New_Event | Wire Down | Include | Include | Equipment | 185 | 2021-10-25 | 14800 | keep | 0 | Oct | 2021 | 0.01008 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-25 09:06 | 2021-10-25 09:07 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21102500037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-10-25 09:07 | 2021-10-25 19:17 | 1 | 010:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21102500114 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 610 | 2021-10-25 | 610 | keep | 0 | Oct | 2021 | 0.00041547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-25 09:08 | 2021-10-25 11:03 | 7 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21102500023 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-10-25 | 805 | keep | 0 | Oct | 2021 | 0.00054828 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-25 09:08 | 2021-10-25 11:08 | 70 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | M21102500024 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-10-25 | 8400 | keep | 0 | Oct | 2021 | 0.0057212 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-25 09:09 | 2021-10-25 13:49 | 1 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER MAL TIEMPO | M21102500026 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2021-10-25 | 280 | keep | 0 | Oct | 2021 | 0.00019071 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-25 09:11 | 2021-10-25 18:00 | 60 | 008:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 EN CORTE DE LINEA SE REEMPLAZO | C21102500020 | New_Event | Cutout Failure | Include | Include | Equipment | 529 | 2021-10-25 | 31740 | keep | 0 | Oct | 2021 | 0.021618 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-25 09:39 | 2021-10-25 12:19 | 1 | 002:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA POR 15 KVA | B21102500040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 160 | 2021-10-25 | 160 | keep | 0 | Oct | 2021 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-25 09:53 | 2021-10-25 10:03 | 10211 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA Y SE PROBO INTERRUPTOR QUEDO EN SERVICIO CARGA POR EL 1206-03 | S21102500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-10-25 | 102110 | keep | 0 | Oct | 2021 | 0.069547 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-10-25 09:53 | 2021-10-25 10:03 | 4133 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA Y SE PROBO INTERRUPTOR QUEDO EN SERVICIO LLEVA 1204-05 | S21102500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-10-25 | 41330 | keep | 0 | Oct | 2021 | 0.02815 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
ARECIBO | 2021-10-25 10:00 | 2021-10-25 13:00 | 100 | 003:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR AISLADORES | A21102500026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 180 | 2021-10-25 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-25 10:03 | 2021-10-25 13:33 | 4133 | 003:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25 KVA POR UNO DE 25 KVA | S21102400167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2021-10-25 | 867930 | keep | 0 | Oct | 2021 | 0.59114 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-25 10:05 | 2021-10-26 11:23 | 15 | 025:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21102500121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1518 | 2021-10-25 | 22770 | keep | 0 | Oct | 2021 | 0.015509 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-25 10:05 | 2021-10-26 09:58 | 10 | 023:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21102500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1433 | 2021-10-25 | 14330 | keep | 0 | Oct | 2021 | 0.0097601 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-25 10:05 | 2021-10-25 15:13 | 15 | 005:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21102500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2021-10-25 | 4620 | keep | 0 | Oct | 2021 | 0.0031467 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-25 10:06 | 2021-10-25 16:28 | 1 | 006:22 | P | OTRAS CAUSAS | 1 X 20 EN CORTE DE LINEA PROBLEMA DEL CLIENTE | C21102500026 | New_Event | Other Causes | Include | Include | Other | 382 | 2021-10-25 | 382 | keep | 0 | Oct | 2021 | 0.00026018 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-10-25 10:10 | 2021-10-25 12:20 | 150 | 002:10 | P | ERROR HUMANO | 1 X 65 EN CORTE DE LINEA POR PERSONAL DESGANCHANDO | A21102500022 | New_Event | Human Error | Include | Include | Other | 130 | 2021-10-25 | 19500 | keep | 0 | Oct | 2021 | 0.013281 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-10-25 10:20 | 2021-10-25 15:45 | 40 | 005:25 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO PARTIDO EN EL FID:33721989 DE MADERA CLASE 4 45' | A21102500027 | New_Event | Defective Pole | Include | Include | Equipment | 325 | 2021-10-25 | 13000 | keep | 0 | Oct | 2021 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-10-25 10:26 | 2021-10-25 15:18 | 1 | 004:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA DESCARAS ELECTRICAS | M21102500040 | New_Event | Bad Weather | Include | Include | Weather | 292 | 2021-10-25 | 292 | keep | 0 | Oct | 2021 | 0.00019888 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-10-25 10:30 | 2021-10-25 17:06 | 10 | 006:36 | P | OTRAS CAUSAS | 1 X 12 EN TRANSFORMADOR TIPO PM POR CRUCE DE TOMA DE SOTERRADA DEL CLIENTE SE DESCONECTO PARA QUE CLIENTE REPARE LA TOMA | P21102500026 | New_Event | Other Causes | Include | Include | Other | 396 | 2021-10-25 | 3960 | keep | 0 | Oct | 2021 | 0.0026971 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-25 10:35 | 2021-10-25 12:04 | 40 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN AEREO PROVISIONAL | B21102500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-10-25 | 3560 | keep | 0 | Oct | 2021 | 0.0024247 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-10-25 10:39 | 2021-10-25 14:14 | 20 | 003:35 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRANSFORMADOR | B21102500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-10-25 | 4300 | keep | 0 | Oct | 2021 | 0.0029287 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-25 10:43 | 2021-10-25 12:05 | 1 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR AVE CRUZO LINEAS | M21102500043 | New_Event |  |  | Include | Wildlife | 82 | 2021-10-25 | 82 | keep | 0 | Oct | 2021 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-10-25 10:51 | 2021-10-25 13:46 | 70 | 002:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C21102500030 | New_Event |  |  | Include | Wildlife | 175 | 2021-10-25 | 12250 | keep | 0 | Oct | 2021 | 0.0083434 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BARRANQUITAS | 2021-10-25 10:51 | 2021-10-25 14:23 | 20 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | C21102500011 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-10-25 | 4240 | keep | 0 | Oct | 2021 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-25 11:03 | 2021-10-25 13:08 | 60 | 002:05 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | M21102500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-10-25 | 7500 | keep | 0 | Oct | 2021 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-25 11:06 | 2021-10-25 11:07 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 2147 | keep | 0 | Oct | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-10-25 11:26 | 2021-10-25 16:31 | 100 | 005:05 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTE DE LINEA | S21102500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2021-10-25 | 30500 | keep | 0 | Oct | 2021 | 0.020773 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-25 11:27 | 2021-10-25 11:29 | 2234 | 000:02 | T | DESGANCHE | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | B21102500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-10-25 | 4468 | keep | 0 | Oct | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-10-25 11:29 | 2021-10-25 13:46 | 20 | 002:17 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN AEREO PROVISIONAL AVERIA DE T 15 A T 16 | B21102500071 | New_Event | UG Cable Fault | Include | Include | Equipment | 137 | 2021-10-25 | 2740 | keep | 0 | Oct | 2021 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-25 11:29 | 2021-10-25 23:30 | 100 | 012:01 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO | B21102500071 | New_Event | UG Cable Fault | Include | Include | Equipment | 721 | 2021-10-25 | 72100 | keep | 0 | Oct | 2021 | 0.049107 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-10-25 11:29 | 2021-10-25 16:00 | 40 | 004:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESHANCHE | B21102500018 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 271 | 2021-10-25 | 10840 | keep | 0 | Oct | 2021 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-25 11:30 | 2021-10-25 12:15 | 7 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21102500021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-10-25 | 315 | keep | 0 | Oct | 2021 | 0.00021455 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-10-25 11:30 | 2021-10-25 14:29 | 60 | 002:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21102500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2021-10-25 | 10740 | keep | 0 | Oct | 2021 | 0.007315 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-10-25 12:12 | 2021-10-25 17:23 | 53 | 005:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C21102500037 | New_Event |  |  | Include | Wildlife | 311 | 2021-10-25 | 16483 | keep | 0 | Oct | 2021 | 0.011226 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
CAGUAS | 2021-10-25 12:13 | 2021-10-26 11:45 | 100 | 023:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21102500098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1412 | 2021-10-25 | 141200 | keep | 0 | Oct | 2021 | 0.096171 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-25 12:45 | 2021-10-25 15:41 | 50 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21102500087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2021-10-25 | 8800 | keep | 0 | Oct | 2021 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-10-25 13:00 | 2021-10-25 17:42 | 8 | 004:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ELIMINO TRANSFORMADOR CON DIFICIL ACCESO Y CON SECUNDARIA AVERIADA, DE 37.5KVA A 4.16KV POR UNO DE 50 KVA A 4.16KV EN AREA DE MAS FACIL ACCESO PARA DAR SERVICIO. | P21102500037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 282 | 2021-10-25 | 2256 | keep | 0 | Oct | 2021 | 0.0015366 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-10-25 13:01 | 2021-10-25 13:45 | 8 | 000:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21102500091 | New_Event |  |  | Include | Wildlife | 44 | 2021-10-25 | 352 | keep | 0 | Oct | 2021 | 0.00023975 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-25 13:08 | 2021-10-25 20:36 | 40 | 007:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21102500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-10-25 | 17920 | keep | 0 | Oct | 2021 | 0.012205 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-25 13:15 | 2021-10-25 16:22 | 34 | 003:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 37.5KVA | C21102500044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 187 | 2021-10-25 | 6358 | keep | 0 | Oct | 2021 | 0.0043304 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CANOVANAS | 2021-10-25 13:16 | 2021-10-26 13:00 | 10 | 023:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA SE PATRULLO | R21102500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1424 | 2021-10-25 | 14240 | keep | 0 | Oct | 2021 | 0.0096988 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-25 13:17 | 2021-10-25 17:53 | 100 | 004:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTES DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21102500045 | New_Event | Wire Down | Include | Include | Equipment | 276 | 2021-10-25 | 27600 | keep | 0 | Oct | 2021 | 0.018798 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-25 13:18 | 2021-10-25 18:47 | 34 | 005:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO | C21102500046 | New_Event | Wire Down | Include | Include | Equipment | 329 | 2021-10-25 | 11186 | keep | 0 | Oct | 2021 | 0.0076187 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2021-10-25 13:29 | 2021-10-25 15:57 | 20 | 002:28 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21102500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2021-10-25 | 2960 | keep | 0 | Oct | 2021 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-10-25 13:30 | 2021-10-25 17:00 | 130 | 003:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21102500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-10-25 | 27300 | keep | 0 | Oct | 2021 | 0.018594 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
UTUADO | 2021-10-25 13:31 | 2021-10-25 14:55 | 1 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A21102500047 | New_Event |  |  | Include | Wildlife | 84 | 2021-10-25 | 84 | keep | 0 | Oct | 2021 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-25 13:35 | 2021-10-26 14:55 | 100 | 025:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102500069 | New_Event | Bad Weather | Include | Include | Weather | 1520 | 2021-10-25 | 152000 | keep | 0 | Oct | 2021 | 0.10353 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-25 13:56 | 2021-10-25 16:53 | 15 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | B21102500097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-10-25 | 2655 | keep | 0 | Oct | 2021 | 0.0018083 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-25 13:59 | 2021-10-26 14:31 | 10 | 024:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21102500125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1472 | 2021-10-25 | 14720 | keep | 0 | Oct | 2021 | 0.010026 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-10-25 14:01 | 2021-10-25 20:10 | 20 | 006:09 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE DEJO RISER ABIERTO POR TERMIINACION AVERIADA SE DEJO SECCIONALIZADO SE CERRO N/O DEL T-3 AL T-4 QUEDANDO TODO EN SERVICIO. | P21102500041 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 369 | 2021-10-25 | 7380 | keep | 0 | Oct | 2021 | 0.0050265 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-10-25 14:17 | 2021-10-25 17:59 | 6 | 003:42 | P | SECUNDARIA/DESGANCHE | DESGANCHE Y REPARO SECUNDARIA | R21102500095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 222 | 2021-10-25 | 1332 | keep | 0 | Oct | 2021 | 0.00090722 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-10-25 14:22 | 2021-10-25 15:48 | 6 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21102500097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-10-25 | 516 | keep | 0 | Oct | 2021 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-10-25 14:27 | 2021-10-25 14:28 | 2694 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21102500051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 2694 | keep | 0 | Oct | 2021 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
FAJARDO | 2021-10-25 14:29 | 2021-10-25 16:20 | 9 | 001:51 | P | ESTRUCTURA AVERIADA | SE ELIMINO POSTE PARTIDO Y RETEZO LINEAS | R21102500098 | New_Event | Defective Pole | Include | Include | Equipment | 111 | 2021-10-25 | 999 | keep | 0 | Oct | 2021 | 0.00068041 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
AGUADILLA | 2021-10-25 14:50 | 2021-10-25 17:10 | 25 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M21102500055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2021-10-25 | 3500 | keep | 0 | Oct | 2021 | 0.0023838 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-10-25 14:59 | 2021-10-25 19:25 | 30 | 004:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 200 AMP EN CORTE DE LINEA | M21102500082 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2021-10-25 | 7980 | keep | 0 | Oct | 2021 | 0.0054351 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-10-25 15:08 | 2021-10-25 19:27 | 325 | 004:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA ZAFADA DE AISLADOR | M21102500083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 259 | 2021-10-25 | 84175 | keep | 0 | Oct | 2021 | 0.057331 | 0.00022136 | Sustained | FALSE | TRUE | Not_TMED_Event | 325
CAGUAS | 2021-10-25 15:31 | 2021-10-25 19:52 | 70 | 004:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-10-25 | 18270 | keep | 0 | Oct | 2021 | 0.012444 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-10-25 15:34 | 2021-10-25 18:51 | 30 | 003:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21102500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-10-25 | 5910 | keep | 0 | Oct | 2021 | 0.0040253 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-25 15:37 | 2021-10-25 19:20 | 70 | 003:43 | P | CABLE SOTERRADO AVERIADO | AVERIAS DEL T49 AL T50 Y T32 AL T33 SE COSNTRUYO AEREO PROVICIONAL DE EXISTENTE | C21102400031 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 223 | 2021-10-25 | 15610 | keep | 0 | Oct | 2021 | 0.010632 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-25 15:40 | 2021-10-25 18:13 | 610 | 002:33 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21102500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-10-25 | 93330 | keep | 0 | Oct | 2021 | 0.063567 | 0.00041547 | Sustained | FALSE | FALSE | Not_TMED_Event | 610
SAN JUAN | 2021-10-25 15:55 | 2021-10-25 20:21 | 20 | 004:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 POR 50 KVA | S21102500093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 266 | 2021-10-25 | 5320 | keep | 0 | Oct | 2021 | 0.0036234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-10-25 16:00 | 2021-10-25 16:01 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2021-10-25 16:21 | 2021-10-25 17:24 | 12 | 001:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR EN EL FID:19930783 MARCA:CHINT 100AMP | A21102500061 | New_Event | Cutout Failure | Include | Include | Equipment | 63 | 2021-10-25 | 756 | keep | 0 | Oct | 2021 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-10-25 16:39 | 2021-10-26 08:53 | 80 | 016:14 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTE DE LINEA | C21102500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 974 | 2021-10-25 | 77920 | keep | 0 | Oct | 2021 | 0.053071 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-10-25 16:41 | 2021-10-25 16:42 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21102500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 527 | keep | 0 | Oct | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
BAYAMON | 2021-10-25 16:44 | 2021-10-25 17:45 | 9 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | S21102500060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-10-25 | 549 | keep | 0 | Oct | 2021 | 0.00037392 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-10-25 16:45 | 2021-10-26 16:51 | 300 | 024:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21102500091 | New_Event | Wire Down | Include | Include | Equipment | 1446 | 2021-10-25 | 433800 | keep | 0 | Oct | 2021 | 0.29546 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
PONCE | 2021-10-25 17:08 | 2021-10-26 09:05 | 32 | 015:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA SE RETIRO GLOBO DE HELIO DE LINEA PRIMARIA | P21102500056 | New_Event |  |  | Include | Wildlife | 957 | 2021-10-25 | 30624 | keep | 0 | Oct | 2021 | 0.020858 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
YAUCO | 2021-10-25 17:11 | 2021-10-26 13:10 | 96 | 019:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21102500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1199 | 2021-10-25 | 115104 | keep | 0 | Oct | 2021 | 0.078397 | 6.5385e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 96
BAYAMON | 2021-10-25 17:14 | 2021-10-25 17:15 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 99% DEL 1909-09 | S21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 222 | keep | 0 | Oct | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-10-25 17:14 | 2021-10-25 17:15 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO EL 99% DE LA CARGA SE ENCUENTRA POR EL 1907-03 | S21102500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-25 | 4456 | keep | 0 | Oct | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
FAJARDO | 2021-10-25 17:15 | 2021-10-25 18:12 | 5 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21102500113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-10-25 | 285 | keep | 0 | Oct | 2021 | 0.00019411 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-25 17:26 | 2021-10-25 20:22 | 1 | 002:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21102500115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 176 | 2021-10-25 | 176 | keep | 0 | Oct | 2021 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-25 17:26 | 2021-10-26 13:01 | 10 | 019:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 X 37.5 AVERIADO | B21102500116 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1175 | 2021-10-25 | 11750 | keep | 0 | Oct | 2021 | 0.0080029 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-25 17:29 | 2021-10-25 18:47 | 75 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21102500117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-10-25 | 5850 | keep | 0 | Oct | 2021 | 0.0039844 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-10-25 17:30 | 2021-10-26 13:40 | 1 | 020:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA | M21102500100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1210 | 2021-10-25 | 1210 | keep | 0 | Oct | 2021 | 0.00082413 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-25 18:23 | 2021-10-25 21:32 | 150 | 003:09 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA | M21102500102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-10-25 | 28350 | keep | 0 | Oct | 2021 | 0.019309 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-10-25 19:00 | 2021-10-26 10:54 | 20 | 015:54 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T 13 HACIA T 14 CERRO N/O EN T 15 HACIA T 14 | C21102500071 | New_Event | UG Cable Fault | Include | Include | Equipment | 954 | 2021-10-25 | 19080 | keep | 0 | Oct | 2021 | 0.012995 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-10-25 19:08 | 2021-10-25 20:03 | 200 | 000:55 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | P21102500067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-10-25 | 11000 | keep | 0 | Oct | 2021 | 0.007492 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-10-25 19:09 | 2021-10-27 14:12 | 1 | 043:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA RETEZO CONDUCTOR | C21102500072 | New_Event | Wire Down | Include | Include | Equipment | 2583 | 2021-10-25 | 2583 | keep | 0 | Oct | 2021 | 0.0017593 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-10-25 19:14 | 2021-10-26 11:20 | 39 | 016:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CURCE CON AVE | R21102500120 | New_Event |  |  | Include | Wildlife | 966 | 2021-10-25 | 37674 | keep | 0 | Oct | 2021 | 0.02566 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
MAYAGÃœEZ | 2021-10-25 19:16 | 2021-10-26 11:20 | 1 | 016:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102500106 | New_Event | Bad Weather | Include | Include | Weather | 964 | 2021-10-25 | 964 | keep | 0 | Oct | 2021 | 0.00065658 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-10-25 19:27 | 2021-10-25 19:42 | 997 | 000:15 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA ZAFADA DE AISLADOR NO HAY PARCIAL | M21102500107 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 15 | 2021-10-25 | 14955 | keep | 0 | Oct | 2021 | 0.010186 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-10-25 19:35 | 2021-10-25 19:42 | 1497 | 000:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA ZAFADA DE AISLADOR PARTE DE LA CARGA TRANSFERIDA DEL 7201-04 | M21102500108 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 7 | 2021-10-25 | 10479 | keep | 0 | Oct | 2021 | 0.0071372 | 0.0010196 | Sustained | FALSE | TRUE | Not_TMED_Event | 1497
UTUADO | 2021-10-25 19:37 | 2021-10-26 09:52 | 8 | 014:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21102500068 | New_Event | Bad Weather | Include | Include | Weather | 855 | 2021-10-25 | 6840 | keep | 0 | Oct | 2021 | 0.0046587 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-25 19:42 | 2021-10-25 22:23 | 325 | 002:41 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA ZAFADA DE AISLADOR | M21102500083 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 161 | 2021-10-25 | 52325 | keep | 0 | Oct | 2021 | 0.035638 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-25 20:42 | 2021-10-26 10:04 | 40 | 013:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21102500076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 802 | 2021-10-25 | 32080 | keep | 0 | Oct | 2021 | 0.02185 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-25 21:47 | 2021-10-26 10:34 | 10 | 012:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZARON 2 CAJAS PRIMARIAS EN TRANSFORMADOR Y SE REPARO SECUNDARIA | B21102500122 | New_Event | Cutout Failure | Include | Include | Equipment | 767 | 2021-10-25 | 7670 | keep | 0 | Oct | 2021 | 0.005224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-25 22:33 | 2021-10-25 22:40 | 1497 | 000:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR A PETICION DE CURTS SCOTT PARA PODER CERRAR MACHETES SOLIDOS MACHETES SOLIDOS ABIERTOS PARA REMPLAZAR AISLADOR PARTIDO PARTE DE LA CARGA TRANSFERIDA DEL 7201-04 | M21102500115 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 7 | 2021-10-25 | 10479 | keep | 0 | Oct | 2021 | 0.0071372 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-25 23:14 | 2021-10-26 12:06 | 100 | 012:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE Y SE REPARO SECUNDARIA | S21102500130 | New_Event | Cutout Failure | Include | Include | Equipment | 772 | 2021-10-25 | 77200 | keep | 0 | Oct | 2021 | 0.052581 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-10-25 23:31 | 2021-10-26 09:54 | 50 | 010:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21102500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 623 | 2021-10-25 | 31150 | keep | 0 | Oct | 2021 | 0.021216 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-26 00:43 | 2021-10-26 01:51 | 2770 | 001:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR 3 VECES SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO CERRADO POR CONTROL | C21102600002 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2021-10-26 | 188360 | keep | 0 | Oct | 2021 | 0.12829 | 0.0018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 2770
CAGUAS | 2021-10-26 01:51 | 2021-10-26 02:21 | 501 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PRIMARIO EN EL SUELO SE ABRIO MACHETES CARR. 173 K.M. 8.1 Y ABRIO MACHETES EN CARR. 173 K.M. 6.5 INTER. CARR. 775 Y CERRARON N/O EN CARR. 775 K.M. 6.7 BO. PIÃ‘AS | C21102600002 | Partial_restoration | Wire Down | Include | Include | Equipment | 30 | 2021-10-26 | 15030 | keep | 0 | Oct | 2021 | 0.010237 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-26 02:06 | 2021-10-26 12:35 | 90 | 010:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102600001 | New_Event | Bad Weather | Include | Include | Weather | 629 | 2021-10-26 | 56610 | keep | 0 | Oct | 2021 | 0.038557 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-10-26 02:21 | 2021-10-26 16:02 | 827 | 013:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO SE CERRO MACHETES | C21102600008 | Additional_clients | Wire Down | Include | Include | Equipment | 821 | 2021-10-26 | 678967 | keep | 0 | Oct | 2021 | 0.46244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-10-26 03:12 | 2021-10-26 03:13 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21102600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 527 | keep | 0 | Oct | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2021-10-26 03:21 | 2021-10-26 16:42 | 100 | 013:21 | P | DESCONECTIVO DEFECTUOSO | 1 X 100 EN RISER SE REMPLAZO MACHETE EN SU-1 Y TERMINACIONES EN SU-1 | S21102600001 | New_Event | Switch Failure | Include | Include | Equipment | 801 | 2021-10-26 | 80100 | keep | 0 | Oct | 2021 | 0.054556 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-26 03:52 | 2021-10-27 11:53 | 45 | 032:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1921 | 2021-10-26 | 86445 | keep | 0 | Oct | 2021 | 0.058877 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CANOVANAS | 2021-10-26 04:02 | 2021-10-26 09:30 | 79 | 005:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON REPTIL | R21102600001 | New_Event |  |  | Include | Wildlife | 328 | 2021-10-26 | 25912 | keep | 0 | Oct | 2021 | 0.017649 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
SAN JUAN | 2021-10-26 04:07 | 2021-10-26 11:14 | 70 | 007:07 | P | PARARRAYOS DEFECTUOSO | 1 X 50 Y 1 X 8 EN CORTE DE LINEA Y TRANSFORMADOR SE REEMPLAZO | R21102600002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 427 | 2021-10-26 | 29890 | keep | 0 | Oct | 2021 | 0.020358 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-10-26 04:49 | 2021-10-26 04:51 | 1494 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21102600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-26 | 2988 | keep | 0 | Oct | 2021 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-10-26 04:51 | 2021-10-26 15:05 | 60 | 010:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102600004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 614 | 2021-10-26 | 36840 | keep | 0 | Oct | 2021 | 0.025092 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-26 05:00 | 2021-10-26 07:27 | 1026 | 002:27 | T | NO SE REPORTO CAUSA | DISPARO | R21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-10-26 | 150822 | keep | 0 | Oct | 2021 | 0.10272 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
BARRANQUITAS | 2021-10-26 05:50 | 2021-10-26 14:52 | 80 | 009:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21102600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2021-10-26 | 43360 | keep | 0 | Oct | 2021 | 0.029532 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-26 06:02 | 2021-10-26 12:20 | 140 | 006:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21102600001 | New_Event | Bad Weather | Include | Include | Weather | 378 | 2021-10-26 | 52920 | keep | 0 | Oct | 2021 | 0.036044 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
MAYAGÃœEZ | 2021-10-26 06:20 | 2021-10-26 14:11 | 15 | 007:51 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2021-10-26 | 7065 | keep | 0 | Oct | 2021 | 0.0048119 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-10-26 06:27 | 2021-10-26 20:00 | 200 | 013:33 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | A21102600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2021-10-26 | 162600 | keep | 0 | Oct | 2021 | 0.11075 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-10-26 06:49 | 2021-10-26 15:49 | 69 | 009:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21102600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 540 | 2021-10-26 | 37260 | keep | 0 | Oct | 2021 | 0.025378 | 4.6996e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 69
CAGUAS | 2021-10-26 06:57 | 2021-10-26 12:02 | 50 | 005:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE X AVE | C21102600022 | New_Event |  |  | Include | Wildlife | 305 | 2021-10-26 | 15250 | keep | 0 | Oct | 2021 | 0.010387 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-10-26 07:17 | 2021-10-26 07:18 | 3012 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | R21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 3012 | keep | 0 | Oct | 2021 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2021-10-26 07:30 | 2021-10-26 18:08 | 53 | 010:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21102600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 638 | 2021-10-26 | 33814 | keep | 0 | Oct | 2021 | 0.023031 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
ARECIBO | 2021-10-26 07:45 | 2021-10-26 15:55 | 60 | 008:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21102600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 490 | 2021-10-26 | 29400 | keep | 0 | Oct | 2021 | 0.020024 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-26 07:56 | 2021-10-26 12:14 | 50 | 004:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21102600034 | New_Event |  |  | Include | Wildlife | 258 | 2021-10-26 | 12900 | keep | 0 | Oct | 2021 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-26 07:59 | 2021-10-26 08:00 | 2873 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 2873 | keep | 0 | Oct | 2021 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
CANOVANAS | 2021-10-26 08:18 | 2021-10-26 15:30 | 56 | 007:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | R21102600030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 432 | 2021-10-26 | 24192 | keep | 0 | Oct | 2021 | 0.016477 | 3.8141e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 56
FAJARDO | 2021-10-26 08:25 | 2021-10-26 11:28 | 33 | 003:03 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | R21102600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-10-26 | 6039 | keep | 0 | Oct | 2021 | 0.0041131 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2021-10-26 08:27 | 2021-10-26 10:39 | 50 | 002:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | A21102600006 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2021-10-26 | 6600 | keep | 0 | Oct | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-26 08:41 | 2021-10-26 11:52 | 2 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 100 AMP EN RISER | A21102600002 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2021-10-26 | 382 | keep | 0 | Oct | 2021 | 0.00026018 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-10-26 08:53 | 2021-10-26 08:55 | 676 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV LAS PIEDRAS | C21102600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-26 | 1352 | keep | 0 | Oct | 2021 | 0.00092084 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-10-26 08:53 | 2021-10-26 08:55 | 2873 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV LAS PIEDRAS | C21102600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-26 | 5746 | keep | 0 | Oct | 2021 | 0.0039136 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-10-26 08:53 | 2021-10-26 08:55 | 3902 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV LAS PIEDRAS | C21102600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-26 | 7804 | keep | 0 | Oct | 2021 | 0.0053153 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
CAGUAS | 2021-10-26 08:54 | 2021-10-26 14:36 | 1 | 005:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE DESGANCHO | C21102600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-10-26 | 342 | keep | 0 | Oct | 2021 | 0.00023293 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-10-26 08:58 | 2021-10-26 08:59 | 676 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV LAS PIEDRAS | C21102600000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-10-26 | 676 | keep | 0 | Oct | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-10-26 08:58 | 2021-10-26 08:59 | 2873 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV LAS PIEDRAS | C21102600000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-10-26 | 2873 | keep | 0 | Oct | 2021 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-10-26 08:58 | 2021-10-26 08:59 | 3902 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV LAS PIEDRAS | C21102600000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-10-26 | 3902 | keep | 0 | Oct | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2021-10-26 08:59 | 2021-10-26 12:09 | 80 | 003:10 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTE DE LINEA | C21102500059 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-10-26 | 15200 | keep | 0 | Oct | 2021 | 0.010353 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-10-26 09:00 | 2021-10-26 17:11 | 168 | 008:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LIEA CRUCE DE FASE PRIMARIA POR RAMA | P21102600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2021-10-26 | 82488 | keep | 0 | Oct | 2021 | 0.056182 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
UTUADO | 2021-10-26 09:10 | 2021-10-26 12:05 | 20 | 002:55 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21102600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-10-26 | 3500 | keep | 0 | Oct | 2021 | 0.0023838 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-26 09:11 | 2021-10-26 09:52 | 4 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA NEUTRAL | R21102600035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-10-26 | 164 | keep | 0 | Oct | 2021 | 0.0001117 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
PONCE | 2021-10-26 09:18 | 2021-10-26 15:24 | 10 | 006:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P21102600020 | New_Event |  |  | Include | Wildlife | 366 | 2021-10-26 | 3660 | keep | 0 | Oct | 2021 | 0.0024928 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-26 09:34 | 2021-10-26 11:27 | 200 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21102600021 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2021-10-26 | 22600 | keep | 0 | Oct | 2021 | 0.015393 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-26 09:35 | 2021-10-26 19:59 | 200 | 010:24 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | S21102600025 | New_Event | Defective Pole | Include | Include | Equipment | 624 | 2021-10-26 | 124800 | keep | 0 | Oct | 2021 | 0.085001 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-10-26 09:44 | 2021-10-26 12:28 | 12 | 002:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y BAJANTE CARGA POR EL 1206-01 | S21102600022 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2021-10-26 | 1968 | keep | 0 | Oct | 2021 | 0.0013404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-26 09:45 | 2021-10-26 09:47 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1303-05 | S21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-26 | 450 | keep | 0 | Oct | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-26 09:45 | 2021-10-26 09:47 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1303-04 | S21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-26 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2021-10-26 09:46 | 2021-10-26 11:00 | 1185 | 001:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE PRIMARIO HACIENDO CONTACTO CON CRUCETA | M21102600027 | New_Event | Wire Down | Include | Include | Equipment | 74 | 2021-10-26 | 87690 | keep | 0 | Oct | 2021 | 0.059725 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
CANOVANAS | 2021-10-26 09:55 | 2021-10-26 15:31 | 60 | 005:36 | P | ESTRUCTURA AVERIADA | 1 X 15 Y 1 X 25 EN TRANSFORMADOR Y CORTE DE LINEA | R21102600034 | New_Event | Defective Pole | Include | Include | Equipment | 336 | 2021-10-26 | 20160 | keep | 0 | Oct | 2021 | 0.013731 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 12:12 | 255 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6600 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-26 | 33405 | keep | 0 | Oct | 2021 | 0.022752 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 12:12 | 928 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6600 LLEVA PARTE DEL 1422-03 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-26 | 121568 | keep | 0 | Oct | 2021 | 0.082799 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 12:12 | 200 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6600 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-26 | 26200 | keep | 0 | Oct | 2021 | 0.017845 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 12:12 | 185 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6600 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-26 | 24235 | keep | 0 | Oct | 2021 | 0.016506 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 12:12 | 73 | 002:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6600 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-26 | 9563 | keep | 0 | Oct | 2021 | 0.0065133 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 12:12 | 372 | 002:11 | T | LINEA DE TRANSMISION 38KV | DISPARO L-6600 CARGA POR EL 1338-02 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2021-10-26 | 48732 | keep | 0 | Oct | 2021 | 0.033191 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2021-10-26 10:01 | 2021-10-26 13:42 | 2203 | 003:41 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETE PARA SECCIONALIZAR 50% EN SERVICIO | S21102600131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2021-10-26 | 486863 | keep | 0 | Oct | 2021 | 0.3316 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2021-10-26 10:10 | 2021-10-26 11:01 | 1 | 000:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO SUBESTACION PORTATL 19 POR MACHETE DE BARRA QUEMADO EN BREAKER 1 SE TRANSFIRIO AL 1908-03 | S21102600042 | New_Event | Switch Failure | Include | Include | Equipment | 51 | 2021-10-26 | 51 | keep | 0 | Oct | 2021 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-26 10:10 | 2021-10-26 11:01 | 1000 | 000:51 | P | DESCONECTIVO DEFECTUOSO | DISPARO SUBESTACION PORTATL 19 MACHETE DE BARRA QUEMADO BREAKER 1 SE TRANSFIRIO AL 1908-03 | S21102600042 | New_Event | Switch Failure | Include | Include | Equipment | 51 | 2021-10-26 | 51000 | keep | 0 | Oct | 2021 | 0.034736 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-10-26 10:10 | 2021-10-26 11:01 | 2422 | 000:51 | S | DESCONECTIVO DEFECTUOSO | DISPARO SUBESTACION PORTATL 19 MACHETE DE BARRA QUEMADO BREAKER 1 SE TRANSFIRIO AL 1908-03 | S21102600042 | New_Event | Switch Failure | Include | Include | Equipment | 51 | 2021-10-26 | 123522 | keep | 0 | Oct | 2021 | 0.08413 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
BARRANQUITAS | 2021-10-26 10:12 | 2021-10-26 10:13 | 1364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102600164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 1364 | keep | 0 | Oct | 2021 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
AGUADILLA | 2021-10-26 10:17 | 2021-10-26 16:00 | 1 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102600044 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2021-10-26 | 343 | keep | 0 | Oct | 2021 | 0.00023362 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-26 10:18 | 2021-10-26 14:54 | 14 | 004:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21102600058 | New_Event |  |  | Include | Wildlife | 276 | 2021-10-26 | 3864 | keep | 0 | Oct | 2021 | 0.0026318 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2021-10-26 10:18 | 2021-10-26 13:59 | 50 | 003:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA CON GLOBO DE HELIO | P21102600026 | New_Event |  |  | Include | Wildlife | 221 | 2021-10-26 | 11050 | keep | 0 | Oct | 2021 | 0.0075261 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-10-26 10:21 | 2021-10-26 12:58 | 3 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21102600015 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-10-26 | 471 | keep | 0 | Oct | 2021 | 0.0003208 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-26 10:23 | 2021-10-26 10:24 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1909-09 | S21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 222 | keep | 0 | Oct | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-10-26 10:23 | 2021-10-26 10:24 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1907-03 | S21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 4456 | keep | 0 | Oct | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
AGUADILLA | 2021-10-26 10:30 | 2021-10-26 17:49 | 200 | 007:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21102600047 | New_Event | Wire Down | Include | Include | Equipment | 439 | 2021-10-26 | 87800 | keep | 0 | Oct | 2021 | 0.0598 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-10-26 10:35 | 2021-10-26 16:47 | 4 | 006:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 8 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | C21102600062 | New_Event | Cutout Failure | Include | Include | Equipment | 372 | 2021-10-26 | 1488 | keep | 0 | Oct | 2021 | 0.0010135 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-10-26 10:36 | 2021-10-26 11:09 | 1117 | 000:33 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR POR FASE DE LINEA 5300 SOBRE LA DISTRIBUCION | C21102600063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 33 | 2021-10-26 | 36861 | keep | 0 | Oct | 2021 | 0.025106 | 0.00076078 | Sustained | FALSE | TRUE | Not_TMED_Event | 1117
SAN JUAN | 2021-10-26 10:40 | 2021-10-26 11:06 | 15 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21102600003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-10-26 | 390 | keep | 0 | Oct | 2021 | 0.00026563 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-26 10:44 | 2021-10-26 14:07 | 150 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102600048 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-10-26 | 30450 | keep | 0 | Oct | 2021 | 0.020739 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-10-26 11:09 | 2021-10-26 14:10 | 100 | 003:01 | P | LINEA DE TRANSMISION 38KV | SE LEVANTO CONDUCTOR | C21102600063 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 181 | 2021-10-26 | 18100 | keep | 0 | Oct | 2021 | 0.012328 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 11:15 | 2021-10-26 11:23 | 761 | 000:08 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | DISPARO NO RECERRO LLEVA 1421-01 SE VERIFICO CON PERSONAL Y ESTABAN FUERA SE PROBO QUEDO EN SERVICIO | S21102600108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 8 | 2021-10-26 | 6088 | keep | 0 | Oct | 2021 | 0.0041465 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-10-26 11:15 | 2021-10-26 11:23 | 1498 | 000:08 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | DISPARO NO RECERRO LLEVA 1421-1 SE VERIFICO CON PERSONAL Y ESTABAN FUERA SE PROBO QUEDO EN SERVICIO CARGA POR EL 1310-04 | S21102600108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 8 | 2021-10-26 | 11984 | keep | 0 | Oct | 2021 | 0.0081622 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2021-10-26 11:23 | 2021-10-26 17:27 | 15 | 006:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21102600028 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 364 | 2021-10-26 | 5460 | keep | 0 | Oct | 2021 | 0.0037188 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-26 11:25 | 2021-10-26 13:21 | 50 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21102600021 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-10-26 | 5800 | keep | 0 | Oct | 2021 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-10-26 11:33 | 2021-10-26 15:00 | 15 | 003:27 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21102600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-10-26 | 3105 | keep | 0 | Oct | 2021 | 0.0021148 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-10-26 11:40 | 2021-10-26 14:47 | 7 | 003:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO | C21102600074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 187 | 2021-10-26 | 1309 | keep | 0 | Oct | 2021 | 0.00089155 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-10-26 11:50 | 2021-10-26 12:20 | 300 | 000:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102600054 | New_Event | Bad Weather | Include | Include | Weather | 30 | 2021-10-26 | 9000 | keep | 0 | Oct | 2021 | 0.0061299 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-10-26 11:56 | 2021-10-26 14:42 | 1 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21102600025 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2021-10-26 | 166 | keep | 0 | Oct | 2021 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 137 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 1644 | keep | 0 | Oct | 2021 | 0.0011197 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 457 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 5484 | keep | 0 | Oct | 2021 | 0.0037351 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 1225 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 LLEVA EL 1203-03 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 14700 | keep | 0 | Oct | 2021 | 0.010012 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 1452 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 17424 | keep | 0 | Oct | 2021 | 0.011867 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 616 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 CARGA POR EL 1203-01 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 7392 | keep | 0 | Oct | 2021 | 0.0050347 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 3800 | 000:12 | P | LINEA DE TRANSMISION 38KV | DISPARO L-3600 80% EN SERVICIO POR PORTATIL 19 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 45600 | keep | 0 | Oct | 2021 | 0.031058 | 0.0025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 3800
SAN JUAN | 2021-10-26 12:06 | 2021-10-26 12:18 | 600 | 000:12 | P | LINEA DE TRANSMISION 38KV | DISPARO L-3600 40% EN SERVICIO POR PORTATIL 19 | S21102600175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-10-26 | 7200 | keep | 0 | Oct | 2021 | 0.0049039 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
YAUCO | 2021-10-26 12:06 | 2021-10-26 14:50 | 50 | 002:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE POR RAMA | P21102600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-10-26 | 8200 | keep | 0 | Oct | 2021 | 0.005585 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-26 12:17 | 2021-10-26 15:47 | 1 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C21102600080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-10-26 | 210 | keep | 0 | Oct | 2021 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-10-26 12:18 | 2021-10-26 12:23 | 100 | 000:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE Y SE REPARO SECUNDARIA | S21102500130 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 5 | 2021-10-26 | 500 | keep | 0 | Oct | 2021 | 0.00034055 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-26 12:18 | 2021-10-26 17:12 | 75 | 004:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL AEREO | B21102600050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2021-10-26 | 22050 | keep | 0 | Oct | 2021 | 0.015018 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 19:30 | 137 | 007:07 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21102600175 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 427 | 2021-10-26 | 58499 | keep | 0 | Oct | 2021 | 0.039843 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 19:30 | 457 | 007:07 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21102600175 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 427 | 2021-10-26 | 195139 | keep | 0 | Oct | 2021 | 0.13291 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 17:40 | 1225 | 005:17 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 LLEVA EL 1203-03 | S21102600175 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 317 | 2021-10-26 | 388325 | keep | 0 | Oct | 2021 | 0.26449 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 17:40 | 1452 | 005:17 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21102600175 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 317 | 2021-10-26 | 460284 | keep | 0 | Oct | 2021 | 0.3135 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 17:40 | 616 | 005:17 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 CARGA POR EL 1203-01 | S21102600175 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 317 | 2021-10-26 | 195272 | keep | 0 | Oct | 2021 | 0.133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 19:30 | 3800 | 007:07 | P | LINEA DE TRANSMISION 38KV | DISPARO L-3600 80% EN SERVICIO POR PORTATIL 19 | S21102600175 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 427 | 2021-10-26 | 1622600 | keep | 0 | Oct | 2021 | 1.1051 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 12:28 | 4133 | 000:05 | T | LINEA DE TRANSMISION 38KV | DISPARO DEL 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-26 | 20665 | keep | 0 | Oct | 2021 | 0.014075 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-10-26 12:23 | 2021-10-26 12:28 | 4133 | 000:05 | T | LINEA DE TRANSMISION 38KV | DISPARO CON RECIERRE EN OFF SE VERIFICO CON PERSONAL EN CAMPO Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO LLEVANDO LA CARGA DEL 1204-05 | S21102600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-10-26 | 20665 | keep | 0 | Oct | 2021 | 0.014075 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
FAJARDO | 2021-10-26 12:25 | 2021-10-26 14:29 | 5 | 002:04 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA | R21102600056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-10-26 | 620 | keep | 0 | Oct | 2021 | 0.00042228 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
PONCE | 2021-10-26 12:38 | 2021-10-26 18:17 | 20 | 005:39 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE DE 40 PIES DE MADERA PARTIDO POR POSTE 45 PIES METAL | P21102600035 | New_Event | Defective Pole | Include | Include | Equipment | 339 | 2021-10-26 | 6780 | keep | 0 | Oct | 2021 | 0.0046178 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-26 12:46 | 2021-10-26 14:50 | 8 | 002:04 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 37.5 KVA | C21102600083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 124 | 2021-10-26 | 992 | keep | 0 | Oct | 2021 | 0.00067565 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-26 12:57 | 2021-10-27 16:00 | 25 | 027:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102600207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1623 | 2021-10-26 | 40575 | keep | 0 | Oct | 2021 | 0.027635 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-10-26 13:05 | 2021-10-26 15:30 | 35 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21102600029 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2021-10-26 | 5075 | keep | 0 | Oct | 2021 | 0.0034566 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-10-26 13:16 | 2021-10-26 14:49 | 7 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21102500020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2021-10-26 | 651 | keep | 0 | Oct | 2021 | 0.00044339 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-26 13:28 | 2021-10-26 16:17 | 20 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21102600069 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2021-10-26 | 3380 | keep | 0 | Oct | 2021 | 0.0023021 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-10-26 13:34 | 2021-10-26 13:35 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 539 | keep | 0 | Oct | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
SAN JUAN | 2021-10-26 13:36 | 2021-10-26 13:37 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 5062 | keep | 0 | Oct | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-10-26 13:42 | 2021-10-26 14:05 | 250 | 000:23 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21102600000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-10-26 | 5750 | keep | 0 | Oct | 2021 | 0.0039163 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 13:45 | 2021-10-26 15:00 | 7 | 001:15 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | R21102600063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-10-26 | 525 | keep | 0 | Oct | 2021 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-10-26 13:50 | 2021-10-27 12:41 | 5 | 022:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21102600072 | New_Event | Bad Weather | Include | Include | Weather | 1371 | 2021-10-26 | 6855 | keep | 0 | Oct | 2021 | 0.0046689 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-10-26 13:56 | 2021-10-26 16:18 | 1 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102600073 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-10-26 | 142 | keep | 0 | Oct | 2021 | 9.6716e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-26 13:58 | 2021-10-27 16:20 | 15 | 026:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21102600038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1582 | 2021-10-26 | 23730 | keep | 0 | Oct | 2021 | 0.016162 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-26 14:05 | 2021-10-26 15:05 | 150 | 001:00 | P | NO SE REPORTO CAUSA | SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21102600000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 60 | 2021-10-26 | 9000 | keep | 0 | Oct | 2021 | 0.0061299 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-26 14:20 | 2021-10-26 18:08 | 40 | 003:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 100AMP EN CORTE DE LINEA | A21102600036 | New_Event | Cutout Failure | Include | Include | Equipment | 228 | 2021-10-26 | 9120 | keep | 0 | Oct | 2021 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-26 14:23 | 2021-10-26 14:34 | 4133 | 000:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DEL 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S21102600261 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-26 | 45463 | keep | 0 | Oct | 2021 | 0.030965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 14:23 | 2021-10-26 14:34 | 4133 | 000:11 | T | LINEA DE TRANSMISION 38KV | SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1204-05 | S21102600261 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-10-26 | 45463 | keep | 0 | Oct | 2021 | 0.030965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-26 14:49 | 2021-10-26 18:24 | 70 | 003:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21102600081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-10-26 | 15050 | keep | 0 | Oct | 2021 | 0.01025 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
FAJARDO | 2021-10-26 14:58 | 2021-10-26 16:48 | 34 | 001:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO DISCO ROTO | R21102600070 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2021-10-26 | 3740 | keep | 0 | Oct | 2021 | 0.0025473 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
ARECIBO | 2021-10-26 14:58 | 2021-10-26 17:45 | 1 | 002:47 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | A21102600057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-10-26 | 167 | keep | 0 | Oct | 2021 | 0.00011374 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-10-26 15:14 | 2021-10-26 15:16 | 4702 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21102600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-26 | 9404 | keep | 0 | Oct | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CANOVANAS | 2021-10-26 15:47 | 2021-10-26 17:52 | 10 | 002:05 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA | R21102600072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-10-26 | 1250 | keep | 0 | Oct | 2021 | 0.00085137 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-26 16:02 | 2021-10-26 18:12 | 70 | 002:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21102600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-10-26 | 9100 | keep | 0 | Oct | 2021 | 0.006198 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-10-26 16:14 | 2021-10-26 16:15 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21102600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-26 | 1227 | keep | 0 | Oct | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BARRANQUITAS | 2021-10-26 16:25 | 2021-10-27 13:25 | 7 | 021:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21102600109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1260 | 2021-10-26 | 8820 | keep | 0 | Oct | 2021 | 0.0060073 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-10-26 16:55 | 2021-10-26 19:55 | 8 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21102600057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2021-10-26 | 1440 | keep | 0 | Oct | 2021 | 0.00098078 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-10-26 17:26 | 2021-10-26 19:19 | 40 | 001:53 | P | SOBRECARGA | 1 X 50 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE LA CAUSA FUE SOBRE CARGA | M21102600102 | New_Event | Trip Due To Overload | Include | Include | Other | 113 | 2021-10-26 | 4520 | keep | 0 | Oct | 2021 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-26 17:40 | 2021-10-26 22:07 | 100 | 004:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE Y SE REPARO SECUNDARIA | S21102500130 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2021-10-26 | 26700 | keep | 0 | Oct | 2021 | 0.018185 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-26 17:46 | 2021-10-26 19:52 | 6 | 002:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA CON ESCAPE DE ACEITE POR 37.5 KVA | A21102600046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 126 | 2021-10-26 | 756 | keep | 0 | Oct | 2021 | 0.00051491 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-26 18:00 | 2021-10-26 19:56 | 15 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | P21102600031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-10-26 | 1740 | keep | 0 | Oct | 2021 | 0.0011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-26 18:07 | 2021-10-26 18:33 | 4133 | 000:26 | T | LINEA DE TRANSMISION 38KV | DISPARO DEL 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S21102600381 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-26 | 107458 | keep | 0 | Oct | 2021 | 0.073189 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-26 18:07 | 2021-10-26 18:33 | 4133 | 000:26 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO POR L-3600 SOBRE CONDUCTOR LLEVANDO LA CARGA DEL 1204-05 | S21102600381 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-10-26 | 107458 | keep | 0 | Oct | 2021 | 0.073189 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-26 18:19 | 2021-10-26 20:39 | 10 | 002:20 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | A21102600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-10-26 | 1400 | keep | 0 | Oct | 2021 | 0.00095353 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-26 18:23 | 2021-10-27 16:32 | 70 | 022:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1329 | 2021-10-26 | 93030 | keep | 0 | Oct | 2021 | 0.063362 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-10-26 18:32 | 2021-10-26 20:29 | 3 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21102600107 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-10-26 | 351 | keep | 0 | Oct | 2021 | 0.00023906 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-10-26 18:33 | 2021-10-26 19:15 | 356 | 000:42 | P | LINEA DE TRANSMISION 38KV | SE RETIRO LINEA 3600 SOBRE CONDUCTOR Y SE CERRARON MACHETES | S21102600381 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-10-26 | 14952 | keep | 0 | Oct | 2021 | 0.010184 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-10-26 18:34 | 2021-10-27 10:09 | 10 | 015:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR AVE | C21102600126 | New_Event |  |  | Include | Wildlife | 935 | 2021-10-26 | 9350 | keep | 0 | Oct | 2021 | 0.0063682 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-26 19:00 | 2021-10-27 12:02 | 15 | 017:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR CARGA POR EL 1102-01 | S21102600426 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1022 | 2021-10-26 | 15330 | keep | 0 | Oct | 2021 | 0.010441 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-10-26 19:35 | 2021-10-27 10:33 | 10 | 014:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R21102600087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 898 | 2021-10-26 | 8980 | keep | 0 | Oct | 2021 | 0.0061162 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-26 19:55 | 2021-10-26 22:18 | 50 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102600063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2021-10-26 | 7150 | keep | 0 | Oct | 2021 | 0.0048698 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-26 20:19 | 2021-10-26 22:15 | 200 | 001:56 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | M21102600117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-10-26 | 23200 | keep | 0 | Oct | 2021 | 0.015801 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-10-26 20:42 | 2021-10-27 15:35 | 10 | 018:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21102600151 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1133 | 2021-10-26 | 11330 | keep | 0 | Oct | 2021 | 0.0077168 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-10-26 21:18 | 2021-10-27 17:17 | 44 | 019:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21102600161 | New_Event | Cutout Failure | Include | Include | Equipment | 1199 | 2021-10-26 | 52756 | keep | 0 | Oct | 2021 | 0.035932 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
BARRANQUITAS | 2021-10-26 21:36 | 2021-10-27 11:47 | 40 | 014:11 | P | DESGANCHE | X EN CORTE DE LINEA | C21102600165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 851 | 2021-10-26 | 34040 | keep | 0 | Oct | 2021 | 0.023184 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-10-26 21:48 | 2021-10-26 21:58 | 10 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21102600046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2021-10-26 | 100 | keep | 0 | Oct | 2021 | 6.811e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-26 22:20 | 2021-10-27 11:45 | 100 | 013:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | M21102600143 | New_Event | Cutout Failure | Include | Include | Equipment | 805 | 2021-10-26 | 80500 | keep | 0 | Oct | 2021 | 0.054828 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-26 22:22 | 2021-10-27 13:39 | 200 | 015:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 917 | 2021-10-26 | 183400 | keep | 0 | Oct | 2021 | 0.12491 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-26 22:30 | 2021-10-27 12:13 | 10 | 013:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR REMPLAZO CAJA AVERIADA Y PARARRAYO | R21102600090 | New_Event | Cutout Failure | Include | Include | Equipment | 823 | 2021-10-26 | 8230 | keep | 0 | Oct | 2021 | 0.0056054 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-10-27 00:21 | 2021-10-27 16:50 | 100 | 016:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS | M21102700001 | New_Event | Cutout Failure | Include | Include | Equipment | 989 | 2021-10-27 | 98900 | keep | 0 | Oct | 2021 | 0.06736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-10-27 00:40 | 2021-10-27 00:41 | 1228 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C21102700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-27 | 1228 | keep | 0 | Oct | 2021 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2021-10-27 00:41 | 2021-10-27 10:12 | 50 | 009:31 | P | DESGANCHE | 1 X 100 C/L | C21102600010 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 571 | 2021-10-27 | 28550 | keep | 0 | Oct | 2021 | 0.019445 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-27 00:47 | 2021-10-27 00:48 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 651 | keep | 0 | Oct | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
FAJARDO | 2021-10-27 00:48 | 2021-10-27 01:18 | 1394 | 000:30 | T | ANIMAL U OBJETO EXTRAÃ‘O | INTERRUPTOR DISPARO NO TIRA ALARMA POR SCADA ANDY ANDREW INFORMO ESTAR SIN SERVICIO SE LE REALIZO PRUEBA Y PROBO BUENO | R21102700001 | New_Event |  |  | Include | Wildlife | 30 | 2021-10-27 | 41820 | keep | 0 | Oct | 2021 | 0.028483 | 0.00094945 | Sustained | FALSE | FALSE | Not_TMED_Event | 1394
SAN JUAN | 2021-10-27 01:06 | 2021-10-27 10:08 | 176 | 009:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | S21102700001 | New_Event | Cutout Failure | Include | Include | Equipment | 542 | 2021-10-27 | 95392 | keep | 0 | Oct | 2021 | 0.064971 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
FAJARDO | 2021-10-27 01:18 | 2021-10-27 10:54 | 40 | 009:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L Y 1 X 10 EN XMR CRUCE POR REPTIL | R21102700009 | Partial_restoration |  |  | Include | Wildlife | 576 | 2021-10-27 | 23040 | keep | 0 | Oct | 2021 | 0.015692 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-27 05:10 | 2021-10-27 15:33 | 150 | 010:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21102700012 | New_Event | Wire Down | Include | Include | Equipment | 623 | 2021-10-27 | 93450 | keep | 0 | Oct | 2021 | 0.063648 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-27 05:50 | 2021-10-27 05:51 | 2560 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21102700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-27 | 2560 | keep | 0 | Oct | 2021 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
MAYAGÃœEZ | 2021-10-27 05:51 | 2021-10-27 15:01 | 4 | 009:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO ROTO | M21102700012 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 550 | 2021-10-27 | 2200 | keep | 0 | Oct | 2021 | 0.0014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-10-27 06:15 | 2021-10-27 14:33 | 250 | 008:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M21102700019 | New_Event | Cutout Failure | Include | Include | Equipment | 498 | 2021-10-27 | 124500 | keep | 0 | Oct | 2021 | 0.084796 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
ARECIBO | 2021-10-27 06:17 | 2021-10-27 12:59 | 40 | 006:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21102700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 402 | 2021-10-27 | 16080 | keep | 0 | Oct | 2021 | 0.010952 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-27 07:00 | 2021-10-27 18:22 | 30 | 011:22 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REMPLAZO PARARRAYO | C21102700019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 682 | 2021-10-27 | 20460 | keep | 0 | Oct | 2021 | 0.013935 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-10-27 07:10 | 2021-10-27 12:45 | 100 | 005:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEAS CAMION IMPACTO POSTES SE REPARO ALAMBRES PRIMARIOS Y SECUNDARIOS | P21102700007 | New_Event |  |  | Include | Wildlife | 335 | 2021-10-27 | 33500 | keep | 0 | Oct | 2021 | 0.022817 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-10-27 07:11 | 2021-10-28 19:40 | 50 | 036:29 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR AVERIADO DE 25KVA A 2.4KV POR UNO DE LA MISMA CAPACIDAD Y POSTE DE METAL 40 PIES | P21102700008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2189 | 2021-10-27 | 109450 | keep | 0 | Oct | 2021 | 0.074546 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-10-27 08:02 | 2021-10-27 11:15 | 30 | 003:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21102700026 | New_Event |  |  | Include | Wildlife | 193 | 2021-10-27 | 5790 | keep | 0 | Oct | 2021 | 0.0039435 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-27 08:11 | 2021-10-27 11:57 | 1 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R21102700017 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2021-10-27 | 226 | keep | 0 | Oct | 2021 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-27 08:19 | 2021-10-28 09:31 | 25 | 025:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21102700280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1512 | 2021-10-27 | 37800 | keep | 0 | Oct | 2021 | 0.025745 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-27 08:28 | 2021-10-27 12:14 | 50 | 003:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21102600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-10-27 | 11300 | keep | 0 | Oct | 2021 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-27 08:48 | 2021-10-27 10:40 | 50 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO LINEA PRIMARIA | M21102600014 | New_Event |  |  | Include | Wildlife | 112 | 2021-10-27 | 5600 | keep | 0 | Oct | 2021 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-27 09:01 | 2021-10-27 14:47 | 1 | 005:46 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR CRUCE LINEA SECUNDARIA POR BEJUCO | P21102700017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 346 | 2021-10-27 | 346 | keep | 0 | Oct | 2021 | 0.00023566 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-27 09:02 | 2021-10-27 09:05 | 450 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DEL 1118-10 NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 20% 1111-1 | S21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-27 | 1350 | keep | 0 | Oct | 2021 | 0.00091948 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
SAN JUAN | 2021-10-27 09:02 | 2021-10-27 09:05 | 2782 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 20% 1111-1 | S21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-27 | 8346 | keep | 0 | Oct | 2021 | 0.0056844 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
AGUADILLA | 2021-10-27 09:04 | 2021-10-27 11:06 | 3 | 002:02 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21102600017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 122 | 2021-10-27 | 366 | keep | 0 | Oct | 2021 | 0.00024928 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-10-27 09:11 | 2021-10-28 11:42 | 1 | 026:31 | P | NO SE REPORTO CAUSA | 3 X 65 EN CORTE DE LINEA NO CAUSA | C21102800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1591 | 2021-10-27 | 1591 | keep | 0 | Oct | 2021 | 0.0010836 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
GUAYAMA | 2021-10-27 09:16 | 2021-10-27 11:38 | 15 | 002:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA A 2400 VOLT MS LINK 13760176 PO 37.5 KVA | P21102700019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 142 | 2021-10-27 | 2130 | keep | 0 | Oct | 2021 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-27 09:26 | 2021-10-27 11:06 | 20 | 001:40 | P | NO SE REPORTO CAUSA | 2 X 100 EN SU-3 | S21102700017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-10-27 | 2000 | keep | 0 | Oct | 2021 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-10-27 09:35 | 2021-10-27 14:43 | 11 | 005:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21102700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2021-10-27 | 3388 | keep | 0 | Oct | 2021 | 0.0023076 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-10-27 09:37 | 2021-10-27 16:47 | 1 | 007:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO PUENTE PRIMARIO ABIERTO SE REMPLAZO TRANSFORMADOR QUEMADO EN EL FID 33507384 MARCA COOPER NUMERO DE SERIE 1855111169 CAPACIDAD 15KVA VOLTAJES 4160/7200V 120/240V X 15 KVA Y UNA CAJA PRIMARIA CHNT DE 100AMP | A21102700010 | New_Event | Wire Down | Include | Include | Equipment | 430 | 2021-10-27 | 430 | keep | 0 | Oct | 2021 | 0.00029287 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-27 09:40 | 2021-10-27 13:30 | 40 | 003:50 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA QUE PERSONAL REALIZARA DESGANCHE | A21102700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-10-27 | 9200 | keep | 0 | Oct | 2021 | 0.0062661 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-10-27 09:57 | 2021-10-27 11:58 | 5 | 002:01 | P | HERRAJE ROTO O PODRIDO | FIJO CAJA A CRUCETA Y REGULO XMR QUEDO 122/244V | C21102600075 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 121 | 2021-10-27 | 605 | keep | 0 | Oct | 2021 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-10-27 10:00 | 2021-10-27 13:30 | 6 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA | A21102700008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2021-10-27 | 1260 | keep | 0 | Oct | 2021 | 0.00085818 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-10-27 10:10 | 2021-10-27 14:45 | 80 | 004:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-10-27 | 22000 | keep | 0 | Oct | 2021 | 0.014984 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-10-27 10:15 | 2021-10-27 11:43 | 30 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21102700045 | New_Event |  |  | Include | Wildlife | 88 | 2021-10-27 | 2640 | keep | 0 | Oct | 2021 | 0.0017981 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-27 10:16 | 2021-10-27 12:27 | 5 | 002:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 KVA X 50 KVA | C21102700038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 131 | 2021-10-27 | 655 | keep | 0 | Oct | 2021 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-10-27 10:25 | 2021-10-27 12:46 | 2789 | 002:21 | T | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE QUEMADO | C21102700047 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2021-10-27 | 393249 | keep | 0 | Oct | 2021 | 0.26784 | 0.0018996 | Sustained | FALSE | FALSE | Not_TMED_Event | 2789
SAN JUAN | 2021-10-27 10:33 | 2021-10-27 12:10 | 25 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA SECCIONALIZAR | S21102700033 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2021-10-27 | 2425 | keep | 0 | Oct | 2021 | 0.0016517 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-10-27 10:37 | 2021-10-27 14:03 | 40 | 003:26 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR RAMA QUEMANDO SOBRE LINEA | R21102700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-10-27 | 8240 | keep | 0 | Oct | 2021 | 0.0056122 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-27 10:53 | 2021-10-27 13:24 | 11 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21102700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-10-27 | 1661 | keep | 0 | Oct | 2021 | 0.0011313 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-10-27 10:56 | 2021-10-27 14:55 | 1 | 003:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21102700038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2021-10-27 | 239 | keep | 0 | Oct | 2021 | 0.00016278 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-27 11:00 | 2021-10-27 14:01 | 25 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21102700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-10-27 | 4525 | keep | 0 | Oct | 2021 | 0.003082 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-10-27 11:06 | 2021-10-27 11:16 | 225 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO AL REPONER FUSIBEL EN SU-3 CARGA POR EL 1303-05 | S21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-10-27 | 2250 | keep | 0 | Oct | 2021 | 0.0015325 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-27 11:06 | 2021-10-27 11:16 | 870 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO AL REPONER FUSIBEL EN SU-3 LLEVA 1303-4 | S21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-10-27 | 8700 | keep | 0 | Oct | 2021 | 0.0059255 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-10-27 11:06 | 2021-10-27 13:36 | 20 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-10-27 | 3000 | keep | 0 | Oct | 2021 | 0.0020433 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-10-27 11:16 | 2021-10-27 14:26 | 12 | 003:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO EN EL FID 1001212967 MARCA COOPER NUMERO DE SERIE 2155033780 CAPACIDAD 50KVA VOLTAJES 4.16/7.2KV 120/240V Y SE REMPLAZO 2 CAJAS PRIMARIAS MARCA CHINT 100AMP CON 2 X 15 EN TRANSFORMADOR | A21102700017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 190 | 2021-10-27 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-10-27 11:18 | 2021-10-27 11:20 | 4702 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21102700022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-27 | 9404 | keep | 0 | Oct | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-10-27 11:32 | 2021-10-27 12:27 | 30 | 000:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21102700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-10-27 | 1650 | keep | 0 | Oct | 2021 | 0.0011238 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-10-27 11:40 | 2021-10-27 14:33 | 7 | 002:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21102700026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 173 | 2021-10-27 | 1211 | keep | 0 | Oct | 2021 | 0.00082481 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-27 11:45 | 2021-10-27 12:25 | 4 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONECTORES SECUNDARIOS | A21102700009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-10-27 | 160 | keep | 0 | Oct | 2021 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-10-27 11:46 | 2021-10-27 13:25 | 20 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-10-27 | 1980 | keep | 0 | Oct | 2021 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-27 11:47 | 2021-10-27 14:30 | 10 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21102700034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-10-27 | 1630 | keep | 0 | Oct | 2021 | 0.0011102 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-10-27 11:54 | 2021-10-27 13:14 | 15 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21102700033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-10-27 | 1200 | keep | 0 | Oct | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-27 12:10 | 2021-10-27 13:22 | 86 | 001:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA Y SE CERRO CORTE DE LINEA | S21102700033 | Additional_clients | Wire Down | Include | Include | Equipment | 72 | 2021-10-27 | 6192 | keep | 0 | Oct | 2021 | 0.0042173 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-27 12:16 | 2021-10-29 15:00 | 8 | 050:44 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD EN EL FID 1000280111 MARCA EATON COOPER NUMERO DE SERIE 2155011557 VOLTAJES 4.8/8.32KV 120/240V | A21102700019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3044 | 2021-10-27 | 24352 | keep | 0 | Oct | 2021 | 0.016586 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-27 12:22 | 2021-10-27 12:24 | 31 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115 KV | B21102700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-27 | 62 | keep | 0 | Oct | 2021 | 4.2228e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:24 | 1859 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115 KV | B21102700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-27 | 3718 | keep | 0 | Oct | 2021 | 0.0025323 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-10-27 12:22 | 2021-10-27 12:24 | 7 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115 KV | B21102700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-10-27 | 14 | keep | 0 | Oct | 2021 | 9.5353e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 3070 | keep | 0 | Oct | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | TRUE | Not_TMED_Event | 3070
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 2735 | keep | 0 | Oct | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | TRUE | Not_TMED_Event | 2735
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 1070 | keep | 0 | Oct | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | TRUE | Not_TMED_Event | 1070
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 1647 | keep | 0 | Oct | 2021 | 0.0011218 | 0.0011218 | Momentary | FALSE | TRUE | Not_TMED_Event | 1647
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 3295 | keep | 0 | Oct | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | TRUE | Not_TMED_Event | 3295
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 1180 | keep | 0 | Oct | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | TRUE | Not_TMED_Event | 1180
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 320 | keep | 0 | Oct | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | TRUE | Not_TMED_Event | 320
BAYAMON | 2021-10-27 12:22 | 2021-10-27 12:23 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21102700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-27 | 2234 | keep | 0 | Oct | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | TRUE | Not_TMED_Event | 2234
SAN JUAN | 2021-10-27 12:28 | 2021-10-27 16:24 | 1 | 003:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | C21102700060 | New_Event | Cutout Failure | Include | Include | Equipment | 236 | 2021-10-27 | 236 | keep | 0 | Oct | 2021 | 0.00016074 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-10-27 12:29 | 2021-10-27 13:17 | 20 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21102700062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2021-10-27 | 960 | keep | 0 | Oct | 2021 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-27 12:33 | 2021-10-27 14:28 | 9 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21102700026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-10-27 | 1035 | keep | 0 | Oct | 2021 | 0.00070493 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-10-27 12:36 | 2021-10-27 17:31 | 25 | 004:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO C/L PARA REPARAR SECUNDARIA | B21102700037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 295 | 2021-10-27 | 7375 | keep | 0 | Oct | 2021 | 0.0050231 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-10-27 12:54 | 2021-10-27 12:55 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE CARGA 1705 03 | B21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 478 | keep | 0 | Oct | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-10-27 12:54 | 2021-10-27 12:55 | 901 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PARTE DE SU CARGA POR 1705 01 | B21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 901 | keep | 0 | Oct | 2021 | 0.00061367 | 0.00061367 | Momentary | FALSE | FALSE | Not_TMED_Event | 901
MAYAGÃœEZ | 2021-10-27 13:12 | 2021-10-27 13:19 | 1253 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-27 | 8771 | keep | 0 | Oct | 2021 | 0.0059739 | 0.00085341 | Sustained | FALSE | TRUE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2021-10-27 13:12 | 2021-10-27 13:19 | 1266 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-27 | 8862 | keep | 0 | Oct | 2021 | 0.0060359 | 0.00086227 | Sustained | FALSE | TRUE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-10-27 13:12 | 2021-10-27 13:19 | 411 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-27 | 2877 | keep | 0 | Oct | 2021 | 0.0019595 | 0.00027993 | Sustained | FALSE | TRUE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-10-27 13:12 | 2021-10-27 13:19 | 108 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1800 | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-10-27 | 756 | keep | 0 | Oct | 2021 | 0.00051491 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
CAGUAS | 2021-10-27 13:13 | 2021-10-27 18:50 | 5 | 005:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X REPTIL | C21102700073 | New_Event |  |  | Include | Wildlife | 337 | 2021-10-27 | 1685 | keep | 0 | Oct | 2021 | 0.0011476 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-10-27 13:17 | 2021-10-27 13:18 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1907-03 | S21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 4456 | keep | 0 | Oct | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
MAYAGÃœEZ | 2021-10-27 13:25 | 2021-10-27 17:52 | 30 | 004:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102700134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2021-10-27 | 8010 | keep | 0 | Oct | 2021 | 0.0054556 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-10-27 13:30 | 2021-10-27 14:34 | 10 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES | P21102700011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-10-27 | 640 | keep | 0 | Oct | 2021 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-10-27 13:31 | 2021-10-27 15:17 | 20 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21102700062 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-10-27 | 2120 | keep | 0 | Oct | 2021 | 0.0014439 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-10-27 14:13 | 2021-10-27 14:29 | 948 | 000:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTORES PARTIDOS | C21102700140 | New_Event | Wire Down | Include | Include | Equipment | 16 | 2021-10-27 | 15168 | keep | 0 | Oct | 2021 | 0.010331 | 0.00064568 | Sustained | FALSE | FALSE | Not_TMED_Event | 948
BAYAMON | 2021-10-27 14:17 | 2021-10-27 17:12 | 30 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L PARA CERRAR PUENTE ABIERTO TRASPATIO | B21102700052 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2021-10-27 | 5250 | keep | 0 | Oct | 2021 | 0.0035758 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-10-27 14:21 | 2021-10-27 17:25 | 1 | 003:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO PUENTE ABIERTO Y REEMPLAZARON AISLADORES ROTOS | R21102700088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 184 | 2021-10-27 | 184 | keep | 0 | Oct | 2021 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-27 14:39 | 2021-10-27 18:50 | 3896 | 004:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BKR PARA LEVANTAR CONDUCTORES DEL TRONCAL EN EL SUELO | C21102700140 | New_Event | Wire Down | Include | Include | Equipment | 251 | 2021-10-27 | 977896 | keep | 0 | Oct | 2021 | 0.66604 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
CAGUAS | 2021-10-27 14:43 | 2021-10-27 16:39 | 10 | 001:56 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C21102700038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 116 | 2021-10-27 | 1160 | keep | 0 | Oct | 2021 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-27 14:44 | 2021-10-27 14:46 | 2391 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POR SCADA | S21102700076 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-10-27 | 4782 | keep | 0 | Oct | 2021 | 0.003257 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
ARECIBO | 2021-10-27 14:45 | 2021-10-27 19:51 | 100 | 005:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO DOS CAJA PRIMARIAS QUEMADAS EN EL CORTE DE LINEA CON EL FID 29541629 MARCA CHNT DE 200AMP | A21102700029 | New_Event | Wire Down | Include | Include | Equipment | 306 | 2021-10-27 | 30600 | keep | 0 | Oct | 2021 | 0.020842 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-27 14:46 | 2021-10-27 21:27 | 23 | 006:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | S21102700100 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 401 | 2021-10-27 | 9223 | keep | 0 | Oct | 2021 | 0.0062817 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2021-10-27 14:50 | 2021-10-27 18:08 | 80 | 003:18 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO SU-7 @ SU-6 PARA SECCIONALIZAR GANG OPERATOR Y TERMINACION AVERIADA EN SU-6 | R21102700092 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 198 | 2021-10-27 | 15840 | keep | 0 | Oct | 2021 | 0.010789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-10-27 14:50 | 2021-10-27 20:50 | 300 | 006:00 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO SU-6 CON GANG OPERATOR Y TERMINACION AVERIADA Y TRANSFIRIO PARTE DE LA CARGA AL 1646-03 | R21102700092 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 360 | 2021-10-27 | 108000 | keep | 0 | Oct | 2021 | 0.073558 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-27 14:58 | 2021-10-27 15:34 | 20 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21102600375 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-10-27 | 720 | keep | 0 | Oct | 2021 | 0.00049039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-10-27 15:02 | 2021-10-27 16:48 | 15 | 001:46 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21102700064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-10-27 | 1590 | keep | 0 | Oct | 2021 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-10-27 15:02 | 2021-10-27 15:03 | 2174 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 2174 | keep | 0 | Oct | 2021 | 0.0014807 | 0.0014807 | Momentary | FALSE | FALSE | Not_TMED_Event | 2174
SAN JUAN | 2021-10-27 15:15 | 2021-10-27 19:42 | 5 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21102700079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2021-10-27 | 1335 | keep | 0 | Oct | 2021 | 0.00090926 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-10-27 15:18 | 2021-10-27 19:06 | 1 | 003:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON DOS CAJAS QUEMADAS | S21102700031 | New_Event | Cutout Failure | Include | Include | Equipment | 228 | 2021-10-27 | 228 | keep | 0 | Oct | 2021 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-10-27 15:20 | 2021-10-27 18:38 | 15 | 003:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA A 13.2KV AVERIADO | P21102700066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 198 | 2021-10-27 | 2970 | keep | 0 | Oct | 2021 | 0.0020229 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-27 15:36 | 2021-10-27 17:05 | 25 | 001:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA Y DISCO | B21102700053 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2021-10-27 | 2225 | keep | 0 | Oct | 2021 | 0.0015154 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-10-27 15:40 | 2021-10-27 17:04 | 6 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21102700164 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-10-27 | 504 | keep | 0 | Oct | 2021 | 0.00034327 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-27 15:48 | 2021-10-27 16:49 | 520 | 001:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR REALIZA CICLO OPERACION RECIERRE Y QUEDA FUERA LINEAS PRIMARIAS CRUZADAS | P21102700072 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2021-10-27 | 31720 | keep | 0 | Oct | 2021 | 0.021604 | 0.00035417 | Sustained | TRUE | TRUE | Not_TMED_Event | 520
ARECIBO | 2021-10-27 16:03 | 2021-10-27 20:10 | 50 | 004:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN FID 1001248386 MARCA CHNT 100AMP | A21102700038 | New_Event | Cutout Failure | Include | Include | Equipment | 247 | 2021-10-27 | 12350 | keep | 0 | Oct | 2021 | 0.0084115 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-27 16:18 | 2021-10-27 18:49 | 36 | 002:31 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMAS DE PALMA | B21102700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-10-27 | 5436 | keep | 0 | Oct | 2021 | 0.0037024 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2021-10-27 16:32 | 2021-10-27 17:10 | 15 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21102700027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-10-27 | 570 | keep | 0 | Oct | 2021 | 0.00038822 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-10-27 16:39 | 2021-10-27 16:40 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21102700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 651 | keep | 0 | Oct | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
HUMACAO | 2021-10-27 16:50 | 2021-10-27 17:35 | 4 | 000:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE POR AVE | C21102700177 | New_Event |  |  | Include | Wildlife | 45 | 2021-10-27 | 180 | keep | 0 | Oct | 2021 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-10-27 17:28 | 2021-10-27 17:29 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21102700204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 3041 | keep | 0 | Oct | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2021-10-27 17:47 | 2021-10-27 21:54 | 200 | 004:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21102700041 | New_Event | Cutout Failure | Include | Include | Equipment | 247 | 2021-10-27 | 49400 | keep | 0 | Oct | 2021 | 0.033646 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-10-27 18:01 | 2021-10-27 22:15 | 150 | 004:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102700042 | New_Event | Bad Weather | Include | Include | Weather | 254 | 2021-10-27 | 38100 | keep | 0 | Oct | 2021 | 0.02595 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-27 18:06 | 2021-10-27 19:18 | 8 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTES SECUNDARIOS | S21102700034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-10-27 | 576 | keep | 0 | Oct | 2021 | 0.00039231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-10-27 19:03 | 2021-10-27 19:49 | 6 | 000:46 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA NORMALIZAR POSTE PARTIDO | B21102700018 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 46 | 2021-10-27 | 276 | keep | 0 | Oct | 2021 | 0.00018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-27 19:13 | 2021-10-27 20:27 | 1109 | 001:14 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO RAMAS EN TRONCAL PRIMARIO Y SE COLOCO EN SERVICIO | P21102700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-10-27 | 82066 | keep | 0 | Oct | 2021 | 0.055895 | 0.00075533 | Sustained | FALSE | FALSE | Not_TMED_Event | 1109
AGUADILLA | 2021-10-27 19:17 | 2021-10-27 21:06 | 50 | 001:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21102700234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-10-27 | 5450 | keep | 0 | Oct | 2021 | 0.003712 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-27 19:29 | 2021-10-27 20:48 | 3046 | 001:19 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO OPERACIONES DE TRANSFERENCIA ENTRE 1646-03 Y 2404-06 PARA LIBERAR PARTE CARGA 1646-03. POR AVERIA EN SU-6 DEL 1646-05 PARTE X 1646-03. | R21102700133 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 79 | 2021-10-27 | 240634 | keep | 0 | Oct | 2021 | 0.16389 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
ARECIBO | 2021-10-27 19:29 | 2021-10-27 20:40 | 800 | 001:11 | P | SOBRECARGA | 1 X 200 EN CONVERTIDOR EL JOURNEYMAN INFORMO QUE EL FUSIBLE FUNDIO POR CARGA | A21102700052 | New_Event | Trip Due To Overload | Include | Include | Other | 71 | 2021-10-27 | 56800 | keep | 0 | Oct | 2021 | 0.038686 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
FAJARDO | 2021-10-27 19:59 | 2021-10-28 08:49 | 30 | 012:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21102700170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 770 | 2021-10-27 | 23100 | keep | 0 | Oct | 2021 | 0.015733 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-27 20:23 | 2021-10-27 22:28 | 60 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21102700088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-10-27 | 7500 | keep | 0 | Oct | 2021 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-10-27 20:36 | 2021-10-28 17:28 | 3 | 020:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR FASE EN PEDESTAL | R21102700197 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1252 | 2021-10-27 | 3756 | keep | 0 | Oct | 2021 | 0.0025582 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-10-27 20:37 | 2021-10-28 09:56 | 50 | 013:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 799 | 2021-10-27 | 39950 | keep | 0 | Oct | 2021 | 0.02721 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-27 21:03 | 2021-10-27 23:58 | 50 | 002:55 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETIRAR RAMAS DE ARBOL SOBRE LAS LINEAS SECUNDARIAS Y REPARAR LINEA SECUNDARIA | M21102700369 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 175 | 2021-10-27 | 8750 | keep | 0 | Oct | 2021 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-27 21:15 | 2021-10-28 03:18 | 1 | 006:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | C21102700216 | New_Event |  |  | Include | Wildlife | 363 | 2021-10-27 | 363 | keep | 0 | Oct | 2021 | 0.00024724 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-10-27 21:42 | 2021-10-28 10:33 | 30 | 012:51 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | R21102700209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 771 | 2021-10-27 | 23130 | keep | 0 | Oct | 2021 | 0.015754 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-10-27 21:46 | 2021-10-28 00:10 | 300 | 002:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ESTABLECIO GOI PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | S21102700112 | New_Event | Wire Down | Include | Include | Equipment | 144 | 2021-10-27 | 43200 | keep | 0 | Oct | 2021 | 0.029423 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2021-10-27 22:17 | 2021-10-28 01:16 | 1827 | 002:59 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 2800 SE SECCIONALIZO Y SE ENERGIZO LA SUBESTACION | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 179 | 2021-10-27 | 327033 | keep | 0 | Oct | 2021 | 0.22274 | 0.0012444 | Sustained | FALSE | TRUE | Not_TMED_Event | 1827
AGUADILLA | 2021-10-27 22:17 | 2021-10-28 01:16 | 1047 | 002:59 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 2800 SE SECCIONALIZO Y SE ENERGIZO LA SUBESTACION | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 179 | 2021-10-27 | 187413 | keep | 0 | Oct | 2021 | 0.12765 | 0.00071311 | Sustained | FALSE | TRUE | Not_TMED_Event | 1047
AGUADILLA | 2021-10-27 22:17 | 2021-10-28 01:16 | 4882 | 002:59 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 2800 SE SECCIONALIZO Y SE ENERGIZO LA SUBESTACION | M21102700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 179 | 2021-10-27 | 873878 | keep | 0 | Oct | 2021 | 0.59519 | 0.0033251 | Sustained | FALSE | TRUE | Not_TMED_Event | 4882
MAYAGÃœEZ | 2021-10-27 22:19 | 2021-10-28 09:18 | 5 | 010:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | M21102700281 | New_Event | Secondary Wire Down | Include | Include | Equipment | 659 | 2021-10-27 | 3295 | keep | 0 | Oct | 2021 | 0.0022442 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-27 22:19 | 2021-10-28 17:26 | 100 | 019:07 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEAS DISTINTOS SE RETIRO RAMAS SOBRE LAS LINEAS | A21102700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1147 | 2021-10-27 | 114700 | keep | 0 | Oct | 2021 | 0.078122 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-27 22:21 | 2021-10-28 16:48 | 30 | 018:27 | P | NO SE REPORTO CAUSA | 1 X 25 EN AEREO PROVISIONAL | S21102700144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1107 | 2021-10-27 | 33210 | keep | 0 | Oct | 2021 | 0.022619 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-10-27 22:29 | 2021-10-27 22:30 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21102700210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-27 | 1648 | keep | 0 | Oct | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CAGUAS | 2021-10-27 22:56 | 2021-10-28 09:59 | 50 | 011:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102700227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 663 | 2021-10-27 | 33150 | keep | 0 | Oct | 2021 | 0.022578 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-28 01:07 | 2021-10-28 18:08 | 10 | 017:01 | P | TRANSFORMADOR AVERIADO | REMPLAZO CAJA Y XMR DE 50 KVA X 50 KVA | C21102800002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1021 | 2021-10-28 | 10210 | keep | 0 | Oct | 2021 | 0.006954 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-28 03:18 | 2021-10-28 03:19 | 2126 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21102800003 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-10-28 | 2126 | keep | 0 | Oct | 2021 | 0.001448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-10-28 03:19 | 2021-10-28 09:47 | 1 | 006:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | C21102700216 | 1st_after_momentary |  |  | Include | Wildlife | 388 | 2021-10-28 | 388 | keep | 0 | Oct | 2021 | 0.00026427 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-10-28 03:22 | 2021-10-28 09:23 | 20 | 006:01 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO CAUSA | R21102800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 361 | 2021-10-28 | 7220 | keep | 0 | Oct | 2021 | 0.0049175 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-10-28 04:25 | 2021-10-28 10:13 | 40 | 005:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R21102800003 | New_Event | Cutout Failure | Include | Include | Equipment | 348 | 2021-10-28 | 13920 | keep | 0 | Oct | 2021 | 0.0094808 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-10-28 04:26 | 2021-10-28 11:46 | 35 | 007:20 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B21102800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2021-10-28 | 15400 | keep | 0 | Oct | 2021 | 0.010489 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2021-10-28 04:50 | 2021-10-29 13:54 | 23 | 033:04 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE AL T28 | C21102800006 | New_Event | UG Cable Fault | Include | Include | Equipment | 1984 | 2021-10-28 | 45632 | keep | 0 | Oct | 2021 | 0.03108 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2021-10-28 05:12 | 2021-10-28 05:14 | 1802 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-28 | 3604 | keep | 0 | Oct | 2021 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2021-10-28 05:21 | 2021-10-28 19:33 | 4 | 014:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CAJA HACIA TRANSFORMADOR | C21102800235 | New_Event | Wire Down | Include | Include | Equipment | 852 | 2021-10-28 | 3408 | keep | 0 | Oct | 2021 | 0.0023212 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-10-28 06:26 | 2021-10-28 12:35 | 50 | 006:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21102800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-10-28 | 18450 | keep | 0 | Oct | 2021 | 0.012566 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-28 06:30 | 2021-10-28 10:58 | 10 | 004:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN C/L SE REMPLAZO AISLADOR | B21102800008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 268 | 2021-10-28 | 2680 | keep | 0 | Oct | 2021 | 0.0018253 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-28 06:34 | 2021-10-28 10:38 | 1 | 004:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2021-10-28 | 244 | keep | 0 | Oct | 2021 | 0.00016619 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-10-28 06:42 | 2021-10-28 09:14 | 60 | 002:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR POR MAL TIEMPO | A21102800002 | New_Event | Bad Weather | Include | Include | Weather | 152 | 2021-10-28 | 9120 | keep | 0 | Oct | 2021 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-10-28 06:43 | 2021-10-28 17:06 | 20 | 010:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN C/L REMPLAZO ASILADORES CAJA Y PARARRAYO | C21102800010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 623 | 2021-10-28 | 12460 | keep | 0 | Oct | 2021 | 0.0084864 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-28 06:51 | 2021-10-28 06:52 | 2770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102800012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 2770 | keep | 0 | Oct | 2021 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
BAYAMON | 2021-10-28 07:15 | 2021-10-28 07:16 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 1720-08 | B2110280000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 2402 | keep | 0 | Oct | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-10-28 07:15 | 2021-10-28 07:16 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 1709-02 | B21102800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 1 | keep | 0 | Oct | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-10-28 07:22 | 2021-10-28 07:23 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | R21102800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 2106 | keep | 0 | Oct | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
BAYAMON | 2021-10-28 07:27 | 2021-10-28 07:28 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21102800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 271 | keep | 0 | Oct | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2021-10-28 07:31 | 2021-10-28 10:51 | 5 | 003:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C21102800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 200 | 2021-10-28 | 1000 | keep | 0 | Oct | 2021 | 0.0006811 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-10-28 07:39 | 2021-10-28 07:40 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
CANOVANAS | 2021-10-28 07:51 | 2021-10-28 07:52 | 4188 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21102800008 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-28 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-10-28 07:52 | 2021-10-28 13:58 | 80 | 006:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR AISLADOR ROTO | R21102800086 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 366 | 2021-10-28 | 29280 | keep | 0 | Oct | 2021 | 0.019942 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-10-28 08:01 | 2021-10-28 11:33 | 50 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21102800002 | New_Event |  |  | Include | Wildlife | 212 | 2021-10-28 | 10600 | keep | 0 | Oct | 2021 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-28 08:08 | 2021-10-28 11:16 | 1089 | 003:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 188 | 2021-10-28 | 204732 | keep | 0 | Oct | 2021 | 0.13944 | 0.00074171 | Sustained | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-10-28 08:08 | 2021-10-28 11:16 | 3896 | 003:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 188 | 2021-10-28 | 732448 | keep | 0 | Oct | 2021 | 0.49887 | 0.0026535 | Sustained | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-10-28 08:08 | 2021-10-28 11:16 | 1467 | 003:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 188 | 2021-10-28 | 275796 | keep | 0 | Oct | 2021 | 0.18784 | 0.00099917 | Sustained | FALSE | TRUE | Not_TMED_Event | 1467
CAGUAS | 2021-10-28 08:10 | 2021-10-28 15:43 | 5 | 007:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21102800023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 453 | 2021-10-28 | 2265 | keep | 0 | Oct | 2021 | 0.0015427 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-28 08:20 | 2021-10-28 19:55 | 75 | 011:35 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2021-10-28 | 52125 | keep | 0 | Oct | 2021 | 0.035502 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
HUMACAO | 2021-10-28 08:25 | 2021-10-28 08:26 | 3833 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21102800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 3833 | keep | 0 | Oct | 2021 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2021-10-28 08:26 | 2021-10-28 13:39 | 50 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21102800109 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 313 | 2021-10-28 | 15650 | keep | 0 | Oct | 2021 | 0.010659 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-28 08:29 | 2021-10-28 15:52 | 50 | 007:23 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PARTIDO POR UNO DE METAL 40 PIES | P21102800004 | New_Event | Defective Pole | Include | Include | Equipment | 443 | 2021-10-28 | 22150 | keep | 0 | Oct | 2021 | 0.015086 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-10-28 08:34 | 2021-10-28 20:09 | 65 | 011:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | C21102800043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 695 | 2021-10-28 | 45175 | keep | 0 | Oct | 2021 | 0.030768 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-10-28 08:37 | 2021-10-28 11:24 | 50 | 002:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21102800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-10-28 | 8350 | keep | 0 | Oct | 2021 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-28 08:38 | 2021-10-28 10:32 | 60 | 001:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21102800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-10-28 | 6840 | keep | 0 | Oct | 2021 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-28 08:52 | 2021-10-28 15:20 | 50 | 006:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21102800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 388 | 2021-10-28 | 19400 | keep | 0 | Oct | 2021 | 0.013213 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-10-28 09:00 | 2021-10-28 15:30 | 6 | 006:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21102800012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 390 | 2021-10-28 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-10-28 09:17 | 2021-10-28 11:02 | 50 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | C21102800071 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2021-10-28 | 5250 | keep | 0 | Oct | 2021 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-28 09:17 | 2021-10-28 14:07 | 10 | 004:50 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR DE 15KVA A 2.4KV POR UNO DE LA MISMA CAPACIDAD POR ESTAR QUEMADO | P21102800007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 290 | 2021-10-28 | 2900 | keep | 0 | Oct | 2021 | 0.0019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-28 09:30 | 2021-10-28 17:54 | 2 | 008:24 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTES PARTIDOS | B21102800000 | New_Event | Defective Pole | Include | Include | Equipment | 504 | 2021-10-28 | 1008 | keep | 0 | Oct | 2021 | 0.00068654 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-28 09:32 | 2021-10-28 16:03 | 15 | 006:31 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE | A21102800016 | New_Event | Defective Pole | Include | Include | Equipment | 391 | 2021-10-28 | 5865 | keep | 0 | Oct | 2021 | 0.0039946 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-28 09:41 | 2021-10-28 10:07 | 12 | 000:26 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA AJUSTAR BUSHING EN EL TRANSFORMADOR | A21102700070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 26 | 2021-10-28 | 312 | keep | 0 | Oct | 2021 | 0.0002125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-10-28 09:43 | 2021-10-28 12:12 | 30 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO ROTO | R21102800013 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-10-28 | 4470 | keep | 0 | Oct | 2021 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-10-28 09:46 | 2021-10-28 17:18 | 4 | 007:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRASNFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | C21102800089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 452 | 2021-10-28 | 1808 | keep | 0 | Oct | 2021 | 0.0012314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-28 10:06 | 2021-10-28 12:09 | 80 | 002:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO SU-7 @ SU-6 PARA REEMPLAZAR MACHETES Y TERMINACIONES QUEMADAS EN SU-6 | R21102800012 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 123 | 2021-10-28 | 9840 | keep | 0 | Oct | 2021 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2021-10-28 10:37 | 2021-10-28 14:57 | 8 | 004:20 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON DERRAME DE 25KVA X 25KVA | R21102800018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 260 | 2021-10-28 | 2080 | keep | 0 | Oct | 2021 | 0.0014167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-10-28 11:01 | 2021-10-28 14:59 | 7 | 003:58 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21102800122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2021-10-28 | 1666 | keep | 0 | Oct | 2021 | 0.0011347 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-28 11:04 | 2021-10-28 12:58 | 164 | 001:54 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR 1531-02 QUE A SU VEZ LLEVA LA CARGA DEL 1421-02. SE SECCIONALIZO AVERIA POSTE EN EN EL SUELO IMPACTADO POR CAMION. ENTRO UN 100% EN SERVICIO | S21102800024 | New_Event |  |  | Include | Wildlife | 114 | 2021-10-28 | 18696 | keep | 0 | Oct | 2021 | 0.012734 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2021-10-28 11:04 | 2021-10-28 12:46 | 716 | 001:42 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR 1531-02 QUE A SU VEZ LLEVA LA CARGA DEL 1421-02. SE SECCIONALIZO AVERIA POSTE EN EN EL SUELO IMPACTADO POR CAMION | S21102800024 | New_Event |  |  | Include | Wildlife | 102 | 2021-10-28 | 73032 | keep | 0 | Oct | 2021 | 0.049742 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
CAGUAS | 2021-10-28 11:06 | 2021-10-28 12:33 | 40 | 001:27 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA INSTALAR STOP POLE PARA ENDEREZAR POSTE | C21102800125 | New_Event | Defective Pole | Include | Include | Equipment | 87 | 2021-10-28 | 3480 | keep | 0 | Oct | 2021 | 0.0023702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-10-28 11:16 | 2021-10-28 21:49 | 10 | 010:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES EN SECUNDARIA Y TRANSFORMADOR | S21102800025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 633 | 2021-10-28 | 6330 | keep | 0 | Oct | 2021 | 0.0043113 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-28 11:17 | 2021-10-28 15:00 | 37 | 003:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION 1910-00 PARA REPARAR PUNTOS CALIENTES EN LA LINEA 4400 | S21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2021-10-28 | 8251 | keep | 0 | Oct | 2021 | 0.0056197 | 2.5201e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 37
BAYAMON | 2021-10-28 11:17 | 2021-10-28 15:00 | 7 | 003:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION 1910-00 PARA REPARAR PUNTOS CALIENTES EN LA LINEA 4400 | S21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2021-10-28 | 1561 | keep | 0 | Oct | 2021 | 0.0010632 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-10-28 11:17 | 2021-10-28 15:00 | 2 | 003:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION 1910-00 PARA REPARAR PUNTOS CALIENTES EN LA LINEA 4400 | S21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2021-10-28 | 446 | keep | 0 | Oct | 2021 | 0.00030377 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
HUMACAO | 2021-10-28 11:26 | 2021-10-29 11:15 | 2 | 023:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | C21102800128 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1429 | 2021-10-28 | 2858 | keep | 0 | Oct | 2021 | 0.0019466 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2021-10-28 11:36 | 2021-10-28 15:14 | 10 | 003:38 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21102800024 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 218 | 2021-10-28 | 2180 | keep | 0 | Oct | 2021 | 0.0014848 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-10-28 11:37 | 2021-10-28 14:55 | 50 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA. NO SE REPORTO CAUSA | P21102800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-10-28 | 9900 | keep | 0 | Oct | 2021 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-28 12:32 | 2021-10-28 18:14 | 30 | 005:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21102800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-10-28 | 10260 | keep | 0 | Oct | 2021 | 0.006988 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-28 12:46 | 2021-10-28 12:58 | 675 | 000:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR 1531-02 QUE A SU VEZ LLEVA LA CARGA DEL 1421-02. SE SECCIONALIZO AVERIA POSTE EN EN EL SUELO IMPACTADO POR CAMION. ENTRO UN 95% EN SERVICIO | S21102800024 | Partial_restoration |  |  | Include | Wildlife | 12 | 2021-10-28 | 8100 | keep | 0 | Oct | 2021 | 0.0055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-10-28 12:53 | 2021-10-28 15:20 | 7 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21102800061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-10-28 | 1029 | keep | 0 | Oct | 2021 | 0.00070085 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-10-28 12:54 | 2021-10-28 19:54 | 200 | 007:00 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2021-10-28 | 84000 | keep | 0 | Oct | 2021 | 0.057212 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-28 12:58 | 2021-10-28 20:45 | 75 | 007:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PARTIDO Y SE CERRARON MACHETES NORMALIZANDO LA CARGA DEL 1531-02 | S21102800059 | Partial_restoration |  |  | Include | Wildlife | 467 | 2021-10-28 | 35025 | keep | 0 | Oct | 2021 | 0.023855 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-28 13:15 | 2021-10-28 18:42 | 80 | 005:27 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO SU-7 @ SU-6 PARA REEMPLAZAR MACHETES Y TERMINACIONES QUEMADAS EN SU-6 | R21102800012 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 327 | 2021-10-28 | 26160 | keep | 0 | Oct | 2021 | 0.017817 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-28 13:27 | 2021-10-28 16:59 | 10 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21102800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2021-10-28 | 2120 | keep | 0 | Oct | 2021 | 0.0014439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-28 13:28 | 2021-10-28 18:50 | 80 | 005:22 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-10-28 | 25760 | keep | 0 | Oct | 2021 | 0.017545 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-28 13:28 | 2021-10-28 14:49 | 70 | 001:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-10-28 | 5670 | keep | 0 | Oct | 2021 | 0.0038618 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-10-28 13:29 | 2021-10-29 15:02 | 2 | 025:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO CONECTORES SECUNDARIOS ZULFATADOS | C21102800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1533 | 2021-10-28 | 3066 | keep | 0 | Oct | 2021 | 0.0020882 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-10-28 13:34 | 2021-10-28 13:36 | 2106 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R21102800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-28 | 4212 | keep | 0 | Oct | 2021 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-10-28 13:36 | 2021-10-28 18:20 | 95 | 004:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21102800115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 284 | 2021-10-28 | 26980 | keep | 0 | Oct | 2021 | 0.018376 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
VEGA BAJA | 2021-10-28 13:45 | 2021-10-28 16:09 | 30 | 002:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21102800056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2021-10-28 | 4320 | keep | 0 | Oct | 2021 | 0.0029423 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-10-28 14:14 | 2021-10-28 16:40 | 50 | 002:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA DE 100A Y 1X20 EN CORTE DE LINEA | P21102800027 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2021-10-28 | 7300 | keep | 0 | Oct | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-28 14:28 | 2021-10-28 17:26 | 4 | 002:58 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REMPLAZAR SECUNDARIA | C21102700037 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 178 | 2021-10-28 | 712 | keep | 0 | Oct | 2021 | 0.00048494 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-10-28 14:32 | 2021-10-28 14:34 | 1403 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21102800142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-28 | 2806 | keep | 0 | Oct | 2021 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
FAJARDO | 2021-10-28 14:33 | 2021-10-28 17:37 | 110 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER Y 1 X 65 EN RISER REEMPLAZO CAJA PRIMARIA | R21102800107 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2021-10-28 | 20240 | keep | 0 | Oct | 2021 | 0.013785 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BAYAMON | 2021-10-28 14:50 | 2021-10-28 18:34 | 12 | 003:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR UNO DE IGUAL CAPACIDAD | B21102800062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 224 | 2021-10-28 | 2688 | keep | 0 | Oct | 2021 | 0.0018308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-10-28 15:06 | 2021-10-28 15:07 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21102800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 325 | keep | 0 | Oct | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
ARECIBO | 2021-10-28 15:21 | 2021-10-28 17:49 | 5 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR VEHICULO CRUZO SECUNDARIA | A21102800038 | New_Event |  |  | Include | Wildlife | 148 | 2021-10-28 | 740 | keep | 0 | Oct | 2021 | 0.00050401 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-28 15:36 | 2021-10-29 10:00 | 1 | 018:24 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR PROBLEMA INTERNO | A21102800041 | New_Event | Other Causes | Include | Include | Other | 1104 | 2021-10-28 | 1104 | keep | 0 | Oct | 2021 | 0.00075193 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-28 15:39 | 2021-10-28 16:10 | 6 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21102800086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-10-28 | 186 | keep | 0 | Oct | 2021 | 0.00012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-28 16:10 | 2021-10-28 17:42 | 50 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA. FINGER CRUZO FASES | P21102800036 | New_Event |  |  | Include | Wildlife | 92 | 2021-10-28 | 4600 | keep | 0 | Oct | 2021 | 0.003133 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-28 16:16 | 2021-10-28 20:04 | 1058 | 003:48 | P | CABLE SOTERRADO AVERIADO | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO DESPUES DE ABRIR MACHETES FTE JARDIN BOTANICO HACIA VENEZUELA DEL 1348-08. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21102800100 | New_Event | UG Cable Fault | Include | Include | Equipment | 228 | 2021-10-28 | 241224 | keep | 0 | Oct | 2021 | 0.1643 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2021-10-28 16:16 | 2021-10-28 20:04 | 300 | 003:48 | P | CABLE SOTERRADO AVERIADO | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO DESPUES DE ABRIR MACHETES FTE JARDIN BOTANICO HACIA VENEZUELA DEL 1348-08. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21102800100 | New_Event | UG Cable Fault | Include | Include | Equipment | 228 | 2021-10-28 | 68400 | keep | 0 | Oct | 2021 | 0.046587 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-28 16:16 | 2021-10-28 20:04 | 1290 | 003:48 | T | CABLE SOTERRADO AVERIADO | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO DESPUES DE ABRIR MACHETES FTE JARDIN BOTANICO HACIA VENEZUELA. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21102800100 | New_Event | UG Cable Fault | Include | Include | Equipment | 228 | 2021-10-28 | 294120 | keep | 0 | Oct | 2021 | 0.20032 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
FAJARDO | 2021-10-28 16:32 | 2021-10-28 17:07 | 1 | 000:35 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21102800119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2021-10-28 | 35 | keep | 0 | Oct | 2021 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-28 17:04 | 2021-10-28 18:21 | 534 | 001:17 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1519-05 PARA REEMPLAZAR MACHETE N/O CONTRA EL 1519-01 | S21102800122 | New_Event | Switch Failure | Include | Include | Equipment | 77 | 2021-10-28 | 41118 | keep | 0 | Oct | 2021 | 0.028005 | 0.0003637 | Sustained | FALSE | FALSE | Not_TMED_Event | 534
BAYAMON | 2021-10-28 17:04 | 2021-10-28 18:21 | 558 | 001:17 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR Y SE REEMPLAZO MACHETE N/O DEL 1519-01 Y 1519-05 | S21102800122 | New_Event | Switch Failure | Include | Include | Equipment | 77 | 2021-10-28 | 42966 | keep | 0 | Oct | 2021 | 0.029264 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
ARECIBO | 2021-10-28 17:05 | 2021-10-28 19:35 | 8 | 002:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21102800048 | New_Event | Cutout Failure | Include | Include | Equipment | 150 | 2021-10-28 | 1200 | keep | 0 | Oct | 2021 | 0.00081731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-10-28 17:06 | 2021-10-28 19:49 | 15 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | B21102800076 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2021-10-28 | 2445 | keep | 0 | Oct | 2021 | 0.0016653 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-28 17:11 | 2021-10-28 18:59 | 15 | 001:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA POR 50KVA | S21102800124 | New_Event | Service Transformer Failure | Include | Include | Equipment | 108 | 2021-10-28 | 1620 | keep | 0 | Oct | 2021 | 0.0011034 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-10-28 17:12 | 2021-10-28 19:47 | 60 | 002:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21102800061 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 155 | 2021-10-28 | 9300 | keep | 0 | Oct | 2021 | 0.0063342 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-10-28 17:20 | 2021-10-29 13:02 | 1 | 019:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO HACIA CAJA PRIMARIA | C21102800152 | New_Event | Wire Down | Include | Include | Equipment | 1182 | 2021-10-28 | 1182 | keep | 0 | Oct | 2021 | 0.00080505 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-10-28 17:22 | 2021-10-28 18:49 | 100 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21102800049 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2021-10-28 | 8700 | keep | 0 | Oct | 2021 | 0.0059255 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-28 18:02 | 2021-10-28 20:49 | 150 | 002:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102800055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-10-28 | 25050 | keep | 0 | Oct | 2021 | 0.017061 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-28 18:15 | 2021-10-28 19:04 | 255 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6600 AFECTANDO EL 1424-06 POR ABROL SOBRE LINEA 6600 Y 1424-06 | S21102800179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-10-28 | 12495 | keep | 0 | Oct | 2021 | 0.0085103 | 0.00017368 | Sustained | FALSE | TRUE | Not_TMED_Event | 255
SAN JUAN | 2021-10-28 18:15 | 2021-10-28 19:04 | 928 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6600 AFECTANDO EL 1424-06 POR ABROL SOBRE LINEA 6600 Y 1424-06 | S21102800179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-10-28 | 45472 | keep | 0 | Oct | 2021 | 0.030971 | 0.00063206 | Sustained | FALSE | TRUE | Not_TMED_Event | 928
SAN JUAN | 2021-10-28 18:15 | 2021-10-28 19:04 | 200 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6600 AFECTANDO EL 1424-06 POR ABROL SOBRE LINEA 6600 Y 1424-06 | S21102800179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-10-28 | 9800 | keep | 0 | Oct | 2021 | 0.0066747 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-28 18:15 | 2021-10-28 19:04 | 185 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6600 AFECTANDO EL 1424-06 POR ABROL SOBRE LINEA 6600 Y 1424-06 | S21102800179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-10-28 | 9065 | keep | 0 | Oct | 2021 | 0.0061741 | 0.000126 | Sustained | FALSE | TRUE | Not_TMED_Event | 185
SAN JUAN | 2021-10-28 18:15 | 2021-10-28 19:04 | 73 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6600 AFECTANDO EL 1424-06 POR ABROL SOBRE LINEA 6600 Y 1424-06 | S21102800179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-10-28 | 3577 | keep | 0 | Oct | 2021 | 0.0024363 | 4.972e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 73
SAN JUAN | 2021-10-28 18:15 | 2021-10-28 19:55 | 2203 | 001:40 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR PARA DESGANCHAR ARBOL SOBRE LINEA 6600 Y 1424-06. | S21102800143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2021-10-28 | 220300 | keep | 0 | Oct | 2021 | 0.15005 | 0.0015005 | Sustained | FALSE | TRUE | Not_TMED_Event | 2203
CAGUAS | 2021-10-28 18:32 | 2021-10-28 21:35 | 5 | 003:03 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO Y LEVANTO SECUNDARIA | C21102800158 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 183 | 2021-10-28 | 915 | keep | 0 | Oct | 2021 | 0.0006232 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-10-28 18:37 | 2021-10-28 20:23 | 100 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA POR PORTA FUSIBLE QUEMADO | P21102800039 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2021-10-28 | 10600 | keep | 0 | Oct | 2021 | 0.0072196 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-28 18:58 | 2021-10-29 10:52 | 200 | 015:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21102800075 | New_Event | Bad Weather | Include | Include | Weather | 954 | 2021-10-28 | 190800 | keep | 0 | Oct | 2021 | 0.12995 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-10-28 19:08 | 2021-10-28 21:46 | 36 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21102800082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-10-28 | 5688 | keep | 0 | Oct | 2021 | 0.0038741 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-28 19:38 | 2021-10-28 19:39 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA EL 1419-09 | S21102800222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 1447 | keep | 0 | Oct | 2021 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-10-28 19:38 | 2021-10-28 19:39 | 266 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA CARGA POR EL 1112-04 | S21102800222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-28 | 266 | keep | 0 | Oct | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-10-28 19:55 | 2021-10-28 21:21 | 800 | 001:26 | P | DESGANCHE | SE DESGANCHO ARBOL Y SE CERRARON MACHETES | S21102800143 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 86 | 2021-10-28 | 68800 | keep | 0 | Oct | 2021 | 0.046859 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-28 19:57 | 2021-10-29 10:25 | 4 | 014:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CAJA HACIA TRANSFORMADOR | C21102800235 | New_Event | Wire Down | Include | Include | Equipment | 868 | 2021-10-28 | 3472 | keep | 0 | Oct | 2021 | 0.0023648 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-28 20:04 | 2021-10-28 21:00 | 800 | 000:56 | P | CABLE SOTERRADO AVERIADO | SE ABRIERON MACHETES C/ EMORY Y SE CERRARON FTE A EMPRESAS DIAZ Y SE CONTINUA PATRULLANDO | S21102800100 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 56 | 2021-10-28 | 44800 | keep | 0 | Oct | 2021 | 0.030513 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-10-28 20:19 | 2021-10-28 22:15 | 50 | 001:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21102800079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-10-28 | 5800 | keep | 0 | Oct | 2021 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-10-28 20:19 | 2021-10-29 17:54 | 50 | 021:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE SEPARO LINEAS CRUZADAS | A21102800079 | New_Event | Wire Down | Include | Include | Equipment | 1295 | 2021-10-28 | 64750 | keep | 0 | Oct | 2021 | 0.044101 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-10-28 21:00 | 2021-10-28 21:11 | 1058 | 000:11 | P | CABLE SOTERRADO AVERIADO | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO DESPUES DE ABRIR MACHETES C/ HOLLY CROSS Y CERRAR EN C/ EMORY PARK GARDENS. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21102800100 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 11 | 2021-10-28 | 11638 | keep | 0 | Oct | 2021 | 0.0079266 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-28 21:00 | 2021-10-28 21:11 | 300 | 000:11 | P | CABLE SOTERRADO AVERIADO | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO DESPUES DE ABRIR MACHETES C/ HOLLY CROSS Y CERRAR EN C/ EMORY PARK GARDENS. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21102800100 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 11 | 2021-10-28 | 3300 | keep | 0 | Oct | 2021 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-28 21:00 | 2021-10-28 21:11 | 1290 | 000:11 | T | CABLE SOTERRADO AVERIADO | DISPARO BAJA DE LA PORTATIL #8 Y SE CERRO EN EL CAMPO DESPUES DE ABRIR MACHETES C/ HOLLY CROSS Y CERRAR EN C/ EMORY PARK GARDENS. LLEVANDO 1348-08, 20% DEL 1348-06 Y 20% 1336-08 | S21102800100 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 11 | 2021-10-28 | 14190 | keep | 0 | Oct | 2021 | 0.0096647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-28 21:11 | 2021-10-28 22:04 | 80 | 000:53 | P | CABLE SOTERRADO AVERIADO | SE INSTALO JUMPER PROVISIONAL | S21102800100 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 53 | 2021-10-28 | 4240 | keep | 0 | Oct | 2021 | 0.0028878 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-28 21:35 | 2021-10-29 11:03 | 12 | 013:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21102800256 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 808 | 2021-10-28 | 9696 | keep | 0 | Oct | 2021 | 0.0066039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-28 21:35 | 2021-10-29 10:56 | 50 | 013:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO CAJA DEFECTUOSA | S21102800265 | New_Event | Cutout Failure | Include | Include | Equipment | 801 | 2021-10-28 | 40050 | keep | 0 | Oct | 2021 | 0.027278 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-28 21:44 | 2021-10-30 10:50 | 6 | 037:06 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR | R21102800161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2226 | 2021-10-28 | 13356 | keep | 0 | Oct | 2021 | 0.0090967 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-10-28 21:44 | 2021-10-29 13:00 | 4 | 015:16 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 25KVA A 2400 VOLTS QUEMADO POR 37.5 KVA A 2400 VOLTIOS. | P21102800065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 916 | 2021-10-28 | 3664 | keep | 0 | Oct | 2021 | 0.0024955 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-28 22:08 | 2021-10-29 11:20 | 50 | 013:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S21102800261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 792 | 2021-10-28 | 39600 | keep | 0 | Oct | 2021 | 0.026971 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-28 22:08 | 2021-10-28 23:14 | 12 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO Y RELOCALIZO LINEAS SECUNDARIAS ROTAS | M21102800113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-10-28 | 792 | keep | 0 | Oct | 2021 | 0.00053943 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BARRANQUITAS | 2021-10-28 22:17 | 2021-10-28 22:18 | 1604 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE BARRANQUITAS A COMERIO | C21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-28 | 1604 | keep | 0 | Oct | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | TRUE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-10-28 22:17 | 2021-10-28 22:18 | 1131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE BARRANQUITAS A COMERIO | C21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-28 | 1131 | keep | 0 | Oct | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | TRUE | Not_TMED_Event | 1131
BARRANQUITAS | 2021-10-28 22:17 | 2021-10-28 22:18 | 2362 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE BARRANQUITAS A COMERIO | C21102800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-28 | 2362 | keep | 0 | Oct | 2021 | 0.0016087 | 0.0016087 | Momentary | FALSE | TRUE | Not_TMED_Event | 2362
CAGUAS | 2021-10-28 22:29 | 2021-10-29 16:30 | 40 | 018:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | C21102800162 | New_Event | Wire Down | Include | Include | Equipment | 1081 | 2021-10-28 | 43240 | keep | 0 | Oct | 2021 | 0.029451 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-10-28 22:58 | 2021-10-29 16:00 | 50 | 017:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN MACHETE | S21102800268 | New_Event | Wire Down | Include | Include | Equipment | 1022 | 2021-10-28 | 51100 | keep | 0 | Oct | 2021 | 0.034804 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-10-29 00:45 | 2021-10-29 00:46 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21102900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
SAN JUAN | 2021-10-29 04:21 | 2021-10-29 05:54 | 1447 | 001:33 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA EL 1419-09 | S21102900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-10-29 | 134571 | keep | 0 | Oct | 2021 | 0.091656 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-10-29 04:21 | 2021-10-29 05:54 | 266 | 001:33 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1112-04 | S21102900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-10-29 | 24738 | keep | 0 | Oct | 2021 | 0.016849 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
CAGUAS | 2021-10-29 05:07 | 2021-10-29 11:16 | 1 | 006:09 | P | OTRAS CAUSAS | 1 X 30 EN BANCO DE TRANSFORMADOR PROBLEMA DEL CLIENTE | C21102900006 | New_Event | Other Causes | Include | Include | Other | 369 | 2021-10-29 | 369 | keep | 0 | Oct | 2021 | 0.00025132 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-10-29 05:23 | 2021-10-29 18:00 | 90 | 012:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21102900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 757 | 2021-10-29 | 68130 | keep | 0 | Oct | 2021 | 0.046403 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-10-29 06:04 | 2021-10-29 07:18 | 1588 | 001:14 | S | BREAKER DEFECTUOSO O NO OPERA | DISPARO DE BKR ALTA SUBESTACION SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-03 | B21102900000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 74 | 2021-10-29 | 117512 | keep | 0 | Oct | 2021 | 0.080037 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-10-29 06:04 | 2021-10-29 11:49 | 723 | 005:45 | S | BREAKER DEFECTUOSO O NO OPERA | DISPARO DE ALTA SUBESTACION. BKR 1711-02 DEFECTUOSO SE TRANSFIRIO LA CARGA AL 1716-03 | B21102900000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 345 | 2021-10-29 | 249435 | keep | 0 | Oct | 2021 | 0.16989 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-10-29 06:04 | 2021-10-29 07:18 | 13 | 001:14 | T | BREAKER DEFECTUOSO O NO OPERA | DISPARO DE BKR ALTA SUBESTACION SE CERRO POR SCADA CARGA TRANSFERIDA AL 1711-01 | B21102900000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 74 | 2021-10-29 | 962 | keep | 0 | Oct | 2021 | 0.00065521 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-10-29 06:04 | 2021-10-29 10:30 | 1976 | 004:26 | S | BREAKER DEFECTUOSO O NO OPERA | DISPARO DE BKR ALTA SUBESTACION. 1711-02 DEFECTUSOS SE TRANSFIRIO AL CARGA AL 1529-12 | B21102900000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 266 | 2021-10-29 | 525616 | keep | 0 | Oct | 2021 | 0.35799 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-10-29 06:04 | 2021-10-29 06:05 | 1812 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA (OPERACION DE TRANSFERENCIA DEL 1711-02 FUERON EJECUTADAS ESE MISMO DIA, PERO 2 HRS. MAS TARDE, 08:21HRS. , SEGUN BITACORA) | B21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 1812 | keep | 0 | Oct | 2021 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
AGUADILLA | 2021-10-29 06:10 | 2021-10-29 10:54 | 300 | 004:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 Y 1 X 25 EN CORTE DE LINEA SE RETEZO LINEA | M21102900002 | New_Event | Wire Down | Include | Include | Equipment | 284 | 2021-10-29 | 85200 | keep | 0 | Oct | 2021 | 0.058029 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-10-29 06:10 | 2021-10-29 10:30 | 80 | 004:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS | M21102900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2021-10-29 | 20800 | keep | 0 | Oct | 2021 | 0.014167 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-10-29 06:33 | 2021-10-29 09:40 | 90 | 003:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21102900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-10-29 | 16830 | keep | 0 | Oct | 2021 | 0.011463 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-10-29 06:54 | 2021-10-29 06:55 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 5062 | keep | 0 | Oct | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2021-10-29 07:19 | 2021-10-29 07:20 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 5961 | keep | 0 | Oct | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
FAJARDO | 2021-10-29 07:57 | 2021-10-29 10:21 | 1 | 002:24 | P | OTRAS CAUSAS | 1 X 30 EN CORTE DE LINEA PROBLEMA DEL CLIENTE | R21102900010 | New_Event | Other Causes | Include | Include | Other | 144 | 2021-10-29 | 144 | keep | 0 | Oct | 2021 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-10-29 08:15 | 2021-10-29 17:51 | 5 | 009:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIO | M21102900007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 576 | 2021-10-29 | 2880 | keep | 0 | Oct | 2021 | 0.0019616 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-10-29 08:25 | 2021-10-29 14:27 | 40 | 006:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21102900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2021-10-29 | 14480 | keep | 0 | Oct | 2021 | 0.0098623 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-29 08:35 | 2021-10-29 11:21 | 33 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA SE PATRULLO | R21102900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2021-10-29 | 5478 | keep | 0 | Oct | 2021 | 0.003731 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
SAN JUAN | 2021-10-29 09:15 | 2021-10-29 10:14 | 225 | 000:59 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04. SE ABRIO DE SU-1 AL SU-6 Y SE CERRO AMARRE | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-10-29 | 13275 | keep | 0 | Oct | 2021 | 0.0090415 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-29 09:15 | 2021-10-29 09:49 | 870 | 000:34 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04. SE ABRIO AMARRE Y SE CERRO POR SCADA | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-10-29 | 29580 | keep | 0 | Oct | 2021 | 0.020147 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-10-29 09:18 | 2021-10-29 15:02 | 7 | 005:44 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE DE 40 PIES METAL FID 31470102 | M21102900016 | New_Event | Defective Pole | Include | Include | Equipment | 344 | 2021-10-29 | 2408 | keep | 0 | Oct | 2021 | 0.0016401 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-10-29 10:03 | 2021-10-29 18:04 | 60 | 008:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 2 X 30 EN CORTES DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REPARARON LINEAS CRUZADAS | B21102900100 | New_Event | Wire Down | Include | Include | Equipment | 481 | 2021-10-29 | 28860 | keep | 0 | Oct | 2021 | 0.019656 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-10-29 10:05 | 2021-10-29 11:15 | 4 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21102800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-10-29 | 280 | keep | 0 | Oct | 2021 | 0.00019071 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-10-29 10:07 | 2021-10-29 13:38 | 7 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN RISER EXCAVADORA ARRANCO CABLERIA | B21102900077 | New_Event |  |  | Include | Wildlife | 211 | 2021-10-29 | 1477 | keep | 0 | Oct | 2021 | 0.001006 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-10-29 10:07 | 2021-10-29 12:21 | 20 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR SE PATRULLO | C21102800152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2021-10-29 | 2680 | keep | 0 | Oct | 2021 | 0.0018253 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-10-29 10:08 | 2021-10-29 12:08 | 27 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L Y SE RETEZO LINEA PRIMARIA | B21102800096 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2021-10-29 | 3240 | keep | 0 | Oct | 2021 | 0.0022067 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
SAN JUAN | 2021-10-29 10:14 | 2021-10-29 10:37 | 150 | 000:23 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE ASU VEZ LLEVA LA CARGA DEL 1303-04. SE ABRIO DE SU-2 AL SU-B. 100% EN SERVICIO | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-10-29 | 3450 | keep | 0 | Oct | 2021 | 0.0023498 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2021-10-29 10:30 | 2021-10-29 16:41 | 13 | 006:11 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR SE DESCONTAMINO | C21102900030 | New_Event | Other Causes | Include | Include | Other | 371 | 2021-10-29 | 4823 | keep | 0 | Oct | 2021 | 0.0032849 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-10-29 10:35 | 2021-10-29 16:51 | 25 | 006:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A21102900011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2021-10-29 | 9400 | keep | 0 | Oct | 2021 | 0.0064023 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-10-29 10:42 | 2021-10-29 16:27 | 70 | 005:45 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21102900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2021-10-29 | 24150 | keep | 0 | Oct | 2021 | 0.016448 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-10-29 10:45 | 2021-10-29 11:28 | 4 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE QUEMADO EN TRANSFORMADOR | P21102900009 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2021-10-29 | 172 | keep | 0 | Oct | 2021 | 0.00011715 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-10-29 10:50 | 2021-10-29 13:32 | 100 | 002:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | R21102900008 | New_Event | Wire Down | Include | Include | Equipment | 162 | 2021-10-29 | 16200 | keep | 0 | Oct | 2021 | 0.011034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-10-29 11:17 | 2021-10-29 14:38 | 10 | 003:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C21102900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-10-29 | 2010 | keep | 0 | Oct | 2021 | 0.001369 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-10-29 11:45 | 2021-10-29 18:00 | 1 | 006:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO Y SE REPARO LINEA SECUNDARIA AVERIADA | A21102900012 | New_Event | Wire Down | Include | Include | Equipment | 375 | 2021-10-29 | 375 | keep | 0 | Oct | 2021 | 0.00025541 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-29 12:00 | 2021-10-29 15:51 | 10 | 003:51 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR, SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | S21102900109 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 231 | 2021-10-29 | 2310 | keep | 0 | Oct | 2021 | 0.0015733 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-29 12:06 | 2021-10-29 12:07 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S12102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 1984 | keep | 0 | Oct | 2021 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-10-29 12:06 | 2021-10-29 12:07 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1711-03 | S12102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 1976 | keep | 0 | Oct | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-10-29 12:06 | 2021-10-29 12:07 | 577 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1529-12 | S12102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 577 | keep | 0 | Oct | 2021 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2021-10-29 12:16 | 2021-10-29 12:19 | 651 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-29 | 1953 | keep | 0 | Oct | 2021 | 0.0013302 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BARRANQUITAS | 2021-10-29 12:31 | 2021-10-29 15:38 | 200 | 003:07 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21102900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-10-29 | 37400 | keep | 0 | Oct | 2021 | 0.025473 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-10-29 12:34 | 2021-10-29 15:46 | 10 | 003:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21102900098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 192 | 2021-10-29 | 1920 | keep | 0 | Oct | 2021 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-29 12:52 | 2021-10-29 14:42 | 30 | 001:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A21102900017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-10-29 | 3300 | keep | 0 | Oct | 2021 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-10-29 12:56 | 2021-10-29 14:35 | 6 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR SE REPARO SECUNDARIA | B21102900098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2021-10-29 | 594 | keep | 0 | Oct | 2021 | 0.00040457 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-10-29 13:06 | 2021-10-29 18:00 | 3 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA NEUTRAL PRIMARIA | C21102900045 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-10-29 | 882 | keep | 0 | Oct | 2021 | 0.00060073 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
ARECIBO | 2021-10-29 13:25 | 2021-10-29 19:30 | 3 | 006:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA AVERIADA | A21102900019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 365 | 2021-10-29 | 1095 | keep | 0 | Oct | 2021 | 0.0007458 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
FAJARDO | 2021-10-29 13:36 | 2021-10-29 16:38 | 60 | 003:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21102900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-10-29 | 10920 | keep | 0 | Oct | 2021 | 0.0074376 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-10-29 14:06 | 2021-10-29 17:43 | 15 | 003:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | A21102900021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 217 | 2021-10-29 | 3255 | keep | 0 | Oct | 2021 | 0.002217 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
FAJARDO | 2021-10-29 14:14 | 2021-10-29 15:19 | 90 | 001:05 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | R21102900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-10-29 | 5850 | keep | 0 | Oct | 2021 | 0.0039844 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-29 14:29 | 2021-10-29 16:35 | 110 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES VIENTOS | M21102900030 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-10-29 | 13860 | keep | 0 | Oct | 2021 | 0.00944 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
CAGUAS | 2021-10-29 14:40 | 2021-10-29 15:02 | 3 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21102900053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2021-10-29 | 66 | keep | 0 | Oct | 2021 | 4.4952e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2021-10-29 14:40 | 2021-10-29 15:21 | 25 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21102900028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-10-29 | 1025 | keep | 0 | Oct | 2021 | 0.00069812 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-29 14:45 | 2021-10-29 14:46 | 4089 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21102900115 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-29 | 4089 | keep | 0 | Oct | 2021 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2021-10-29 14:51 | 2021-10-29 20:43 | 4089 | 005:52 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 1806-03 Y AL CERRAR ABRIERON TODOS LOS BREKERS 1, 2, 3 Y LOS DE LA ALTA SE SECCIONALIZO AVERIA DEL 1806-03 Y SE ENERGIZARON EL 1 Y 2 LUEGO SE REPARO CONDUCTOR Y SE CERRO POR SCADA EL 1806-03 | B21102900115 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 352 | 2021-10-29 | 1439328 | keep | 0 | Oct | 2021 | 0.98032 | 0.002785 | Sustained | FALSE | FALSE | Not_TMED_Event | 4089
GUAYAMA | 2021-10-29 14:51 | 2021-10-29 16:47 | 1 | 001:56 | P | NO SE REPORTO CAUSA | 1X20 EN MONTURA TRIFASICA DE BOMBA DE AAA. NO SE REPORTA CAUSA | P21102900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-10-29 | 116 | keep | 0 | Oct | 2021 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-29 14:53 | 2021-10-29 17:48 | 3798 | 002:55 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 1806-03 Y AL CERRAR ABRIERON TODOS LOS BREKERS 1, 2, 3 Y LOS DE LA ALTA SE SECCIONALIZO AVERIA DEL 1806-03 Y SE ENERGIZARON EL 1 Y 2 | B21102900115 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2021-10-29 | 664650 | keep | 0 | Oct | 2021 | 0.45269 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2021-10-29 14:53 | 2021-10-29 17:49 | 4622 | 002:56 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL 1806-03 Y AL CERRAR ABRIERON TODOS LOS BREKERS 1, 2, 3 Y LOS DE LA ALTA SE SECCIONALIZO AVERIA DEL 1806-03 Y SE ENERGIZARON EL 1 Y 2 | B21102900115 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2021-10-29 | 813472 | keep | 0 | Oct | 2021 | 0.55405 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2021-10-29 14:54 | 2021-10-29 18:27 | 60 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTE DE LINEA | B21102900117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-10-29 | 12780 | keep | 0 | Oct | 2021 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-10-29 15:09 | 2021-10-29 20:17 | 50 | 005:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR LINEA PRIMARIA Y HACER DESGANCHE. SE CERRO CORTE DE LINEA | P21102900027 | New_Event | Wire Down | Include | Include | Equipment | 308 | 2021-10-29 | 15400 | keep | 0 | Oct | 2021 | 0.010489 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-29 15:39 | 2021-10-29 17:39 | 30 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A MACHETE | M21102900036 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2021-10-29 | 3600 | keep | 0 | Oct | 2021 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-10-29 15:50 | 2021-10-29 17:36 | 10 | 001:46 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR, SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | S21102900117 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 106 | 2021-10-29 | 1060 | keep | 0 | Oct | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-29 16:00 | 2021-10-29 17:34 | 600 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE CERRARON PUENTES ABIERTOS Y SE REEMPLAZARON DE 1/0 A 4/0 | S21102800268 | Additional_clients | Wire Down | Include | Include | Equipment | 94 | 2021-10-29 | 56400 | keep | 0 | Oct | 2021 | 0.038414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-10-29 16:52 | 2021-10-30 13:44 | 119 | 020:52 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTES DE LINEA SE PATRULLO | C21102900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1252 | 2021-10-29 | 148988 | keep | 0 | Oct | 2021 | 0.10148 | 8.105e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 119
PONCE | 2021-10-29 16:56 | 2021-10-29 16:57 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211029000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 3718 | keep | 0 | Oct | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-10-29 16:57 | 2021-10-29 21:01 | 50 | 004:04 | P | NO SE REPORTO CAUSA | 1X65 EN CORTE DE LINEA NO REPORTAN CAUSA | P21102900033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 244 | 2021-10-29 | 12200 | keep | 0 | Oct | 2021 | 0.0083094 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-29 17:16 | 2021-10-29 17:46 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | S21102800246 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-10-29 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-10-29 17:26 | 2021-10-29 18:00 | 11 | 000:34 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REPARAR BARRA EN PEDESTAL | R21102900025 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 34 | 2021-10-29 | 374 | keep | 0 | Oct | 2021 | 0.00025473 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-10-29 17:34 | 2021-10-29 18:50 | 30 | 001:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO OTRO PUENTE ABIERTO EN ANCLADA TRASPATIO | S21102800268 | Partial_restoration | Wire Down | Include | Include | Equipment | 76 | 2021-10-29 | 2280 | keep | 0 | Oct | 2021 | 0.0015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-29 17:38 | 2021-10-29 17:39 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO LA CAUSA | M21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 6285 | keep | 0 | Oct | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
ARECIBO | 2021-10-29 17:49 | 2021-10-29 20:49 | 150 | 003:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21102900031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-10-29 | 27000 | keep | 0 | Oct | 2021 | 0.01839 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-10-29 17:53 | 2021-10-29 19:57 | 22 | 002:04 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO AVERIADO | M21102900050 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 124 | 2021-10-29 | 2728 | keep | 0 | Oct | 2021 | 0.001858 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
MAYAGÃœEZ | 2021-10-29 17:53 | 2021-10-29 20:20 | 1 | 002:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO | M21102900052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 147 | 2021-10-29 | 147 | keep | 0 | Oct | 2021 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-29 18:07 | 2021-10-29 21:48 | 65 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA | A21102900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2021-10-29 | 14365 | keep | 0 | Oct | 2021 | 0.0097839 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-10-29 18:34 | 2021-10-30 11:32 | 15 | 016:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA TRANSFORMADOR | S21102900131 | New_Event | Cutout Failure | Include | Include | Equipment | 1018 | 2021-10-29 | 15270 | keep | 0 | Oct | 2021 | 0.0104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-10-29 18:43 | 2021-10-29 19:25 | 12 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES | S21102800075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-10-29 | 504 | keep | 0 | Oct | 2021 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-29 18:46 | 2021-10-29 18:47 | 600 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | S21102900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-29 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-10-29 18:50 | 2021-10-29 19:23 | 600 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE CERRARON PUENTES ABIERTOS EN ANCLADA Y TRASPATIO | S21102800268 | Additional_clients | Wire Down | Include | Include | Equipment | 33 | 2021-10-29 | 19800 | keep | 0 | Oct | 2021 | 0.013486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-29 18:57 | 2021-10-29 18:58 | 600 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | S21102900000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-10-29 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-10-29 18:58 | 2021-10-29 20:53 | 200 | 001:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21102900138 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 115 | 2021-10-29 | 23000 | keep | 0 | Oct | 2021 | 0.015665 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-10-29 19:56 | 2021-10-30 10:16 | 50 | 014:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 80 EN C/L | B21102900199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2021-10-29 | 43000 | keep | 0 | Oct | 2021 | 0.029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-10-29 20:48 | 2021-10-30 20:29 | 7 | 023:41 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21102900073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1421 | 2021-10-29 | 9947 | keep | 0 | Oct | 2021 | 0.0067749 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-10-29 20:53 | 2021-10-29 22:10 | 600 | 001:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA LEVANTAR CONDUCTOR | S21102900000 | Additional_clients | Wire Down | Include | Include | Equipment | 77 | 2021-10-29 | 46200 | keep | 0 | Oct | 2021 | 0.031467 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-29 21:40 | 2021-10-29 21:41 | 800 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1303-02 Y LLEVA 20% DEL 1204-02 | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 800 | keep | 0 | Oct | 2021 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
SAN JUAN | 2021-10-29 21:40 | 2021-10-29 21:41 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 LLEVANDO LAS CARGAS DEL 1303-01 Y 1346-06 | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 1681 | keep | 0 | Oct | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-29 21:40 | 2021-10-29 21:41 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA EL 20% DEL 1204-02 | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 2435 | keep | 0 | Oct | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-29 21:40 | 2021-10-29 21:41 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 LLEVANDO LAS CARGAS DEL 1303-01 Y 1346-06 | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 1598 | keep | 0 | Oct | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-10-29 22:10 | 2021-10-30 14:22 | 12 | 016:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN RISER | S21102900161 | Partial_restoration | Wire Down | Include | Include | Equipment | 972 | 2021-10-29 | 11664 | keep | 0 | Oct | 2021 | 0.0079443 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-10-29 23:04 | 2021-10-30 08:36 | 1 | 009:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21102900038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 572 | 2021-10-29 | 572 | keep | 0 | Oct | 2021 | 0.00038959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-29 23:57 | 2021-10-29 23:58 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1709-05 | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 1533 | keep | 0 | Oct | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-10-29 23:57 | 2021-10-29 23:58 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1709-03 | S21102900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-29 | 2364 | keep | 0 | Oct | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
FAJARDO | 2021-10-30 00:26 | 2021-10-31 19:00 | 25 | 042:34 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN PROVISIONAL SE CONTRUYO PROVISIONAL AEREO DEL T-14 @ T-4A | R21103000002 | New_Event | UG Cable Fault | Include | Include | Equipment | 2554 | 2021-10-30 | 63850 | keep | 0 | Oct | 2021 | 0.043488 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-10-30 01:07 | 2021-10-30 10:31 | 20 | 009:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21103000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 564 | 2021-10-30 | 11280 | keep | 0 | Oct | 2021 | 0.0076828 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-10-30 02:35 | 2021-10-30 16:58 | 1026 | 014:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO IR 3006-3E SE REMPLAZO POSTE IMPACTADO | C21103000003 | New_Event |  |  | Include | Wildlife | 863 | 2021-10-30 | 885438 | keep | 0 | Oct | 2021 | 0.60307 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
BAYAMON | 2021-10-30 03:42 | 2021-10-30 03:43 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21103000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 1746 | keep | 0 | Oct | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
ARECIBO | 2021-10-30 03:42 | 2021-10-30 03:43 | 2366 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21103000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 2366 | keep | 0 | Oct | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
CANOVANAS | 2021-10-30 04:29 | 2021-10-30 04:30 | 3699 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21103000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-30 | 3699 | keep | 0 | Oct | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2021-10-30 04:30 | 2021-10-30 10:51 | 90 | 006:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETORNO CONDUCTOR ZAFADO SOBRE CRUCETA | R21103000004 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 381 | 2021-10-30 | 34290 | keep | 0 | Oct | 2021 | 0.023355 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BARRANQUITAS | 2021-10-30 05:21 | 2021-10-30 11:16 | 73 | 005:55 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO | C21103000016 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 355 | 2021-10-30 | 25915 | keep | 0 | Oct | 2021 | 0.017651 | 4.972e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 73
BAYAMON | 2021-10-30 05:27 | 2021-10-30 11:27 | 50 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L. SE REEMPLAZO CAJA AVERIADA | B21103000008 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2021-10-30 | 18000 | keep | 0 | Oct | 2021 | 0.01226 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-30 05:39 | 2021-10-30 09:35 | 100 | 003:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21103000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2021-10-30 | 23600 | keep | 0 | Oct | 2021 | 0.016074 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-30 06:27 | 2021-10-30 09:20 | 8 | 002:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21103000007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 173 | 2021-10-30 | 1384 | keep | 0 | Oct | 2021 | 0.00094264 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-10-30 06:33 | 2021-10-30 06:34 | 5062 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R21103000000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-30 | 5062 | keep | 0 | Oct | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-10-30 06:34 | 2021-10-30 11:43 | 100 | 005:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R21103000007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 309 | 2021-10-30 | 30900 | keep | 0 | Oct | 2021 | 0.021046 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-30 07:09 | 2021-10-30 13:53 | 30 | 006:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA CRUZANDO LINEAS | S21103000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 404 | 2021-10-30 | 12120 | keep | 0 | Oct | 2021 | 0.0082549 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-10-30 07:15 | 2021-10-30 10:50 | 25 | 003:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21103000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-10-30 | 5375 | keep | 0 | Oct | 2021 | 0.0036609 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-10-30 07:38 | 2021-10-30 22:20 | 20 | 014:42 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-5 POR TRAMO AVERIADO DE T-4 @ T-5 AUN FUERA T-7 POR OTRA AVERIA DE T-6 @ T-7 | B21103000018 | New_Event | UG Cable Fault | Include | Include | Equipment | 882 | 2021-10-30 | 17640 | keep | 0 | Oct | 2021 | 0.012015 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-10-30 07:46 | 2021-10-30 13:37 | 90 | 005:51 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN SU 20 SE REEMPLAZO | C21103000016 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 351 | 2021-10-30 | 31590 | keep | 0 | Oct | 2021 | 0.021516 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-30 08:20 | 2021-10-30 08:22 | 4304 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M21103000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-30 | 8608 | keep | 0 | Oct | 2021 | 0.0058629 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
SAN JUAN | 2021-10-30 08:52 | 2021-10-30 08:53 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21103000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 2782 | keep | 0 | Oct | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2021-10-30 08:55 | 2021-10-30 16:13 | 90 | 007:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA CERRO PUENTE PRIMARIO | R21103000012 | New_Event | Wire Down | Include | Include | Equipment | 438 | 2021-10-30 | 39420 | keep | 0 | Oct | 2021 | 0.026849 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-10-30 08:59 | 2021-10-31 09:49 | 2 | 024:50 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR POR DESGANCHE | M21103000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1490 | 2021-10-30 | 2980 | keep | 0 | Oct | 2021 | 0.0020297 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-10-30 09:00 | 2021-10-30 09:01 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21103100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 1475 | keep | 0 | Oct | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-10-30 09:01 | 2021-10-30 15:26 | 51 | 006:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21103000009 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 385 | 2021-10-30 | 19635 | keep | 0 | Oct | 2021 | 0.013373 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-10-30 09:05 | 2021-10-30 12:20 | 5 | 003:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA | M21103000013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2021-10-30 | 975 | keep | 0 | Oct | 2021 | 0.00066407 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-10-30 09:06 | 2021-10-30 11:55 | 100 | 002:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA 2 X 30 EN CORTE DE LINEA POR DESGANCHE | A21103000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-10-30 | 16900 | keep | 0 | Oct | 2021 | 0.011511 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-30 09:07 | 2021-10-30 10:19 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21103000007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-10-30 | 720 | keep | 0 | Oct | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-10-30 09:30 | 2021-10-30 12:45 | 12 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZO DE PEDESTAL SECUNDARIO | P21103000002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2021-10-30 | 2340 | keep | 0 | Oct | 2021 | 0.0015938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-10-30 09:34 | 2021-10-30 17:00 | 25 | 007:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE LEVANTO SECUNDARIA Y SE HIZO DESGANCHE | S21103000016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 446 | 2021-10-30 | 11150 | keep | 0 | Oct | 2021 | 0.0075942 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-10-30 10:06 | 2021-10-30 15:26 | 3 | 005:20 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR UN POSTE PRIMARIO Y SECUNDARIO ROTOS | R20103000016 | New_Event | Defective Pole | Include | Include | Equipment | 320 | 2021-10-30 | 960 | keep | 0 | Oct | 2021 | 0.00065385 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-10-30 10:22 | 2021-10-30 14:28 | 20 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21103000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-10-30 | 4920 | keep | 0 | Oct | 2021 | 0.003351 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-10-30 10:31 | 2021-10-30 10:48 | 220 | 000:17 | P | DESGANCHE | 3 X 80 Y 1 X 65 EN CORTE DE LINEA | C21103000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2021-10-30 | 3740 | keep | 0 | Oct | 2021 | 0.0025473 | 0.00014984 | Sustained | FALSE | TRUE | Not_TMED_Event | 220
MAYAGÃœEZ | 2021-10-30 10:39 | 2021-10-30 16:35 | 100 | 005:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21103000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2021-10-30 | 35600 | keep | 0 | Oct | 2021 | 0.024247 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-10-30 10:54 | 2021-10-30 12:30 | 70 | 001:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21103000024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-10-30 | 6720 | keep | 0 | Oct | 2021 | 0.004577 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-10-30 11:07 | 2021-10-30 14:45 | 50 | 003:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M21103000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-10-30 | 10900 | keep | 0 | Oct | 2021 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-10-30 11:12 | 2021-10-30 15:46 | 50 | 004:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21103000007 | New_Event |  |  | Include | Wildlife | 274 | 2021-10-30 | 13700 | keep | 0 | Oct | 2021 | 0.009331 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-10-30 11:22 | 2021-10-30 16:00 | 180 | 004:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | M21103000035 | New_Event | Wire Down | Include | Include | Equipment | 278 | 2021-10-30 | 50040 | keep | 0 | Oct | 2021 | 0.034082 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
ARECIBO | 2021-10-30 11:24 | 2021-10-30 14:38 | 75 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR IGUANA QUE CRUZO CON PARARRAYO | A21103000015 | New_Event |  |  | Include | Wildlife | 194 | 2021-10-30 | 14550 | keep | 0 | Oct | 2021 | 0.0099099 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-10-30 11:26 | 2021-10-30 14:08 | 150 | 002:42 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR POR DESGANCHE | A21103000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2021-10-30 | 24300 | keep | 0 | Oct | 2021 | 0.016551 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-10-30 11:30 | 2021-10-30 13:15 | 10 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | P21103000004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-10-30 | 1050 | keep | 0 | Oct | 2021 | 0.00071515 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-10-30 11:51 | 2021-10-30 11:52 | 4369 | 000:01 | T | DESGANCHE | RECIERRE | C21103000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-30 | 4369 | keep | 0 | Oct | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
PONCE | 2021-10-30 11:51 | 2021-10-30 17:35 | 90 | 005:44 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21103000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-10-30 | 30960 | keep | 0 | Oct | 2021 | 0.021087 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-10-30 11:52 | 2021-10-30 17:40 | 100 | 005:48 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21103000040 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 348 | 2021-10-30 | 34800 | keep | 0 | Oct | 2021 | 0.023702 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 300 | 000:02 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 1401-08 LLEVA PARTE DE LA CARGA DE 1303-02 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00020433 | Momentary | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 12:17 | 627 | 000:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 24 | 2021-10-30 | 15048 | keep | 0 | Oct | 2021 | 0.010249 | 0.00042705 | Sustained | FALSE | TRUE | Not_TMED_Event | 627
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 12:17 | 293 | 000:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 24 | 2021-10-30 | 7032 | keep | 0 | Oct | 2021 | 0.0047895 | 0.00019956 | Sustained | FALSE | TRUE | Not_TMED_Event | 293
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 12:17 | 761 | 000:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 24 | 2021-10-30 | 18264 | keep | 0 | Oct | 2021 | 0.01244 | 0.00051831 | Sustained | FALSE | TRUE | Not_TMED_Event | 761
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 12:17 | 451 | 000:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 24 | 2021-10-30 | 10824 | keep | 0 | Oct | 2021 | 0.0073722 | 0.00030717 | Sustained | FALSE | TRUE | Not_TMED_Event | 451
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 922 | 000:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 1401-08 LLEVA CARGA DE 1346-05 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 1844 | keep | 0 | Oct | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | TRUE | Not_TMED_Event | 922
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 300 | 000:02 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 1401-08 LLEVA PARTE DE LA CARGA DE 1348-08 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 600 | keep | 0 | Oct | 2021 | 0.00040866 | 0.00020433 | Momentary | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 837 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 CARGA DE 1401-06 ESTA ATRAVES DEL 1401-07 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 1674 | keep | 0 | Oct | 2021 | 0.0011402 | 0.00057008 | Momentary | FALSE | TRUE | Not_TMED_Event | 837
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 908 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 1407-07 LLEVA CARGA DEL 1401-06 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 1816 | keep | 0 | Oct | 2021 | 0.0012369 | 0.00061843 | Momentary | FALSE | TRUE | Not_TMED_Event | 908
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 135 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 1401-08 LLEVA CARGA DE 1346-05 Y PARTE DEL 1348-08 Y PARTE DEL 1303-02 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 270 | keep | 0 | Oct | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 135
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 1 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 2 | keep | 0 | Oct | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 11:55 | 1295 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-10-30 | 2590 | keep | 0 | Oct | 2021 | 0.001764 | 0.00088202 | Momentary | FALSE | TRUE | Not_TMED_Event | 1295
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 12:17 | 1498 | 000:24 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 CARGA DE 1421-01 ESTABA TRANSFERIDA AL 1310-04 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 24 | 2021-10-30 | 35952 | keep | 0 | Oct | 2021 | 0.024487 | 0.0010203 | Sustained | FALSE | TRUE | Not_TMED_Event | 1498
SAN JUAN | 2021-10-30 11:53 | 2021-10-30 12:17 | 766 | 000:24 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 CARGA DE 1421-05 ESTABA TRANSFERIDA AL 1310-03 | S21103000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 24 | 2021-10-30 | 18384 | keep | 0 | Oct | 2021 | 0.012521 | 0.00052172 | Sustained | FALSE | TRUE | Not_TMED_Event | 766
HUMACAO | 2021-10-30 12:13 | 2021-10-30 12:14 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE CERRO POR CONTROL | C21103000034 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-30 | 2450 | keep | 0 | Oct | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-10-30 12:14 | 2021-10-30 13:55 | 50 | 001:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C21103000039 | 1st_after_momentary |  |  | Include | Wildlife | 101 | 2021-10-30 | 5050 | keep | 0 | Oct | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-10-30 12:31 | 2021-10-30 15:17 | 10 | 002:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21102900037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 166 | 2021-10-30 | 1660 | keep | 0 | Oct | 2021 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-10-30 12:34 | 2021-10-30 15:16 | 50 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R21103000022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2021-10-30 | 8100 | keep | 0 | Oct | 2021 | 0.0055169 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-30 12:38 | 2021-10-30 17:10 | 10 | 004:32 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | C21103000043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 272 | 2021-10-30 | 2720 | keep | 0 | Oct | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-30 13:07 | 2021-10-30 16:15 | 80 | 003:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA Y 2 CAJAS QUEMADAS | S21103000070 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2021-10-30 | 15040 | keep | 0 | Oct | 2021 | 0.010244 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-30 13:15 | 2021-10-30 16:20 | 80 | 003:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21103000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-10-30 | 14800 | keep | 0 | Oct | 2021 | 0.01008 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-10-30 13:35 | 2021-10-30 14:24 | 1 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDRIAS | M21103000011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-10-30 | 49 | keep | 0 | Oct | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-10-30 13:36 | 2021-10-30 14:31 | 20 | 000:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21103000046 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 55 | 2021-10-30 | 1100 | keep | 0 | Oct | 2021 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-30 13:46 | 2021-10-30 19:05 | 100 | 005:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE CERRO RISER | S21103000074 | New_Event | Wire Down | Include | Include | Equipment | 319 | 2021-10-30 | 31900 | keep | 0 | Oct | 2021 | 0.021727 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-10-30 13:54 | 2021-10-30 14:41 | 40 | 000:47 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA EN LA LINEA | S21103000077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-10-30 | 1880 | keep | 0 | Oct | 2021 | 0.0012805 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-30 13:55 | 2021-10-30 13:56 | 1017 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21103000055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 1017 | keep | 0 | Oct | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
GUAYAMA | 2021-10-30 14:00 | 2021-10-30 15:55 | 60 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21103000014 | New_Event |  |  | Include | Wildlife | 115 | 2021-10-30 | 6900 | keep | 0 | Oct | 2021 | 0.0046996 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-10-30 14:18 | 2021-10-30 14:20 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21103000050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-30 | 4468 | keep | 0 | Oct | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BARRANQUITAS | 2021-10-30 14:20 | 2021-10-30 17:06 | 100 | 002:46 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21103000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-10-30 | 16600 | keep | 0 | Oct | 2021 | 0.011306 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-30 14:33 | 2021-10-30 17:50 | 12 | 003:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO 3 AISLADORES SE CERRO PUENTE A CAJA TRANSFORMADOR | S21103000081 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 197 | 2021-10-30 | 2364 | keep | 0 | Oct | 2021 | 0.0016101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-30 14:41 | 2021-10-30 14:44 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-04 CON R/R OFF LLEVA CARGA DEL 1620-01 | S21103000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-30 | 108 | keep | 0 | Oct | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-10-30 14:41 | 2021-10-30 14:44 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-04 CON R/R OFF LLEVA CARGA DEL 1620-01 | S21103000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-10-30 | 516 | keep | 0 | Oct | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2021-10-30 14:44 | 2021-10-30 15:05 | 10 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21103000052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-10-30 | 210 | keep | 0 | Oct | 2021 | 0.00014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-10-30 14:46 | 2021-10-30 16:42 | 40 | 001:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21103000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-10-30 | 4640 | keep | 0 | Oct | 2021 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-10-30 14:47 | 2021-10-30 14:48 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21103000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 3699 | keep | 0 | Oct | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2021-10-30 14:53 | 2021-10-30 17:49 | 50 | 002:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | S21103000083 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2021-10-30 | 8800 | keep | 0 | Oct | 2021 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-10-30 15:18 | 2021-10-31 12:49 | 100 | 021:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21103000024 | New_Event | Wire Down | Include | Include | Equipment | 1291 | 2021-10-30 | 129100 | keep | 0 | Oct | 2021 | 0.087929 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-10-30 15:33 | 2021-10-30 16:10 | 85 | 000:37 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21103000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-10-30 | 3145 | keep | 0 | Oct | 2021 | 0.002142 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
PONCE | 2021-10-30 15:43 | 2021-10-30 16:22 | 107 | 000:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21103000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2021-10-30 | 4173 | keep | 0 | Oct | 2021 | 0.0028422 | 7.2877e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-10-30 16:09 | 2021-10-31 12:23 | 150 | 020:14 | P | DESGANCHE | 1 X 80 , 1 X 100 , 1 X 65 EN CORTES DE LINEA. SE RETIRARON RAMAS SOBRE LAS LINEAS PRIMARIAS | M21103000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1214 | 2021-10-30 | 182100 | keep | 0 | Oct | 2021 | 0.12403 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BARRANQUITAS | 2021-10-30 16:26 | 2021-10-31 08:58 | 1 | 016:32 | P | OTRAS CAUSAS | 1 X 15 EN BANCO DE TRANSFORMADORES PROBLEMA DEL CLIENTE | C21103000078 | New_Event | Other Causes | Include | Include | Other | 992 | 2021-10-30 | 992 | keep | 0 | Oct | 2021 | 0.00067565 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-30 16:49 | 2021-10-30 18:44 | 100 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A21103000025 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-10-30 | 11500 | keep | 0 | Oct | 2021 | 0.0078326 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-10-30 16:55 | 2021-10-31 16:44 | 4 | 023:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 37.5 KVA | A21103000026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1429 | 2021-10-30 | 5716 | keep | 0 | Oct | 2021 | 0.0038931 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-10-30 17:08 | 2021-10-30 18:20 | 60 | 001:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LAS LINEAS | A21103000027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-10-30 | 4320 | keep | 0 | Oct | 2021 | 0.0029423 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-10-30 17:13 | 2021-10-30 20:16 | 40 | 003:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA PRIMARIA A CORTE DE LINEA | P21103000021 | New_Event | Wire Down | Include | Include | Equipment | 183 | 2021-10-30 | 7320 | keep | 0 | Oct | 2021 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-10-30 17:13 | 2021-10-30 17:33 | 2468 | 000:20 | T | ERROR HUMANO | PERSONAL TECNICO RETIRANDO ALAMBRE DESENERGIZADO QUE CAYO EN ALIMENTADOR CRUZO ALIMENTADOR | B21103000059 | New_Event | Human Error | Include | Include | Other | 20 | 2021-10-30 | 49360 | keep | 0 | Oct | 2021 | 0.033619 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
ARECIBO | 2021-10-30 18:34 | 2021-10-31 11:00 | 12 | 016:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PARTIDA 100 AMP DE TRANSFORMADOR | A21103000034 | New_Event | Cutout Failure | Include | Include | Equipment | 986 | 2021-10-30 | 11832 | keep | 0 | Oct | 2021 | 0.0080587 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-10-30 18:55 | 2021-10-31 15:31 | 12 | 020:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21103000095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1236 | 2021-10-30 | 14832 | keep | 0 | Oct | 2021 | 0.010102 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-10-30 19:06 | 2021-10-31 10:31 | 100 | 015:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21103000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 925 | 2021-10-30 | 92500 | keep | 0 | Oct | 2021 | 0.063001 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-10-30 19:14 | 2021-10-30 21:00 | 180 | 001:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21103000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-10-30 | 19080 | keep | 0 | Oct | 2021 | 0.012995 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
FAJARDO | 2021-10-30 19:27 | 2021-10-30 19:28 | 2041 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R21103000000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-10-30 | 2041 | keep | 0 | Oct | 2021 | 0.0013901 | 0.0013901 | Momentary | FALSE | FALSE | Not_TMED_Event | 2041
FAJARDO | 2021-10-30 19:28 | 2021-10-30 22:38 | 100 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 EN CORTE DE LINEA | R21103000046 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 190 | 2021-10-30 | 19000 | keep | 0 | Oct | 2021 | 0.012941 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-10-30 19:51 | 2021-10-30 19:52 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21103000050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 4188 | keep | 0 | Oct | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
VEGA BAJA | 2021-10-30 20:16 | 2021-10-31 11:48 | 10 | 015:32 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | B21103000067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 932 | 2021-10-30 | 9320 | keep | 0 | Oct | 2021 | 0.0063478 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-10-30 20:16 | 2021-10-31 13:59 | 10 | 017:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B21103000049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1063 | 2021-10-30 | 10630 | keep | 0 | Oct | 2021 | 0.00724 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-30 21:27 | 2021-10-31 10:45 | 10 | 013:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | B21103000072 | New_Event | Cutout Failure | Include | Include | Equipment | 798 | 2021-10-30 | 7980 | keep | 0 | Oct | 2021 | 0.0054351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-10-30 21:37 | 2021-10-31 11:25 | 100 | 013:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 50 EN CORTES DE LINEA LLUVIAS | C21103000087 | New_Event | Bad Weather | Include | Include | Weather | 828 | 2021-10-30 | 82800 | keep | 0 | Oct | 2021 | 0.056395 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-10-30 21:48 | 2021-10-30 21:49 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21103000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 2450 | keep | 0 | Oct | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
CANOVANAS | 2021-10-30 21:59 | 2021-10-31 09:25 | 2 | 011:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REEMPLAZO | R21103000052 | New_Event | Cutout Failure | Include | Include | Equipment | 686 | 2021-10-30 | 1372 | keep | 0 | Oct | 2021 | 0.00093446 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-10-30 22:09 | 2021-10-31 01:27 | 150 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21103000039 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2021-10-30 | 29700 | keep | 0 | Oct | 2021 | 0.020229 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-10-30 22:15 | 2021-10-31 16:48 | 50 | 018:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE X AVE | C21103000093 | New_Event |  |  | Include | Wildlife | 1113 | 2021-10-30 | 55650 | keep | 0 | Oct | 2021 | 0.037903 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-10-30 22:30 | 2021-10-31 10:56 | 4 | 012:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO | R21103000053 | New_Event | Cutout Failure | Include | Include | Equipment | 746 | 2021-10-30 | 2984 | keep | 0 | Oct | 2021 | 0.0020324 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-10-30 22:39 | 2021-10-31 15:15 | 100 | 016:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA ARBOL TUMBO LINEA PRIMARIA SE ABREN PUENTES PARA SECCIONALIZAR AVERIA CONTINUA LOS TRABAJOS CON EVENTO P21103100019 | P21103000027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 996 | 2021-10-30 | 99600 | keep | 0 | Oct | 2021 | 0.067837 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-10-30 23:37 | 2021-10-30 23:38 | 641 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21103000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-30 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
ARECIBO | 2021-10-31 00:15 | 2021-10-31 17:32 | 8 | 017:17 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21103100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1037 | 2021-10-31 | 8296 | keep | 0 | Oct | 2021 | 0.0056504 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
HUMACAO | 2021-10-31 03:10 | 2021-10-31 03:11 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 2354 | keep | 0 | Oct | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2021-10-31 03:13 | 2021-10-31 11:28 | 1026 | 008:15 | T | DESCONECTIVO DEFECTUOSO | DISPARO | R21103100016 | New_Event | Switch Failure | Include | Include | Equipment | 495 | 2021-10-31 | 507870 | keep | 0 | Oct | 2021 | 0.34591 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
MAYAGÃœEZ | 2021-10-31 03:28 | 2021-10-31 03:29 | 1352 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M21103100000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-10-31 | 1352 | keep | 0 | Oct | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-10-31 03:28 | 2021-10-31 03:29 | 871 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DEL INTERRUPTOR 6012-05 EL CUAL LLEVA LA CARGA DEL 6014-03 NO SE REPORTO CAUSA | M21103100000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-10-31 | 871 | keep | 0 | Oct | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-10-31 03:29 | 2021-10-31 10:03 | 400 | 006:34 | P | ESTRUCTURA AVERIADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO POSTE AVERIADO | M21103100033 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 394 | 2021-10-31 | 157600 | keep | 0 | Oct | 2021 | 0.10734 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CANOVANAS | 2021-10-31 04:12 | 2021-10-31 15:10 | 60 | 010:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR | R21103100019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 658 | 2021-10-31 | 39480 | keep | 0 | Oct | 2021 | 0.02689 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-10-31 04:46 | 2021-10-31 14:19 | 65 | 009:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA REEMPLAZO POSTE IMPACTADO POR AUTO | R21103100022 | New_Event |  |  | Include | Wildlife | 573 | 2021-10-31 | 37245 | keep | 0 | Oct | 2021 | 0.025367 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
AGUADILLA | 2021-10-31 05:27 | 2021-10-31 05:28 | 1192 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21103100005 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-10-31 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-10-31 05:28 | 2021-10-31 17:55 | 1 | 012:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN RISER MAL TIEMPO | M21103100050 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 747 | 2021-10-31 | 747 | keep | 0 | Oct | 2021 | 0.00050878 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-31 06:12 | 2021-10-31 15:29 | 200 | 009:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21103100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 557 | 2021-10-31 | 111400 | keep | 0 | Oct | 2021 | 0.075874 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-10-31 06:25 | 2021-10-31 06:26 | 2697 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | A21103100000 | New_Event |  |  | Include | Wildlife | 1 | 2021-10-31 | 2697 | keep | 0 | Oct | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-10-31 06:26 | 2021-10-31 21:53 | 80 | 015:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21103100056 | 1st_after_momentary |  |  | Include | Wildlife | 927 | 2021-10-31 | 74160 | keep | 0 | Oct | 2021 | 0.05051 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-10-31 06:50 | 2021-10-31 06:51 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1303-05 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 225 | keep | 0 | Oct | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-10-31 06:50 | 2021-10-31 06:51 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1303-04 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 870 | keep | 0 | Oct | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-10-31 06:51 | 2021-10-31 09:38 | 50 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21103100007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-10-31 | 8350 | keep | 0 | Oct | 2021 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-31 07:10 | 2021-10-31 07:13 | 4028 | 000:03 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21103100003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 3 | 2021-10-31 | 12084 | keep | 0 | Oct | 2021 | 0.0082304 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2021-10-31 07:13 | 2021-10-31 16:50 | 10 | 009:37 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO Y SE REEMPLAZO CAJA AVERIADA EN XMR | B21103100004 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 577 | 2021-10-31 | 5770 | keep | 0 | Oct | 2021 | 0.0039299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-31 07:20 | 2021-10-31 08:57 | 50 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21103100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-10-31 | 4850 | keep | 0 | Oct | 2021 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-10-31 07:24 | 2021-10-31 11:30 | 50 | 004:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21103100004 | New_Event |  |  | Include | Wildlife | 246 | 2021-10-31 | 12300 | keep | 0 | Oct | 2021 | 0.0083775 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-31 07:32 | 2021-10-31 09:39 | 80 | 002:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M21103100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-10-31 | 10160 | keep | 0 | Oct | 2021 | 0.0069199 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-10-31 07:37 | 2021-10-31 20:34 | 2 | 012:57 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21103100005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 777 | 2021-10-31 | 1554 | keep | 0 | Oct | 2021 | 0.0010584 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-10-31 07:47 | 2021-11-01 10:42 | 4 | 026:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y PARARRAYO EN TRANSFORMADOR | C21103100017 | New_Event | Cutout Failure | Include | Include | Equipment | 1615 | 2021-10-31 | 6460 | keep | 0 | Oct | 2021 | 0.0043999 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-10-31 08:30 | 2021-10-31 13:59 | 15 | 005:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS Y LINEA SECUNDARIA | M21103100014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 329 | 2021-10-31 | 4935 | keep | 0 | Oct | 2021 | 0.0033612 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-10-31 08:55 | 2021-10-31 13:00 | 90 | 004:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21103100027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2021-10-31 | 22050 | keep | 0 | Oct | 2021 | 0.015018 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
PONCE | 2021-10-31 09:30 | 2021-10-31 11:26 | 42 | 001:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21103100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-10-31 | 4872 | keep | 0 | Oct | 2021 | 0.0033183 | 2.8606e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 42
BAYAMON | 2021-10-31 09:31 | 2021-10-31 09:32 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 4431 | keep | 0 | Oct | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
CANOVANAS | 2021-10-31 10:00 | 2021-10-31 16:37 | 150 | 006:37 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | R21103100056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 397 | 2021-10-31 | 59550 | keep | 0 | Oct | 2021 | 0.040559 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-10-31 10:03 | 2021-10-31 15:22 | 50 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21103100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2021-10-31 | 15950 | keep | 0 | Oct | 2021 | 0.010863 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-10-31 10:03 | 2021-10-31 10:18 | 1352 | 000:15 | T | ESTRUCTURA AVERIADA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M21103100000 | New_Event | Defective Pole | Include | Include | Equipment | 15 | 2021-10-31 | 20280 | keep | 0 | Oct | 2021 | 0.013813 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-10-31 10:03 | 2021-10-31 10:18 | 871 | 000:15 | T | ESTRUCTURA AVERIADA | DISPARO DEL INTERRUPTOR 6012-05 EL CUAL LLEVA LA CARGA DEL 6014-03 NO SE REPORTO CAUSA | M21103100000 | New_Event | Defective Pole | Include | Include | Equipment | 15 | 2021-10-31 | 13065 | keep | 0 | Oct | 2021 | 0.0088985 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-10-31 10:03 | 2021-10-31 15:13 | 20 | 005:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21103100025 | New_Event | Bad Weather | Include | Include | Weather | 310 | 2021-10-31 | 6200 | keep | 0 | Oct | 2021 | 0.0042228 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-10-31 10:05 | 2021-10-31 10:06 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1206-02 | S21103100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 641 | keep | 0 | Oct | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-10-31 10:05 | 2021-10-31 10:06 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-01 | S21103100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 733 | keep | 0 | Oct | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2021-10-31 10:13 | 2021-10-31 11:54 | 10 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | S21103000093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-10-31 | 1010 | keep | 0 | Oct | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-31 10:18 | 2021-10-31 18:33 | 400 | 008:15 | P | ESTRUCTURA AVERIADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO POSTE AVERIADO | M21103100033 | Partial_restoration | Defective Pole | Include | Include | Equipment | 495 | 2021-10-31 | 198000 | keep | 0 | Oct | 2021 | 0.13486 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-10-31 10:25 | 2021-10-31 17:43 | 60 | 007:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21103100010 | New_Event | Bad Weather | Include | Include | Weather | 438 | 2021-10-31 | 26280 | keep | 0 | Oct | 2021 | 0.017899 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-31 10:43 | 2021-10-31 11:48 | 1681 | 001:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR. SE PATRULLO Y SE CERRO POR SCADA CARGA POR EL 1303-04 | S21103100042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 65 | 2021-10-31 | 109265 | keep | 0 | Oct | 2021 | 0.07442 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-10-31 10:43 | 2021-10-31 10:44 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1346-04 | S21103100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 726 | keep | 0 | Oct | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-10-31 10:43 | 2021-10-31 10:44 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21103100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 3932 | keep | 0 | Oct | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-10-31 10:43 | 2021-10-31 11:48 | 1598 | 001:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR. SE PATRULLO Y SE CERRO POR SCADA | S21103100042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 65 | 2021-10-31 | 103870 | keep | 0 | Oct | 2021 | 0.070745 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2021-10-31 10:57 | 2021-10-31 15:43 | 50 | 004:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21103100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2021-10-31 | 14300 | keep | 0 | Oct | 2021 | 0.0097397 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-10-31 11:15 | 2021-10-31 14:08 | 40 | 002:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21103100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-10-31 | 6920 | keep | 0 | Oct | 2021 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-31 11:18 | 2021-10-31 13:29 | 6 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | C21103100041 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2021-10-31 | 786 | keep | 0 | Oct | 2021 | 0.00053534 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-10-31 11:28 | 2021-10-31 12:48 | 200 | 001:20 | P | DESCONECTIVO DEFECTUOSO | PERSONAL LOCALIZANDO AVERIA | R21103100016 | New_Event | Switch Failure | Include | Include | Equipment | 80 | 2021-10-31 | 16000 | keep | 0 | Oct | 2021 | 0.010898 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-10-31 11:32 | 2021-10-31 14:18 | 40 | 002:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21103100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-10-31 | 6640 | keep | 0 | Oct | 2021 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-10-31 11:35 | 2021-10-31 12:22 | 1 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C21103100042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-10-31 | 47 | keep | 0 | Oct | 2021 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-10-31 11:36 | 2021-10-31 11:37 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21103000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 73 | keep | 0 | Oct | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
CAGUAS | 2021-10-31 11:36 | 2021-10-31 13:30 | 100 | 001:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21103100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-10-31 | 11400 | keep | 0 | Oct | 2021 | 0.0077645 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-10-31 11:37 | 2021-10-31 17:00 | 25 | 005:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21103100012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 323 | 2021-10-31 | 8075 | keep | 0 | Oct | 2021 | 0.0054998 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-10-31 11:52 | 2021-10-31 16:32 | 60 | 004:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | R21103100066 | New_Event | Cutout Failure | Include | Include | Equipment | 280 | 2021-10-31 | 16800 | keep | 0 | Oct | 2021 | 0.011442 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-31 11:59 | 2021-10-31 14:19 | 1681 | 002:20 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CARGO INTERRUPTOR Y SE CERRO POR CONTROL LLEVA CARGA 1346-6 Y 1303-1 CARGA POR EL 1303-004 | S21103100069 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2021-10-31 | 235340 | keep | 0 | Oct | 2021 | 0.16029 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-31 11:59 | 2021-10-31 12:00 | 2435 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21103100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 2435 | keep | 0 | Oct | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-10-31 11:59 | 2021-10-31 14:19 | 1598 | 002:20 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CARGO INTERRUPTOR Y SE CERRO POR CONTROL LLEVA CARGA 1346-6 Y 1303-1 | S21103100069 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2021-10-31 | 223720 | keep | 0 | Oct | 2021 | 0.15237 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-31 11:59 | 2021-10-31 12:00 | 143 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21103100067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 143 | keep | 0 | Oct | 2021 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
GUAYAMA | 2021-10-31 12:05 | 2021-10-31 13:20 | 15 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21103100012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-10-31 | 1125 | keep | 0 | Oct | 2021 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-10-31 12:07 | 2021-11-01 10:26 | 15 | 022:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21103100018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1339 | 2021-10-31 | 20085 | keep | 0 | Oct | 2021 | 0.01368 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-10-31 12:09 | 2021-10-31 14:17 | 75 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21103100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-10-31 | 9600 | keep | 0 | Oct | 2021 | 0.0065385 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-10-31 12:28 | 2021-10-31 16:31 | 40 | 004:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21103100051 | New_Event | Cutout Failure | Include | Include | Equipment | 243 | 2021-10-31 | 9720 | keep | 0 | Oct | 2021 | 0.0066202 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-10-31 12:48 | 2021-10-31 13:02 | 1026 | 000:14 | T | DESCONECTIVO DEFECTUOSO | DISPARO | R21103100016 | Additional_clients | Switch Failure | Include | Include | Equipment | 14 | 2021-10-31 | 14364 | keep | 0 | Oct | 2021 | 0.0097833 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-31 13:02 | 2021-10-31 17:25 | 400 | 004:23 | P | DESCONECTIVO DEFECTUOSO | SECCIONALIZARON LAZO AVERIADO DEL MH-10 @ MH-1 | R21103100016 | Partial_restoration | Switch Failure | Include | Include | Equipment | 263 | 2021-10-31 | 105200 | keep | 0 | Oct | 2021 | 0.071651 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-10-31 13:26 | 2021-10-31 15:06 | 20 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | M21103100043 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-10-31 | 2000 | keep | 0 | Oct | 2021 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-10-31 14:02 | 2021-10-31 19:29 | 40 | 005:27 | P | DESGANCHE | 1 X 40 EN C/L | C21103100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2021-10-31 | 13080 | keep | 0 | Oct | 2021 | 0.0089087 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-10-31 14:06 | 2021-10-31 16:25 | 11 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE | P21103100015 | New_Event |  |  | Include | Wildlife | 139 | 2021-10-31 | 1529 | keep | 0 | Oct | 2021 | 0.0010414 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2021-10-31 14:21 | 2021-10-31 17:52 | 65 | 003:31 | P | DESGANCHE | 1 X 30 Y 1 X 50 EN CORTE DE LINEA | R21103100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-10-31 | 13715 | keep | 0 | Oct | 2021 | 0.0093412 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 600 | 001:52 | P | LINEA DE TRANSMISION 115KV | DISPARO L-38300 CARGA POR EL 1529-15 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 67200 | keep | 0 | Oct | 2021 | 0.04577 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 74 | 001:52 | T | LINEA DE TRANSMISION 115KV | DISPARO L-38300 CARGA POR EL 1529-11 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 8288 | keep | 0 | Oct | 2021 | 0.0056449 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 1370 | 001:52 | S | LINEA DE TRANSMISION 115KV | DISPARO L-38300 LLEVA EL 1521-02 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 153440 | keep | 0 | Oct | 2021 | 0.10451 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 1984 | 001:52 | S | LINEA DE TRANSMISION 115KV | DISPARO L-38300 LLEVA EL 1911-07 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 222208 | keep | 0 | Oct | 2021 | 0.15134 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 199 | 001:52 | S | LINEA DE TRANSMISION 115KV | DISPARO L-38300 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 22288 | keep | 0 | Oct | 2021 | 0.01518 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 1802 | 001:52 | S | LINEA DE TRANSMISION 115KV | DISPARO L-38300 LLEVA EL 30% DEL 1346-02 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 201824 | keep | 0 | Oct | 2021 | 0.13746 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-10-31 14:39 | 2021-10-31 16:31 | 577 | 001:52 | T | LINEA DE TRANSMISION 115KV | DISPARO L-38300 CARGA POR EL 1529-12 | S21103100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 112 | 2021-10-31 | 64624 | keep | 0 | Oct | 2021 | 0.044015 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
PONCE | 2021-10-31 15:15 | 2021-11-02 12:19 | 50 | 045:04 | P | DESGANCHE | SE REPARO LINEA ROTA POR ARBOL PARTIO LINEA | P21103100019 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2704 | 2021-10-31 | 135200 | keep | 0 | Oct | 2021 | 0.092084 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-10-31 15:50 | 2021-10-31 15:51 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 3941 | keep | 0 | Oct | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
ARECIBO | 2021-10-31 15:53 | 2021-10-31 15:54 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21103100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-31 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BAYAMON | 2021-10-31 15:55 | 2021-10-31 15:56 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-02 LLEVANDO LA CARGA DEL 1720-08 | B21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 2402 | keep | 0 | Oct | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-10-31 15:55 | 2021-10-31 15:56 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-02 LLEVANDO LA CARGA DEL 1720-08 | B21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 1 | keep | 0 | Oct | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-10-31 15:57 | 2021-10-31 15:58 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21103100031 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-31 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-10-31 16:00 | 2021-10-31 16:01 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21103100032 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-31 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
HUMACAO | 2021-10-31 16:04 | 2021-10-31 18:12 | 15 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L NO CAUSA | C21103100070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-10-31 | 1920 | keep | 0 | Oct | 2021 | 0.0013077 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-10-31 16:06 | 2021-10-31 16:07 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21103100033 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-31 | 5042 | keep | 0 | Oct | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-10-31 16:07 | 2021-11-01 10:34 | 9 | 018:27 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | A21103100037 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1107 | 2021-10-31 | 9963 | keep | 0 | Oct | 2021 | 0.0067858 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2021-10-31 16:20 | 2021-11-01 09:39 | 10 | 017:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21103100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1039 | 2021-10-31 | 10390 | keep | 0 | Oct | 2021 | 0.0070766 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-10-31 16:31 | 2021-11-01 12:17 | 80 | 019:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21103100277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1186 | 2021-10-31 | 94880 | keep | 0 | Oct | 2021 | 0.064622 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-10-31 16:32 | 2021-10-31 16:33 | 199 | 000:01 | T | DESGANCHE | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | S21103100266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-31 | 199 | keep | 0 | Oct | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2021-10-31 16:33 | 2021-11-01 12:16 | 10 | 019:43 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | S21103100276 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1183 | 2021-10-31 | 11830 | keep | 0 | Oct | 2021 | 0.0080574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-10-31 16:33 | 2021-10-31 18:14 | 2720 | 001:41 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS SE CERRO INTERRUPTOR | A21103100040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2021-10-31 | 274720 | keep | 0 | Oct | 2021 | 0.18711 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-10-31 16:36 | 2021-10-31 16:37 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21103100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 3431 | keep | 0 | Oct | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2021-10-31 16:37 | 2021-10-31 19:29 | 20 | 002:52 | P | CABLE SOTERRADO AVERIADO | SE INSTALO AEREO PROVISIONAL DE T-6 @ T-7 | B21103100022 | New_Event | UG Cable Fault | Include | Include | Equipment | 172 | 2021-10-31 | 3440 | keep | 0 | Oct | 2021 | 0.002343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-10-31 16:46 | 2021-10-31 18:23 | 20 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21103100043 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-10-31 | 1940 | keep | 0 | Oct | 2021 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-10-31 16:46 | 2021-10-31 20:13 | 35 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A RISER | B21103100023 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2021-10-31 | 7245 | keep | 0 | Oct | 2021 | 0.0049345 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-10-31 16:56 | 2021-10-31 16:57 | 449 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR SE LE CREO EL EVENTO LUEGO YA EL SISTEMA NO LO CREO | P21110100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-10-31 | 449 | keep | 0 | Oct | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2021-10-31 16:57 | 2021-11-01 23:11 | 50 | 030:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110100058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1814 | 2021-10-31 | 90700 | keep | 0 | Oct | 2021 | 0.061775 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-10-31 17:09 | 2021-11-02 19:58 | 20 | 050:49 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL | B21103100025 | New_Event | UG Cable Fault | Include | Include | Equipment | 3049 | 2021-10-31 | 60980 | keep | 0 | Oct | 2021 | 0.041533 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-10-31 17:09 | 2021-11-01 10:31 | 30 | 017:22 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN AEREO PROVISIONAL HACIA T-79. AVERIA SOTERRADA DE T-78 @ T-79 Y DE T-77 @ T-78 | B21103100025 | New_Event | UG Cable Fault | Include | Include | Equipment | 1042 | 2021-10-31 | 31260 | keep | 0 | Oct | 2021 | 0.021291 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-10-31 17:18 | 2021-10-31 17:19 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 4664 | keep | 0 | Oct | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
SAN JUAN | 2021-10-31 17:25 | 2021-10-31 17:53 | 1026 | 000:28 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL REALIZANDO OPERACIONES EN LAZO AVERIADO DEL MH-10 @ MH-1 | R21103100016 | Additional_clients | Switch Failure | Include | Include | Equipment | 28 | 2021-10-31 | 28728 | keep | 0 | Oct | 2021 | 0.019567 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-10-31 17:35 | 2021-10-31 17:36 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21103100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-31 | 3006 | keep | 0 | Oct | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-10-31 17:35 | 2021-10-31 17:36 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21103100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-31 | 179 | keep | 0 | Oct | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | TRUE | Not_TMED_Event | 179
MAYAGÃœEZ | 2021-10-31 17:35 | 2021-10-31 17:36 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21103100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-31 | 3147 | keep | 0 | Oct | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-10-31 17:35 | 2021-10-31 17:36 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M21103100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-10-31 | 4304 | keep | 0 | Oct | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
HUMACAO | 2021-10-31 17:46 | 2021-10-31 17:47 | 100 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L CERRO PUENTE | C21103100016 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-10-31 | 100 | keep | 0 | Oct | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-10-31 17:48 | 2021-10-31 17:49 | 1000 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1401-08 1 VEZ QUEDO FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE 1303-2 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 1000 | keep | 0 | Oct | 2021 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-10-31 17:48 | 2021-10-31 17:49 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1401-08 1 VEZ QUEDO FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-5 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-10-31 17:48 | 2021-10-31 17:49 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1401-08 1 VEZ QUEDO FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE DEL 1348-8 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 500 | keep | 0 | Oct | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-10-31 17:48 | 2021-10-31 17:49 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1 VEZ QUEDO FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-5, PARTE DEL 1348-8 Y PARTE 1303-2 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 135 | keep | 0 | Oct | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2021-10-31 17:49 | 2021-11-01 13:24 | 10 | 019:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA, CAJA PRIMARIA Y PARARRAYO | C21103100073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1175 | 2021-10-31 | 11750 | keep | 0 | Oct | 2021 | 0.0080029 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-31 17:53 | 2021-10-31 17:55 | 400 | 000:02 | P | DESCONECTIVO DEFECTUOSO | SECCIONALIZARON LAZO AVERIADO DEL MH-10 @ MH-1 | R21103100016 | Partial_restoration | Switch Failure | Include | Include | Equipment | 2 | 2021-10-31 | 800 | keep | 0 | Oct | 2021 | 0.00054488 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-10-31 17:55 | 2021-10-31 17:56 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL REALIZANDO OPERACIONES EN LAZO AVERIADO DEL MH-10 @ MH-1 | R21103100016 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-10-31 | 1026 | keep | 0 | Oct | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-10-31 17:56 | 2021-10-31 18:19 | 400 | 000:23 | P | DESCONECTIVO DEFECTUOSO | SECCIONALIZARON LAZO AVERIADO DEL MH-10 @ MH-1 | R21103100016 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 23 | 2021-10-31 | 9200 | keep | 0 | Oct | 2021 | 0.0062661 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2021-10-31 18:00 | 2021-10-31 19:45 | 10 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21103100017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-10-31 | 1050 | keep | 0 | Oct | 2021 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-10-31 18:19 | 2021-11-01 06:33 | 300 | 012:14 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO 2 VACCUUM SWITCH Y 1 BOLT T | R21110100007 | Partial_restoration | Switch Failure | Include | Include | Equipment | 734 | 2021-10-31 | 220200 | keep | 0 | Oct | 2021 | 0.14998 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-10-31 18:27 | 2021-10-31 19:20 | 60 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21103100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-10-31 | 3180 | keep | 0 | Oct | 2021 | 0.0021659 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-10-31 18:29 | 2021-11-01 12:26 | 15 | 017:57 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y DESGANCHE | S21103100288 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1077 | 2021-10-31 | 16155 | keep | 0 | Oct | 2021 | 0.011003 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-10-31 18:48 | 2021-10-31 20:50 | 7 | 002:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR SE REMPLAZO SECUNDARIA | S21103100290 | New_Event | Secondary Wire Down | Include | Include | Equipment | 122 | 2021-10-31 | 854 | keep | 0 | Oct | 2021 | 0.00058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-10-31 18:48 | 2021-10-31 19:05 | 20 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21103100011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2021-10-31 | 340 | keep | 0 | Oct | 2021 | 0.00023157 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-10-31 19:23 | 2021-10-31 19:24 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1336-06 QUE LLEVA PARTE 1303-2 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 300 | keep | 0 | Oct | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-31 19:23 | 2021-10-31 19:24 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1336-06 QUE LLEVA PARTE 1303-2 | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 6481 | keep | 0 | Oct | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-10-31 19:23 | 2021-10-31 19:24 | 40 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 40 | keep | 0 | Oct | 2021 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-10-31 20:03 | 2021-11-01 13:19 | 98 | 017:16 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO 2 DISCOS Y DESGANCHARON | C21103100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1036 | 2021-10-31 | 101528 | keep | 0 | Oct | 2021 | 0.06915 | 6.6747e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 98
BAYAMON | 2021-10-31 20:07 | 2021-10-31 20:08 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21103100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 3295 | keep | 0 | Oct | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295