SAN JUAN | 2022-01-17 11:07 | 2022-01-17 14:00 | 50 | 002:53 | P | DESGANCHE | 1X100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-17 | 8650 | keep | 0 | Jan | 2022 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-17 11:09 | 2022-01-17 15:53 | 200 | 004:44 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22011700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2022-01-17 | 56800 | keep | 0 | Jan | 2022 | 0.038686 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-01-17 11:26 | 2022-01-17 14:40 | 10 | 003:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22011700025 | New_Event | Bad Weather | Include | Include | Weather | 194 | 2022-01-17 | 1940 | keep | 0 | Jan | 2022 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-17 11:34 | 2022-01-17 16:40 | 600 | 005:06 | P | ERROR HUMANO | 2 X 140 EN CORTE DE LINEA. SE LEVANTO CONDUCTOR EN EL SUELO DEBIDO A DESGANCHE COMPAÃ‘IA XPERT DEJO CAER RAMA SOBRE LINEA | B22011700022 | Partial_restoration | Human Error | Include | Include | Other | 306 | 2022-01-17 | 183600 | keep | 0 | Jan | 2022 | 0.12505 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-17 11:50 | 2022-01-17 15:35 | 140 | 003:45 | P | NO SE REPORTO CAUSA | 1 X40 Y 1 X 100 EN CORTE DE LINEA | C22011700089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2022-01-17 | 31500 | keep | 0 | Jan | 2022 | 0.021455 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2022-01-17 11:59 | 2022-01-17 13:17 | 60 | 001:18 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN C/L | C22011700090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-01-17 | 4680 | keep | 0 | Jan | 2022 | 0.0031875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-17 12:03 | 2022-01-17 15:56 | 100 | 003:53 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22011700057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2022-01-17 | 23300 | keep | 0 | Jan | 2022 | 0.01587 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-01-17 12:19 | 2022-01-17 12:20 | 2747 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22011700029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-17 | 2747 | keep | 0 | Jan | 2022 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2022-01-17 12:20 | 2022-01-17 15:26 | 65 | 003:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P22011700036 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-01-17 | 12090 | keep | 0 | Jan | 2022 | 0.0082344 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-01-17 13:02 | 2022-01-17 14:16 | 12 | 001:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22011700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-01-17 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-17 13:07 | 2022-01-18 10:00 | 1 | 020:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER UL2 INDICO NO IDENTIFICO CAUSA | M22011700062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1253 | 2022-01-17 | 1253 | keep | 0 | Jan | 2022 | 0.00085341 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-17 13:11 | 2022-01-17 13:23 | 164 | 0:12 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1531-02 LLEVA TRANSFERIDA LA CARGA DEL 1421-02 | S22011700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-01-17 | 1968 | keep | 0 | Jan | 2022 | 0.0013404 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-01-17 13:11 | 2022-01-17 13:23 | 716 | 000:12 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA CARGA DEL 1421-02 | S22011700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-01-17 | 8592 | keep | 0 | Jan | 2022 | 0.005852 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
BARRANQUITAS | 2022-01-17 13:31 | 2022-01-17 13:32 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-17 | 1834 | keep | 0 | Jan | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-01-17 13:34 | 2022-01-17 13:37 | 199 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22011700068 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2022-01-17 | 597 | keep | 0 | Jan | 2022 | 0.00040661 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-01-17 13:35 | 2022-01-17 15:00 | 200 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA 2 X 100 EN CORTE DE LINEA Y 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011700064 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2022-01-17 | 17000 | keep | 0 | Jan | 2022 | 0.011579 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-01-17 13:37 | 2022-01-17 20:31 | 70 | 006:54 | P | DESCONECTIVO DEFECTUOSO | SE IDENTIFICO MACHETE AVERIADO EN FID 17436790 | S22011700080 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 414 | 2022-01-17 | 28980 | keep | 0 | Jan | 2022 | 0.019738 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-17 13:45 | 2022-01-17 14:45 | 20 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011700070 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2022-01-17 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-17 13:46 | 2022-01-17 16:39 | 7 | 002:53 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA PARA DESGANCHAR Y REPARAR SECUNDARIA | R22011700033 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 173 | 2022-01-17 | 1211 | keep | 0 | Jan | 2022 | 0.00082481 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-01-17 13:50 | 2022-01-17 14:58 | 15 | 001:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR Y SE REPARO SECUNDARIA | C22011700113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 68 | 2022-01-17 | 1020 | keep | 0 | Jan | 2022 | 0.00069472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-17 13:58 | 2022-01-17 13:59 | 2560 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22011700073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-17 | 2560 | keep | 0 | Jan | 2022 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
MAYAGÃœEZ | 2022-01-17 13:59 | 2022-01-17 19:00 | 50 | 005:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | M22011700089 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2022-01-17 | 15050 | keep | 0 | Jan | 2022 | 0.01025 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-17 14:05 | 2022-01-17 16:03 | 40 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22011700078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-01-17 | 4720 | keep | 0 | Jan | 2022 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-01-17 14:15 | 2022-01-17 16:09 | 10 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22011700118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-01-17 | 1140 | keep | 0 | Jan | 2022 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-17 14:47 | 2022-01-17 14:48 | 1827 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMAS SOBRE LINEAS | M22011700078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-17 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-01-17 14:48 | 2022-01-17 17:55 | 25 | 003:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BEJUCO SOBRE LAS LINEAS | M22011700088 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-01-17 | 4675 | keep | 0 | Jan | 2022 | 0.0031841 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-17 14:51 | 2022-01-17 16:39 | 20 | 001:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C22011700126 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2022-01-17 | 2160 | keep | 0 | Jan | 2022 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-17 14:53 | 2022-01-17 18:01 | 10 | 003:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REMPLAZO CAJA TRANSFORMADOR AVERIADA | M22011700080 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2022-01-17 | 1880 | keep | 0 | Jan | 2022 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-17 14:53 | 2022-01-17 18:24 | 7 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | M22011700079 | New_Event |  |  | Include | Wildlife | 211 | 2022-01-17 | 1477 | keep | 0 | Jan | 2022 | 0.001006 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-01-17 15:02 | 2022-01-17 16:59 | 11 | 001:57 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR DE 37.5 KVA A 4160 VOLTS POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22011700044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 117 | 2022-01-17 | 1287 | keep | 0 | Jan | 2022 | 0.00087657 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-01-17 15:02 | 2022-01-17 16:30 | 10 | 001:28 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR, SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B22011700058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 88 | 2022-01-17 | 880 | keep | 0 | Jan | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-17 15:08 | 2022-01-17 15:09 | 1417 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DEL INTERRUPTOR PARARRAYOS DEFECTUOSO | M22011700084 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-17 | 1417 | keep | 0 | Jan | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2022-01-17 15:09 | 2022-01-17 17:20 | 300 | 002:11 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE RETIRO PARARRAYOS DEFECTUOSO | M22011700090 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 131 | 2022-01-17 | 39300 | keep | 0 | Jan | 2022 | 0.026767 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-01-17 15:16 | 2022-01-17 15:17 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22011700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-17 | 2039 | keep | 0 | Jan | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
AGUADILLA | 2022-01-17 15:40 | 2022-01-17 17:20 | 12 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA Y CONEXIONES SECUNDARIAS | M22011700029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-01-17 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-17 15:48 | 2022-01-17 17:50 | 2402 | 002:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1709-02 LLEVANDO LA CARGA DEL 1720-08 GOI BY-220117-01 | S22011700069 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-01-17 | 293044 | keep | 0 | Jan | 2022 | 0.19959 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-01-17 15:48 | 2022-01-17 20:38 | 1 | 004:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1709-02 LLEVANDO LA CARGA DEL 1720-08 | B22011700069 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2022-01-17 | 290 | keep | 0 | Jan | 2022 | 0.00019752 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-17 15:52 | 2022-01-17 16:56 | 10 | 001:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R22011700040 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2022-01-17 | 640 | keep | 0 | Jan | 2022 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-17 16:09 | 2022-01-17 17:50 | 100 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011700100 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2022-01-17 | 10100 | keep | 0 | Jan | 2022 | 0.0068791 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-17 16:15 | 2022-01-17 17:03 | 4 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RERARAR LINEA SECUNDARIA | A22011700038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2022-01-17 | 192 | keep | 0 | Jan | 2022 | 0.00013077 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-17 16:26 | 2022-01-17 18:27 | 40 | 002:01 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L. SE REEMPLAZO PARARRAYO | B22011700078 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 121 | 2022-01-17 | 4840 | keep | 0 | Jan | 2022 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-01-17 16:58 | 2022-01-17 19:28 | 7 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C22011700137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2022-01-17 | 1050 | keep | 0 | Jan | 2022 | 0.00071515 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-01-17 17:05 | 2022-01-17 19:15 | 40 | 002:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE | P22011700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-01-17 | 5200 | keep | 0 | Jan | 2022 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-17 17:08 | 2022-01-17 17:45 | 15 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011700126 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-01-17 | 555 | keep | 0 | Jan | 2022 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-17 17:20 | 2022-01-17 17:21 | 1417 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DEL INTERRUPTOR PARARRAYOS DEFECTUOSO | M22011700112 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-17 | 1417 | keep | 0 | Jan | 2022 | 0.00096511 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-17 17:21 | 2022-01-17 18:10 | 300 | 000:49 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE RETIRO PARARRAYOS DEFECTUOSO | M22011700090 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 49 | 2022-01-17 | 14700 | keep | 0 | Jan | 2022 | 0.010012 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-01-17 17:30 | 2022-01-17 18:07 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R22011700047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-01-17 | 370 | keep | 0 | Jan | 2022 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-17 17:44 | 2022-01-17 18:20 | 15 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011700043 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2022-01-17 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-17 17:50 | 2022-01-17 18:19 | 1920 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 20% EN SERVICIO DEL 1709-02 GOI BY-220117-01 | S22011700069 | Partial_restoration | Wire Down | Include | Include | Equipment | 29 | 2022-01-17 | 55680 | keep | 0 | Jan | 2022 | 0.037923 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-17 17:55 | 2022-01-18 13:40 | 8 | 019:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 75 KVA | M22011700118 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1185 | 2022-01-17 | 9480 | keep | 0 | Jan | 2022 | 0.0064568 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-01-17 18:19 | 2022-01-17 18:22 | 280 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1709-02 CON 20% DE SU CARGA AL CERRAR MACHETES EN FID 23078170. SE ABRIERON NUEVAMENTE Y SE CERRO ALIMENTADOR 1709-02. GOI BY-220117-01 | S22011700069 | Partial_restoration | Wire Down | Include | Include | Equipment | 3 | 2022-01-17 | 840 | keep | 0 | Jan | 2022 | 0.00057212 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-17 18:20 | 2022-01-18 13:45 | 250 | 019:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR PRIMARIO Y SE CERRO MACHETES GOI BY-220117-01 | B22011700069 | New_Event | Wire Down | Include | Include | Equipment | 1165 | 2022-01-17 | 291250 | keep | 0 | Jan | 2022 | 0.19837 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-01-17 18:22 | 2022-01-17 20:38 | 1123 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 80% EN SERVICIO AL ABRIR MACHETES EN FID15774835 Y CERRANDO EN FID 23078170. GOI BY-220117-01 | S22011700069 | New_Event | Wire Down | Include | Include | Equipment | 136 | 2022-01-17 | 152728 | keep | 0 | Jan | 2022 | 0.10402 | 0.00076487 | Sustained | FALSE | FALSE | Not_TMED_Event | 1123
YAUCO | 2022-01-17 18:23 | 2022-01-18 12:15 | 30 | 017:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22011700057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1072 | 2022-01-17 | 32160 | keep | 0 | Jan | 2022 | 0.021904 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-17 18:27 | 2022-01-17 21:39 | 20 | 003:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO T-83 AVERIADO MEDIANTE GOI BY-220117-03. SE AFECTO TAMBIEN EL T-84 | B22011700023 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 192 | 2022-01-17 | 3840 | keep | 0 | Jan | 2022 | 0.0026154 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-17 18:33 | 2022-01-17 18:34 | 766 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO EL 1709-03 LLEVANDO EL 1709-05. 50% DEL 1709-03 ESTA POR EL 1909-07 | B22011700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-17 | 766 | keep | 0 | Jan | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-01-17 18:33 | 2022-01-17 18:34 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO EL 1709-03 LLEVANDO EL 1709-05. 50% DEL 1709-03 ESTA POR EL 1909-07 | B22011700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-17 | 2364 | keep | 0 | Jan | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
MAYAGÃœEZ | 2022-01-17 18:44 | 2022-01-18 12:56 | 60 | 018:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011700122 | New_Event | Bad Weather | Include | Include | Weather | 1092 | 2022-01-17 | 65520 | keep | 0 | Jan | 2022 | 0.044625 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-01-17 18:55 | 2022-01-18 10:17 | 7 | 015:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22011700146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 922 | 2022-01-17 | 6454 | keep | 0 | Jan | 2022 | 0.0043958 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-17 19:40 | 2022-01-18 11:55 | 41 | 016:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22011700174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 975 | 2022-01-17 | 39975 | keep | 0 | Jan | 2022 | 0.027227 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2022-01-17 19:41 | 2022-01-17 20:23 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARARON CONEXIONES | B22011700083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-01-17 | 420 | keep | 0 | Jan | 2022 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-17 20:10 | 2022-01-17 20:38 | 193 | 000:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22011700055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-01-17 | 5404 | keep | 0 | Jan | 2022 | 0.0036806 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
SAN JUAN | 2022-01-17 20:24 | 2022-01-17 21:53 | 7 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | R22011700059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2022-01-17 | 623 | keep | 0 | Jan | 2022 | 0.00042432 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-17 20:31 | 2022-01-17 21:42 | 199 | 001:11 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO MEDIANTE GOI BY-220117-02 | S22011700068 | Additional_clients | Switch Failure | Include | Include | Equipment | 71 | 2022-01-17 | 14129 | keep | 0 | Jan | 2022 | 0.0096232 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-17 20:41 | 2022-01-17 22:30 | 50 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S22011700193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-01-17 | 5450 | keep | 0 | Jan | 2022 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-17 21:02 | 2022-01-18 09:34 | 30 | 012:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE LLEVO LINEA A AISLADOR | B22011700097 | New_Event | Wire Down | Include | Include | Equipment | 752 | 2022-01-17 | 22560 | keep | 0 | Jan | 2022 | 0.015366 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-17 21:18 | 2022-01-18 10:04 | 32 | 012:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22011700204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 766 | 2022-01-17 | 24512 | keep | 0 | Jan | 2022 | 0.016695 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2022-01-17 22:15 | 2022-01-18 09:55 | 40 | 011:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | M22011700140 | New_Event |  |  | Include | Wildlife | 700 | 2022-01-17 | 28000 | keep | 0 | Jan | 2022 | 0.019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-17 22:30 | 2022-01-17 22:31 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22011700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-17 | 1478 | keep | 0 | Jan | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
SAN JUAN | 2022-01-18 | 2022-01-18 00:01 | 922 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1401-08 DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-01-18 | 2022-01-18 00:01 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 135 | keep | 0 | Jan | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
AGUADILLA | 2022-01-18 00:17 | 2022-01-18 09:30 | 15 | 009:13 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR INDICA UL2 NO IDENTIFICO CAUSA | M22011800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 553 | 2022-01-18 | 8295 | keep | 0 | Jan | 2022 | 0.0056497 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-18 04:41 | 2022-01-18 13:36 | 200 | 008:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22011800002 | New_Event | Cutout Failure | Include | Include | Equipment | 535 | 2022-01-18 | 107000 | keep | 0 | Jan | 2022 | 0.072877 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-01-18 06:18 | 2022-01-18 13:44 | 200 | 007:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | R22011800007 | New_Event | Wire Down | Include | Include | Equipment | 446 | 2022-01-18 | 89200 | keep | 0 | Jan | 2022 | 0.060754 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-01-18 06:29 | 2022-01-18 07:49 | 1058 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO SE TRANSFIRIO CARGA AL 1424-08 PARA BRINDAR SERVICIO AL HOSPITAL 20% DE LA CARGA POR EL 1348-08 | S22011800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2022-01-18 | 84640 | keep | 0 | Jan | 2022 | 0.057648 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-01-18 06:29 | 2022-01-18 07:49 | 251 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE TRANSFIRIO CARGA AL 1424-08. SE REMPLAZO AISLADOR PARTIDO DEL 1348-8. 20% POR EL 1348-08 | S22011800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2022-01-18 | 20080 | keep | 0 | Jan | 2022 | 0.013676 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
SAN JUAN | 2022-01-18 06:29 | 2022-01-18 09:18 | 1290 | 002:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REMPLAZO AISLADOR PARTIDO Y SE CERRO INTERRUPTOR. LLEVA 20% DEL 1348-06 Y 20% DEL 1336-08 | S22011800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 169 | 2022-01-18 | 218010 | keep | 0 | Jan | 2022 | 0.14849 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
MAYAGÃœEZ | 2022-01-18 06:54 | 2022-01-18 12:50 | 100 | 005:56 | P | DESGANCHE | 2 X 65 Y 2 X 50 EN CORTES DE LINEAS SE RETIRO BAMBUS SOBRE LAS LINEAS | M22011800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2022-01-18 | 35600 | keep | 0 | Jan | 2022 | 0.024247 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-18 07:04 | 2022-01-18 09:44 | 125 | 002:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22011800006 | New_Event |  |  | Include | Wildlife | 160 | 2022-01-18 | 20000 | keep | 0 | Jan | 2022 | 0.013622 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
GUAYAMA | 2022-01-18 07:15 | 2022-01-18 10:51 | 1 | 003:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE DE LINEA PRIMARIA A CAJA EN RISER | P22011800003 | New_Event | Wire Down | Include | Include | Equipment | 216 | 2022-01-18 | 216 | keep | 0 | Jan | 2022 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-18 07:25 | 2022-01-18 11:10 | 15 | 003:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO 80 PIES DE SECUNDARIA | C22011800008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 225 | 2022-01-18 | 3375 | keep | 0 | Jan | 2022 | 0.0022987 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-01-18 07:39 | 2022-01-18 13:37 | 50 | 005:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN TRONCAL | C22011800009 | New_Event | Wire Down | Include | Include | Equipment | 358 | 2022-01-18 | 17900 | keep | 0 | Jan | 2022 | 0.012192 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-18 07:51 | 2022-01-18 18:25 | 40 | 010:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 634 | 2022-01-18 | 25360 | keep | 0 | Jan | 2022 | 0.017273 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-18 08:33 | 2022-01-18 12:06 | 41 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22011800053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-01-18 | 8733 | keep | 0 | Jan | 2022 | 0.005948 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
VEGA BAJA | 2022-01-18 08:53 | 2022-01-18 10:24 | 6 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | B22011800013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2022-01-18 | 546 | keep | 0 | Jan | 2022 | 0.00037188 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-01-18 08:55 | 2022-01-18 11:43 | 6 | 002:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | R22011800018 | New_Event |  |  | Include | Wildlife | 168 | 2022-01-18 | 1008 | keep | 0 | Jan | 2022 | 0.00068654 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-01-18 09:04 | 2022-01-18 18:22 | 2 | 009:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A22011800014 | New_Event | Wire Down | Include | Include | Equipment | 558 | 2022-01-18 | 1116 | keep | 0 | Jan | 2022 | 0.0007601 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-01-18 09:05 | 2022-01-18 09:07 | 4304 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN ON NO RECERRO NO SE REPORTO CAUSA SE CERRO POR CONTROL SCADA | M22011800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-18 | 8608 | keep | 0 | Jan | 2022 | 0.0058629 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2022-01-18 09:13 | 2022-01-18 18:40 | 50 | 009:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y NEUTRAL PARTIDO | M22011800037 | New_Event | Wire Down | Include | Include | Equipment | 567 | 2022-01-18 | 28350 | keep | 0 | Jan | 2022 | 0.019309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-18 09:18 | 2022-01-18 09:21 | 1615 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-18 | 4845 | keep | 0 | Jan | 2022 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
ARECIBO | 2022-01-18 09:18 | 2022-01-18 13:44 | 50 | 004:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-01-18 | 13300 | keep | 0 | Jan | 2022 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-18 09:19 | 2022-01-18 15:13 | 10 | 005:54 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR. SE REALIZO DESGANCHE DE ENREDADERA | C22011800027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 354 | 2022-01-18 | 3540 | keep | 0 | Jan | 2022 | 0.0024111 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-18 09:31 | 2022-01-18 10:09 | 1291 | 000:38 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 30% POR EL 1529-15 | S21011800100 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-01-18 | 49058 | keep | 0 | Jan | 2022 | 0.033413 | 0.00087929 | Sustained | FALSE | FALSE | Not_TMED_Event | 1291
BAYAMON | 2022-01-18 09:31 | 2022-01-18 10:09 | 1370 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 | S22011800100 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-01-18 | 52060 | keep | 0 | Jan | 2022 | 0.035458 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-01-18 09:31 | 2022-01-18 10:09 | 1984 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 | S22011800100 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-01-18 | 75392 | keep | 0 | Jan | 2022 | 0.051349 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-01-18 09:31 | 2022-01-18 10:09 | 199 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 | S22011800100 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-01-18 | 7562 | keep | 0 | Jan | 2022 | 0.0051504 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-01-18 09:31 | 2022-01-18 10:09 | 1802 | 000:38 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 | S22011800100 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-01-18 | 68476 | keep | 0 | Jan | 2022 | 0.046639 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-01-18 09:31 | 2022-01-18 11:27 | 37 | 001:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4400 | S22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-01-18 | 4292 | keep | 0 | Jan | 2022 | 0.0029233 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-01-18 09:31 | 2022-01-18 11:27 | 7 | 001:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4400 | S22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-01-18 | 812 | keep | 0 | Jan | 2022 | 0.00055305 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-18 09:31 | 2022-01-18 11:27 | 2 | 001:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4400 | S22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-01-18 | 232 | keep | 0 | Jan | 2022 | 0.00015801 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-18 09:31 | 2022-01-18 10:09 | 577 | 000:38 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 CARGA POR 1529-12 | S22011800000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-01-18 | 21926 | keep | 0 | Jan | 2022 | 0.014934 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
MAYAGÃœEZ | 2022-01-18 09:36 | 2022-01-18 21:34 | 100 | 011:58 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA SE SECCIONALIZO ALIMENTADOR QUE DA SERVICIO A AREA DE UTUADO REQUIERE PATRULLAJE DE DIA POR PERSONAL DE UTUADO | M22011800041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 718 | 2022-01-18 | 71800 | keep | 0 | Jan | 2022 | 0.048903 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-18 09:50 | 2022-01-18 10:42 | 10 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M22011800043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-01-18 | 520 | keep | 0 | Jan | 2022 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-18 09:52 | 2022-01-18 11:29 | 3 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO RISER HACIA PM PARA ACOMODARLO BIEN EN BASE FUE IMPACTADO | C22011800018 | New_Event |  |  | Include | Wildlife | 97 | 2022-01-18 | 291 | keep | 0 | Jan | 2022 | 0.0001982 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-01-18 10:03 | 2022-01-18 11:48 | 162 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR LAGARTO | C22011800019 | New_Event |  |  | Include | Wildlife | 105 | 2022-01-18 | 17010 | keep | 0 | Jan | 2022 | 0.011585 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
ARECIBO | 2022-01-18 10:08 | 2022-01-18 18:40 | 60 | 008:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011800020 | New_Event | Bad Weather | Include | Include | Weather | 512 | 2022-01-18 | 30720 | keep | 0 | Jan | 2022 | 0.020923 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-01-18 10:10 | 2022-01-18 11:06 | 10 | 000:56 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 13.2 KV DEBIDO A ESCAPE DE ACEITE | P22011800011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 56 | 2022-01-18 | 560 | keep | 0 | Jan | 2022 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-18 10:11 | 2022-01-18 13:47 | 3 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22011800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2022-01-18 | 648 | keep | 0 | Jan | 2022 | 0.00044135 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-01-18 10:17 | 2022-01-18 15:25 | 13 | 005:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 25KVA POR UNO DE 50KVA | C22011800020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 308 | 2022-01-18 | 4004 | keep | 0 | Jan | 2022 | 0.0027271 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2022-01-18 10:22 | 2022-01-18 12:56 | 3 | 002:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA PARA REPARAR BAJANTE SECUNDARIO Y REEMPLAZO SECUNDARIA | C22011800021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 154 | 2022-01-18 | 462 | keep | 0 | Jan | 2022 | 0.00031467 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-01-18 10:35 | 2022-01-18 11:39 | 2 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22011800032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-01-18 | 128 | keep | 0 | Jan | 2022 | 8.718e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-18 10:43 | 2022-01-18 14:25 | 60 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTE DE LINEA | B22011800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-01-18 | 13320 | keep | 0 | Jan | 2022 | 0.0090722 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-18 11:11 | 2022-01-18 12:45 | 13 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON RATA | R22011800034 | New_Event |  |  | Include | Wildlife | 94 | 2022-01-18 | 1222 | keep | 0 | Jan | 2022 | 0.0008323 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-01-18 11:19 | 2022-01-18 14:53 | 10 | 003:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE REALIZO ENREDADERA | C22011800027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 214 | 2022-01-18 | 2140 | keep | 0 | Jan | 2022 | 0.0014575 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-18 11:25 | 2022-01-18 12:16 | 1 | 000:51 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYOS | C22011800029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 51 | 2022-01-18 | 51 | keep | 0 | Jan | 2022 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-18 11:34 | 2022-01-18 13:58 | 6 | 002:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P22011800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-01-18 | 864 | keep | 0 | Jan | 2022 | 0.00058847 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-18 11:36 | 2022-01-18 12:09 | 35 | 000:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | C22011800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2022-01-18 | 1155 | keep | 0 | Jan | 2022 | 0.00078667 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-01-18 11:40 | 2022-01-18 11:54 | 9 | 000:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22011800001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 14 | 2022-01-18 | 126 | keep | 0 | Jan | 2022 | 8.5818e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-01-18 11:45 | 2022-01-18 17:35 | 10 | 005:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22011800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-01-18 | 3500 | keep | 0 | Jan | 2022 | 0.0023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-18 12:05 | 2022-01-18 16:14 | 50 | 004:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA Y SE SECCIONALIZO POSTE PARTIDO IMPACTADO POR CAMINIO | S22011800156 | New_Event |  |  | Include | Wildlife | 249 | 2022-01-18 | 12450 | keep | 0 | Jan | 2022 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-18 12:23 | 2022-01-18 15:43 | 100 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M22011800059 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2022-01-18 | 20000 | keep | 0 | Jan | 2022 | 0.013622 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-18 12:31 | 2022-01-18 14:14 | 1 | 001:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A22011800029 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2022-01-18 | 103 | keep | 0 | Jan | 2022 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-18 13:10 | 2022-01-18 13:51 | 15 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B22011800024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2022-01-18 | 615 | keep | 0 | Jan | 2022 | 0.00041887 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-01-18 13:19 | 2022-01-18 19:26 | 9 | 006:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE IMPACTADO POR VEHICULO PRIVADO | R22011800041 | New_Event |  |  | Include | Wildlife | 367 | 2022-01-18 | 3303 | keep | 0 | Jan | 2022 | 0.0022497 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-01-18 13:22 | 2022-01-18 17:09 | 200 | 003:47 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | B22011800043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-01-18 | 45400 | keep | 0 | Jan | 2022 | 0.030922 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-01-18 13:24 | 2022-01-18 16:30 | 80 | 003:06 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S22011800167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2022-01-18 | 14880 | keep | 0 | Jan | 2022 | 0.010135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-01-18 13:35 | 2022-01-18 15:15 | 10 | 001:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA EN XMR, SE REPARO BAJANTE SECUNDARIA Y SE RETIRO ENREDADERA | C22011800041 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2022-01-18 | 1000 | keep | 0 | Jan | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-01-18 13:37 | 2022-01-18 15:00 | 150 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO MEDIANTE GOI CG-220118-01 | C22011800009 | New_Event | Wire Down | Include | Include | Equipment | 83 | 2022-01-18 | 12450 | keep | 0 | Jan | 2022 | 0.0084796 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-01-18 13:37 | 2022-01-18 18:44 | 12 | 005:07 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR DE 37.5 A 4160 POR UNO DE LA MISMA CAPACIDAD | P22011800031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 307 | 2022-01-18 | 3684 | keep | 0 | Jan | 2022 | 0.0025092 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-18 13:40 | 2022-01-18 15:02 | 10 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22011800071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2022-01-18 | 820 | keep | 0 | Jan | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-18 13:50 | 2022-01-18 16:10 | 9 | 002:20 | P | ERROR HUMANO | 2 X 40 EN CORTE DE LINEA COMPAÃ‘IA PRIVADA XPERTS REALIZANDO DESGANCHE CRUZARON FASE CON RAMA DE ARBOL. | P22011800032 | New_Event | Human Error | Include | Include | Other | 140 | 2022-01-18 | 1260 | keep | 0 | Jan | 2022 | 0.00085818 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-01-18 14:00 | 2022-01-18 16:22 | 761 | 002:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1310-04 QUE A SU VEZ LLEVA LA CARGA DEL 1421-01. SE REALIZO DESGANCHE Y SE CERRO INTERRUPTOR | S22011800171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-18 | 108062 | keep | 0 | Jan | 2022 | 0.073601 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-01-18 14:00 | 2022-01-18 16:22 | 164 | 002:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1310-04 QUE A SU VEZ LLEVA LA CARGA DEL 1421-01. SE REALIZO DESGANCHE Y SE CERRO INTERRUPTOR | S22011800171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-18 | 23288 | keep | 0 | Jan | 2022 | 0.015861 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
CANOVANAS | 2022-01-18 14:08 | 2022-01-18 16:49 | 3 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | R22011800043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2022-01-18 | 483 | keep | 0 | Jan | 2022 | 0.00032897 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-01-18 14:10 | 2022-01-18 17:58 | 40 | 003:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L SE RETIRO AVE | C22011800043 | New_Event |  |  | Include | Wildlife | 228 | 2022-01-18 | 9120 | keep | 0 | Jan | 2022 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-01-18 14:11 | 2022-01-18 15:38 | 1 | 001:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | R22011800044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 87 | 2022-01-18 | 87 | keep | 0 | Jan | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-18 14:19 | 2022-01-18 16:40 | 15 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22011800052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2022-01-18 | 2115 | keep | 0 | Jan | 2022 | 0.0014405 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-01-18 14:30 | 2022-01-18 17:25 | 20 | 002:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50KVA POR 50 KVA | A22011800037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 175 | 2022-01-18 | 3500 | keep | 0 | Jan | 2022 | 0.0023838 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-18 14:33 | 2022-01-18 18:24 | 350 | 003:51 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE DE AMARRE QUEMADO ENTRE 1525-02 Y 1525-05 | S22011800197 | New_Event | Switch Failure | Include | Include | Equipment | 231 | 2022-01-18 | 80850 | keep | 0 | Jan | 2022 | 0.055067 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2022-01-18 14:38 | 2022-01-18 16:45 | 50 | 002:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | M22011800081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-01-18 | 6350 | keep | 0 | Jan | 2022 | 0.004325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-18 14:40 | 2022-01-18 14:41 | 75 | 000:01 | P | NO SE REPORTO CAUSA | 20% DE LA CARGA TRANSFERIDA AL 1717-04 INTERRUPTOR RECERRO | B22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 75 | keep | 0 | Jan | 2022 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-01-18 14:40 | 2022-01-18 14:41 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 20% 1716-02 | B22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 1362 | keep | 0 | Jan | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
ARECIBO | 2022-01-18 14:44 | 2022-01-18 16:28 | 40 | 001:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-01-18 | 4160 | keep | 0 | Jan | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-18 14:46 | 2022-01-18 15:40 | 9 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA Y REGULAR VOLTAJE | P22011800036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-18 | 486 | keep | 0 | Jan | 2022 | 0.00033101 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-18 14:47 | 2022-01-18 22:33 | 80 | 007:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 466 | 2022-01-18 | 37280 | keep | 0 | Jan | 2022 | 0.025391 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-01-18 14:50 | 2022-01-18 16:03 | 40 | 001:13 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO RAMA | C22011800047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-01-18 | 2920 | keep | 0 | Jan | 2022 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-18 15:35 | 2022-01-18 18:44 | 15 | 003:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | B22011800060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 189 | 2022-01-18 | 2835 | keep | 0 | Jan | 2022 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-01-18 15:43 | 2022-01-18 17:30 | 40 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22011800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-01-18 | 4280 | keep | 0 | Jan | 2022 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-18 15:45 | 2022-01-18 20:00 | 10 | 004:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA AVERIADO | B22011800061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 255 | 2022-01-18 | 2550 | keep | 0 | Jan | 2022 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-01-18 16:02 | 2022-01-18 17:27 | 20 | 001:25 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA | R22011800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-01-18 | 1700 | keep | 0 | Jan | 2022 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-18 16:15 | 2022-01-18 17:16 | 20 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22011800069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-01-18 | 1220 | keep | 0 | Jan | 2022 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-18 16:20 | 2022-01-19 04:30 | 30 | 012:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PARTIDO IMPACTADO POR CAMION | S22011800156 | New_Event |  |  | Include | Wildlife | 730 | 2022-01-18 | 21900 | keep | 0 | Jan | 2022 | 0.014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-01-18 16:57 | 2022-01-18 18:43 | 3 | 001:46 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | R22011800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-01-18 | 318 | keep | 0 | Jan | 2022 | 0.00021659 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-01-18 17:35 | 2022-01-18 18:13 | 100 | 000:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R22011800055 | New_Event |  |  | Include | Wildlife | 38 | 2022-01-18 | 3800 | keep | 0 | Jan | 2022 | 0.0025882 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-01-18 17:35 | 2022-01-18 17:36 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22011800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 3973 | keep | 0 | Jan | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
BAYAMON | 2022-01-18 17:43 | 2022-01-18 22:08 | 75 | 004:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA | S22011800279 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2022-01-18 | 19875 | keep | 0 | Jan | 2022 | 0.013537 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-01-18 17:51 | 2022-01-18 17:53 | 1291 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-02 QUE A SU VEZ LLEVA EL 60% DEL 1346-03 30% POR EL 1529-15 | S22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-18 | 2582 | keep | 0 | Jan | 2022 | 0.0017586 | 0.00087929 | Momentary | FALSE | FALSE | Not_TMED_Event | 1291
SAN JUAN | 2022-01-18 17:51 | 2022-01-18 17:53 | 1453 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-02 QUE A SU VEZ LLEVA EL 60% DEL 1346-03 | S22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-18 | 2906 | keep | 0 | Jan | 2022 | 0.0019793 | 0.00098963 | Momentary | FALSE | FALSE | Not_TMED_Event | 1453
SAN JUAN | 2022-01-18 17:51 | 2022-01-18 17:53 | 540 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-02 QUE A SU VEZ LLEVA EL 60% DEL 1346-03 Y 30% DEL 1529-15 | S22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-18 | 1080 | keep | 0 | Jan | 2022 | 0.00073558 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:59 | 1935 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-18 | 15480 | keep | 0 | Jan | 2022 | 0.010543 | 0.0013179 | Sustained | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:59 | 3 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-18 | 24 | keep | 0 | Jan | 2022 | 1.6346e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:59 | 61 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-18 | 488 | keep | 0 | Jan | 2022 | 0.00033237 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:59 | 1501 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-18 | 12008 | keep | 0 | Jan | 2022 | 0.0081786 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:59 | 546 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-18 | 4368 | keep | 0 | Jan | 2022 | 0.002975 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:56 | 959 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 9800 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-18 | 4795 | keep | 0 | Jan | 2022 | 0.0032659 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:56 | 1297 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 9800 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-18 | 6485 | keep | 0 | Jan | 2022 | 0.0044169 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:56 | 451 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 9800 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-18 | 2255 | keep | 0 | Jan | 2022 | 0.0015359 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:56 | 1264 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 9800 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-18 | 6320 | keep | 0 | Jan | 2022 | 0.0043045 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2022-01-18 17:51 | 2022-01-18 17:56 | 62 | 000:05 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 Y 9800 PARTE DE SU CARGA TRANSFERIDA AL 1330-01 | B22011800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-18 | 310 | keep | 0 | Jan | 2022 | 0.00021114 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
AGUADILLA | 2022-01-18 18:24 | 2022-01-18 20:38 | 60 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011800110 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2022-01-18 | 8040 | keep | 0 | Jan | 2022 | 0.005476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-01-18 18:28 | 2022-01-18 18:54 | 5 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22011800073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-01-18 | 130 | keep | 0 | Jan | 2022 | 8.8542e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-18 18:42 | 2022-01-18 22:00 | 50 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22011800084 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-01-18 | 9900 | keep | 0 | Jan | 2022 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-18 19:04 | 2022-01-18 23:23 | 15 | 004:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y SE REPARARON CONEXIONES SECUNDARIAS | S22011800300 | New_Event | Cutout Failure | Include | Include | Equipment | 259 | 2022-01-18 | 3885 | keep | 0 | Jan | 2022 | 0.0026461 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-01-18 19:55 | 2022-01-19 11:45 | 7 | 015:50 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22011800049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 950 | 2022-01-18 | 6650 | keep | 0 | Jan | 2022 | 0.0045293 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-01-18 20:08 | 2022-01-18 21:27 | 15 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22011800088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2022-01-18 | 1185 | keep | 0 | Jan | 2022 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-18 20:24 | 2022-01-18 20:40 | 2 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | R22011800064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2022-01-18 | 32 | keep | 0 | Jan | 2022 | 2.1795e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-18 20:30 | 2022-01-18 23:02 | 2 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22011800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-01-18 | 304 | keep | 0 | Jan | 2022 | 0.00020705 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-01-18 20:32 | 2022-01-19 11:23 | 70 | 014:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 891 | 2022-01-18 | 62370 | keep | 0 | Jan | 2022 | 0.04248 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-18 20:41 | 2022-01-18 23:25 | 80 | 002:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-01-18 | 13120 | keep | 0 | Jan | 2022 | 0.008936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-18 20:55 | 2022-01-19 12:11 | 80 | 015:16 | P | ESTRUCTURA AVERIADA | 2 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | A22011800054 | New_Event | Defective Pole | Include | Include | Equipment | 916 | 2022-01-18 | 73280 | keep | 0 | Jan | 2022 | 0.049911 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-18 21:39 | 2022-01-18 21:40 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 QUE LLEVA LA CARGA DEL 1204-05 | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-18 21:39 | 2022-01-18 21:40 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 QUE LLEVA LA CARGA DEL 1204-05 | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
ARECIBO | 2022-01-18 22:53 | 2022-01-19 10:06 | 100 | 011:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA INDICA UL2 NO IDENTIFICO CAUSA | A22011800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 673 | 2022-01-18 | 67300 | keep | 0 | Jan | 2022 | 0.045838 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-18 23:15 | 2022-01-18 23:16 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-18 | 6481 | keep | 0 | Jan | 2022 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2022-01-18 23:15 | 2022-01-18 23:51 | 6244 | 000:36 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR | S22011800311 | New_Event | UG Cable Fault | Include | Include | Equipment | 36 | 2022-01-18 | 224784 | keep | 0 | Jan | 2022 | 0.1531 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
SAN JUAN | 2022-01-18 23:51 | 2022-01-18 23:55 | 4995 | 000:04 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR | S22011800311 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 4 | 2022-01-18 | 19980 | keep | 0 | Jan | 2022 | 0.013608 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-18 23:55 | 2022-01-19 00:30 | 312 | 000:35 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR | S22011800311 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 35 | 2022-01-18 | 10920 | keep | 0 | Jan | 2022 | 0.0074376 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2022-01-19 00:30 | 2022-01-19 17:20 | 313 | 016:50 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL SU-25 AL CONDOMINIO LAGUNA VIEW | S22011800311 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1010 | 2022-01-19 | 316130 | keep | 0 | Jan | 2022 | 0.21531 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-19 00:54 | 2022-01-19 12:44 | 40 | 011:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER Y 1 NX DE 50 AMP EN SU - 1 CRUCE X RATON | C22011900001 | New_Event |  |  | Include | Wildlife | 710 | 2022-01-19 | 28400 | keep | 0 | Jan | 2022 | 0.019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-19 01:48 | 2022-01-19 09:11 | 15 | 007:23 | P | DESGANCHE | 1 X 80 EN C/L | R22011900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 443 | 2022-01-19 | 6645 | keep | 0 | Jan | 2022 | 0.0045259 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-01-19 01:59 | 2022-01-19 02:00 | 1526 | 000:01 | T | DESGANCHE | RECERRO | B22011900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-19 | 1526 | keep | 0 | Jan | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-01-19 02:00 | 2022-01-19 12:30 | 80 | 010:30 | P | DESGANCHE | 1 X 100 EN C/L. SE IDENTIFICARON RAMAS CERCA DE LINEA Y SE REFIRIO A COMPAÃ‘IA PRIVADA WTS | B22011900004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 630 | 2022-01-19 | 50400 | keep | 0 | Jan | 2022 | 0.034327 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-01-19 05:22 | 2022-01-19 09:25 | 80 | 004:03 | P | DESGANCHE | 1 X 100 EN C/L | C22011900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-01-19 | 19440 | keep | 0 | Jan | 2022 | 0.01324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-19 05:49 | 2022-01-19 08:40 | 56 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22011900020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-01-19 | 9576 | keep | 0 | Jan | 2022 | 0.0065222 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2022-01-19 06:37 | 2022-01-19 09:30 | 250 | 002:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22011900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-19 | 43250 | keep | 0 | Jan | 2022 | 0.029457 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-01-19 06:52 | 2022-01-19 06:53 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22011900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 2858 | keep | 0 | Jan | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
CANOVANAS | 2022-01-19 07:03 | 2022-01-19 10:00 | 50 | 002:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R22011900002 | New_Event |  |  | Include | Wildlife | 177 | 2022-01-19 | 8850 | keep | 0 | Jan | 2022 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-19 07:18 | 2022-01-19 12:29 | 30 | 005:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA ENERGIZADA SE ABRIO INTERRUPTOR PARA REPARAR ESTA ES LA PARCIAL | A22011900002 | New_Event | Wire Down | Include | Include | Equipment | 311 | 2022-01-19 | 9330 | keep | 0 | Jan | 2022 | 0.0063546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-01-19 07:37 | 2022-01-19 09:02 | 30 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R22011900003 | New_Event |  |  | Include | Wildlife | 85 | 2022-01-19 | 2550 | keep | 0 | Jan | 2022 | 0.0017368 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-19 07:43 | 2022-01-19 12:24 | 20 | 004:41 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | A22011900004 | New_Event | Defective Pole | Include | Include | Equipment | 281 | 2022-01-19 | 5620 | keep | 0 | Jan | 2022 | 0.0038278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-19 08:13 | 2022-01-19 12:44 | 10 | 004:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 X 37.5KVA DERRAME ACEITE | B22011900006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 271 | 2022-01-19 | 2710 | keep | 0 | Jan | 2022 | 0.0018458 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-19 08:33 | 2022-01-19 10:38 | 10 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO CONEXIONES SECUNDARIA | B22011900008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2022-01-19 | 1250 | keep | 0 | Jan | 2022 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-19 09:05 | 2022-01-19 14:28 | 50 | 005:23 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO DE MADERA PARTIDO | P22011900007 | New_Event | Defective Pole | Include | Include | Equipment | 323 | 2022-01-19 | 16150 | keep | 0 | Jan | 2022 | 0.011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-19 09:10 | 2022-01-19 10:16 | 50 | 001:06 | P | DESGANCHE | 1 X 80 EN C/L | R22011900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-01-19 | 3300 | keep | 0 | Jan | 2022 | 0.0022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-19 09:11 | 2022-01-19 11:09 | 10 | 001:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARARON CONEXIONES EN SECUNDARIA | B22011900012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 118 | 2022-01-19 | 1180 | keep | 0 | Jan | 2022 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-19 09:23 | 2022-01-19 12:31 | 80 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C22011900028 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2022-01-19 | 15040 | keep | 0 | Jan | 2022 | 0.010244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-19 09:29 | 2022-01-20 12:04 | 1 | 026:35 | P | CABLE SOTERRADO AVERIADO | SE REPARO TOMA SOTERRADA | S22011900035 | New_Event | UG Cable Fault | Include | Include | Equipment | 1595 | 2022-01-19 | 1595 | keep | 0 | Jan | 2022 | 0.0010863 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-19 09:30 | 2022-01-19 14:30 | 70 | 005:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA CULMINAR REEMPLAZO DE POSTE IMPACTADO POR CAMION | S22011900031 | New_Event |  |  | Include | Wildlife | 300 | 2022-01-19 | 21000 | keep | 0 | Jan | 2022 | 0.014303 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-01-19 09:43 | 2022-01-19 13:19 | 60 | 003:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L. SE RETIRO Y REPARO SECUNDARIA ENCIMA DE PRIMARIA. CAMION SE LLEVO SECUNDARIA Y SE ENRREDO CON RAMAL PRIMARIO | S22011900036 | New_Event |  |  | Include | Wildlife | 216 | 2022-01-19 | 12960 | keep | 0 | Jan | 2022 | 0.008827 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-19 09:52 | 2022-01-19 15:58 | 25 | 006:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASES | A22011900016 | New_Event |  |  | Include | Wildlife | 366 | 2022-01-19 | 9150 | keep | 0 | Jan | 2022 | 0.006232 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-19 09:59 | 2022-01-19 10:00 | 1484 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 30% POR EL 1336-08 | S22011900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 1484 | keep | 0 | Jan | 2022 | 0.0010107 | 0.0010107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1484
SAN JUAN | 2022-01-19 09:59 | 2022-01-19 10:00 | 53 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVA CARGA 1336-09 | S22011900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 53 | keep | 0 | Jan | 2022 | 3.6098e-05 | 3.6098e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2022-01-19 09:59 | 2022-01-19 10:00 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVA CARGA DEL 1336-09 | S22011800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 207 | keep | 0 | Jan | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
VEGA BAJA | 2022-01-19 10:12 | 2022-01-19 15:52 | 6 | 005:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22011900017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 340 | 2022-01-19 | 2040 | keep | 0 | Jan | 2022 | 0.0013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-19 10:30 | 2022-01-19 13:32 | 35 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22011900047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-01-19 | 6370 | keep | 0 | Jan | 2022 | 0.0043386 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-01-19 10:32 | 2022-01-19 12:30 | 40 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA MAQUINARIA PESADA LIMPIANDO UN TERRENO CRUZO LINEAS | M22011900040 | New_Event |  |  | Include | Wildlife | 118 | 2022-01-19 | 4720 | keep | 0 | Jan | 2022 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-19 11:17 | 2022-01-19 17:35 | 120 | 006:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22011900046 | New_Event | Cutout Failure | Include | Include | Equipment | 378 | 2022-01-19 | 45360 | keep | 0 | Jan | 2022 | 0.030894 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-01-19 11:40 | 2022-01-19 12:04 | 1883 | 000:24 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ALIMENTADOR SE CERRO INTERRUPTOR CAMION CRUZO LINEAS | A22011900027 | New_Event |  |  | Include | Wildlife | 24 | 2022-01-19 | 45192 | keep | 0 | Jan | 2022 | 0.03078 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
BAYAMON | 2022-01-19 11:44 | 2022-01-19 17:01 | 3 | 005:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR SE RETIRO GALLINA DE PALO | S22011900054 | New_Event |  |  | Include | Wildlife | 317 | 2022-01-19 | 951 | keep | 0 | Jan | 2022 | 0.00064772 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-19 11:49 | 2022-01-19 17:24 | 50 | 005:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22011900056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2022-01-19 | 16750 | keep | 0 | Jan | 2022 | 0.011408 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-01-19 11:51 | 2022-01-19 15:30 | 100 | 003:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R22011900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-01-19 | 21900 | keep | 0 | Jan | 2022 | 0.014916 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-19 12:04 | 2022-01-19 14:21 | 1300 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO ALAMBRE PARTIDO AISLADOR QUEMADO Y MACHETE QUEMADO POR IMPACTO DE CAMION A POSTE | A22011900038 | Partial_restoration |  |  | Include | Wildlife | 137 | 2022-01-19 | 178100 | keep | 0 | Jan | 2022 | 0.1213 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-19 12:11 | 2022-01-19 20:04 | 50 | 007:53 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE CERRO PUENTES | A22011800054 | Partial_restoration | Defective Pole | Include | Include | Equipment | 473 | 2022-01-19 | 23650 | keep | 0 | Jan | 2022 | 0.016108 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-19 12:29 | 2022-01-19 12:49 | 199 | 000:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR 8013-04 | A22011900043 | New_Event | Wire Down | Include | Include | Equipment | 20 | 2022-01-19 | 3980 | keep | 0 | Jan | 2022 | 0.0027108 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2022-01-19 12:29 | 2022-01-19 12:49 | 24 | 000:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR LINEA PRIMARIA PARTIDA EN ALIMENTADOR 8013-03 | A22011900043 | New_Event | Wire Down | Include | Include | Equipment | 20 | 2022-01-19 | 480 | keep | 0 | Jan | 2022 | 0.00032693 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2022-01-19 12:58 | 2022-01-19 14:01 | 6 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22011900028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-01-19 | 378 | keep | 0 | Jan | 2022 | 0.00025745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-19 13:04 | 2022-01-19 15:04 | 40 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22011900067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-01-19 | 4800 | keep | 0 | Jan | 2022 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-19 13:09 | 2022-01-19 16:21 | 6 | 003:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | S22011900068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 192 | 2022-01-19 | 1152 | keep | 0 | Jan | 2022 | 0.00078462 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-01-19 13:33 | 2022-01-19 15:22 | 50 | 001:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22011900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-01-19 | 5450 | keep | 0 | Jan | 2022 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-19 13:40 | 2022-01-19 17:00 | 50 | 003:20 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22011900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-01-19 | 10000 | keep | 0 | Jan | 2022 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-19 13:46 | 2022-01-19 15:59 | 50 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | P22011900026 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2022-01-19 | 6650 | keep | 0 | Jan | 2022 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-19 13:51 | 2022-01-19 17:57 | 3 | 004:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22011900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 246 | 2022-01-19 | 738 | keep | 0 | Jan | 2022 | 0.00050265 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-01-19 13:59 | 2022-01-19 14:00 | 1681 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06 CARGA DE 1303-04 POR 1303-05 | S22011900000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-19 | 1681 | keep | 0 | Jan | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-01-19 13:59 | 2022-01-19 14:00 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06 CARGA DE 1303-04 POR 1303-05 | S22011900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 1598 | keep | 0 | Jan | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2022-01-19 13:59 | 2022-01-19 16:55 | 30 | 002:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-01-19 | 5280 | keep | 0 | Jan | 2022 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-01-19 14:10 | 2022-01-19 14:37 | 10 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL EN LINEA SECUNDARIA | R22011900031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-01-19 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-19 14:16 | 2022-01-19 17:38 | 2 | 003:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 15KVA X 15KVA | M22011900069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 202 | 2022-01-19 | 404 | keep | 0 | Jan | 2022 | 0.00027516 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-01-19 14:19 | 2022-01-19 15:42 | 4 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22011900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-01-19 | 332 | keep | 0 | Jan | 2022 | 0.00022612 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-01-19 14:32 | 2022-01-19 17:39 | 409 | 003:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO LINEA PRIMARIA ROTA | M22011900072 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2022-01-19 | 76483 | keep | 0 | Jan | 2022 | 0.052092 | 0.00027857 | Sustained | FALSE | FALSE | Not_TMED_Event | 409
BAYAMON | 2022-01-19 14:44 | 2022-01-19 15:24 | 3 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22011900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-01-19 | 120 | keep | 0 | Jan | 2022 | 8.1731e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-19 15:07 | 2022-01-19 17:22 | 6 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22011900036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2022-01-19 | 810 | keep | 0 | Jan | 2022 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-19 15:23 | 2022-01-19 15:52 | 25 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011900076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-01-19 | 725 | keep | 0 | Jan | 2022 | 0.00049379 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-19 15:39 | 2022-01-19 21:15 | 10 | 005:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | A22011900062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 336 | 2022-01-19 | 3360 | keep | 0 | Jan | 2022 | 0.0022885 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-19 15:53 | 2022-01-19 19:17 | 60 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C22011900067 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2022-01-19 | 12240 | keep | 0 | Jan | 2022 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-19 15:54 | 2022-01-19 17:00 | 45 | 001:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA CORREGIR CONDICION | P22011900038 | New_Event | Wire Down | Include | Include | Equipment | 66 | 2022-01-19 | 2970 | keep | 0 | Jan | 2022 | 0.0020229 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2022-01-19 16:07 | 2022-01-19 17:12 | 10 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22011900039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-01-19 | 650 | keep | 0 | Jan | 2022 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-19 16:13 | 2022-01-19 17:10 | 6 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | B22011900039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-01-19 | 342 | keep | 0 | Jan | 2022 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-19 16:20 | 2022-01-19 18:10 | 36 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22011900040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-01-19 | 3960 | keep | 0 | Jan | 2022 | 0.0026971 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2022-01-19 16:30 | 2022-01-19 17:55 | 10 | 001:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22011900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-01-19 | 850 | keep | 0 | Jan | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-19 16:35 | 2022-01-19 20:00 | 80 | 003:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A22011900068 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2022-01-19 | 16400 | keep | 0 | Jan | 2022 | 0.01117 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-01-19 16:36 | 2022-01-19 17:50 | 50 | 001:14 | P | DESGANCHE | 1 X 80 EN C/L | C22011900070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-01-19 | 3700 | keep | 0 | Jan | 2022 | 0.0025201 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-01-19 16:40 | 2022-01-20 08:44 | 5 | 016:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN XMR MAL TIEMPO | C22011900071 | New_Event | Bad Weather | Include | Include | Weather | 964 | 2022-01-19 | 4820 | keep | 0 | Jan | 2022 | 0.0032829 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-01-19 16:45 | 2022-01-19 23:35 | 10 | 006:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | S22011900089 | New_Event | Cutout Failure | Include | Include | Equipment | 410 | 2022-01-19 | 4100 | keep | 0 | Jan | 2022 | 0.0027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-19 16:58 | 2022-01-19 18:35 | 35 | 001:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22011900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-01-19 | 3395 | keep | 0 | Jan | 2022 | 0.0023123 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-01-19 17:00 | 2022-01-19 17:16 | 130 | 000:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | P22011900038 | Additional_clients | Wire Down | Include | Include | Equipment | 16 | 2022-01-19 | 2080 | keep | 0 | Jan | 2022 | 0.0014167 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-19 17:10 | 2022-01-19 17:56 | 6 | 000:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | R22011900035 | New_Event |  |  | Include | Wildlife | 46 | 2022-01-19 | 276 | keep | 0 | Jan | 2022 | 0.00018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-19 17:43 | 2022-01-19 19:15 | 1 | 001:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22011900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-01-19 | 92 | keep | 0 | Jan | 2022 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-19 18:36 | 2022-01-19 21:25 | 60 | 002:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMPERES | M22011900099 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2022-01-19 | 10140 | keep | 0 | Jan | 2022 | 0.0069063 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-01-19 18:39 | 2022-01-19 19:59 | 3 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | R22011900037 | New_Event |  |  | Include | Wildlife | 80 | 2022-01-19 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-01-19 18:40 | 2022-01-19 20:10 | 12 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A22011900076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-01-19 | 1080 | keep | 0 | Jan | 2022 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-19 18:48 | 2022-01-19 18:49 | 1124 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011900038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 1124 | keep | 0 | Jan | 2022 | 0.00076555 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
BAYAMON | 2022-01-19 19:04 | 2022-01-19 19:05 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22011900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 3070 | keep | 0 | Jan | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
PONCE | 2022-01-19 19:06 | 2022-01-19 22:25 | 150 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE LINEA NO CAUSA | P22011900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-01-19 | 29850 | keep | 0 | Jan | 2022 | 0.020331 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-01-19 19:11 | 2022-01-20 07:53 | 10 | 012:42 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011900081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 762 | 2022-01-19 | 7620 | keep | 0 | Jan | 2022 | 0.0051899 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-19 19:37 | 2022-01-19 22:29 | 34 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | P22011800058 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-01-19 | 5848 | keep | 0 | Jan | 2022 | 0.003983 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
HUMACAO | 2022-01-19 19:48 | 2022-01-19 19:49 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C22011900078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-19 | 2126 | keep | 0 | Jan | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2022-01-20 03:26 | 2022-01-20 03:29 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO CARGA 1620-01 | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-20 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-20 03:26 | 2022-01-20 03:29 | 172 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO CARGA 1620-01 | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-20 | 516 | keep | 0 | Jan | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CANOVANAS | 2022-01-20 03:32 | 2022-01-20 03:33 | 4188 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R22012000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-20 | 4188 | keep | 0 | Jan | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-01-20 03:40 | 2022-01-20 06:26 | 10 | 002:46 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R22012000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-01-20 | 1660 | keep | 0 | Jan | 2022 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-20 05:24 | 2022-01-20 10:21 | 200 | 004:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REEMPLAZO PIN POLE TOP | B22012000008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 297 | 2022-01-20 | 59400 | keep | 0 | Jan | 2022 | 0.040457 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-01-20 05:50 | 2022-01-20 05:51 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 325 | keep | 0 | Jan | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-01-20 06:20 | 2022-01-20 11:09 | 3 | 004:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | R22012000012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 289 | 2022-01-20 | 867 | keep | 0 | Jan | 2022 | 0.00059051 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-20 06:47 | 2022-01-20 12:48 | 12 | 006:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN XMR. SE REEMPLAZO DOS CAJAS AVERIADAS | S22012000009 | New_Event | Cutout Failure | Include | Include | Equipment | 361 | 2022-01-20 | 4332 | keep | 0 | Jan | 2022 | 0.0029505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-20 06:50 | 2022-01-20 09:00 | 50 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-11 & 1 X 20 EN C/L | B22012000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-01-20 | 6500 | keep | 0 | Jan | 2022 | 0.0044271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-20 07:03 | 2022-01-20 09:51 | 100 | 002:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | R22012000015 | New_Event |  |  | Include | Wildlife | 168 | 2022-01-20 | 16800 | keep | 0 | Jan | 2022 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-20 07:06 | 2022-01-20 09:15 | 50 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO LINEAS MOMENTÃNEAMENTE | A22012000008 | New_Event |  |  | Include | Wildlife | 129 | 2022-01-20 | 6450 | keep | 0 | Jan | 2022 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-01-20 07:10 | 2022-01-20 10:20 | 150 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22012000009 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2022-01-20 | 28500 | keep | 0 | Jan | 2022 | 0.019411 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-01-20 07:19 | 2022-01-20 11:09 | 65 | 003:50 | P | DESGANCHE | 1 X 25 Y 1 X 50 EN C/L'S | C22012000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-01-20 | 14950 | keep | 0 | Jan | 2022 | 0.010182 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2022-01-20 07:24 | 2022-01-20 10:50 | 70 | 003:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22012000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-01-20 | 14420 | keep | 0 | Jan | 2022 | 0.0098214 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-01-20 07:32 | 2022-01-20 10:25 | 40 | 002:53 | P | DESGANCHE | 1 X 50 EN C/L | C22012000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-20 | 6920 | keep | 0 | Jan | 2022 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-20 07:45 | 2022-01-20 12:37 | 60 | 004:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22012000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2022-01-20 | 17520 | keep | 0 | Jan | 2022 | 0.011933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-01-20 07:51 | 2022-01-20 07:52 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22012000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 1047 | keep | 0 | Jan | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
UTUADO | 2022-01-20 08:06 | 2022-01-20 11:20 | 15 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA EXCAVADORA CRUZO LINEAS | A22012000014 | New_Event |  |  | Include | Wildlife | 194 | 2022-01-20 | 2910 | keep | 0 | Jan | 2022 | 0.001982 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-20 08:11 | 2022-01-20 12:05 | 6 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE ZULFATADO | R22012000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2022-01-20 | 1404 | keep | 0 | Jan | 2022 | 0.00095626 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-01-20 08:18 | 2022-01-20 11:19 | 50 | 003:01 | P | DESGANCHE | 1 X 50 EN C/L | C22012000022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-01-20 | 9050 | keep | 0 | Jan | 2022 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-20 08:25 | 2022-01-20 17:00 | 9 | 008:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22012000011 | New_Event | Bad Weather | Include | Include | Weather | 515 | 2022-01-20 | 4635 | keep | 0 | Jan | 2022 | 0.0031569 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-01-20 08:40 | 2022-01-20 15:40 | 70 | 007:00 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO PARTIDO | C22012000027 | New_Event | Defective Pole | Include | Include | Equipment | 420 | 2022-01-20 | 29400 | keep | 0 | Jan | 2022 | 0.020024 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-20 08:51 | 2022-01-20 10:59 | 7 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | M22012000019 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2022-01-20 | 896 | keep | 0 | Jan | 2022 | 0.00061026 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-20 08:53 | 2022-01-20 08:54 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1909-08 LLEVANDO EL 1907-05 | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 2435 | keep | 0 | Jan | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-01-20 08:53 | 2022-01-20 08:54 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1909-08 LLEVANDO EL 1907-05 | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 2956 | keep | 0 | Jan | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
UTUADO | 2022-01-20 09:09 | 2022-01-20 10:16 | 60 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA INFORMA EL JOURNEYMAN QUE NO SE ENCONTRO CAUSA | A22012000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-01-20 | 4020 | keep | 0 | Jan | 2022 | 0.002738 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-20 09:13 | 2022-01-20 11:20 | 4 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA EN PEDESTAL | C22011900066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2022-01-20 | 508 | keep | 0 | Jan | 2022 | 0.000346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-20 09:14 | 2022-01-20 09:18 | 225 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 LLEVA 1303-04 Y SE CERRO POR SCADA | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-20 | 900 | keep | 0 | Jan | 2022 | 0.00061299 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-20 09:14 | 2022-01-20 09:18 | 870 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 LLEVA 1303-04 Y SE CERRO POR SCADA | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-20 | 3480 | keep | 0 | Jan | 2022 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
FAJARDO | 2022-01-20 09:15 | 2022-01-20 12:59 | 100 | 003:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22012000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-01-20 | 22400 | keep | 0 | Jan | 2022 | 0.015257 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-20 09:17 | 2022-01-20 10:45 | 8 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C22011900065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2022-01-20 | 704 | keep | 0 | Jan | 2022 | 0.00047949 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-20 09:28 | 2022-01-20 09:29 | 888 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR BAJANTE DE CAJA A TRANSFORMADOR ZAFADO | M22012000028 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-20 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-01-20 09:29 | 2022-01-20 12:00 | 10 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CAJA A TRANSFORMADOR TRANSFORMADOR | M22012000037 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 151 | 2022-01-20 | 1510 | keep | 0 | Jan | 2022 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-20 09:37 | 2022-01-20 09:38 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 3025 | keep | 0 | Jan | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
MAYAGÃœEZ | 2022-01-20 09:41 | 2022-01-20 12:03 | 30 | 002:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M22012000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-20 | 4260 | keep | 0 | Jan | 2022 | 0.0029015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-20 09:56 | 2022-01-20 14:00 | 10 | 004:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22012000022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 244 | 2022-01-20 | 2440 | keep | 0 | Jan | 2022 | 0.0016619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-01-20 10:01 | 2022-01-20 13:32 | 16 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA CRUCE CON AVE | R22012000026 | New_Event |  |  | Include | Wildlife | 211 | 2022-01-20 | 3376 | keep | 0 | Jan | 2022 | 0.0022994 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-01-20 10:15 | 2022-01-20 17:34 | 20 | 007:19 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZARON DOS TRANSFORMADORES AVERIADOS UNO DE 50KVA X 50KVA Y OTRO DE 37.5KVA X 50KVA | A22012000033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 439 | 2022-01-20 | 8780 | keep | 0 | Jan | 2022 | 0.00598 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-20 10:25 | 2022-01-20 11:46 | 65 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CAMION IMPACTO TENSOR | C22012000060 | New_Event |  |  | Include | Wildlife | 81 | 2022-01-20 | 5265 | keep | 0 | Jan | 2022 | 0.003586 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-01-20 10:26 | 2022-01-20 17:25 | 6 | 006:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22012000061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 419 | 2022-01-20 | 2514 | keep | 0 | Jan | 2022 | 0.0017123 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-20 10:52 | 2022-01-20 12:03 | 10 | 001:11 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE Y REPARAR SECUNDARIA EN VARIO PUNTOS | B22012000022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 71 | 2022-01-20 | 710 | keep | 0 | Jan | 2022 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-20 10:55 | 2022-01-20 12:35 | 15 | 001:40 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y DESGANCHE | C22012000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-01-20 | 1500 | keep | 0 | Jan | 2022 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-20 11:08 | 2022-01-20 14:05 | 70 | 002:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22012000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-01-20 | 12390 | keep | 0 | Jan | 2022 | 0.0084388 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-01-20 11:36 | 2022-01-20 14:30 | 100 | 002:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTES DE LINEA CRUCE CON AVE | R22012000037 | New_Event |  |  | Include | Wildlife | 174 | 2022-01-20 | 17400 | keep | 0 | Jan | 2022 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-20 11:39 | 2022-01-20 12:32 | 40 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA INDICA FOREMAN QUE NO SE ENCONTRO CAUSA | A22012000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-01-20 | 2120 | keep | 0 | Jan | 2022 | 0.0014439 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-20 11:40 | 2022-01-20 12:24 | 7 | 000:44 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO BARRA SECA EN MH-46 | P22012000020 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 44 | 2022-01-20 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-01-20 11:45 | 2022-01-20 14:53 | 10 | 003:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 25 KVA X 25KVA | R22012000038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 188 | 2022-01-20 | 1880 | keep | 0 | Jan | 2022 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-01-20 11:49 | 2022-01-20 13:41 | 52 | 001:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22012000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-01-20 | 5824 | keep | 0 | Jan | 2022 | 0.0039667 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2022-01-20 11:52 | 2022-01-20 13:18 | 40 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22012000073 | New_Event |  |  | Include | Wildlife | 86 | 2022-01-20 | 3440 | keep | 0 | Jan | 2022 | 0.002343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-20 12:01 | 2022-01-20 12:24 | 16 | 000:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22012000035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 23 | 2022-01-20 | 368 | keep | 0 | Jan | 2022 | 0.00025064 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-01-20 12:53 | 2022-01-20 14:17 | 50 | 001:24 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | B22012000053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-01-20 | 4200 | keep | 0 | Jan | 2022 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-20 12:58 | 2022-01-20 15:32 | 6 | 002:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22012000056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 154 | 2022-01-20 | 924 | keep | 0 | Jan | 2022 | 0.00062933 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-01-20 13:00 | 2022-01-20 14:10 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22012000042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-01-20 | 700 | keep | 0 | Jan | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-20 13:01 | 2022-01-20 15:38 | 30 | 002:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22012000078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-01-20 | 4710 | keep | 0 | Jan | 2022 | 0.003208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-20 13:32 | 2022-01-20 13:33 | 2276 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 2276 | keep | 0 | Jan | 2022 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
ARECIBO | 2022-01-20 13:33 | 2022-01-20 13:34 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 2201 | keep | 0 | Jan | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
CAGUAS | 2022-01-20 13:36 | 2022-01-20 15:26 | 10 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BARRAS DE PEDESTAL | C22012000082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2022-01-20 | 1100 | keep | 0 | Jan | 2022 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-20 13:44 | 2022-01-20 14:50 | 10 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22012000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2022-01-20 | 660 | keep | 0 | Jan | 2022 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-01-20 13:45 | 2022-01-20 13:46 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220120000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 1475 | keep | 0 | Jan | 2022 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
ARECIBO | 2022-01-20 13:49 | 2022-01-20 17:43 | 60 | 003:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22012000063 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 234 | 2022-01-20 | 14040 | keep | 0 | Jan | 2022 | 0.0095626 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-20 13:57 | 2022-01-20 15:40 | 4 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 6 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22012000073 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2022-01-20 | 412 | keep | 0 | Jan | 2022 | 0.00028061 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-01-20 14:11 | 2022-01-20 15:50 | 20 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA FOREMAN NO ENCONTRO CAUSA | A22012000065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-01-20 | 1980 | keep | 0 | Jan | 2022 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-20 14:11 | 2022-01-20 17:23 | 10 | 003:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22012000087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 192 | 2022-01-20 | 1920 | keep | 0 | Jan | 2022 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-20 14:11 | 2022-01-20 17:04 | 10 | 002:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO XMR Y SE REPARO SECUNDARIA QUE SE LLEVO UN CAMION | B22012000087 | New_Event |  |  | Include | Wildlife | 173 | 2022-01-20 | 1730 | keep | 0 | Jan | 2022 | 0.0011783 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-20 14:27 | 2022-01-20 14:28 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 225 | keep | 0 | Jan | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-20 14:27 | 2022-01-20 14:28 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 870 | keep | 0 | Jan | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2022-01-20 14:28 | 2022-01-20 18:44 | 40 | 004:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE REPARO NEUTRAL PRIMARIO Y RETEZO LAS LINEAS | C22012000088 | New_Event | Wire Down | Include | Include | Equipment | 256 | 2022-01-20 | 10240 | keep | 0 | Jan | 2022 | 0.0069744 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-20 14:30 | 2022-01-20 17:00 | 3 | 002:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22011700063 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 150 | 2022-01-20 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-01-20 14:34 | 2022-01-20 14:35 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22012000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 1945 | keep | 0 | Jan | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
FAJARDO | 2022-01-20 14:37 | 2022-01-20 16:15 | 130 | 001:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22012000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-01-20 | 12740 | keep | 0 | Jan | 2022 | 0.0086772 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2022-01-20 14:45 | 2022-01-20 15:02 | 3 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | A22012000068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2022-01-20 | 51 | keep | 0 | Jan | 2022 | 3.4736e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-01-20 14:48 | 2022-01-20 15:55 | 10 | 001:07 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L NO CAUSA | C22012000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-01-20 | 670 | keep | 0 | Jan | 2022 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-20 14:53 | 2022-01-20 18:24 | 10 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA AVE CRUZO FASES | M22012000085 | New_Event |  |  | Include | Wildlife | 211 | 2022-01-20 | 2110 | keep | 0 | Jan | 2022 | 0.0014371 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-20 14:53 | 2022-01-20 14:54 | 569 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M22012000086 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-20 | 569 | keep | 0 | Jan | 2022 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2022-01-20 14:54 | 2022-01-20 14:58 | 200 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | M22012000092 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 4 | 2022-01-20 | 800 | keep | 0 | Jan | 2022 | 0.00054488 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-01-20 14:56 | 2022-01-20 16:08 | 30 | 001:12 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22012000069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-01-20 | 2160 | keep | 0 | Jan | 2022 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-20 14:57 | 2022-01-20 17:55 | 60 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22012000087 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2022-01-20 | 10680 | keep | 0 | Jan | 2022 | 0.0072741 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-01-20 14:58 | 2022-01-20 15:00 | 569 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON | M22012000088 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 2 | 2022-01-20 | 1138 | keep | 0 | Jan | 2022 | 0.00077509 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
PONCE | 2022-01-20 15:00 | 2022-01-20 15:01 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22012000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 969 | keep | 0 | Jan | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
AGUADILLA | 2022-01-20 15:00 | 2022-01-20 17:35 | 200 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | M22012000092 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 155 | 2022-01-20 | 31000 | keep | 0 | Jan | 2022 | 0.021114 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-01-20 15:04 | 2022-01-20 16:29 | 60 | 001:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | A22012000071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-01-20 | 5100 | keep | 0 | Jan | 2022 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-20 15:19 | 2022-01-20 18:04 | 50 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S22012000052 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2022-01-20 | 8250 | keep | 0 | Jan | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-20 15:19 | 2022-01-20 16:50 | 3 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22012000098 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2022-01-20 | 273 | keep | 0 | Jan | 2022 | 0.00018594 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-20 15:21 | 2022-01-20 20:31 | 2560 | 005:10 | T | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEAS Y SE RETIRO CARGA PARA CERRAR INTERRUPTOR | M22012000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-01-20 | 793600 | keep | 0 | Jan | 2022 | 0.54052 | 0.0017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 2560
PONCE | 2022-01-20 15:29 | 2022-01-20 15:30 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22012000037 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 969 | keep | 0 | Jan | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
SAN JUAN | 2022-01-20 15:31 | 2022-01-20 18:08 | 35 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22012000054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-01-20 | 5495 | keep | 0 | Jan | 2022 | 0.0037426 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-01-20 15:33 | 2022-01-20 15:34 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 4431 | keep | 0 | Jan | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
PONCE | 2022-01-20 15:41 | 2022-01-20 17:10 | 5 | 001:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA PARA CERRAR PUENTE PRIMARIO | P22012000040 | New_Event | Wire Down | Include | Include | Equipment | 89 | 2022-01-20 | 445 | keep | 0 | Jan | 2022 | 0.00030309 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-20 16:26 | 2022-01-20 16:27 | 3070 | 000:01 | T | DESGANCHE | RECERRO | B22012000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-20 | 3070 | keep | 0 | Jan | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-01-20 16:27 | 2022-01-20 16:29 | 1842 | 000:02 | P | DESGANCHE | SE CERRO MACHETES FID 8330860 LUEGO DE LEVANTAR CONDUCTOR Y DE REALIZAR DESGANCHE MEDIANTE GOI BY-220120-01 | B22012000083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-20 | 3684 | keep | 0 | Jan | 2022 | 0.0025092 | 0.0012546 | Momentary | FALSE | FALSE | Not_TMED_Event | 1842
BAYAMON | 2022-01-20 16:29 | 2022-01-20 16:30 | 3070 | 000:01 | T | DESGANCHE | RECERRO | B22012000083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-20 | 3070 | keep | 0 | Jan | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-01-20 16:30 | 2022-01-20 17:45 | 3070 | 001:15 | T | DESGANCHE | DISPARO ALIMENTADOR 9501-01 POR RAMA QUE CAYO SOBRE ALIMENTADOR Y PROVOCO CONDUCTOR EN EL SUELO. SE ESTABLECIO GOI BY-220120-01. 40% EN SERVICIO | B22012000083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-01-20 | 230250 | keep | 0 | Jan | 2022 | 0.15682 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
ARECIBO | 2022-01-20 16:36 | 2022-01-20 17:20 | 1 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE RECONECTO TOMA SECUNDARIA EN PEDESTAL SOTERRADO | A22012000083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-01-20 | 44 | keep | 0 | Jan | 2022 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-20 16:37 | 2022-01-20 18:14 | 60 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR AVE | P22012000044 | New_Event |  |  | Include | Wildlife | 97 | 2022-01-20 | 5820 | keep | 0 | Jan | 2022 | 0.003964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-20 16:40 | 2022-01-20 18:57 | 100 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22012000116 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2022-01-20 | 13700 | keep | 0 | Jan | 2022 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-20 16:43 | 2022-01-20 17:18 | 1 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO VARIAS CONDICIONES EN LA TOMA | R22012000058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-01-20 | 35 | keep | 0 | Jan | 2022 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-20 17:00 | 2022-01-20 18:40 | 10 | 001:40 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR, SE REPARO NEUTRAL Y SE REALIZO DESGANCHE MASIVO | B22012000097 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 100 | 2022-01-20 | 1000 | keep | 0 | Jan | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-20 17:16 | 2022-01-20 18:19 | 50 | 001:03 | P | DESGANCHE | 2 X 40 EN C/L. SE RETIRO RAMA SOBRE LINEA | S22012000061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-01-20 | 3150 | keep | 0 | Jan | 2022 | 0.0021455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-01-20 17:17 | 2022-01-20 18:14 | 35 | 000:57 | P | DESGANCHE | 1 X 25 EN C/L. SE DESGANCHO Y SE LEVANTO CONDUCTOR | B22012000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-01-20 | 1995 | keep | 0 | Jan | 2022 | 0.0013588 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-01-20 17:18 | 2022-01-20 17:29 | 3005 | 000:11 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO CRUCE X GALLINA DE PALO EN EL RISER DE SALIDA | C22012000104 | New_Event |  |  | Include | Wildlife | 11 | 2022-01-20 | 33055 | keep | 0 | Jan | 2022 | 0.022514 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
SAN JUAN | 2022-01-20 17:19 | 2022-01-20 20:24 | 4 | 003:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VIARIAS CONDICIONES EN LA LINEA | R22012000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 185 | 2022-01-20 | 740 | keep | 0 | Jan | 2022 | 0.00050401 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-01-20 17:28 | 2022-01-20 20:23 | 50 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22012000087 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2022-01-20 | 8750 | keep | 0 | Jan | 2022 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-01-20 17:38 | 2022-01-21 10:20 | 40 | 016:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEAS | A22012000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1002 | 2022-01-20 | 40080 | keep | 0 | Jan | 2022 | 0.027298 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-20 17:43 | 2022-01-20 18:52 | 75 | 001:09 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22012000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-01-20 | 5175 | keep | 0 | Jan | 2022 | 0.0035247 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-01-20 17:45 | 2022-01-20 19:50 | 1842 | 002:05 | P | DESGANCHE | SE CERRO MACHETES FID 8330860 LUEGO DE LEVANTAR CONDUCTOR Y DE REALIZAR DESGANCHE MEDIANTE GOI BY-220120-01 | B22012000083 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-01-20 | 230250 | keep | 0 | Jan | 2022 | 0.15682 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-01-20 17:52 | 2022-01-20 18:46 | 50 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22012000117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-01-20 | 2700 | keep | 0 | Jan | 2022 | 0.001839 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-20 18:29 | 2022-01-20 18:45 | 1 | 000:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22012000065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2022-01-20 | 16 | keep | 0 | Jan | 2022 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-20 18:30 | 2022-01-20 18:31 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22012000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 3630 | keep | 0 | Jan | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-01-20 18:35 | 2022-01-20 18:38 | 1097 | 000:03 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DEL AREA | M22012000147 | New_Event | Other Causes | Include | Include | Other | 3 | 2022-01-20 | 3291 | keep | 0 | Jan | 2022 | 0.0022415 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2022-01-20 18:36 | 2022-01-20 21:33 | 64 | 002:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S22012000064 | New_Event | Cutout Failure | Include | Include | Equipment | 177 | 2022-01-20 | 11328 | keep | 0 | Jan | 2022 | 0.0077154 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
AGUADILLA | 2022-01-20 18:36 | 2022-01-20 18:37 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22012000148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-20 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2022-01-20 18:40 | 2022-01-21 15:03 | 5 | 020:23 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REEMPLAZAR POSTE SECUNDARIO | C22012000125 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1223 | 2022-01-20 | 6115 | keep | 0 | Jan | 2022 | 0.0041649 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-20 18:44 | 2022-01-20 23:01 | 10 | 004:17 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | S22012000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-01-20 | 2570 | keep | 0 | Jan | 2022 | 0.0017504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-20 18:44 | 2022-01-20 19:40 | 5 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES DE BAJANTES SECUNDARIOS | A22012000099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-01-20 | 280 | keep | 0 | Jan | 2022 | 0.00019071 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-01-20 18:45 | 2022-01-20 20:51 | 50 | 002:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO AISLADOR | C22012000127 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 126 | 2022-01-20 | 6300 | keep | 0 | Jan | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-01-20 19:06 | 2022-01-21 09:23 | 10 | 014:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA A 2.4 KV | P22012000051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 857 | 2022-01-20 | 8570 | keep | 0 | Jan | 2022 | 0.005837 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-20 19:12 | 2022-01-20 21:58 | 55 | 002:46 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22012000069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-01-20 | 9130 | keep | 0 | Jan | 2022 | 0.0062184 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2022-01-20 19:30 | 2022-01-21 08:05 | 50 | 012:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22012100120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2022-01-20 | 37750 | keep | 0 | Jan | 2022 | 0.025711 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-01-20 19:31 | 2022-01-20 21:08 | 86 | 001:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22012000072 | New_Event | Cutout Failure | Include | Include | Equipment | 97 | 2022-01-20 | 8342 | keep | 0 | Jan | 2022 | 0.0056817 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
MAYAGÃœEZ | 2022-01-20 19:51 | 2022-01-20 22:14 | 100 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22012000167 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2022-01-20 | 14300 | keep | 0 | Jan | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-20 20:25 | 2022-01-21 14:30 | 40 | 018:05 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REEMPLAZAR POSTE PARTIDO | C22012000142 | New_Event | Defective Pole | Include | Include | Equipment | 1085 | 2022-01-20 | 43400 | keep | 0 | Jan | 2022 | 0.02956 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-20 20:31 | 2022-01-20 20:37 | 1000 | 000:06 | P | PROTECCION DEFECTUOSA | INTERRUPTOR NO CIERRA CON CARGA SE CERRO MACHETES QUE SE HABIAN ABIERTO PARA CERRAR INTERRUPTOR 6401-04 | M22012000099 | New_Event | Protection Miscoordination | Include | Include | Other | 6 | 2022-01-20 | 6000 | keep | 0 | Jan | 2022 | 0.0040866 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
MAYAGÃœEZ | 2022-01-20 20:37 | 2022-01-20 20:46 | 1200 | 000:09 | P | PROTECCION DEFECTUOSA | INTERRUPTOR NO CIERRA CON CARGA SE CERRO CORTE DE LINEA QUE SE HABIS ABIERTO PARA HACER PRUEBA AL 6401-04 | M22012000099 | Additional_clients | Protection Miscoordination | Include | Include | Other | 9 | 2022-01-20 | 10800 | keep | 0 | Jan | 2022 | 0.0073558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-20 20:46 | 2022-01-20 21:05 | 360 | 000:19 | P | DESGANCHE | SE CERRO CORTE DE LINEA QUE SE HABIA ABIERTO PARA CERRAR EL 6401-04 | M22012000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2022-01-20 | 6840 | keep | 0 | Jan | 2022 | 0.0046587 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
CANOVANAS | 2022-01-20 21:25 | 2022-01-20 23:20 | 3 | 001:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | R22012000068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2022-01-20 | 345 | keep | 0 | Jan | 2022 | 0.00023498 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-01-20 21:47 | 2022-01-21 10:30 | 10 | 012:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | R22012000081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 763 | 2022-01-20 | 7630 | keep | 0 | Jan | 2022 | 0.0051968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-01-20 22:21 | 2022-01-21 11:03 | 10 | 012:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X10 EN TRANSFORMADOR Y SE RETIRO AVE DEL TENDIDO ELECTRICO | R22012000083 | New_Event |  |  | Include | Wildlife | 762 | 2022-01-20 | 7620 | keep | 0 | Jan | 2022 | 0.0051899 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-20 22:28 | 2022-01-20 22:29 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION | P22012000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-20 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
ARECIBO | 2022-01-20 22:46 | 2022-01-21 11:06 | 30 | 012:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN XMR INFORMA UT2 NO IDENTIFICO CAUSA | A22012000102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 740 | 2022-01-20 | 22200 | keep | 0 | Jan | 2022 | 0.01512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-01-20 22:57 | 2022-01-21 00:55 | 293 | 001:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22012000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-01-20 | 34574 | keep | 0 | Jan | 2022 | 0.023548 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
PONCE | 2022-01-21 00:11 | 2022-01-21 10:23 | 15 | 010:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN TRANSFORMADOR NO SE REPORTO LA CAUSA | P22012100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 612 | 2022-01-21 | 9180 | keep | 0 | Jan | 2022 | 0.0062525 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-01-21 01:01 | 2022-01-21 01:02 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 2354 | keep | 0 | Jan | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2022-01-21 03:24 | 2022-01-21 11:07 | 200 | 007:43 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22012100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2022-01-21 | 92600 | keep | 0 | Jan | 2022 | 0.063069 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-01-21 04:51 | 2022-01-21 06:41 | 1979 | 001:50 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. AVE CRUZO FASE EN LA BARRA DE LA SUBESTACION | P22012100020 | New_Event |  |  | Include | Wildlife | 110 | 2022-01-21 | 217690 | keep | 0 | Jan | 2022 | 0.14827 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2022-01-21 04:51 | 2022-01-21 06:41 | 3114 | 001:50 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. AVE CRUZO FASE EN LA BARRA DE LA SUBESTACION | P22012100020 | New_Event |  |  | Include | Wildlife | 110 | 2022-01-21 | 342540 | keep | 0 | Jan | 2022 | 0.2333 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-01-21 04:51 | 2022-01-21 06:41 | 5069 | 001:50 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. AVE CRUZO FASE EN LA BARRA DE LA SUBESTACION | P22012100020 | New_Event |  |  | Include | Wildlife | 110 | 2022-01-21 | 557590 | keep | 0 | Jan | 2022 | 0.37977 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-01-21 04:51 | 2022-01-21 06:55 | 2696 | 002:04 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT AVE CRUZO FASE EN LA BARRA DE LA SUBESTACION | P220121000XX | New_Event |  |  | Include | Wildlife | 124 | 2022-01-21 | 334304 | keep | 0 | Jan | 2022 | 0.22769 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-01-21 04:51 | 2022-01-21 06:41 | 5063 | 001:50 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. AVE CRUZO FASE EN LA BARRA DE LA SUBESTACION | P22012100020 | New_Event |  |  | Include | Wildlife | 110 | 2022-01-21 | 556930 | keep | 0 | Jan | 2022 | 0.37932 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
HUMACAO | 2022-01-21 05:04 | 2022-01-21 10:41 | 5 | 005:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22012100001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 337 | 2022-01-21 | 1685 | keep | 0 | Jan | 2022 | 0.0011476 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-01-21 05:07 | 2022-01-21 09:33 | 3 | 004:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO PORTAFUSIBLE | S22012100003 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2022-01-21 | 798 | keep | 0 | Jan | 2022 | 0.00054351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-21 05:09 | 2022-01-21 09:30 | 25 | 004:21 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA INFORMA EL JOURNEYMAN SECTOR REQUIERE DESGANCHE | M22012100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-01-21 | 6525 | keep | 0 | Jan | 2022 | 0.0044441 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-01-21 05:50 | 2022-01-21 05:51 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 325 | keep | 0 | Jan | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CANOVANAS | 2022-01-21 06:02 | 2022-01-21 10:03 | 72 | 004:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN CORTE DE LINEA 1X65 EN OTRO CORTE DE LINEA Y SE REEMPLAZO CAJA PRIMARIA | R22012100003 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2022-01-21 | 17352 | keep | 0 | Jan | 2022 | 0.011818 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
VEGA BAJA | 2022-01-21 07:20 | 2022-01-21 07:21 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22012100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 325 | keep | 0 | Jan | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
ARECIBO | 2022-01-21 07:37 | 2022-01-21 07:38 | 2201 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | A22012100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-21 | 2201 | keep | 0 | Jan | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-01-21 07:38 | 2022-01-21 12:14 | 50 | 004:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INFORMA FOREMAN REQUIERE DESGANCHE | A22012100007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-01-21 | 13800 | keep | 0 | Jan | 2022 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-21 07:52 | 2022-01-21 07:55 | 306 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22012100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-21 | 918 | keep | 0 | Jan | 2022 | 0.00062525 | 0.00020842 | Momentary | FALSE | FALSE | Not_TMED_Event | 306
SAN JUAN | 2022-01-21 07:52 | 2022-01-21 07:55 | 1 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22012100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-21 | 3 | keep | 0 | Jan | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-21 07:59 | 2022-01-21 12:24 | 25 | 004:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | R22012100016 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2022-01-21 | 6625 | keep | 0 | Jan | 2022 | 0.0045123 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-01-21 08:15 | 2022-01-21 08:16 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 27 | keep | 0 | Jan | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
CAGUAS | 2022-01-21 08:22 | 2022-01-21 11:32 | 6 | 003:10 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C22012100018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 190 | 2022-01-21 | 1140 | keep | 0 | Jan | 2022 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-21 08:37 | 2022-01-21 08:38 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 4085 | keep | 0 | Jan | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2022-01-21 08:44 | 2022-01-21 10:16 | 4 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO DE XMR Y SE REPARO SECUNDARIA | S22012100010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-01-21 | 368 | keep | 0 | Jan | 2022 | 0.00025064 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-21 08:44 | 2022-01-21 10:16 | 6 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE RELOCALIZO SECUNDARIA | S22012100014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-01-21 | 552 | keep | 0 | Jan | 2022 | 0.00037596 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-01-21 08:44 | 2022-01-21 15:30 | 30 | 006:46 | P | ESTRUCTURA AVERIADA | SE INSTALO POSTE INTERMEDIO PARA PODER PASAR LINEA A POSTE NUEVO | M22012100032 | New_Event | Defective Pole | Include | Include | Equipment | 406 | 2022-01-21 | 12180 | keep | 0 | Jan | 2022 | 0.0082957 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-21 09:00 | 2022-01-21 11:45 | 10 | 002:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 10 KVA POR UNO DE 37.5 KVA | M22012100065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2022-01-21 | 1650 | keep | 0 | Jan | 2022 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-21 09:08 | 2022-01-21 19:30 | 30 | 010:22 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22012100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 622 | 2022-01-21 | 18660 | keep | 0 | Jan | 2022 | 0.012709 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-21 09:37 | 2022-01-21 18:11 | 60 | 008:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22012100049 | New_Event | Wire Down | Include | Include | Equipment | 514 | 2022-01-21 | 30840 | keep | 0 | Jan | 2022 | 0.021005 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-01-21 09:55 | 2022-01-21 11:00 | 50 | 001:05 | P | DESGANCHE | 1X100 EN CORTE DE LINEA | R22012100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-01-21 | 3250 | keep | 0 | Jan | 2022 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-21 10:16 | 2022-01-21 20:08 | 25 | 009:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA LEVANTAR NEUTRAL PRIMARIO | C22012100047 | New_Event | Wire Down | Include | Include | Equipment | 592 | 2022-01-21 | 14800 | keep | 0 | Jan | 2022 | 0.01008 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-21 10:20 | 2022-01-21 11:23 | 10 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BARRA SULFATADA SOTERRADA | B22012100016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-01-21 | 630 | keep | 0 | Jan | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-21 10:21 | 2022-01-21 13:05 | 10 | 002:44 | P | SECUNDARIA/DESGANCHE | 1X15 EN TRANSFORMADOR | R22012100036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 164 | 2022-01-21 | 1640 | keep | 0 | Jan | 2022 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-21 10:24 | 2022-01-21 11:04 | 8 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22012100017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-01-21 | 320 | keep | 0 | Jan | 2022 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-01-21 10:54 | 2022-01-21 14:01 | 39 | 003:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22012100040 | New_Event |  |  | Include | Wildlife | 187 | 2022-01-21 | 7293 | keep | 0 | Jan | 2022 | 0.0049672 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
ARECIBO | 2022-01-21 11:10 | 2022-01-21 11:52 | 15 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012100022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-01-21 | 630 | keep | 0 | Jan | 2022 | 0.00042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-01-21 11:17 | 2022-01-21 18:05 | 3 | 006:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22012100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2022-01-21 | 1224 | keep | 0 | Jan | 2022 | 0.00083366 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-21 11:29 | 2022-01-21 15:10 | 10 | 003:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA DE XMR AVERIADA | B22012100024 | New_Event | Cutout Failure | Include | Include | Equipment | 221 | 2022-01-21 | 2210 | keep | 0 | Jan | 2022 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-21 11:40 | 2022-01-21 15:00 | 10 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR POR IGUANA QUE CRUZO LINEAS | M22012100076 | New_Event |  |  | Include | Wildlife | 200 | 2022-01-21 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-21 12:02 | 2022-01-21 12:33 | 11 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22012100114 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2022-01-21 | 341 | keep | 0 | Jan | 2022 | 0.00023225 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-01-21 12:03 | 2022-01-21 19:32 | 55 | 007:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L LEVANTO CONDUCTOR | C22012100063 | New_Event | Wire Down | Include | Include | Equipment | 449 | 2022-01-21 | 24695 | keep | 0 | Jan | 2022 | 0.01682 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
UTUADO | 2022-01-21 12:03 | 2022-01-21 12:37 | 3 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | A22012100030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2022-01-21 | 102 | keep | 0 | Jan | 2022 | 6.9472e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-21 12:05 | 2022-01-21 16:32 | 10 | 004:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA AVERIADA EN BANCO DE XMR | S22012100028 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2022-01-21 | 2670 | keep | 0 | Jan | 2022 | 0.0018185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-21 12:34 | 2022-01-21 15:26 | 80 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A22012100032 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-01-21 | 13760 | keep | 0 | Jan | 2022 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-01-21 12:35 | 2022-01-21 16:45 | 100 | 004:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22012100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-01-21 | 25000 | keep | 0 | Jan | 2022 | 0.017027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-21 12:44 | 2022-01-21 16:53 | 30 | 004:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A22012100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-01-21 | 7470 | keep | 0 | Jan | 2022 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-01-21 12:54 | 2022-01-21 13:16 | 65 | 000:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22012100118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2022-01-21 | 1430 | keep | 0 | Jan | 2022 | 0.00097397 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-01-21 12:57 | 2022-01-21 14:55 | 60 | 001:58 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B22012100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-01-21 | 7080 | keep | 0 | Jan | 2022 | 0.0048222 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-21 12:58 | 2022-01-21 16:12 | 10 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22012100031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-01-21 | 1940 | keep | 0 | Jan | 2022 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-21 13:05 | 2022-01-21 15:10 | 40 | 002:05 | P | DESGANCHE | 1 X 50 EN C/L. SE REALIZO DESGANCHE EN VARIOS PUNTOS MEDIANTE GOI BY-220121-01 | B22012100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-01-21 | 5000 | keep | 0 | Jan | 2022 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-01-21 13:10 | 2022-01-21 18:38 | 7 | 005:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22012100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2022-01-21 | 2296 | keep | 0 | Jan | 2022 | 0.0015638 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-21 13:13 | 2022-01-21 16:16 | 40 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22012100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-01-21 | 7320 | keep | 0 | Jan | 2022 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-01-21 13:14 | 2022-01-21 15:35 | 30 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M22012100085 | New_Event | Wire Down | Include | Include | Equipment | 141 | 2022-01-21 | 4230 | keep | 0 | Jan | 2022 | 0.002881 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-01-21 13:15 | 2022-01-21 15:35 | 6 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | P22012100120 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2022-01-21 | 840 | keep | 0 | Jan | 2022 | 0.00057212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-21 13:17 | 2022-01-21 15:04 | 40 | 001:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L LEVANTO CONDUCTOR | C22012100081 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2022-01-21 | 4280 | keep | 0 | Jan | 2022 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-21 13:21 | 2022-01-21 13:23 | 90 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1100-05 Y SE CERRO POR SCADA | S22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-21 | 180 | keep | 0 | Jan | 2022 | 0.0001226 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-01-21 13:23 | 2022-01-21 20:05 | 50 | 006:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M22012100088 | New_Event | Wire Down | Include | Include | Equipment | 402 | 2022-01-21 | 20100 | keep | 0 | Jan | 2022 | 0.01369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-21 13:25 | 2022-01-21 16:58 | 50 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22012100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-01-21 | 10650 | keep | 0 | Jan | 2022 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-21 13:30 | 2022-01-21 16:15 | 8 | 002:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 25 KVA X 25 KVA | A22012100043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2022-01-21 | 1320 | keep | 0 | Jan | 2022 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-21 13:40 | 2022-01-21 15:10 | 10 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 25 KVA X 37.5 KVA | A22012100045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2022-01-21 | 900 | keep | 0 | Jan | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-21 13:43 | 2022-01-21 14:43 | 6 | 001:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22012100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-01-21 | 360 | keep | 0 | Jan | 2022 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-21 13:48 | 2022-01-21 14:31 | 60 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA POR LINEAS PRIMARIAS CRUZADAS | M22012100090 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-01-21 | 2580 | keep | 0 | Jan | 2022 | 0.0017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-21 13:52 | 2022-01-21 14:51 | 10 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO PEDESTAL | B22012100041 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-01-21 | 590 | keep | 0 | Jan | 2022 | 0.00040185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-21 13:59 | 2022-01-21 14:30 | 6 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | R22012100045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2022-01-21 | 186 | keep | 0 | Jan | 2022 | 0.00012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-21 14:09 | 2022-01-21 17:16 | 200 | 003:07 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22012100101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-01-21 | 37400 | keep | 0 | Jan | 2022 | 0.025473 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-01-21 14:30 | 2022-01-21 18:45 | 6 | 004:15 | P | ESTRUCTURA AVERIADA | REEMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | C22012000142 | Partial_restoration | Defective Pole | Include | Include | Equipment | 255 | 2022-01-21 | 1530 | keep | 0 | Jan | 2022 | 0.0010421 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-21 14:41 | 2022-01-21 14:42 | 1831 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A22012100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-21 | 1831 | keep | 0 | Jan | 2022 | 0.0012471 | 0.0012471 | Momentary | FALSE | FALSE | Not_TMED_Event | 1831
ARECIBO | 2022-01-21 14:42 | 2022-01-21 19:17 | 20 | 004:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22012100058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-01-21 | 5500 | keep | 0 | Jan | 2022 | 0.003746 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-01-21 14:48 | 2022-01-21 17:14 | 50 | 002:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22012100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2022-01-21 | 7300 | keep | 0 | Jan | 2022 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-21 15:10 | 2022-01-21 18:53 | 50 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | P22012100131 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2022-01-21 | 11150 | keep | 0 | Jan | 2022 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-01-21 15:13 | 2022-01-21 19:15 | 40 | 004:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22012100105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2022-01-21 | 9680 | keep | 0 | Jan | 2022 | 0.006593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-21 15:17 | 2022-01-21 16:45 | 3 | 001:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P22012100132 | New_Event | Wire Down | Include | Include | Equipment | 88 | 2022-01-21 | 264 | keep | 0 | Jan | 2022 | 0.00017981 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-21 15:21 | 2022-01-21 16:42 | 20 | 001:21 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22012100112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-01-21 | 1620 | keep | 0 | Jan | 2022 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-21 15:26 | 2022-01-21 19:19 | 1 | 003:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22012100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-01-21 | 233 | keep | 0 | Jan | 2022 | 0.0001587 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-21 15:26 | 2022-01-21 15:36 | 2201 | 000:10 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR AL CERRAR CORTE DE LINEA | A22012100121 | Additional_clients | Cutout Failure | Include | Include | Equipment | 10 | 2022-01-21 | 22010 | keep | 0 | Jan | 2022 | 0.014991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-21 15:46 | 2022-01-21 16:16 | 15 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22012200024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-01-21 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-01-21 15:48 | 2022-01-21 17:51 | 40 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22012100050 | New_Event |  |  | Include | Wildlife | 123 | 2022-01-21 | 4920 | keep | 0 | Jan | 2022 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-21 15:56 | 2022-01-22 11:44 | 1 | 019:48 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE DESGANCHO | B22012100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1188 | 2022-01-21 | 1188 | keep | 0 | Jan | 2022 | 0.00080914 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-21 16:18 | 2022-01-21 17:15 | 10 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BARRAS SULFATADAS | B22012100053 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-01-21 | 570 | keep | 0 | Jan | 2022 | 0.00038822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-21 16:19 | 2022-01-21 16:20 | 1007 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22012100138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 1007 | keep | 0 | Jan | 2022 | 0.00068586 | 0.00068586 | Momentary | FALSE | FALSE | Not_TMED_Event | 1007
ARECIBO | 2022-01-21 16:19 | 2022-01-21 18:20 | 40 | 002:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A22012100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-01-21 | 4840 | keep | 0 | Jan | 2022 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-01-21 16:21 | 2022-01-21 17:07 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BARRAS SULFATADAS | B22012100036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-01-21 | 460 | keep | 0 | Jan | 2022 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-21 16:37 | 2022-01-21 18:24 | 40 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22012100111 | New_Event |  |  | Include | Wildlife | 107 | 2022-01-21 | 4280 | keep | 0 | Jan | 2022 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-21 16:45 | 2022-01-21 16:46 | 200 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO BAJANTE PRIMARIO HACE CONTACTO CON TAPA DE TRANSFORMADOR | P22012100141 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-01-21 | 200 | keep | 0 | Jan | 2022 | 0.00013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-21 16:46 | 2022-01-21 18:22 | 3 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P22012100132 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 96 | 2022-01-21 | 288 | keep | 0 | Jan | 2022 | 0.00019616 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-21 17:16 | 2022-01-21 17:17 | 2560 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR SE NECESITA REALIZAR DESGANCHE | M22012100121 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-21 | 2560 | keep | 0 | Jan | 2022 | 0.0017436 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-21 17:17 | 2022-01-21 17:27 | 200 | 000:10 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22012100101 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-01-21 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-01-21 17:19 | 2022-01-21 17:44 | 3114 | 000:25 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR CON CARGA DEL 5018-04 SE ABRIO AMARRE Y SE COLOCO EN SERVICIO AVERIA EN ALIMENTADOR 5018-04 | P22012100144 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 25 | 2022-01-21 | 77850 | keep | 0 | Jan | 2022 | 0.053023 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-01-21 17:19 | 2022-01-21 18:04 | 2696 | 000:45 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR SE ABRIO RISER DE ENTRADA SISTEMA SOTERRADO EN CALLE VILLA Y SE COLOCO INTERRRUPTOR EN SERVICIO | P22012100156 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 45 | 2022-01-21 | 121320 | keep | 0 | Jan | 2022 | 0.08263 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2022-01-21 17:19 | 2022-01-21 18:15 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANE SECUNDARIO | B22012100055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-01-21 | 560 | keep | 0 | Jan | 2022 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-21 17:35 | 2022-01-21 21:16 | 3 | 003:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22012100122 | New_Event | Secondary Wire Down | Include | Include | Equipment | 221 | 2022-01-21 | 663 | keep | 0 | Jan | 2022 | 0.00045157 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-01-21 17:44 | 2022-01-21 20:08 | 100 | 002:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22012100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-01-21 | 14400 | keep | 0 | Jan | 2022 | 0.0098078 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-21 17:46 | 2022-01-21 21:33 | 35 | 003:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22012100077 | New_Event | Bad Weather | Include | Include | Weather | 227 | 2022-01-21 | 7945 | keep | 0 | Jan | 2022 | 0.0054113 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-01-21 17:48 | 2022-01-21 19:55 | 65 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L SE RETIRO AVE CRUZANDO LINEAS | B22012100058 | New_Event |  |  | Include | Wildlife | 127 | 2022-01-21 | 8255 | keep | 0 | Jan | 2022 | 0.0056224 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-01-21 17:57 | 2022-01-21 20:11 | 100 | 002:14 | P | DESGANCHE | 2 X 100 EN C/L SE RETIRO RAMA | B22012100059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-01-21 | 13400 | keep | 0 | Jan | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-01-21 18:04 | 2022-01-21 18:25 | 1500 | 000:21 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL CERRA EN MH-412 CALLE LUNA & MENDEZ VIGO | P22012100161 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 21 | 2022-01-21 | 31500 | keep | 0 | Jan | 2022 | 0.021455 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-21 18:25 | 2022-01-21 18:26 | 2696 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL CERRAR EN MH-412 SE HABRIO HACIA PULL BOX Y SE COLOCO INTERRUPTOR EN SERVICIO | P22012100164 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-01-21 | 2696 | keep | 0 | Jan | 2022 | 0.0018362 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-21 18:26 | 2022-01-22 10:36 | 15 | 016:10 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA AVERIADA HACIA CAJA SECA EN MH-412 | P22012100162 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 970 | 2022-01-21 | 14550 | keep | 0 | Jan | 2022 | 0.0099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-01-21 18:29 | 2022-01-22 11:18 | 40 | 016:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA | C22012100119 | New_Event | Wire Down | Include | Include | Equipment | 1009 | 2022-01-21 | 40360 | keep | 0 | Jan | 2022 | 0.027489 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-21 19:01 | 2022-01-22 14:04 | 10 | 019:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN TRANSFORMADOR IGUANA CRUZO FASES | M22012100128 | New_Event |  |  | Include | Wildlife | 1143 | 2022-01-21 | 11430 | keep | 0 | Jan | 2022 | 0.0077849 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-21 19:06 | 2022-01-21 22:37 | 30 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22012100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-01-21 | 6330 | keep | 0 | Jan | 2022 | 0.0043113 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-21 19:10 | 2022-01-21 21:19 | 8 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A22012100088 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2022-01-21 | 1032 | keep | 0 | Jan | 2022 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-01-21 19:14 | 2022-01-22 14:13 | 15 | 018:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 25 KVA | A22012100089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1139 | 2022-01-21 | 17085 | keep | 0 | Jan | 2022 | 0.011637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-01-21 20:08 | 2022-01-22 10:44 | 10 | 014:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M22012100129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 876 | 2022-01-21 | 8760 | keep | 0 | Jan | 2022 | 0.0059664 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-21 21:49 | 2022-01-21 21:50 | 721 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 721 | keep | 0 | Jan | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
CAGUAS | 2022-01-21 21:49 | 2022-01-22 09:32 | 40 | 011:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA | C22012100124 | New_Event | Wire Down | Include | Include | Equipment | 703 | 2022-01-21 | 28120 | keep | 0 | Jan | 2022 | 0.019152 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-21 22:20 | 2022-01-22 12:50 | 5 | 014:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22012100098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 870 | 2022-01-21 | 4350 | keep | 0 | Jan | 2022 | 0.0029628 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-21 22:33 | 2022-01-22 13:02 | 12 | 014:29 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE Y LEVANTAR SECUNDARIA | S22012100061 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 869 | 2022-01-21 | 10428 | keep | 0 | Jan | 2022 | 0.0071025 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-21 22:41 | 2022-01-21 22:42 | 918 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22012100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-21 | 918 | keep | 0 | Jan | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
ARECIBO | 2022-01-21 23:34 | 2022-01-21 23:35 | 2201 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | A22012100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-21 | 2201 | keep | 0 | Jan | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-01-21 23:35 | 2022-01-22 09:24 | 60 | 009:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A22012200005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 589 | 2022-01-21 | 35340 | keep | 0 | Jan | 2022 | 0.02407 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-01-22 00:03 | 2022-01-22 00:04 | 1467 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO | C22012200001 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-22 | 1467 | keep | 0 | Jan | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-01-22 00:04 | 2022-01-22 09:41 | 40 | 009:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C22012200004 | 1st_after_momentary |  |  | Include | Wildlife | 577 | 2022-01-22 | 23080 | keep | 0 | Jan | 2022 | 0.01572 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-01-22 00:20 | 2022-01-22 00:21 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 1310 | keep | 0 | Jan | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2022-01-22 00:21 | 2022-01-22 07:20 | 60 | 006:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22012200001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 419 | 2022-01-22 | 25140 | keep | 0 | Jan | 2022 | 0.017123 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-22 01:09 | 2022-01-22 09:46 | 12 | 008:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS QUEMADOS | P22012200001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 517 | 2022-01-22 | 6204 | keep | 0 | Jan | 2022 | 0.0042255 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-22 01:10 | 2022-01-22 01:11 | 539 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 539 | keep | 0 | Jan | 2022 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
CAGUAS | 2022-01-22 01:19 | 2022-01-22 10:48 | 40 | 009:29 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | C22012200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 569 | 2022-01-22 | 22760 | keep | 0 | Jan | 2022 | 0.015502 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-22 01:54 | 2022-01-22 01:55 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 4634 | keep | 0 | Jan | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2022-01-22 03:17 | 2022-01-22 03:18 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 4622 | keep | 0 | Jan | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
SAN JUAN | 2022-01-22 05:29 | 2022-01-22 05:31 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-22 05:29 | 2022-01-22 05:31 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 1740 | keep | 0 | Jan | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2022-01-22 07:00 | 2022-01-22 10:43 | 4 | 003:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P22012200008 | New_Event | Cutout Failure | Include | Include | Equipment | 223 | 2022-01-22 | 892 | keep | 0 | Jan | 2022 | 0.00060754 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-01-22 07:02 | 2022-01-22 09:40 | 40 | 002:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO LLUVIA FUERTE | C22012200005 | New_Event | Bad Weather | Include | Include | Weather | 158 | 2022-01-22 | 6320 | keep | 0 | Jan | 2022 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-22 07:07 | 2022-01-22 11:08 | 1 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22012200006 | New_Event |  |  | Include | Wildlife | 241 | 2022-01-22 | 241 | keep | 0 | Jan | 2022 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-22 07:11 | 2022-01-22 10:33 | 100 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 50 EN CORTE DE LINEA | B22012200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-01-22 | 20200 | keep | 0 | Jan | 2022 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-01-22 07:17 | 2022-01-22 09:28 | 15 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22012200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2022-01-22 | 1965 | keep | 0 | Jan | 2022 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-01-22 08:08 | 2022-01-22 09:53 | 100 | 001:45 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | R22012200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-01-22 | 10500 | keep | 0 | Jan | 2022 | 0.0071515 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-01-22 08:12 | 2022-01-22 08:13 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 3699 | keep | 0 | Jan | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2022-01-22 08:22 | 2022-01-22 08:23 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 3718 | keep | 0 | Jan | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2022-01-22 08:28 | 2022-01-22 15:40 | 300 | 007:12 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M22012200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 432 | 2022-01-22 | 129600 | keep | 0 | Jan | 2022 | 0.08827 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-01-22 08:45 | 2022-01-22 10:18 | 19 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | S22012200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-01-22 | 1767 | keep | 0 | Jan | 2022 | 0.0012035 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-01-22 08:49 | 2022-01-22 09:01 | 1 | 000:12 | T | ERROR HUMANO | DISPARO PERSONAL REALIZANDO OPERACIONES PARA LA V/L D2022-00043 | R22012200012 | New_Event | Human Error | Include | Include | Other | 12 | 2022-01-22 | 12 | keep | 0 | Jan | 2022 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-22 08:50 | 2022-01-22 13:32 | 15 | 004:42 | P | TRANSFORMADOR AVERIADO | SE RELOCALIZO SECUNDARIA A OTRO TRANSFORMADOR | S22012200004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 282 | 2022-01-22 | 4230 | keep | 0 | Jan | 2022 | 0.002881 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-01-22 09:02 | 2022-01-22 11:30 | 100 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | R22012200014 | New_Event |  |  | Include | Wildlife | 148 | 2022-01-22 | 14800 | keep | 0 | Jan | 2022 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-22 09:08 | 2022-01-22 11:22 | 15 | 002:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22012200019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 134 | 2022-01-22 | 2010 | keep | 0 | Jan | 2022 | 0.001369 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-01-22 09:10 | 2022-01-22 11:02 | 625 | 001:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | R22012200017 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2022-01-22 | 70000 | keep | 0 | Jan | 2022 | 0.047677 | 0.00042568 | Sustained | FALSE | FALSE | Not_TMED_Event | 625
SAN JUAN | 2022-01-22 09:43 | 2022-01-22 12:18 | 65 | 002:35 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | S22012200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-01-22 | 10075 | keep | 0 | Jan | 2022 | 0.006862 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-01-22 09:45 | 2022-01-22 11:17 | 55 | 001:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA AVERIADA | R22012200030 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2022-01-22 | 5060 | keep | 0 | Jan | 2022 | 0.0034463 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-01-22 09:51 | 2022-01-22 11:55 | 20 | 002:04 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN C/L ELIMINO PARARRAYO PRIVADO | R22012200032 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 124 | 2022-01-22 | 2480 | keep | 0 | Jan | 2022 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-22 10:03 | 2022-01-22 15:10 | 60 | 005:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22012200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 307 | 2022-01-22 | 18420 | keep | 0 | Jan | 2022 | 0.012546 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-22 10:07 | 2022-01-22 10:08 | 4634 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22012200019 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-22 | 4634 | keep | 0 | Jan | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-01-22 10:08 | 2022-01-22 10:57 | 2 | 000:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN BANCO DE XMR'S CRUCE X AVE | C22012200016 | 1st_after_momentary |  |  | Include | Wildlife | 49 | 2022-01-22 | 98 | keep | 0 | Jan | 2022 | 6.6747e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-01-22 10:10 | 2022-01-22 11:42 | 15 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22012100048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-01-22 | 1380 | keep | 0 | Jan | 2022 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-22 10:16 | 2022-01-22 12:33 | 15 | 002:17 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22012200020 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 137 | 2022-01-22 | 2055 | keep | 0 | Jan | 2022 | 0.0013997 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-22 10:19 | 2022-01-22 14:10 | 15 | 003:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMP. | A22012200010 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2022-01-22 | 3465 | keep | 0 | Jan | 2022 | 0.00236 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-01-22 10:49 | 2022-01-22 14:32 | 7 | 003:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22012200011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 223 | 2022-01-22 | 1561 | keep | 0 | Jan | 2022 | 0.0010632 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-01-22 11:02 | 2022-01-22 12:40 | 100 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR CON GOI SJ-220122-50 | R22012200061 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-01-22 | 9800 | keep | 0 | Jan | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-01-22 11:03 | 2022-01-22 14:35 | 2 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONECTORES ZULFATADOS | R22012200056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2022-01-22 | 424 | keep | 0 | Jan | 2022 | 0.00028878 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-22 11:17 | 2022-01-22 14:27 | 13 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | S22012200015 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2022-01-22 | 2470 | keep | 0 | Jan | 2022 | 0.0016823 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2022-01-22 11:18 | 2022-01-23 10:57 | 7 | 023:39 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | R22012200058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1419 | 2022-01-22 | 9933 | keep | 0 | Jan | 2022 | 0.0067653 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-01-22 11:19 | 2022-01-22 14:48 | 5 | 003:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P22012200014 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2022-01-22 | 1045 | keep | 0 | Jan | 2022 | 0.00071174 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-01-22 11:33 | 2022-01-22 16:44 | 1 | 005:11 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22012200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-01-22 | 311 | keep | 0 | Jan | 2022 | 0.00021182 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-22 11:41 | 2022-01-22 14:00 | 6 | 002:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO PEDESTAL SECUNDARIO | A22012200019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 139 | 2022-01-22 | 834 | keep | 0 | Jan | 2022 | 0.00056803 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-01-22 11:49 | 2022-01-22 14:17 | 6 | 002:28 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | R22012200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-01-22 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-22 12:17 | 2022-01-22 14:21 | 6 | 002:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE DESCONTAMINO CAJA PRIMARIA | R22012200068 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2022-01-22 | 744 | keep | 0 | Jan | 2022 | 0.00050674 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-22 12:32 | 2022-01-22 13:45 | 60 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22012200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-01-22 | 4380 | keep | 0 | Jan | 2022 | 0.0029832 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-22 12:48 | 2022-01-22 21:10 | 15 | 008:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA | B22012200032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 502 | 2022-01-22 | 7530 | keep | 0 | Jan | 2022 | 0.0051286 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-22 13:12 | 2022-01-22 15:30 | 300 | 002:18 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22012200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-01-22 | 41400 | keep | 0 | Jan | 2022 | 0.028197 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-01-22 13:29 | 2022-01-22 13:31 | 3 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02 1707-03, 1707-04 & 1707-05 | B22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 6 | keep | 0 | Jan | 2022 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-22 13:29 | 2022-01-22 13:31 | 61 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02 1707-03, 1707-04 & 1707-05 | B22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 122 | keep | 0 | Jan | 2022 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-01-22 13:29 | 2022-01-22 13:31 | 1501 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02 1707-03, 1707-04 & 1707-05 | B22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 3002 | keep | 0 | Jan | 2022 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-01-22 13:29 | 2022-01-22 13:31 | 546 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02 1707-03, 1707-04 & 1707-05 | B22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 1092 | keep | 0 | Jan | 2022 | 0.00074376 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
SAN JUAN | 2022-01-22 13:47 | 2022-01-22 18:46 | 336 | 004:59 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22012200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-01-22 | 100464 | keep | 0 | Jan | 2022 | 0.068426 | 0.00022885 | Sustained | FALSE | FALSE | Not_TMED_Event | 336
HUMACAO | 2022-01-22 13:56 | 2022-01-22 15:52 | 6 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22012200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-01-22 | 696 | keep | 0 | Jan | 2022 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-22 14:07 | 2022-01-22 18:23 | 7 | 004:16 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 15 KVA X 25 KVA | C22012200031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 256 | 2022-01-22 | 1792 | keep | 0 | Jan | 2022 | 0.0012205 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-22 14:34 | 2022-01-22 15:05 | 15 | 000:31 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE | B22012200022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 31 | 2022-01-22 | 465 | keep | 0 | Jan | 2022 | 0.00031671 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-22 14:46 | 2022-01-22 14:48 | 382 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1620-04 CERRADO POR CONTROL | S22012200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 764 | keep | 0 | Jan | 2022 | 0.00052036 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
SAN JUAN | 2022-01-22 14:46 | 2022-01-22 14:48 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1620-04 CERRADO POR CONTROL | S22012200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 72 | keep | 0 | Jan | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-22 14:46 | 2022-01-22 14:48 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 1620-01 Y 95% DEL 1336-10 CERRADO POR CONTROL | S22012200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-22 | 344 | keep | 0 | Jan | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
PONCE | 2022-01-22 15:18 | 2022-01-22 17:40 | 65 | 002:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22012200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-22 | 9230 | keep | 0 | Jan | 2022 | 0.0062865 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-01-22 15:24 | 2022-01-22 16:00 | 15 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22012200042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-01-22 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-22 15:26 | 2022-01-22 17:10 | 1 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-1 HACIA EL TRANSCLOSURE NO CAUSA | S22012200036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-01-22 | 104 | keep | 0 | Jan | 2022 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-22 15:31 | 2022-01-22 16:58 | 25 | 001:27 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22012200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-01-22 | 2175 | keep | 0 | Jan | 2022 | 0.0014814 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-01-22 15:46 | 2022-01-22 18:43 | 50 | 002:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22012200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-01-22 | 8850 | keep | 0 | Jan | 2022 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-22 16:09 | 2022-01-22 18:36 | 32 | 002:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C22012200033 | New_Event | Wire Down | Include | Include | Equipment | 147 | 2022-01-22 | 4704 | keep | 0 | Jan | 2022 | 0.0032039 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
MAYAGÃœEZ | 2022-01-22 16:22 | 2022-01-23 12:29 | 20 | 020:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 1 X 40 1 X 30 EN 3 RISER DISTINTOS Y 1 X 10 EN BANCO DE TRANSFORMADORES DESCARGA ELECTRICA | M22012200052 | New_Event | Bad Weather | Include | Include | Weather | 1207 | 2022-01-22 | 24140 | keep | 0 | Jan | 2022 | 0.016442 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-22 16:24 | 2022-01-22 17:34 | 40 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22012200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-01-22 | 2800 | keep | 0 | Jan | 2022 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-22 17:00 | 2022-01-22 21:32 | 1483 | 004:32 | P | DESCONECTIVO DEFECTUOSO | DISPARO 1336-07 INTERRUPTOR LLEVANDO 60% DE LA CARGA DEL 1336-08 Y 30% DE LA CARGA DEL 1204-04 SE LE SACO CARGA CERRADO POR CONTROL | S22012200323 | New_Event | Switch Failure | Include | Include | Equipment | 272 | 2022-01-22 | 403376 | keep | 0 | Jan | 2022 | 0.27474 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-22 17:00 | 2022-01-22 20:54 | 5290 | 003:54 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE SECCIONALIZO AVERIA DEL RISER AL MH-D Y SE CERRO POR SCADA. ENTRO SOLO UN 5% APROXIMADAMENTE. | S22012200045 | New_Event | Switch Failure | Include | Include | Equipment | 234 | 2022-01-22 | 1237860 | keep | 0 | Jan | 2022 | 0.8431 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-22 17:00 | 2022-01-22 20:28 | 207 | 003:28 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL 1336-08 LLEVANDO LA CARGA DEL 1336-09 SE ABRIO N/O ENTRE 1336-08 Y 1336-09 Y SE CERR N/O ENTRE 1336-09 Y 1404-07 | S22012200323 | New_Event | Switch Failure | Include | Include | Equipment | 208 | 2022-01-22 | 43056 | keep | 0 | Jan | 2022 | 0.029325 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-01-22 17:09 | 2022-01-22 17:16 | 2245 | 000:07 | T | ERROR HUMANO | PERSONAL REALIZANDO OPERACIONEAS EN EL CAMPO POR VL D2022-000043 DISPARO ALIMENTADOR | R22012200088 | New_Event | Human Error | Include | Include | Other | 7 | 2022-01-22 | 15715 | keep | 0 | Jan | 2022 | 0.010703 | 0.0015291 | Sustained | FALSE | FALSE | Not_TMED_Event | 2245
MAYAGÃœEZ | 2022-01-22 17:16 | 2022-01-23 20:44 | 160 | 027:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22012200057 | New_Event | Wire Down | Include | Include | Equipment | 1648 | 2022-01-22 | 263680 | keep | 0 | Jan | 2022 | 0.17959 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
CANOVANAS | 2022-01-22 17:55 | 2022-01-22 19:22 | 3 | 001:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE ZAFADO | R22012200093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 87 | 2022-01-22 | 261 | keep | 0 | Jan | 2022 | 0.00017777 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-22 18:07 | 2022-01-22 18:08 | 3708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | S22012200136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 3708 | keep | 0 | Jan | 2022 | 0.0025255 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
ARECIBO | 2022-01-22 18:16 | 2022-01-22 21:21 | 4 | 003:05 | P | SECUNDARIA/ESTRUCTURA AVERIADA | POSTE SECUNDARIO PARTIDO SE RETIRO PELIGRO Y SE SECCIONALIZO | A22012200030 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 185 | 2022-01-22 | 740 | keep | 0 | Jan | 2022 | 0.00050401 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-01-22 18:38 | 2022-01-23 11:54 | 10 | 017:16 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | M22012200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1036 | 2022-01-22 | 10360 | keep | 0 | Jan | 2022 | 0.0070561 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-22 18:54 | 2022-01-22 19:02 | 15 | 000:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22012200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-01-22 | 120 | keep | 0 | Jan | 2022 | 8.1731e-05 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-01-22 19:03 | 2022-01-22 21:25 | 10 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P22012200035 | New_Event | Wire Down | Include | Include | Equipment | 142 | 2022-01-22 | 1420 | keep | 0 | Jan | 2022 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-22 19:46 | 2022-01-22 22:26 | 50 | 002:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | P22012200041 | New_Event | Wire Down | Include | Include | Equipment | 160 | 2022-01-22 | 8000 | keep | 0 | Jan | 2022 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-22 20:02 | 2022-01-22 20:03 | 6244 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR REALIZANDO OPERACIONES CONTRA EL 1336-08 | S22012200323 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-22 | 6244 | keep | 0 | Jan | 2022 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
FAJARDO | 2022-01-22 20:46 | 2022-01-22 22:26 | 30 | 001:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22012200098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-01-22 | 3000 | keep | 0 | Jan | 2022 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-22 20:54 | 2022-01-22 21:32 | 5025 | 000:38 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO AVERIA Y SE TRANSFIRIO 95% AL 1336-07 | S22012200045 | Partial_restoration | Switch Failure | Include | Include | Equipment | 38 | 2022-01-22 | 190950 | keep | 0 | Jan | 2022 | 0.13006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-22 21:12 | 2022-01-22 21:13 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 1702 | keep | 0 | Jan | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
SAN JUAN | 2022-01-22 21:32 | 2022-01-22 21:43 | 52 | 000:11 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO DE RISER FID 101406238 HACIA MH-D Y SE CERRO INTERRUPTOR | S22012200045 | Partial_restoration | Switch Failure | Include | Include | Equipment | 11 | 2022-01-22 | 572 | keep | 0 | Jan | 2022 | 0.00038959 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-01-22 21:37 | 2022-01-22 22:44 | 40 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22012200071 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2022-01-22 | 2680 | keep | 0 | Jan | 2022 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-22 21:42 | 2022-01-23 00:37 | 50 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEA PRIMARIA ROTA | A22012200045 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2022-01-22 | 8750 | keep | 0 | Jan | 2022 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-22 21:43 | 2022-01-22 21:47 | 1483 | 000:04 | P | SOBRECARGA | DISPARO 1336-07 INTERRUPTOR LLEVANDO 60% DE LA CARGA DEL 1336-08 Y 30% DE LA CARGA DEL 1204-04 SE LE SACO CARGA CERRADO POR CONTROL | S22012200323 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2022-01-22 | 5932 | keep | 0 | Jan | 2022 | 0.0040403 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-22 21:43 | 2022-01-22 21:47 | 6244 | 000:04 | T | SOBRECARGA | DISPARO INTERRUPTOR LLEVANDO 95% DE LA CARGA DEL 1336-08 Y 30% DE LA CARGA DEL 1204-04 | S22012200323 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2022-01-22 | 24976 | keep | 0 | Jan | 2022 | 0.017011 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
SAN JUAN | 2022-01-22 21:43 | 2022-01-22 21:47 | 5025 | 000:04 | P | SOBRECARGA | DISPARO 1336-07 INTERRUPTOR LLEVANDO 95% DE LA CARGA DEL 1336-08 Y 30% DE LA CARGA DEL 1204-04 | S22012200323 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2022-01-22 | 20100 | keep | 0 | Jan | 2022 | 0.01369 | 0.0034225 | Momentary | FALSE | FALSE | Not_TMED_Event | 5025
SAN JUAN | 2022-01-22 21:47 | 2022-01-22 21:54 | 52 | 000:07 | P | DESCONECTIVO DEFECTUOSO | TRAMO SECCIONALIZADO SE ABRIO DE RISER FID 101406238 HACIA MH-D | S22012200045 | Partial_restoration | Switch Failure | Include | Include | Equipment | 7 | 2022-01-22 | 364 | keep | 0 | Jan | 2022 | 0.00024792 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-22 21:54 | 2022-01-22 22:27 | 1483 | 000:33 | P | SOBRECARGA | SE LE TRANSFIRIO 30% DE LA CARGA AL 1303-02 PARA BAJAR CARGA AL 1336-07 | S22012200323 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 33 | 2022-01-22 | 48939 | keep | 0 | Jan | 2022 | 0.033332 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-22 21:54 | 2022-01-22 22:07 | 6244 | 000:13 | T | SOBRECARGA | DISPARO INTERRUPTOR LLEVANDO 95% DE LA CARGA DEL 1336-08 Y 30% DE LA CARGA DEL 1204-04 SE LE SACO LA CARGA 30% DEL 1204-04 CERRADO POR CONTROL Y SE TRANSFIRIO AL 1303-02 | S22012200323 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 13 | 2022-01-22 | 81172 | keep | 0 | Jan | 2022 | 0.055286 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
SAN JUAN | 2022-01-22 21:54 | 2022-01-22 22:07 | 5025 | 000:13 | P | SOBRECARGA | DISPARO 1336-07 INTERRUPTOR LLEVANDO 95% DE LA CARGA DEL 1336-08 Y 30% DE LA CARGA DEL 1204-04. SE TRANSFIRIO LA CARGA DEL 1204-04 AL 1303-02 | S22012200323 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 13 | 2022-01-22 | 65325 | keep | 0 | Jan | 2022 | 0.044493 | 0.0034225 | Sustained | FALSE | FALSE | Not_TMED_Event | 5025
CAGUAS | 2022-01-22 21:55 | 2022-01-23 00:06 | 40 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22012200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2022-01-22 | 5240 | keep | 0 | Jan | 2022 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-22 22:07 | 2022-01-23 08:55 | 52 | 010:48 | P | DESCONECTIVO DEFECTUOSO | TRAMO SECCIONALIZADO SE ABRIO DE RISER FID 101406238 HACIA MH-D | S22012200045 | Partial_restoration | Switch Failure | Include | Include | Equipment | 648 | 2022-01-22 | 33696 | keep | 0 | Jan | 2022 | 0.02295 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-01-22 22:35 | 2022-01-22 22:36 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22012200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-22 | 1192 | keep | 0 | Jan | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2022-01-23 00:37 | 2022-01-23 10:55 | 150 | 010:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO PUENTES | A22012200045 | Additional_clients | Wire Down | Include | Include | Equipment | 618 | 2022-01-23 | 92700 | keep | 0 | Jan | 2022 | 0.063138 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-23 00:40 | 2022-01-23 03:09 | 30 | 002:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO ARBOL SOBRE LINEA | B22012300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-01-23 | 4470 | keep | 0 | Jan | 2022 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-23 01:57 | 2022-01-23 01:58 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22012300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 2201 | keep | 0 | Jan | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
FAJARDO | 2022-01-23 02:18 | 2022-01-23 03:31 | 40 | 001:13 | P | NO SE REPORTO CAUSA | SE CERRARON FUSIBLES EN CORTE DE LINEA NO FUNDIERON | R22012300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-01-23 | 2920 | keep | 0 | Jan | 2022 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-23 02:26 | 2022-01-23 02:27 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B22012300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 3070 | keep | 0 | Jan | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
ARECIBO | 2022-01-23 02:27 | 2022-01-23 02:28 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22012300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 2201 | keep | 0 | Jan | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-01-23 02:34 | 2022-01-23 02:35 | 2694 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | A22012300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 2694 | keep | 0 | Jan | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
HUMACAO | 2022-01-23 04:31 | 2022-01-23 04:32 | 1467 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | C22012300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-23 | 1467 | keep | 0 | Jan | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-01-23 04:32 | 2022-01-23 10:57 | 50 | 006:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L VEHICULO IMPACTO TENSOR | C22012300003 | 1st_after_momentary |  |  | Include | Wildlife | 385 | 2022-01-23 | 19250 | keep | 0 | Jan | 2022 | 0.013111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-01-23 06:06 | 2022-01-23 07:46 | 20 | 001:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22012300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-01-23 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-01-23 07:12 | 2022-01-23 09:33 | 85 | 002:21 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DEGANCHE | C22012300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-01-23 | 11985 | keep | 0 | Jan | 2022 | 0.0081629 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2022-01-23 07:40 | 2022-01-23 09:20 | 1979 | 001:40 | T | NO SE REPORTO CAUSA | DISPARO DEL ALIMENTADOR NO SE ENCONTRO CAUSA SE CERRO ELECTRICAMENTE YA QUE DIO FAIL TO OPERATE AL OPERARLO POR SCADA | P22012300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-01-23 | 197900 | keep | 0 | Jan | 2022 | 0.13479 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
AGUADILLA | 2022-01-23 07:40 | 2022-01-23 15:17 | 1 | 007:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN RISER CONECTOR ABIERTO EN MALAS CONDICIONES | M22012300003 | New_Event | Wire Down | Include | Include | Equipment | 457 | 2022-01-23 | 457 | keep | 0 | Jan | 2022 | 0.00031126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-23 08:00 | 2022-01-23 16:33 | 20 | 008:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2022-01-23 | 10260 | keep | 0 | Jan | 2022 | 0.006988 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-01-23 08:05 | 2022-01-23 08:34 | 2126 | 000:29 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA DIO FAIL TO OP CERRADO ELECTRICAMENTE | C22012300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-01-23 | 61654 | keep | 0 | Jan | 2022 | 0.041992 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2022-01-23 08:07 | 2022-01-23 10:19 | 8 | 002:12 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A22012300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-01-23 | 1056 | keep | 0 | Jan | 2022 | 0.00071924 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-01-23 08:10 | 2022-01-23 09:38 | 10 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | S22012300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-01-23 | 880 | keep | 0 | Jan | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-23 08:25 | 2022-01-23 15:25 | 8 | 007:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A22012300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2022-01-23 | 3360 | keep | 0 | Jan | 2022 | 0.0022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-01-23 08:41 | 2022-01-23 12:01 | 1 | 003:20 | P | DESGANCHE | 2 X 100 EN C/L | S22012300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-01-23 | 200 | keep | 0 | Jan | 2022 | 0.00013622 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-23 08:46 | 2022-01-23 08:48 | 1983 | 000:02 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1801-02 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B22012300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-23 | 3966 | keep | 0 | Jan | 2022 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-01-23 08:46 | 2022-01-23 08:48 | 186 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA 1711-04 | B22012300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-23 | 372 | keep | 0 | Jan | 2022 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
MAYAGÃœEZ | 2022-01-23 09:12 | 2022-01-23 14:55 | 100 | 005:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2022-01-23 | 34300 | keep | 0 | Jan | 2022 | 0.023362 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-23 09:16 | 2022-01-23 10:06 | 4 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS EN PEDESTAL | C22012300019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-01-23 | 200 | keep | 0 | Jan | 2022 | 0.00013622 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-23 09:23 | 2022-01-23 13:45 | 1 | 004:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | S22012300059 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2022-01-23 | 262 | keep | 0 | Jan | 2022 | 0.00017845 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-23 09:26 | 2022-01-23 09:27 | 1117 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 1117 | keep | 0 | Jan | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-01-23 09:26 | 2022-01-23 09:27 | 1671 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 1671 | keep | 0 | Jan | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2022-01-23 09:26 | 2022-01-23 09:27 | 527 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 527 | keep | 0 | Jan | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2022-01-23 09:26 | 2022-01-23 09:27 | 671 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 671 | keep | 0 | Jan | 2022 | 0.00045702 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
HUMACAO | 2022-01-23 09:28 | 2022-01-23 13:21 | 6 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22012300022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2022-01-23 | 1398 | keep | 0 | Jan | 2022 | 0.00095217 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-01-23 09:28 | 2022-01-23 13:21 | 5 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22012300022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2022-01-23 | 1165 | keep | 0 | Jan | 2022 | 0.00079348 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-01-23 09:28 | 2022-01-23 14:48 | 40 | 005:20 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | C22012300021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2022-01-23 | 12800 | keep | 0 | Jan | 2022 | 0.008718 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-23 09:36 | 2022-01-23 13:31 | 31 | 003:55 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA DESGANCHAR Y LEVANTAR SECUNDARIA | S22012300017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 235 | 2022-01-23 | 7285 | keep | 0 | Jan | 2022 | 0.0049618 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
AGUADILLA | 2022-01-23 10:15 | 2022-01-23 13:09 | 3 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22012300006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2022-01-23 | 522 | keep | 0 | Jan | 2022 | 0.00035553 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-01-23 10:15 | 2022-01-23 10:16 | 1227 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A22012300026 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-23 | 1227 | keep | 0 | Jan | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-01-23 10:16 | 2022-01-23 16:40 | 20 | 006:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEA ARREADAS | A22012300030 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 384 | 2022-01-23 | 7680 | keep | 0 | Jan | 2022 | 0.0052308 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-01-23 10:40 | 2022-01-23 12:33 | 1 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | R22012300012 | New_Event |  |  | Include | Wildlife | 113 | 2022-01-23 | 113 | keep | 0 | Jan | 2022 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-23 10:41 | 2022-01-23 13:54 | 100 | 003:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22012300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-01-23 | 19300 | keep | 0 | Jan | 2022 | 0.013145 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-23 11:31 | 2022-01-23 15:45 | 10 | 004:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22012300021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 254 | 2022-01-23 | 2540 | keep | 0 | Jan | 2022 | 0.00173 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-23 11:46 | 2022-01-23 14:23 | 10 | 002:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | A22012300039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 157 | 2022-01-23 | 1570 | keep | 0 | Jan | 2022 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-23 11:54 | 2022-01-23 12:56 | 26 | 001:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22012300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-01-23 | 1612 | keep | 0 | Jan | 2022 | 0.0010979 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
PONCE | 2022-01-23 12:50 | 2022-01-23 12:51 | 1 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN MONTURA DE TRANSFORMADOR AVE CRUZO LINEA | P22012300011 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-23 | 1 | keep | 0 | Jan | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-23 12:52 | 2022-01-23 14:00 | 10 | 001:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN XMR REEMPLAZO CONECTORES EN BAJANTES SECUNDARIOS DE XMR | R22012300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 68 | 2022-01-23 | 680 | keep | 0 | Jan | 2022 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-23 12:57 | 2022-01-23 17:24 | 20 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22012300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2022-01-23 | 5340 | keep | 0 | Jan | 2022 | 0.003637 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-23 13:03 | 2022-01-23 15:33 | 95 | 002:30 | P | OTRAS CAUSAS | 1 X 80 EN C/L Y 2 X 50 EN RISER @ SU-1 PROBLEMA DE CONTAMINACION EN BOVEDA PRIVADA DEL CONDOMINIO | R22012300016 | New_Event | Other Causes | Include | Include | Other | 150 | 2022-01-23 | 14250 | keep | 0 | Jan | 2022 | 0.0097056 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BARRANQUITAS | 2022-01-23 13:04 | 2022-01-23 13:05 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 4800 Y 8500 | C22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 2725 | keep | 0 | Jan | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-01-23 13:04 | 2022-01-23 13:05 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 4800 Y 8500 | C22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 1834 | keep | 0 | Jan | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-01-23 13:04 | 2022-01-23 13:05 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 4800 Y 8500 | C22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 1437 | keep | 0 | Jan | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-01-23 13:04 | 2022-01-23 13:05 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 4800 Y 8500 | C22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 2565 | keep | 0 | Jan | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-01-23 13:04 | 2022-01-23 13:05 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 4800 Y 8500 | C22012300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-23 | 3565 | keep | 0 | Jan | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
VEGA BAJA | 2022-01-23 13:21 | 2022-01-23 15:43 | 10 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22012300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-01-23 | 1420 | keep | 0 | Jan | 2022 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-23 13:44 | 2022-01-23 18:48 | 20 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | P22012300033 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2022-01-23 | 6080 | keep | 0 | Jan | 2022 | 0.0041411 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-23 13:45 | 2022-01-23 13:46 | 860 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE CERRO POR SCADA 20% POR EL 1303-02 | S22012300000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-23 | 860 | keep | 0 | Jan | 2022 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
SAN JUAN | 2022-01-23 13:45 | 2022-01-23 13:46 | 1483 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE CERRO POR SCADA 30% POR EL 1303-02 | S22012300000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-23 | 1483 | keep | 0 | Jan | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-23 13:45 | 2022-01-23 13:46 | 2435 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR SCADA LLEVA 20% DE 1204-02 Y 305 DEL 1204-04 | S22012300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-23 | 2435 | keep | 0 | Jan | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-01-23 13:46 | 2022-01-24 10:19 | 1 | 020:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | S22012300059 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1233 | 2022-01-23 | 1233 | keep | 0 | Jan | 2022 | 0.00083979 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-23 13:53 | 2022-01-23 15:40 | 51 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | S22012300037 | New_Event |  |  | Include | Wildlife | 107 | 2022-01-23 | 5457 | keep | 0 | Jan | 2022 | 0.0037167 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-01-23 14:37 | 2022-01-23 19:32 | 150 | 004:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2022-01-23 | 44250 | keep | 0 | Jan | 2022 | 0.030138 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-01-23 14:43 | 2022-01-23 17:29 | 88 | 002:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22012600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-01-23 | 14608 | keep | 0 | Jan | 2022 | 0.0099494 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
BAYAMON | 2022-01-23 14:53 | 2022-01-23 19:57 | 40 | 005:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 1 X 65 EN CORTES DE LINEA SE LLEVO CONDUCTOR A AISLADOR | B22012300014 | New_Event | Wire Down | Include | Include | Equipment | 304 | 2022-01-23 | 12160 | keep | 0 | Jan | 2022 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-23 15:03 | 2022-01-23 15:04 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22012300037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 2113 | keep | 0 | Jan | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
ARECIBO | 2022-01-23 15:04 | 2022-01-23 15:05 | 308 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | A22012300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-23 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2022-01-23 15:05 | 2022-01-23 18:26 | 1 | 003:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO FASES | A22012300067 | 1st_after_momentary |  |  | Include | Wildlife | 201 | 2022-01-23 | 201 | keep | 0 | Jan | 2022 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-23 15:12 | 2022-01-23 16:31 | 1 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22012300034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-01-23 | 79 | keep | 0 | Jan | 2022 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-23 15:17 | 2022-01-23 16:35 | 360 | 001:18 | T | DESGANCHE | SE CERRO POR SCADA SECCIONALIZANDO ALIMENTADOR POR DESGANCHE | B22012300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-01-23 | 28080 | keep | 0 | Jan | 2022 | 0.019125 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
BAYAMON | 2022-01-23 15:24 | 2022-01-23 22:59 | 182 | 007:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | B22012300020 | New_Event |  |  | Include | Wildlife | 455 | 2022-01-23 | 82810 | keep | 0 | Jan | 2022 | 0.056402 | 0.00012396 | Sustained | FALSE | FALSE | Not_TMED_Event | 182
BAYAMON | 2022-01-23 15:25 | 2022-01-23 21:28 | 30 | 006:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22012300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2022-01-23 | 10890 | keep | 0 | Jan | 2022 | 0.0074171 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-23 15:31 | 2022-01-23 16:29 | 60 | 000:58 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR PENCAS EN FUEGO | S22012300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-01-23 | 3480 | keep | 0 | Jan | 2022 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-23 15:38 | 2022-01-23 21:25 | 10 | 005:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 37.5 KVA | A22012300066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 347 | 2022-01-23 | 3470 | keep | 0 | Jan | 2022 | 0.0023634 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-23 15:43 | 2022-01-23 15:44 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22012300031 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 2216 | keep | 0 | Jan | 2022 | 0.0015093 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-23 15:44 | 2022-01-23 17:11 | 10 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22012300008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-01-23 | 870 | keep | 0 | Jan | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-23 15:49 | 2022-01-23 15:50 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012300021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-23 | 1234 | keep | 0 | Jan | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
SAN JUAN | 2022-01-23 15:52 | 2022-01-23 18:49 | 30 | 002:57 | P | OTRAS CAUSAS | 1 X 50 EN SU-4 @ BOVEDA CONDOMINO FALTA DE MANTENIMIENTO EN SUB CONDOMINIO | R22012300022 | New_Event | Other Causes | Include | Include | Other | 177 | 2022-01-23 | 5310 | keep | 0 | Jan | 2022 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-23 15:54 | 2022-01-23 17:49 | 75 | 001:55 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-01-23 | 8625 | keep | 0 | Jan | 2022 | 0.0058744 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-01-23 16:06 | 2022-01-23 19:06 | 13 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA | S22012300046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-01-23 | 2340 | keep | 0 | Jan | 2022 | 0.0015938 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-01-23 16:12 | 2022-01-23 16:39 | 651 | 000:27 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22012300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2022-01-23 | 17577 | keep | 0 | Jan | 2022 | 0.011972 | 0.00044339 | Sustained | FALSE | FALSE | Not_TMED_Event | 651
VEGA BAJA | 2022-01-23 16:35 | 2022-01-23 18:34 | 924 | 001:59 | P | DESGANCHE | SE CERRO MACHETES REALIZANDO DESGANCHE DE BAMBUAS | B22012300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-01-23 | 109956 | keep | 0 | Jan | 2022 | 0.074891 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-23 16:41 | 2022-01-23 17:20 | 9 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | R22012300023 | New_Event |  |  | Include | Wildlife | 39 | 2022-01-23 | 351 | keep | 0 | Jan | 2022 | 0.00023906 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-23 17:08 | 2022-01-24 10:00 | 12 | 016:52 | P | CABLE SOTERRADO AVERIADO | 1 X 15 EN CORTE DE LINEA CABLE SOTERRADO AVERIADO SE ENERGIZO A TRAVES DE CABLE ALTERNO DISPONIBLE | M22012300047 | New_Event | UG Cable Fault | Include | Include | Equipment | 1012 | 2022-01-23 | 12144 | keep | 0 | Jan | 2022 | 0.0082712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-01-23 17:54 | 2022-01-24 00:07 | 2 | 006:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22012300056 | New_Event | Bad Weather | Include | Include | Weather | 373 | 2022-01-23 | 746 | keep | 0 | Jan | 2022 | 0.0005081 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-01-23 17:58 | 2022-01-23 19:17 | 50 | 001:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22012300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-01-23 | 3950 | keep | 0 | Jan | 2022 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-01-23 18:18 | 2022-01-24 01:41 | 50 | 007:23 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA PERSONAL INDICO NO IDENTIFICO CAUSA | M22012300059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 443 | 2022-01-23 | 22150 | keep | 0 | Jan | 2022 | 0.015086 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-01-23 19:29 | 2022-01-24 00:47 | 1 | 005:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | M22012300065 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2022-01-23 | 318 | keep | 0 | Jan | 2022 | 0.00021659 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-23 20:08 | 2022-01-23 21:31 | 1420 | 001:23 | T | CABLE SOTERRADO AVERIADO | RECERRO UNA VEZ CARGA ESTABA POR EL 1530-06 SE REALIZO PRUEBA PROBO MALO TIENE RISER DE SALIDA AVERIADO SE TRANSFIRIO LA CARGA AL 1530-07 | S22012300055 | New_Event | UG Cable Fault | Include | Include | Equipment | 83 | 2022-01-23 | 117860 | keep | 0 | Jan | 2022 | 0.080274 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-01-23 20:08 | 2022-01-23 21:31 | 437 | 001:23 | T | CABLE SOTERRADO AVERIADO | RECERRO UNA VEZ SE REALIZO PRUEBA PROBO MALO TIENE RISER DE SALIDA AVERIADO SE TRANSFIRIO LA CARGA AL 1530-07 | S22012300055 | New_Event | UG Cable Fault | Include | Include | Equipment | 83 | 2022-01-23 | 36271 | keep | 0 | Jan | 2022 | 0.024704 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
CANOVANAS | 2022-01-23 21:30 | 2022-01-24 00:48 | 10 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R22012300027 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-01-23 | 1980 | keep | 0 | Jan | 2022 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-23 22:31 | 2022-01-23 22:33 | 922 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO I VEZ SE LE REALIZO PRUEBA Y PROBO BUENO CARGA POR EL 1401-08 | S22012300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-23 | 1844 | keep | 0 | Jan | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-01-23 22:31 | 2022-01-23 22:33 | 135 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO I VEZ SE LE REALIZO PRUEBA Y PROBO BUENO LLEVA LA CARGA DEL 1346-05 | S22012300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-23 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
PONCE | 2022-01-23 23:26 | 2022-01-24 11:57 | 50 | 012:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22012300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 751 | 2022-01-23 | 37550 | keep | 0 | Jan | 2022 | 0.025575 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-24 00:40 | 2022-01-24 22:33 | 60 | 021:53 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE CAIDO | B22012400004 | New_Event | Defective Pole | Include | Include | Equipment | 1313 | 2022-01-24 | 78780 | keep | 0 | Jan | 2022 | 0.053657 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-01-24 01:31 | 2022-01-24 14:56 | 20 | 013:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y NEUTRAL PRIMARIO | C22012400003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 805 | 2022-01-24 | 16100 | keep | 0 | Jan | 2022 | 0.010966 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-01-24 01:48 | 2022-01-24 08:32 | 200 | 006:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR | R22012400004 | New_Event | Wire Down | Include | Include | Equipment | 404 | 2022-01-24 | 80800 | keep | 0 | Jan | 2022 | 0.055033 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-01-24 04:06 | 2022-01-24 10:51 | 100 | 006:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2X100 EN CORTE DE LINEA Y SE RETIRO AVE DEL 13KV | B22012400007 | New_Event |  |  | Include | Wildlife | 405 | 2022-01-24 | 40500 | keep | 0 | Jan | 2022 | 0.027584 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-01-24 07:16 | 2022-01-24 07:17 | 5063 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22012400002 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-24 | 5063 | keep | 0 | Jan | 2022 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2022-01-24 07:17 | 2022-01-24 09:25 | 25 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO NEUTRAL PRIMARIO Y SE CAMBIO CAJA PRIMARIA DE CORTE DE LINEA | P22012400005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 128 | 2022-01-24 | 3200 | keep | 0 | Jan | 2022 | 0.0021795 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-01-24 07:24 | 2022-01-24 10:30 | 100 | 003:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 50 EN DIFERENTES CORTES DE LINEA SE FIJO CAJA PRIMARIA | P22012400003 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2022-01-24 | 18600 | keep | 0 | Jan | 2022 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-24 07:41 | 2022-01-24 10:17 | 50 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE | C22012400039 | New_Event |  |  | Include | Wildlife | 156 | 2022-01-24 | 7800 | keep | 0 | Jan | 2022 | 0.0053125 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-24 08:05 | 2022-01-24 16:30 | 17 | 008:25 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA ELIMINAR POSTE PARTIDO Y RELOCALIZAR 2 XMRS | C22012400009 | New_Event | Defective Pole | Include | Include | Equipment | 505 | 2022-01-24 | 8585 | keep | 0 | Jan | 2022 | 0.0058472 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-01-24 08:13 | 2022-01-24 09:52 | 10 | 001:39 | P | DESGANCHE | 1X15 EN TRANSFORMADOR | B22012400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-01-24 | 990 | keep | 0 | Jan | 2022 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-24 08:32 | 2022-01-24 21:03 | 30 | 012:31 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T-25 @ T-26 Y AVERIA VIEJA DEL T-27 @ T-26. CONSTRUYO PROVISIONAL DEL T-27 @ T-26 SE REEMPLAZO 1 X 10 EN C/L PROVISIONAL AEREO | R22012400047 | New_Event | UG Cable Fault | Include | Include | Equipment | 751 | 2022-01-24 | 22530 | keep | 0 | Jan | 2022 | 0.015345 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-01-24 08:32 | 2022-01-24 08:33 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 4188 | keep | 0 | Jan | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-01-24 08:33 | 2022-01-24 12:02 | 200 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR | R22012400004 | Partial_restoration | Wire Down | Include | Include | Equipment | 209 | 2022-01-24 | 41800 | keep | 0 | Jan | 2022 | 0.02847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-01-24 08:39 | 2022-01-24 13:55 | 250 | 005:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012400025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2022-01-24 | 79000 | keep | 0 | Jan | 2022 | 0.053807 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
FAJARDO | 2022-01-24 08:48 | 2022-01-24 09:27 | 1 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR TOMA AVERIADA | R22012400002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-01-24 | 39 | keep | 0 | Jan | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-24 08:50 | 2022-01-24 14:30 | 100 | 005:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA JOURNEYMAN INFORMA QUE EL SECTOR REQUIERE DESGANCHE | M22012400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2022-01-24 | 34000 | keep | 0 | Jan | 2022 | 0.023157 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-24 08:54 | 2022-01-24 11:37 | 50 | 002:43 | P | NO SE REPORTO CAUSA | 1X100 EN CORTE DE LINEA | B22012400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2022-01-24 | 8150 | keep | 0 | Jan | 2022 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-24 08:55 | 2022-01-24 08:56 | 3174 | 000:01 | P | CABLE SOTERRADO AVERIADO | REALIZADO OPERACIONES DE CAMPO PARA NORMALIZAR CARGAS DEL 1336-08 DISPARO ALIMENTADOR 1404-06 QUE LLEVA 80% DEL 1404-07 Y 40% DEL 1336-08. RELACIONADO AL SWITCH FROM SJ-220124-01 | S22012400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-24 | 3174 | keep | 0 | Jan | 2022 | 0.0021618 | 0.0021618 | Momentary | FALSE | FALSE | Not_TMED_Event | 3174
SAN JUAN | 2022-01-24 08:55 | 2022-01-24 08:56 | 143 | 000:01 | T | CABLE SOTERRADO AVERIADO | REALIZADO OPERACIONES DE CAMPO PARA NORMALIZAR CARGAS DEL 1336-08 DISPARO ALIMENTADOR 1404-06 QUE LLEVA 80% DEL 1404-07 Y 40% 1336-08. RELACIONADO AL SWITCH FROM SJ-220124-01 | S22012400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-24 | 143 | keep | 0 | Jan | 2022 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-01-24 08:55 | 2022-01-24 08:56 | 272 | 000:01 | P | CABLE SOTERRADO AVERIADO | REALIZADO OPERACIONES DE CAMPO PARA NORMALIZAR CARGAS DEL 1336-08 DISPARO ALIMENTADOR 1404-06 QUE LLEVA 80% DEL 1404-07 Y 40% 1336-08. RELACIONADO AL SWITCH FROM SJ-220124-01 | S22012400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-24 | 272 | keep | 0 | Jan | 2022 | 0.00018526 | 0.00018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 272
ARECIBO | 2022-01-24 08:58 | 2022-01-24 14:25 | 75 | 005:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INDICA FOREMAN REQUIERE DESGANCHE | A22012400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-01-24 | 24525 | keep | 0 | Jan | 2022 | 0.016704 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-01-24 09:02 | 2022-01-24 13:58 | 40 | 004:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-01-24 | 11840 | keep | 0 | Jan | 2022 | 0.0080642 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-24 09:05 | 2022-01-24 13:00 | 40 | 003:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 100 KVA POR UNO DE 75 KVA | M22012400013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 235 | 2022-01-24 | 9400 | keep | 0 | Jan | 2022 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-24 09:10 | 2022-01-24 13:31 | 30 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22012400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2022-01-24 | 7830 | keep | 0 | Jan | 2022 | 0.005333 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-01-24 09:11 | 2022-01-24 11:46 | 1464 | 002:35 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO ALIMENTADOR POR POSTE PARTIDO POR ACCIDENTE DE AUTO SE ABRIERON PUENTES PARA SECCIONALIZAR AVERIA | P22012400009 | New_Event |  |  | Include | Wildlife | 155 | 2022-01-24 | 226920 | keep | 0 | Jan | 2022 | 0.15455 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
CANOVANAS | 2022-01-24 09:12 | 2022-01-24 13:27 | 20 | 004:15 | P | DESGANCHE | 1 X 25 EN XMR | R22012400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-01-24 | 5100 | keep | 0 | Jan | 2022 | 0.0034736 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-01-24 09:16 | 2022-01-24 09:17 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22012400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 1746 | keep | 0 | Jan | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
HUMACAO | 2022-01-24 09:23 | 2022-01-24 12:15 | 15 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 25 EN PM | C22012400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2022-01-24 | 2580 | keep | 0 | Jan | 2022 | 0.0017572 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-24 09:30 | 2022-01-24 12:48 | 60 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADORES PARA RETIRAR CARGA Y REMPLAZAR UNA CAJA PRIMARIA DE 100 AMP UN PARARRAYOS Y CERRAR NEUTRAL PRIMARIO ABIERTO | A22012400001 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-01-24 | 11880 | keep | 0 | Jan | 2022 | 0.0080914 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-01-24 09:31 | 2022-01-24 15:16 | 60 | 005:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 40 EN CORTES DE LINEAS REEMPLAZARON CAJA PRIMARIA AVERIADA | R22012400012 | New_Event | Cutout Failure | Include | Include | Equipment | 345 | 2022-01-24 | 20700 | keep | 0 | Jan | 2022 | 0.014099 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-24 09:33 | 2022-01-24 11:55 | 100 | 002:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22012400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-24 | 14200 | keep | 0 | Jan | 2022 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-24 09:35 | 2022-01-24 13:35 | 2 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA PARA RAPARAR PUENTES PRIMARIOS ABIERTOS | A22012400002 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2022-01-24 | 480 | keep | 0 | Jan | 2022 | 0.00032693 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-24 09:36 | 2022-01-24 13:22 | 50 | 003:46 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S22012400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-01-24 | 11300 | keep | 0 | Jan | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-24 09:45 | 2022-01-24 10:09 | 10 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22012400015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-01-24 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-24 09:52 | 2022-01-24 11:15 | 100 | 001:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | ABRIO CORTE DE LINEA PARA REEMPLAZAR CAJA PRIMARIA | C22012400039 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2022-01-24 | 8300 | keep | 0 | Jan | 2022 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-01-24 10:06 | 2022-01-24 14:00 | 5 | 003:54 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | R22012400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2022-01-24 | 1170 | keep | 0 | Jan | 2022 | 0.00079688 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-01-24 10:06 | 2022-01-24 10:18 | 20 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BARRAS SECUNDARIAS | C22012400004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2022-01-24 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-01-24 10:15 | 2022-01-24 15:30 | 12 | 005:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS Y RELOCALIZAR TRANSFORMADOR | M22012400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 315 | 2022-01-24 | 3780 | keep | 0 | Jan | 2022 | 0.0025745 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-24 10:20 | 2022-01-24 11:19 | 7 | 000:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR UNO DE 37.5KVA | A22012400020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 59 | 2022-01-24 | 413 | keep | 0 | Jan | 2022 | 0.00028129 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-01-24 10:20 | 2022-01-24 13:22 | 2635 | 003:02 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE DESGANCHO | C22012400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-01-24 | 479570 | keep | 0 | Jan | 2022 | 0.32663 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
HUMACAO | 2022-01-24 10:21 | 2022-01-24 11:58 | 10 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR Y SE REPARO SECUNDARIA | C22012300046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2022-01-24 | 970 | keep | 0 | Jan | 2022 | 0.00066066 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-24 10:22 | 2022-01-24 13:37 | 20 | 003:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR SE REEMPLAZO POSTE SECUNDARIO | C22012400043 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 195 | 2022-01-24 | 3900 | keep | 0 | Jan | 2022 | 0.0026563 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-01-24 10:28 | 2022-01-24 10:33 | 1569 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P22012400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-01-24 | 7845 | keep | 0 | Jan | 2022 | 0.0053432 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
PONCE | 2022-01-24 10:29 | 2022-01-24 10:31 | 2446 | 000:02 | T | ERROR HUMANO | RECIERRE ALIMENTADOR CON " HOLD OFF" POR RETIRO DE SERVICIO EN MED QUATRO TRABAJOS INTERNOS DE LA SUBESTACION | P22012400025 | New_Event | Human Error | Include | Include | Other | 2 | 2022-01-24 | 4892 | keep | 0 | Jan | 2022 | 0.0033319 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
MAYAGÃœEZ | 2022-01-24 10:38 | 2022-01-24 16:50 | 15 | 006:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M22012400031 | New_Event |  |  | Include | Wildlife | 372 | 2022-01-24 | 5580 | keep | 0 | Jan | 2022 | 0.0038005 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-24 10:44 | 2022-01-24 10:45 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 QUE ADEMAS LLEVA LA CARGA DEL 1909-09 | B22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 222 | keep | 0 | Jan | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-01-24 10:44 | 2022-01-24 10:45 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 QUE ADEMAS LLEVA LA CARGA DEL 1909-09 | B22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 4456 | keep | 0 | Jan | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-01-24 10:56 | 2022-01-24 15:31 | 1 | 004:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO XMR SE REPARO SECUNDARIA Y SE REMPLAZO PORTAFUSIBLES | S22012400021 | New_Event | Cutout Failure | Include | Include | Equipment | 275 | 2022-01-24 | 275 | keep | 0 | Jan | 2022 | 0.0001873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-24 11:06 | 2022-01-24 11:07 | 5630 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22012400000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-24 | 5630 | keep | 0 | Jan | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-01-24 11:07 | 2022-01-24 18:02 | 1 | 006:55 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L ELIMINO PARARRAYO | C22012400077 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 415 | 2022-01-24 | 415 | keep | 0 | Jan | 2022 | 0.00028265 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-24 11:38 | 2022-01-24 16:17 | 50 | 004:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22012400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-01-24 | 13950 | keep | 0 | Jan | 2022 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-24 11:44 | 2022-01-24 13:16 | 8 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22012400020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-01-24 | 736 | keep | 0 | Jan | 2022 | 0.00050129 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-01-24 11:46 | 2022-01-24 18:50 | 25 | 007:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PRIMARIO PARTIDO POR ACCIDENTE DE AUTO SE ABREN PUENTES PARA SECCIONALIZAR AVERIA | P22012400041 | New_Event |  |  | Include | Wildlife | 424 | 2022-01-24 | 10600 | keep | 0 | Jan | 2022 | 0.0072196 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-01-24 12:09 | 2022-01-24 12:10 | 569 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22012400047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 569 | keep | 0 | Jan | 2022 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
YAUCO | 2022-01-24 12:23 | 2022-01-24 12:24 | 661 | 000:01 | T | DESGANCHE | RECIERRE | P220124000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-24 | 661 | keep | 0 | Jan | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2022-01-24 12:24 | 2022-01-24 16:07 | 62 | 003:43 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P22012400049 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-01-24 | 13826 | keep | 0 | Jan | 2022 | 0.0094168 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
CAGUAS | 2022-01-24 12:42 | 2022-01-24 16:54 | 30 | 004:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN C/L LEVANTO CONDUCTOR | C22012400085 | New_Event | Wire Down | Include | Include | Equipment | 252 | 2022-01-24 | 7560 | keep | 0 | Jan | 2022 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-24 13:10 | 2022-01-24 14:33 | 25 | 001:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERRIADO 50KVA X 50KVA | S22012400026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 83 | 2022-01-24 | 2075 | keep | 0 | Jan | 2022 | 0.0014133 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-24 13:10 | 2022-01-24 14:52 | 15 | 001:42 | P | NO SE REPORTO CAUSA | 1X30 DE RISER @ T-3 | B22012400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-01-24 | 1530 | keep | 0 | Jan | 2022 | 0.0010421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-24 13:15 | 2022-01-24 14:09 | 1 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-24 | 54 | keep | 0 | Jan | 2022 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-24 13:17 | 2022-01-24 16:22 | 100 | 003:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y SE REEMPLAZO CAJA PRIMARIA | C22012400094 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2022-01-24 | 18500 | keep | 0 | Jan | 2022 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-24 13:19 | 2022-01-24 18:02 | 6 | 004:43 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S22012100027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 283 | 2022-01-24 | 1698 | keep | 0 | Jan | 2022 | 0.0011565 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-01-24 13:23 | 2022-01-24 16:01 | 100 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P22012400042 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2022-01-24 | 15800 | keep | 0 | Jan | 2022 | 0.010761 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-24 13:26 | 2022-01-24 13:50 | 2891 | 000:24 | T | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR SE CERRO EN EL CAMPO | R22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-01-24 | 69384 | keep | 0 | Jan | 2022 | 0.047257 | 0.001969 | Sustained | FALSE | FALSE | Not_TMED_Event | 2891
CAGUAS | 2022-01-24 13:30 | 2022-01-24 14:17 | 20 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22012400091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2022-01-24 | 940 | keep | 0 | Jan | 2022 | 0.00064023 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-24 13:53 | 2022-01-24 15:32 | 1 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER HACIA PM PRIVADO | S22012400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-01-24 | 99 | keep | 0 | Jan | 2022 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-01-24 14:05 | 2022-01-24 14:43 | 8 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22012400048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-01-24 | 304 | keep | 0 | Jan | 2022 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-24 14:12 | 2022-01-24 16:20 | 60 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22012400044 | New_Event |  |  | Include | Wildlife | 128 | 2022-01-24 | 7680 | keep | 0 | Jan | 2022 | 0.0052308 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-01-24 14:18 | 2022-01-24 16:06 | 1 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER CRUCE POR AVE | R22012400073 | New_Event |  |  | Include | Wildlife | 108 | 2022-01-24 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-24 14:19 | 2022-01-24 15:02 | 10 | 000:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 50 KVA X 50 KVA | A22012400043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 43 | 2022-01-24 | 430 | keep | 0 | Jan | 2022 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-24 14:32 | 2022-01-24 15:30 | 30 | 000:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO XMR PARA CERRAR PUENTES | C22012400094 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2022-01-24 | 1740 | keep | 0 | Jan | 2022 | 0.0011851 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-24 14:32 | 2022-01-24 15:30 | 20 | 000:58 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR PEDESTAL | C22012400107 | Partial_restoration | Secondary Defective Pole | Include | Include | Equipment | 58 | 2022-01-24 | 1160 | keep | 0 | Jan | 2022 | 0.00079007 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-24 14:32 | 2022-01-24 16:36 | 20 | 002:04 | P | DESGANCHE | 1X40 EN CORTE DE LINEA | B22012400043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-01-24 | 2480 | keep | 0 | Jan | 2022 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-24 14:33 | 2022-01-24 18:40 | 20 | 004:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INFORMA EL JOURNEYMAN SECTOR REQUIERE DESGANCHE | M22012400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-01-24 | 4940 | keep | 0 | Jan | 2022 | 0.0033646 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-24 14:36 | 2022-01-24 16:15 | 300 | 001:39 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-01-24 | 29700 | keep | 0 | Jan | 2022 | 0.020229 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-01-24 14:45 | 2022-01-24 15:35 | 60 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R22012400078 | New_Event |  |  | Include | Wildlife | 50 | 2022-01-24 | 3000 | keep | 0 | Jan | 2022 | 0.0020433 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-24 15:04 | 2022-01-24 15:05 | 679 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 85% DE LA CARGA DEL 1705-05 | B22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 679 | keep | 0 | Jan | 2022 | 0.00046246 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2022-01-24 15:04 | 2022-01-24 15:05 | 96 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1705-02 LLEVA TRANSFERIDO EL 85% DE LA CARGA DEL 1705-05 | B22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 96 | keep | 0 | Jan | 2022 | 6.5385e-05 | 6.5385e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 96
CAGUAS | 2022-01-24 15:05 | 2022-01-24 16:13 | 20 | 001:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C22012400108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 68 | 2022-01-24 | 1360 | keep | 0 | Jan | 2022 | 0.00092629 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-24 15:13 | 2022-01-24 15:14 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22012400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 3941 | keep | 0 | Jan | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
VEGA BAJA | 2022-01-24 15:17 | 2022-01-25 10:22 | 1 | 019:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B22012400047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1145 | 2022-01-24 | 1145 | keep | 0 | Jan | 2022 | 0.00077985 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-24 15:32 | 2022-01-24 16:16 | 10 | 000:44 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU -1 | C22012400114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2022-01-24 | 440 | keep | 0 | Jan | 2022 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-01-24 15:39 | 2022-01-24 17:39 | 100 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L CAMION IMPACTO TENSOR | C22012400116 | New_Event |  |  | Include | Wildlife | 120 | 2022-01-24 | 12000 | keep | 0 | Jan | 2022 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-01-24 15:44 | 2022-01-25 14:43 | 44 | 022:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C22012400117 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1379 | 2022-01-24 | 60676 | keep | 0 | Jan | 2022 | 0.041326 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
HUMACAO | 2022-01-24 15:47 | 2022-01-24 17:14 | 22 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO REPORTO CAUSA | C22012400118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-01-24 | 1914 | keep | 0 | Jan | 2022 | 0.0013036 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2022-01-24 15:50 | 2022-01-24 16:40 | 10 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22012400067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-01-24 | 500 | keep | 0 | Jan | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-24 15:50 | 2022-01-24 16:35 | 15 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22012400075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-01-24 | 675 | keep | 0 | Jan | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-24 16:00 | 2022-01-24 17:30 | 6 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22012400073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-01-24 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-24 16:35 | 2022-01-24 18:06 | 95 | 001:31 | P | DESGANCHE | 1 X 50 1 X 40 Y 1 X 30 EN CORTES DE LINEAS | R22012400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-01-24 | 8645 | keep | 0 | Jan | 2022 | 0.0058881 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CAGUAS | 2022-01-24 16:36 | 2022-01-24 20:32 | 35 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CAMION IMPACTO POSTE | C22012400127 | New_Event |  |  | Include | Wildlife | 236 | 2022-01-24 | 8260 | keep | 0 | Jan | 2022 | 0.0056258 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-01-24 16:46 | 2022-01-24 17:26 | 10 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR INDICA FOREMAN NO IDENTIFICO CAUSA | A22012400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-01-24 | 400 | keep | 0 | Jan | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-01-24 16:48 | 2022-01-24 17:05 | 1 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | P22012400074 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2022-01-24 | 17 | keep | 0 | Jan | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-24 17:00 | 2022-01-24 17:01 | 4882 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22012400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-24 | 4882 | keep | 0 | Jan | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-01-24 17:01 | 2022-01-24 21:15 | 200 | 004:14 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA INDICA JOURNEYMAN SECTOR REQUIERE DESGANCHE | M22012400084 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-01-24 | 50800 | keep | 0 | Jan | 2022 | 0.0346 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-01-24 17:04 | 2022-01-24 19:10 | 50 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVICIONAL AEREO NO SE REPORTO LA CAUSA | P22012400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-01-24 | 6300 | keep | 0 | Jan | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-24 17:21 | 2022-01-24 17:22 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22012400061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-24 | 3431 | keep | 0 | Jan | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
SAN JUAN | 2022-01-24 17:34 | 2022-01-24 20:21 | 26 | 002:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S22012400045 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2022-01-24 | 4342 | keep | 0 | Jan | 2022 | 0.0029573 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 2100 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 168000 | keep | 0 | Jan | 2022 | 0.11442 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 922 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 73760 | keep | 0 | Jan | 2022 | 0.050238 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 1676 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 134080 | keep | 0 | Jan | 2022 | 0.091321 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 2844 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 227520 | keep | 0 | Jan | 2022 | 0.15496 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 2775 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 222000 | keep | 0 | Jan | 2022 | 0.1512 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 1457 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 116560 | keep | 0 | Jan | 2022 | 0.079388 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 1086 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 86880 | keep | 0 | Jan | 2022 | 0.059174 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 2134 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 170720 | keep | 0 | Jan | 2022 | 0.11628 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 1464 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 117120 | keep | 0 | Jan | 2022 | 0.07977 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 1833 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 146640 | keep | 0 | Jan | 2022 | 0.099876 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 1565 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 125200 | keep | 0 | Jan | 2022 | 0.085273 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-24 18:50 | 2022-01-24 20:10 | 977 | 001:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3700 | P22012400083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-01-24 | 78160 | keep | 0 | Jan | 2022 | 0.053234 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
SAN JUAN | 2022-01-24 18:51 | 2022-01-24 21:56 | 60 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22012400096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-01-24 | 11100 | keep | 0 | Jan | 2022 | 0.0075602 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-24 18:59 | 2022-01-25 09:35 | 8 | 014:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22012400064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 876 | 2022-01-24 | 7008 | keep | 0 | Jan | 2022 | 0.0047731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-24 19:10 | 2022-01-25 04:29 | 100 | 009:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22012400095 | New_Event | Bad Weather | Include | Include | Weather | 559 | 2022-01-24 | 55900 | keep | 0 | Jan | 2022 | 0.038073 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-01-24 19:40 | 2022-01-24 20:06 | 15 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22012400049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-01-24 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-24 19:46 | 2022-01-25 10:09 | 200 | 014:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A22012400066 | New_Event | Wire Down | Include | Include | Equipment | 863 | 2022-01-24 | 172600 | keep | 0 | Jan | 2022 | 0.11756 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-01-24 19:54 | 2022-01-25 10:47 | 1 | 014:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADOR | C22012500136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 893 | 2022-01-24 | 893 | keep | 0 | Jan | 2022 | 0.00060822 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-01-24 20:10 | 2022-01-24 21:41 | 25 | 001:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PRIMARIO PARTIDO POR ACCIDENTE DE AUTO SE ABREN PUENTES PARA SECCIONALIZAR AVERIA | P22012400041 | Partial_restoration |  |  | Include | Wildlife | 91 | 2022-01-24 | 2275 | keep | 0 | Jan | 2022 | 0.0015495 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-24 20:15 | 2022-01-24 20:40 | 15 | 000:25 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSOFRMADOR PARA REALIZAR DESGANCHE | S22012400046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 25 | 2022-01-24 | 375 | keep | 0 | Jan | 2022 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-01-24 20:20 | 2022-01-24 22:55 | 150 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA Y SE ABRIO MACHETES PARA REEMPLAZO DE DOS CAJAS POR TRATARSE DE UN UTILITY LINEMAN 2 QUE NO PUEDE REALIZAR TRABAJOS EN VIVO SEGUN INFORMO | B22012400059 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-01-24 | 23250 | keep | 0 | Jan | 2022 | 0.015835 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-01-24 20:57 | 2022-01-24 23:53 | 21 | 002:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 25 AMP CRUCE POR RATA EN T-40 | R22012400098 | New_Event |  |  | Include | Wildlife | 176 | 2022-01-24 | 3696 | keep | 0 | Jan | 2022 | 0.0025173 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-01-24 21:11 | 2022-01-25 01:56 | 100 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1X 80 CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22012240102 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2022-01-24 | 28500 | keep | 0 | Jan | 2022 | 0.019411 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-24 21:13 | 2022-01-25 11:16 | 60 | 014:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA | C22012400146 | New_Event |  |  | Include | Wildlife | 843 | 2022-01-24 | 50580 | keep | 0 | Jan | 2022 | 0.03445 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-01-24 21:41 | 2022-01-24 22:30 | 1464 | 000:49 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR PARA CERRAR PUENTES PRIMARIOS | P22012400178 | Additional_clients |  |  | Include | Wildlife | 49 | 2022-01-24 | 71736 | keep | 0 | Jan | 2022 | 0.048859 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-24 22:16 | 2022-01-25 07:15 | 75 | 008:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22012400180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2022-01-24 | 40425 | keep | 0 | Jan | 2022 | 0.027533 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-01-24 22:55 | 2022-01-25 00:37 | 852 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA Y SE ABRIO MACHETES PARA REEMPLAZO DE DOS CAJAS POR TRATARSE DE UN UTILITY LINEMAN 2 QUE NO PUEDE REALIZAR TRABAJOS EN VIVO SEGUN INFORMO | B22012400059 | Additional_clients | Cutout Failure | Include | Include | Equipment | 102 | 2022-01-24 | 86904 | keep | 0 | Jan | 2022 | 0.05919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:32 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-24 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:32 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-24 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:32 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-24 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:32 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-24 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 2775 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 5550 | keep | 0 | Jan | 2022 | 0.0037801 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 1457 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 2914 | keep | 0 | Jan | 2022 | 0.0019847 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 1086 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 2172 | keep | 0 | Jan | 2022 | 0.0014793 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 2134 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 4268 | keep | 0 | Jan | 2022 | 0.0029069 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 1464 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 2928 | keep | 0 | Jan | 2022 | 0.0019942 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 1833 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 3666 | keep | 0 | Jan | 2022 | 0.0024969 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 3130 | keep | 0 | Jan | 2022 | 0.0021318 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-24 23:31 | 2022-01-24 23:33 | 977 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220124000XX | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-24 | 1954 | keep | 0 | Jan | 2022 | 0.0013309 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-01-24 23:57 | 2022-01-25 09:54 | 10 | 009:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR Y PARARRAYOS AVERIADO | M22012400112 | New_Event | Cutout Failure | Include | Include | Equipment | 597 | 2022-01-24 | 5970 | keep | 0 | Jan | 2022 | 0.0040661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-25 01:44 | 2022-01-25 09:35 | 40 | 007:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA PERSONAL NO IDENTIFICO CAUSA | A22012500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2022-01-25 | 18840 | keep | 0 | Jan | 2022 | 0.012832 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-25 03:36 | 2022-01-25 03:37 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220125000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
CANOVANAS | 2022-01-25 05:08 | 2022-01-25 05:09 | 2524 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR CERRADO POR CONTROL | R22012500003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-25 | 2524 | keep | 0 | Jan | 2022 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-01-25 05:09 | 2022-01-25 10:35 | 140 | 005:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 1 X 40 Y 1 X 80 EN CORTES DE LINEAS REEMPLAZO AISLADOR ROTO | R22012500004 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 326 | 2022-01-25 | 45640 | keep | 0 | Jan | 2022 | 0.031085 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2022-01-25 05:18 | 2022-01-25 13:36 | 100 | 008:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22012500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 498 | 2022-01-25 | 49800 | keep | 0 | Jan | 2022 | 0.033919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-25 07:14 | 2022-01-25 07:15 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-25 07:14 | 2022-01-25 07:15 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
HUMACAO | 2022-01-25 07:45 | 2022-01-25 14:05 | 79 | 006:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22012500008 | New_Event |  |  | Include | Wildlife | 380 | 2022-01-25 | 30020 | keep | 0 | Jan | 2022 | 0.020446 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
AGUADILLA | 2022-01-25 08:25 | 2022-01-25 10:32 | 2366 | 002:07 | T | DESGANCHE | DISPARO DE INTERRUPTOR NO CIERRA POR SCADA SE PATRULLO POR JOSE UGARTE E INDICA QUE REQUIERE DESGANCHE PERO QUE SE PODIA CERRAR MIGUEL RAMOS LO CERRO Y QUEDO EN SERVICIO. | M22012500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-01-25 | 300482 | keep | 0 | Jan | 2022 | 0.20466 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-01-25 09:05 | 2022-01-25 10:14 | 20 | 001:09 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA QUE PERSONAL DE LA OFICINA COMERCIAL TRABAJARA CON PERSONAL PRIVADO EN REMPLAZO DE BASE DE CONTADORES MULTIPLES | M22012500009 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 69 | 2022-01-25 | 1380 | keep | 0 | Jan | 2022 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-25 09:20 | 2022-01-25 10:17 | 3 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | C22012500022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-01-25 | 171 | keep | 0 | Jan | 2022 | 0.00011647 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-25 09:21 | 2022-01-25 17:28 | 5 | 008:07 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR SE REMPLAZO POSTE PARTIDO POR EMERGENCIA Y SE REPARO SECUNDARIA | S22012500011 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 487 | 2022-01-25 | 2435 | keep | 0 | Jan | 2022 | 0.0016585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-25 09:29 | 2022-01-25 09:30 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22012500008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
BAYAMON | 2022-01-25 09:30 | 2022-01-25 10:09 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO CONEXION SECUNDARIA | S22012400024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-01-25 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-25 09:30 | 2022-01-25 11:32 | 4 | 002:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES | C22012500024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 122 | 2022-01-25 | 488 | keep | 0 | Jan | 2022 | 0.00033237 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-25 09:33 | 2022-01-25 09:36 | 1964 | 000:03 | T | ERROR HUMANO | PERSONAL DE CDS DISPARO EL ALIMENTADOR EN TRABAJOS PARA CORREGIR INDICACION ERRONEA DE STATUS DEL INTERRUPTOR POR SCADA. LLEVANDO 60% DEL 1110-03 | S22012500000 | New_Event | Human Error | Include | Include | Other | 3 | 2022-01-25 | 5892 | keep | 0 | Jan | 2022 | 0.004013 | 0.0013377 | Momentary | FALSE | FALSE | Not_TMED_Event | 1964
SAN JUAN | 2022-01-25 09:33 | 2022-01-25 09:39 | 915 | 000:06 | P | ERROR HUMANO | PERSONAL DE CDS DISPARO EL ALIMENTADOR EN TRABAJOS PARA CORREGIR INDICACION ERRONEA DE STATUS DEL INTERRUPTOR POR SCADA. LLEVANDO 60% DEL 1110-03 | S22012500000 | New_Event | Human Error | Include | Include | Other | 6 | 2022-01-25 | 5490 | keep | 0 | Jan | 2022 | 0.0037392 | 0.0006232 | Sustained | FALSE | FALSE | Not_TMED_Event | 915
SAN JUAN | 2022-01-25 09:33 | 2022-01-25 09:35 | 1587 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA CARGA DEL 1336-09 Y 30% DEL 1204-04 | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-25 | 3174 | keep | 0 | Jan | 2022 | 0.0021618 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
SAN JUAN | 2022-01-25 09:33 | 2022-01-25 09:35 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA CARGA DEL 1336-09 Y 30% DEL 1204-04 | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-25 | 10580 | keep | 0 | Jan | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-25 09:33 | 2022-01-25 09:35 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA CARGA DEL 1336-09 Y 30% DEL 1204-04 | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-25 | 414 | keep | 0 | Jan | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
PONCE | 2022-01-25 09:40 | 2022-01-25 12:50 | 18 | 003:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE RESTABLECIO CARGA | P22012500012 | New_Event | Wire Down | Include | Include | Equipment | 190 | 2022-01-25 | 3420 | keep | 0 | Jan | 2022 | 0.0023293 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-01-25 09:45 | 2022-01-25 13:21 | 100 | 003:36 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA EL PERSONAL INFORMO QUE NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22012500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2022-01-25 | 21600 | keep | 0 | Jan | 2022 | 0.014712 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-25 09:50 | 2022-01-25 10:20 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012400056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-01-25 | 300 | keep | 0 | Jan | 2022 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-25 09:58 | 2022-01-25 13:00 | 2 | 003:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | R22012500040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 182 | 2022-01-25 | 364 | keep | 0 | Jan | 2022 | 0.00024792 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-01-25 09:58 | 2022-01-25 10:37 | 100 | 000:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22012500030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2022-01-25 | 3900 | keep | 0 | Jan | 2022 | 0.0026563 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-25 10:22 | 2022-01-25 14:03 | 33 | 003:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 X 50KVA | S22012500032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 221 | 2022-01-25 | 7293 | keep | 0 | Jan | 2022 | 0.0049672 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
AGUADILLA | 2022-01-25 10:32 | 2022-01-25 13:00 | 200 | 002:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO Y SE RETEZO LINEA | M22012500016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 148 | 2022-01-25 | 29600 | keep | 0 | Jan | 2022 | 0.02016 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-01-25 10:34 | 2022-01-25 15:39 | 14 | 005:05 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | P22012500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-01-25 | 4270 | keep | 0 | Jan | 2022 | 0.0029083 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-01-25 10:35 | 2022-01-25 10:43 | 2524 | 000:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL | R22012500042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2022-01-25 | 20192 | keep | 0 | Jan | 2022 | 0.013753 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
BAYAMON | 2022-01-25 10:37 | 2022-01-25 11:02 | 12 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22012200007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-01-25 | 300 | keep | 0 | Jan | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-25 10:43 | 2022-01-25 12:18 | 140 | 001:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 1 X 40 Y 1 X 80 EN CORTES DE LINEAS REEMPLAZO AISLADOR ROTO | R22012500004 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 95 | 2022-01-25 | 13300 | keep | 0 | Jan | 2022 | 0.0090586 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-25 10:59 | 2022-01-25 11:53 | 330 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE CORTE DE LINEA PARA REEMPLAZAR POSTE PRIMARIO PARTIDO POR ACCIDENTE DE AUTO | P22012500035 | New_Event |  |  | Include | Wildlife | 54 | 2022-01-25 | 17820 | keep | 0 | Jan | 2022 | 0.012137 | 0.00022476 | Sustained | FALSE | FALSE | Not_TMED_Event | 330
PONCE | 2022-01-25 11:10 | 2022-01-25 11:40 | 7 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P22012500002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-01-25 | 210 | keep | 0 | Jan | 2022 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-25 11:27 | 2022-01-25 11:28 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 3046 | keep | 0 | Jan | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
ARECIBO | 2022-01-25 11:37 | 2022-01-25 12:56 | 15 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO MONTURA PARA REPARAR PUENTE SECUNDARIO | A22012500020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2022-01-25 | 1185 | keep | 0 | Jan | 2022 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-01-25 11:40 | 2022-01-25 11:41 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012500049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 2286 | keep | 0 | Jan | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 1093 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1093 | keep | 0 | Jan | 2022 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 1067 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1067 | keep | 0 | Jan | 2022 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 836 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 836 | keep | 0 | Jan | 2022 | 0.0005694 | 0.0005694 | Momentary | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1339 | keep | 0 | Jan | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 1295 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1295 | keep | 0 | Jan | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 978 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 978 | keep | 0 | Jan | 2022 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 1730 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 1730 | keep | 0 | Jan | 2022 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 891 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 891 | keep | 0 | Jan | 2022 | 0.00060686 | 0.00060686 | Momentary | FALSE | FALSE | Not_TMED_Event | 891
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 527 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 527 | keep | 0 | Jan | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-01-25 11:46 | 2022-01-25 11:47 | 542 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 | P22012500029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-25 | 542 | keep | 0 | Jan | 2022 | 0.00036915 | 0.00036915 | Momentary | FALSE | FALSE | Not_TMED_Event | 542
BAYAMON | 2022-01-25 11:48 | 2022-01-25 13:13 | 1085 | 001:25 | T | DESGANCHE | DISPARO Y SE SECCIONALIZO EN MACHETES FID 1001622978. 80% EN SERVICIO | S22012500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-01-25 | 92225 | keep | 0 | Jan | 2022 | 0.062814 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
PONCE | 2022-01-25 11:53 | 2022-01-25 12:13 | 158 | 000:20 | P | DESGANCHE | DISPARO INTERRUPTOR 5817-02 CON CARGA PARCIAL 48 % DE 5801-04 CRUCE DE FASE PRIMARIA POR RAMA CARGA 5817-02 POR 5817-01 | P22012500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-01-25 | 3160 | keep | 0 | Jan | 2022 | 0.0021523 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
PONCE | 2022-01-25 11:53 | 2022-01-25 12:13 | 234 | 000:20 | T | DESGANCHE | DISPARO INTERRUPTOR 5817-02 CON CARGA PARCIAL DEL 48 % 5801-04 CRUCE DE FASE PRIMARIA POR RAMA CARGA 5817-02 POR 5817-01 | P22012500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-01-25 | 4680 | keep | 0 | Jan | 2022 | 0.0031875 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2022-01-25 11:53 | 2022-01-25 12:13 | 2468 | 000:20 | T | DESGANCHE | DISPARO INTERRUPTOR 5817-02 CON CARGA PARCIAL 48 % DE 5801-04 CRUCE DE FASE PRIMARIA POR RAMA CARGA 5817-02 POR 5817-01 | P22012500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-01-25 | 49360 | keep | 0 | Jan | 2022 | 0.033619 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
UTUADO | 2022-01-25 11:59 | 2022-01-25 16:22 | 20 | 004:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CLIENTE CORTANDO ARBOL CRUZO LINEA | A22012500022 | New_Event |  |  | Include | Wildlife | 263 | 2022-01-25 | 5260 | keep | 0 | Jan | 2022 | 0.0035826 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-25 12:08 | 2022-01-25 14:48 | 1 | 002:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22012500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2022-01-25 | 160 | keep | 0 | Jan | 2022 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-25 12:13 | 2022-01-25 20:28 | 330 | 008:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE CORTE DE LINEA PARA REEMPLAZAR POSTE PRIMARIO PARTIDO POR ACCIDENTE DE AUTO | P22012500035 | Partial_restoration |  |  | Include | Wildlife | 495 | 2022-01-25 | 163350 | keep | 0 | Jan | 2022 | 0.11126 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-25 12:18 | 2022-01-25 12:26 | 2524 | 000:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL | R22012500042 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2022-01-25 | 20192 | keep | 0 | Jan | 2022 | 0.013753 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-25 12:26 | 2022-01-25 14:03 | 140 | 001:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 1 X 40 Y 1 X 80 EN CORTES DE LINEAS REEMPLAZO AISLADOR ROTO | R22012500004 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 97 | 2022-01-25 | 13580 | keep | 0 | Jan | 2022 | 0.0092493 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-25 12:35 | 2022-01-25 12:36 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 6 | keep | 0 | Jan | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-01-25 12:39 | 2022-01-25 14:59 | 20 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22012500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-01-25 | 2800 | keep | 0 | Jan | 2022 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-25 12:42 | 2022-01-25 15:17 | 15 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22012500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-01-25 | 2325 | keep | 0 | Jan | 2022 | 0.0015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-25 12:52 | 2022-01-25 12:53 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 271 | keep | 0 | Jan | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-01-25 12:53 | 2022-01-25 15:59 | 95 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER @ SU-7 CRUCE POR CULEBRA EN SU-7 | R22012500050 | New_Event |  |  | Include | Wildlife | 186 | 2022-01-25 | 17670 | keep | 0 | Jan | 2022 | 0.012035 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2022-01-25 13:13 | 2022-01-25 15:19 | 217 | 002:06 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S22012500026 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-01-25 | 27342 | keep | 0 | Jan | 2022 | 0.018623 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-25 13:35 | 2022-01-25 17:37 | 20 | 004:02 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22012500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-01-25 | 4840 | keep | 0 | Jan | 2022 | 0.0032965 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-25 13:38 | 2022-01-25 14:33 | 2560 | 000:55 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR DISPARA Y NO CIERRA CON CARGA SE RETIRO CARGA SE CERRO INTERRUPTOR | M22012500045 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 55 | 2022-01-25 | 140800 | keep | 0 | Jan | 2022 | 0.095898 | 0.0017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 2560
SAN JUAN | 2022-01-25 13:52 | 2022-01-25 19:09 | 45 | 005:17 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO SU-4E PARA REPARAR PISTOLA EN T-23 | R22012500056 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 317 | 2022-01-25 | 14265 | keep | 0 | Jan | 2022 | 0.0097158 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-01-25 13:54 | 2022-01-25 14:30 | 6 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22012500047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-01-25 | 216 | keep | 0 | Jan | 2022 | 0.00014712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-25 13:58 | 2022-01-25 13:59 | 1444 | 000:01 | T | DESGANCHE | CARGA POR 6014-02 | M22012500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-25 | 1444 | keep | 0 | Jan | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-01-25 13:58 | 2022-01-25 13:59 | 3630 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REQUIERE DESGANCHE LLEVA LA CARGA DEL 6014-01 | M22012500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-25 | 3630 | keep | 0 | Jan | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-01-25 13:59 | 2022-01-25 17:55 | 30 | 003:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS INDICO REQUIERE DESGANCHE | M22012500065 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-01-25 | 7080 | keep | 0 | Jan | 2022 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-01-25 14:08 | 2022-01-25 17:55 | 1 | 003:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22012500036 | New_Event | Bad Weather | Include | Include | Weather | 227 | 2022-01-25 | 227 | keep | 0 | Jan | 2022 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-25 14:13 | 2022-01-25 16:15 | 70 | 002:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22012500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-01-25 | 8540 | keep | 0 | Jan | 2022 | 0.0058166 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-25 14:33 | 2022-01-25 14:40 | 1500 | 000:07 | P | BREAKER DEFECTUOSO O NO OPERA | SE RESTABLECIO CARGA RETIRADA PARA CERRAR INTERRUPTOR | M22012500045 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 7 | 2022-01-25 | 10500 | keep | 0 | Jan | 2022 | 0.0071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-25 14:49 | 2022-01-26 10:54 | 1 | 020:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEA A TIERRA | M22012500063 | New_Event |  |  | Include | Wildlife | 1205 | 2022-01-25 | 1205 | keep | 0 | Jan | 2022 | 0.00082072 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-25 14:54 | 2022-01-25 17:07 | 120 | 002:13 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22012500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-01-25 | 15960 | keep | 0 | Jan | 2022 | 0.01087 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-01-25 15:26 | 2022-01-25 16:26 | 10 | 001:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA | C22012500050 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2022-01-25 | 600 | keep | 0 | Jan | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-25 16:36 | 2022-01-25 16:39 | 2466 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-25 | 7398 | keep | 0 | Jan | 2022 | 0.0050387 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
MAYAGÃœEZ | 2022-01-25 16:49 | 2022-01-25 19:42 | 25 | 002:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS INDICO REQUIERE DESGANCHE | M22012500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-25 | 4325 | keep | 0 | Jan | 2022 | 0.0029457 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-01-25 17:05 | 2022-01-25 20:36 | 15 | 003:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22012500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 211 | 2022-01-25 | 3165 | keep | 0 | Jan | 2022 | 0.0021557 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-25 17:09 | 2022-01-25 18:09 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | B22012500036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-01-25 | 600 | keep | 0 | Jan | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-25 17:19 | 2022-01-25 17:22 | 1 | 000:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA NEUTRAL | C22012500057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3 | 2022-01-25 | 3 | keep | 0 | Jan | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-25 17:19 | 2022-01-25 19:04 | 70 | 001:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22012500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-01-25 | 7350 | keep | 0 | Jan | 2022 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-25 17:30 | 2022-01-25 18:43 | 5 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22012500067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2022-01-25 | 365 | keep | 0 | Jan | 2022 | 0.0002486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-01-25 17:30 | 2022-01-25 20:30 | 50 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22012500047 | New_Event | Wire Down | Include | Include | Equipment | 180 | 2022-01-25 | 9000 | keep | 0 | Jan | 2022 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-01-25 17:45 | 2022-01-25 18:42 | 80 | 000:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22012500066 | New_Event |  |  | Include | Wildlife | 57 | 2022-01-25 | 4560 | keep | 0 | Jan | 2022 | 0.0031058 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-25 18:18 | 2022-01-26 18:45 | 80 | 024:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO QUEMANDOSE | A22012500049 | New_Event | Wire Down | Include | Include | Equipment | 1467 | 2022-01-25 | 117360 | keep | 0 | Jan | 2022 | 0.079933 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-25 18:35 | 2022-01-25 19:20 | 15 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22012500040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-01-25 | 675 | keep | 0 | Jan | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-01-25 18:53 | 2022-01-25 21:36 | 100 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | P22012500065 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2022-01-25 | 16300 | keep | 0 | Jan | 2022 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-01-25 18:54 | 2022-01-26 09:29 | 10 | 014:35 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR | C22012500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 875 | 2022-01-25 | 8750 | keep | 0 | Jan | 2022 | 0.0059596 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-25 18:55 | 2022-01-26 09:26 | 3 | 014:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C22012500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 871 | 2022-01-25 | 2613 | keep | 0 | Jan | 2022 | 0.0017797 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-01-25 19:05 | 2022-01-26 10:25 | 5 | 015:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | C22012500063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 920 | 2022-01-25 | 4600 | keep | 0 | Jan | 2022 | 0.003133 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-01-25 19:55 | 2022-01-25 19:56 | 2308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220125000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 2308 | keep | 0 | Jan | 2022 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
PONCE | 2022-01-25 20:06 | 2022-01-26 05:38 | 300 | 009:32 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE FIJO BAJANTE PRIMARIO A MACHETE | P22012500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 572 | 2022-01-25 | 171600 | keep | 0 | Jan | 2022 | 0.11688 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-01-25 20:23 | 2022-01-25 20:24 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6014-02 | M22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 1444 | keep | 0 | Jan | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-01-25 20:23 | 2022-01-25 20:24 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-01 | M22012500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-25 | 3630 | keep | 0 | Jan | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2022-01-25 20:33 | 2022-01-25 22:48 | 100 | 002:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | B22012500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-01-25 | 13500 | keep | 0 | Jan | 2022 | 0.0091948 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-26 01:12 | 2022-01-26 09:29 | 3 | 008:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C22012600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2022-01-26 | 1491 | keep | 0 | Jan | 2022 | 0.0010155 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-01-26 01:13 | 2022-01-26 09:45 | 70 | 008:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22012600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 512 | 2022-01-26 | 35840 | keep | 0 | Jan | 2022 | 0.02441 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-01-26 01:49 | 2022-01-26 09:57 | 60 | 008:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22012600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2022-01-26 | 29280 | keep | 0 | Jan | 2022 | 0.019942 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-26 02:49 | 2022-01-26 09:21 | 80 | 006:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INDICA FOREMAN REQUIERE DESGANCHE | M22012600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-01-26 | 31360 | keep | 0 | Jan | 2022 | 0.021359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-26 03:05 | 2022-01-26 05:18 | 4 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22012600002 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2022-01-26 | 532 | keep | 0 | Jan | 2022 | 0.00036234 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-01-26 03:56 | 2022-01-26 03:57 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22012600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-26 | 2113 | keep | 0 | Jan | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2022-01-26 05:41 | 2022-01-26 19:12 | 74 | 013:31 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO DE RISER @ T-4 | S22012600035 | New_Event | UG Cable Fault | Include | Include | Equipment | 811 | 2022-01-26 | 60014 | keep | 0 | Jan | 2022 | 0.040875 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
GUAYAMA | 2022-01-26 06:56 | 2022-01-26 13:15 | 1 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22012600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2022-01-26 | 379 | keep | 0 | Jan | 2022 | 0.00025814 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-26 07:07 | 2022-01-26 07:08 | 1548 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-26 | 1548 | keep | 0 | Jan | 2022 | 0.0010543 | 0.0010543 | Momentary | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-01-26 07:07 | 2022-01-26 07:08 | 274 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-26 | 274 | keep | 0 | Jan | 2022 | 0.00018662 | 0.00018662 | Momentary | FALSE | FALSE | Not_TMED_Event | 274
ARECIBO | 2022-01-26 07:07 | 2022-01-26 07:08 | 185 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-26 | 185 | keep | 0 | Jan | 2022 | 0.000126 | 0.000126 | Momentary | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-01-26 07:07 | 2022-01-26 07:08 | 9 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-26 | 9 | keep | 0 | Jan | 2022 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-01-26 07:07 | 2022-01-26 07:08 | 385 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-26 | 385 | keep | 0 | Jan | 2022 | 0.00026222 | 0.00026222 | Momentary | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2022-01-26 07:07 | 2022-01-26 07:08 | 264 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-26 | 264 | keep | 0 | Jan | 2022 | 0.00017981 | 0.00017981 | Momentary | FALSE | FALSE | Not_TMED_Event | 264
ARECIBO | 2022-01-26 07:07 | 2022-01-26 09:36 | 316 | 002:29 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT SE RECARGO DE SF6 EL INTERRUPTOR 0050 DE LA SUBESTACION 8015 Y SE CERRO | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 149 | 2022-01-26 | 47084 | keep | 0 | Jan | 2022 | 0.032069 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-01-26 07:07 | 2022-01-26 09:36 | 1227 | 002:29 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT SE RECARGO DE SF6 EL INTERRUPTOR 0050 DE LA SUBESTACION 8015 Y SE CERRO | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 149 | 2022-01-26 | 182823 | keep | 0 | Jan | 2022 | 0.12452 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-01-26 07:07 | 2022-01-26 09:36 | 3431 | 002:29 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA ARECIBO SECT SE RECARGO DE SF6 EL INTERRUPTOR 0050 DE LA SUBESTACION 8015 Y SE CERRO | A22012600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 149 | 2022-01-26 | 511219 | keep | 0 | Jan | 2022 | 0.34819 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
CANOVANAS | 2022-01-26 07:34 | 2022-01-26 09:49 | 80 | 002:15 | P | DESGANCHE | 1 X 100 EN C/L Y 2 X 40 EN C/L. HAY QUE REALIZAR DESGANCHE | R22012600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-01-26 | 10800 | keep | 0 | Jan | 2022 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-26 07:43 | 2022-01-26 07:44 | 3115 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 QUE A SU VEZ LLEVA EL 40% DEL 1710-05 | B22012600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-26 | 3115 | keep | 0 | Jan | 2022 | 0.0021216 | 0.0021216 | Momentary | FALSE | FALSE | Not_TMED_Event | 3115
BAYAMON | 2022-01-26 07:43 | 2022-01-26 07:44 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1718-03 QUE A SU VEZ LLEVA EL 40% DEL 1710-05 | B22012600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-26 | 2605 | keep | 0 | Jan | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-01-26 08:16 | 2022-01-26 10:01 | 100 | 001:45 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA Y SE ELIMO PARARRAYO | B22012600002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 105 | 2022-01-26 | 10500 | keep | 0 | Jan | 2022 | 0.0071515 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-26 08:17 | 2022-01-26 11:24 | 10 | 003:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE XMR NO FUNDIO FUSIBLE | R22012600009 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2022-01-26 | 1870 | keep | 0 | Jan | 2022 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-26 08:39 | 2022-01-26 12:25 | 3597 | 003:46 | T | BREAKER DEFECTUOSO O NO OPERA | BOBINA DE INTERRUPTOR QUEMADA SE TRANSFIRIO CARGA AL 1719-16 | B22012600010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 226 | 2022-01-26 | 812922 | keep | 0 | Jan | 2022 | 0.55368 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-01-26 08:39 | 2022-01-26 12:25 | 877 | 003:46 | P | BREAKER DEFECTUOSO O NO OPERA | 25% DE LA CARGA POR EL 1719-15 | B22012600010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 226 | 2022-01-26 | 198202 | keep | 0 | Jan | 2022 | 0.13499 | 0.00059732 | Sustained | FALSE | FALSE | Not_TMED_Event | 877
CAGUAS | 2022-01-26 09:00 | 2022-01-26 11:09 | 4 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C22012600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-01-26 | 516 | keep | 0 | Jan | 2022 | 0.00035145 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-01-26 09:04 | 2022-01-26 22:22 | 50 | 013:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22012600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 798 | 2022-01-26 | 39900 | keep | 0 | Jan | 2022 | 0.027176 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-26 09:34 | 2022-01-26 11:38 | 15 | 002:04 | P | TRANSFORMADOR AVERIADO | SE CAMBIA TRANSFORMADOR DE 75 KVA A 2.4 KV POR UNO DE LA MISMA CAPACIDAD | P22012600022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 124 | 2022-01-26 | 1860 | keep | 0 | Jan | 2022 | 0.0012668 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-26 09:35 | 2022-01-26 14:51 | 10 | 005:16 | P | TRANSFORMADOR AVERIADO | 1X15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 25KVA | C22012600011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 316 | 2022-01-26 | 3160 | keep | 0 | Jan | 2022 | 0.0021523 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-26 09:39 | 2022-01-26 10:06 | 30 | 000:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22012600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2022-01-26 | 810 | keep | 0 | Jan | 2022 | 0.00055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-26 09:41 | 2022-01-26 11:13 | 40 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | A22012600074 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2022-01-26 | 3680 | keep | 0 | Jan | 2022 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-01-26 09:48 | 2022-01-26 15:24 | 8 | 005:36 | P | ESTRUCTURA AVERIADA | SE ABRIO C/L PARA REMPLAZO DE POSTE PARTIDO | C22012600012 | New_Event | Defective Pole | Include | Include | Equipment | 336 | 2022-01-26 | 2688 | keep | 0 | Jan | 2022 | 0.0018308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-26 10:30 | 2022-01-26 13:30 | 14 | 003:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | A22012600085 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 180 | 2022-01-26 | 2520 | keep | 0 | Jan | 2022 | 0.0017164 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-01-26 10:44 | 2022-01-26 10:45 | 2402 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | B22012600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-26 | 2402 | keep | 0 | Jan | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-01-26 10:45 | 2022-01-26 16:11 | 25 | 005:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B22012600183 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 326 | 2022-01-26 | 8150 | keep | 0 | Jan | 2022 | 0.0055509 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-01-26 10:47 | 2022-01-26 10:48 | 1818 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR LINEA PRIMARIA PARTIDA | M22012600031 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-26 | 1818 | keep | 0 | Jan | 2022 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
MAYAGÃœEZ | 2022-01-26 10:48 | 2022-01-26 12:25 | 400 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO MACHETES PARA REPARAR | M22012600033 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 97 | 2022-01-26 | 38800 | keep | 0 | Jan | 2022 | 0.026427 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
YAUCO | 2022-01-26 11:44 | 2022-01-26 13:55 | 1 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 3 CAJAS PRIMARIAS | P22012600056 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-01-26 | 131 | keep | 0 | Jan | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-26 12:11 | 2022-01-26 16:00 | 8 | 003:49 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S22012600034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 229 | 2022-01-26 | 1832 | keep | 0 | Jan | 2022 | 0.0012478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-01-26 12:14 | 2022-01-26 13:34 | 10 | 001:20 | P | NO SE REPORTO CAUSA | SE CERRO FUSIBLE DE TRANSFORMADOR NO FUNDIO | C22012600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2022-01-26 | 800 | keep | 0 | Jan | 2022 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-26 12:16 | 2022-01-26 15:46 | 20 | 003:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE CERRO PUENTE | S22012600037 | New_Event | Wire Down | Include | Include | Equipment | 210 | 2022-01-26 | 4200 | keep | 0 | Jan | 2022 | 0.0028606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-26 12:25 | 2022-01-26 15:56 | 15 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22012600217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-01-26 | 3165 | keep | 0 | Jan | 2022 | 0.0021557 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-26 12:25 | 2022-01-26 14:27 | 1200 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO MACHETES | M22012600059 | Additional_clients | Wire Down | Include | Include | Equipment | 122 | 2022-01-26 | 146400 | keep | 0 | Jan | 2022 | 0.099712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-26 12:36 | 2022-01-26 13:43 | 2 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR CON CONECTOR AVERIADO | M22012600044 | New_Event | Wire Down | Include | Include | Equipment | 67 | 2022-01-26 | 134 | keep | 0 | Jan | 2022 | 9.1267e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-01-26 12:37 | 2022-01-26 12:38 | 2141 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22012600026 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-26 | 2141 | keep | 0 | Jan | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
BAYAMON | 2022-01-26 12:38 | 2022-01-26 13:16 | 50 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22012600209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2022-01-26 | 1900 | keep | 0 | Jan | 2022 | 0.0012941 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-26 12:38 | 2022-01-26 15:14 | 100 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X200 EN CORTE DE LINEA CRUCE X AVE | C22012600034 | 1st_after_momentary |  |  | Include | Wildlife | 156 | 2022-01-26 | 15600 | keep | 0 | Jan | 2022 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-26 12:40 | 2022-01-26 16:44 | 40 | 004:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22012600030 | New_Event |  |  | Include | Wildlife | 244 | 2022-01-26 | 9760 | keep | 0 | Jan | 2022 | 0.0066475 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-26 12:44 | 2022-01-26 14:46 | 1 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 @ SU-1A | S22012600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-01-26 | 122 | keep | 0 | Jan | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-26 12:53 | 2022-01-26 14:58 | 60 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR GLOBO | R22012600031 | New_Event |  |  | Include | Wildlife | 125 | 2022-01-26 | 7500 | keep | 0 | Jan | 2022 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-26 13:01 | 2022-01-26 16:29 | 1 | 003:28 | P | NO SE REPORTO CAUSA | 2 X 20 EN MONTURA AAA NO SE REPORTO CAUSA | P22012600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-01-26 | 208 | keep | 0 | Jan | 2022 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-26 13:02 | 2022-01-26 22:34 | 6 | 009:32 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | C22012600035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 572 | 2022-01-26 | 3432 | keep | 0 | Jan | 2022 | 0.0023375 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-26 13:20 | 2022-01-26 17:40 | 70 | 004:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN SWITCHING UNIT ROEDOR CRUZO LINEAS | A22012600106 | New_Event |  |  | Include | Wildlife | 260 | 2022-01-26 | 18200 | keep | 0 | Jan | 2022 | 0.012396 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-26 13:23 | 2022-01-26 16:50 | 70 | 003:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | M22012600054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-01-26 | 14490 | keep | 0 | Jan | 2022 | 0.0098691 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-01-26 13:23 | 2022-01-26 16:40 | 1 | 003:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE MONTURA DE TRANSFORMADORES | A22012600108 | New_Event | Wire Down | Include | Include | Equipment | 197 | 2022-01-26 | 197 | keep | 0 | Jan | 2022 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-26 13:32 | 2022-01-26 18:00 | 35 | 004:28 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22012600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-01-26 | 9380 | keep | 0 | Jan | 2022 | 0.0063887 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-01-26 13:44 | 2022-01-26 19:28 | 50 | 005:44 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 40 EN C/L REMPLAZO POSTE SECUNDARIO | C22012600040 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 344 | 2022-01-26 | 17200 | keep | 0 | Jan | 2022 | 0.011715 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-26 14:02 | 2022-01-26 15:13 | 20 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22012600223 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-01-26 | 1420 | keep | 0 | Jan | 2022 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-01-26 14:21 | 2022-01-26 19:10 | 50 | 004:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22012600117 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 289 | 2022-01-26 | 14450 | keep | 0 | Jan | 2022 | 0.0098418 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-26 14:35 | 2022-01-26 16:07 | 2560 | 001:32 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO LINEAS CRUZADAS POR TENSOR PARTIDO POR MAQUINA Y SE CERRO EL INTERRUPTOR | M22012600075 | New_Event |  |  | Include | Wildlife | 92 | 2022-01-26 | 235520 | keep | 0 | Jan | 2022 | 0.16041 | 0.0017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 2560
HUMACAO | 2022-01-26 14:52 | 2022-01-26 19:25 | 9 | 004:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA | C22012600047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 273 | 2022-01-26 | 2457 | keep | 0 | Jan | 2022 | 0.0016735 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-01-26 15:13 | 2022-01-26 17:46 | 50 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B22012600230 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-01-26 | 7650 | keep | 0 | Jan | 2022 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-26 15:16 | 2022-01-26 16:34 | 10 | 001:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA EN TANSFORMADOR | P22012600076 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2022-01-26 | 780 | keep | 0 | Jan | 2022 | 0.00053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-26 15:30 | 2022-01-26 17:00 | 25 | 001:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA PRIMARIA | B22012600232 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2022-01-26 | 2250 | keep | 0 | Jan | 2022 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-26 15:50 | 2022-01-26 16:10 | 25 | 000:20 | P | NO SE REPORTO CAUSA | 1X50 EN CORTE DE LINEA NO CAUSA | C22012600052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-01-26 | 500 | keep | 0 | Jan | 2022 | 0.00034055 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-01-26 16:07 | 2022-01-26 20:53 | 530 | 004:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | MAQUINA PARTIO TENSOR DE 38 KV Y CRUZO ALIMENTADOR 6401-04 SE CORRIGIO CONDICION Y SE CERRO MACHETES | M22012600089 | Partial_restoration |  |  | Include | Wildlife | 286 | 2022-01-26 | 151580 | keep | 0 | Jan | 2022 | 0.10324 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-26 16:11 | 2022-01-26 17:31 | 15 | 001:20 | P | DESGANCHE | SE RETEZO SECUNDARIA Y SE REALIZO DESGANCHE | B22012600224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-01-26 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-26 16:31 | 2022-01-26 20:19 | 20 | 003:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE REMPLAZO CAJA PRIMARIA | S22012600056 | New_Event | Wire Down | Include | Include | Equipment | 228 | 2022-01-26 | 4560 | keep | 0 | Jan | 2022 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-01-26 16:56 | 2022-01-27 12:41 | 100 | 019:45 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22012700058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1185 | 2022-01-26 | 118500 | keep | 0 | Jan | 2022 | 0.08071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-26 17:06 | 2022-01-26 20:38 | 40 | 003:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR QUEMADO | A22012600143 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 212 | 2022-01-26 | 8480 | keep | 0 | Jan | 2022 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-01-26 17:15 | 2022-01-26 19:29 | 100 | 002:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L REMPLAZO CAJA QUEMADA | C22012600060 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2022-01-26 | 13400 | keep | 0 | Jan | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-26 17:28 | 2022-01-26 20:56 | 60 | 003:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22012600129 | New_Event | Wire Down | Include | Include | Equipment | 208 | 2022-01-26 | 12480 | keep | 0 | Jan | 2022 | 0.0085001 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-26 18:03 | 2022-01-27 11:45 | 60 | 017:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22012600133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1062 | 2022-01-26 | 63720 | keep | 0 | Jan | 2022 | 0.043399 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-26 18:30 | 2022-01-26 21:28 | 30 | 002:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22012600135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-01-26 | 5340 | keep | 0 | Jan | 2022 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-26 18:35 | 2022-01-26 20:50 | 2 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA | A22012600136 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2022-01-26 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-26 18:40 | 2022-01-26 20:59 | 65 | 002:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA Y REALIZO DESGANCHE | R22012600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-01-26 | 9035 | keep | 0 | Jan | 2022 | 0.0061537 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-01-26 19:12 | 2022-01-26 20:44 | 20 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR IGUANA | R22012600044 | New_Event |  |  | Include | Wildlife | 92 | 2022-01-26 | 1840 | keep | 0 | Jan | 2022 | 0.0012532 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-26 19:25 | 2022-01-26 19:29 | 1825 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE RIO CAÃ‘AS A LA MUDA | S22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 7300 | keep | 0 | Jan | 2022 | 0.004972 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-01-26 19:25 | 2022-01-26 19:29 | 47 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE RIO CAÃ‘AS A LA MUDA | S22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 188 | keep | 0 | Jan | 2022 | 0.00012805 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-01-26 19:25 | 2022-01-26 19:29 | 315 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE RIO CAÃ‘AS A LA MUDA | S22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 1260 | keep | 0 | Jan | 2022 | 0.00085818 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-01-26 19:25 | 2022-01-26 19:29 | 2 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE RIO CAÃ‘AS A LA MUDA | S22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 8 | keep | 0 | Jan | 2022 | 5.4488e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-26 19:25 | 2022-01-26 19:29 | 2391 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE RIO CAÃ‘AS A LA MUDA | S22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 9564 | keep | 0 | Jan | 2022 | 0.006514 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2022-01-26 19:25 | 2022-01-26 19:29 | 300 | 000:04 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CARGA DE CONVERTIDOR DE 1908-03 POR 1343-03 MAMEY Y 1343-05 LINDA GARDENS RESPECTIVAMENTE | S22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-01-26 19:25 | 2022-01-26 19:29 | 2276 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 9104 | keep | 0 | Jan | 2022 | 0.0062007 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-01-26 19:25 | 2022-01-26 19:29 | 777 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 3108 | keep | 0 | Jan | 2022 | 0.0021168 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-01-26 19:25 | 2022-01-26 19:29 | 12 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 48 | keep | 0 | Jan | 2022 | 3.2693e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-26 19:25 | 2022-01-26 19:29 | 1290 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22012600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-26 | 5160 | keep | 0 | Jan | 2022 | 0.0035145 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
GUAYAMA | 2022-01-26 19:43 | 2022-01-26 20:47 | 10 | 001:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | P22012600084 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2022-01-26 | 640 | keep | 0 | Jan | 2022 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-26 19:48 | 2022-01-26 21:49 | 100 | 002:01 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE | P22012600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-01-26 | 12100 | keep | 0 | Jan | 2022 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-26 20:52 | 2022-01-27 13:32 | 150 | 016:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | M22012600131 | New_Event | Wire Down | Include | Include | Equipment | 1000 | 2022-01-26 | 150000 | keep | 0 | Jan | 2022 | 0.10216 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-01-26 20:56 | 2022-01-26 20:57 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-26 | 3699 | keep | 0 | Jan | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
MAYAGÃœEZ | 2022-01-26 23:05 | 2022-01-26 23:44 | 1 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO FASE A TIERRA | M22012600140 | New_Event |  |  | Include | Wildlife | 39 | 2022-01-26 | 39 | keep | 0 | Jan | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-27 02:07 | 2022-01-27 02:08 | 2402 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | B22012700004 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-27 | 2402 | keep | 0 | Jan | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-01-27 02:08 | 2022-01-27 04:25 | 180 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 140 Y 1 X 80 EN C/L AVERIA CAUSADA POR AVE | B22012700004 | 1st_after_momentary |  |  | Include | Wildlife | 137 | 2022-01-27 | 24660 | keep | 0 | Jan | 2022 | 0.016796 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CAGUAS | 2022-01-27 02:39 | 2022-01-27 11:57 | 200 | 009:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22012700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 558 | 2022-01-27 | 111600 | keep | 0 | Jan | 2022 | 0.07601 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-01-27 03:10 | 2022-01-27 04:23 | 5290 | 001:13 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR. SE SECCIONALIZO AVERIA AISLADOR PARTIDO Y SE CERRO POR SCADA | S22012700038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2022-01-27 | 386170 | keep | 0 | Jan | 2022 | 0.26302 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-27 04:18 | 2022-01-27 04:19 | 3718 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22012700000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-27 | 3718 | keep | 0 | Jan | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-01-27 04:23 | 2022-01-27 05:17 | 1058 | 000:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE NORMALIZO CARGA | S22012700038 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 54 | 2022-01-27 | 57132 | keep | 0 | Jan | 2022 | 0.038912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-27 04:54 | 2022-01-27 04:55 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 1526 | keep | 0 | Jan | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-01-27 04:55 | 2022-01-27 11:40 | 50 | 006:45 | P | NO SE REPORTO CAUSA | 1X100 EN CORTE DE LINEA | B22012700018 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 405 | 2022-01-27 | 20250 | keep | 0 | Jan | 2022 | 0.013792 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-27 07:23 | 2022-01-27 07:25 | 600 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE LA CARGA 1206-03 | S22012700142 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-01-27 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-01-27 07:23 | 2022-01-27 07:25 | 3718 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE LA CARGA 1206-03 | S22012700142 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-01-27 | 7436 | keep | 0 | Jan | 2022 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-01-27 07:24 | 2022-01-27 11:00 | 46 | 003:36 | P | DESGANCHE | 1 X 40 EN C/L | R22012700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-01-27 | 9936 | keep | 0 | Jan | 2022 | 0.0067674 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BARRANQUITAS | 2022-01-27 07:25 | 2022-01-27 09:05 | 4 | 001:40 | P | DESGANCHE | 1 X 8 EN CORTE DE LINEA | C22012700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-01-27 | 400 | keep | 0 | Jan | 2022 | 0.00027244 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-27 07:32 | 2022-01-27 12:39 | 430 | 005:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1404-09 SE CERRO POR SCADA LLEVANDO 90% DEL 1420-05 POR GLOBOS METALICOS EN LA LINEA | S22012700000 | New_Event |  |  | Include | Wildlife | 307 | 2022-01-27 | 132010 | keep | 0 | Jan | 2022 | 0.089911 | 0.00029287 | Sustained | FALSE | FALSE | Not_TMED_Event | 430
SAN JUAN | 2022-01-27 07:32 | 2022-01-27 12:39 | 4 | 005:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1404-09 SE CERRO POR SCADA LLEVANDO 90% DEL 1420-05 POR GLOBOS METALICOS EN LA LINEA | S22012700000 | New_Event |  |  | Include | Wildlife | 307 | 2022-01-27 | 1228 | keep | 0 | Jan | 2022 | 0.00083639 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 09:17 | 450 | 001:44 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE TRANSFIRIO SUBESTACION A LINEA 1000 1437-04 LLEVA 60% 1301-02 | S22012700174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-01-27 | 46800 | keep | 0 | Jan | 2022 | 0.031875 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 12:00 | 849 | 004:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 267 | 2022-01-27 | 226683 | keep | 0 | Jan | 2022 | 0.15439 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 13:32 | 893 | 005:59 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE HABIA DEJADO FUERA A CAUSA DE CRUCE DE LINEA POR ANDAMIO DE CONTRATISTA LLEVA UN 10% DEL 1422-02 | S22012700195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 359 | 2022-01-27 | 320587 | keep | 0 | Jan | 2022 | 0.21835 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 12:00 | 602 | 004:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 267 | 2022-01-27 | 160734 | keep | 0 | Jan | 2022 | 0.10948 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 12:00 | 43 | 004:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 267 | 2022-01-27 | 11481 | keep | 0 | Jan | 2022 | 0.0078197 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 12:00 | 1389 | 004:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 267 | 2022-01-27 | 370863 | keep | 0 | Jan | 2022 | 0.25259 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 13:32 | 68 | 005:59 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 10% DE LA CARGA POR EL 1418-02 | S22012700195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 359 | 2022-01-27 | 24412 | keep | 0 | Jan | 2022 | 0.016627 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 09:17 | 601 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE TRANSFIRIO SUBESTACION A LINEA 1000 | S22012700174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-01-27 | 62504 | keep | 0 | Jan | 2022 | 0.042571 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 09:17 | 640 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE TRANSFIRIO SUBESTACION A LINEA 1000 | S22012700174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-01-27 | 66560 | keep | 0 | Jan | 2022 | 0.045334 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 09:17 | 1699 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE TRANSFIRIO SUBESTACION A LINEA 1000 | S22012700174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-01-27 | 176696 | keep | 0 | Jan | 2022 | 0.12035 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 09:17 | 892 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE TRANSFIRIO SUBESTACION A LINEA 1000 1437-04 LLEVA 60% 1301-02 | S22012700174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-01-27 | 92768 | keep | 0 | Jan | 2022 | 0.063184 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-01-27 07:33 | 2022-01-27 09:17 | 1066 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 SE TRANSFIRIO SUBESTACION A LINEA 1000 | S22012700174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-01-27 | 110864 | keep | 0 | Jan | 2022 | 0.075509 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 08:58 | 1000 | 001:24 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 1424-08 LLEVA 100% CARGA 1348-07 80 % 1348-06 | S22012700197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-27 | 84000 | keep | 0 | Jan | 2022 | 0.057212 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 08:58 | 278 | 001:24 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 1424-08 LLEVA 100% CARGA 1348-07 80 % 1348-06 | S22012700197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-27 | 23352 | keep | 0 | Jan | 2022 | 0.015905 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 605 | 006:23 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 90% DE LA CARGA POR EL 1423-04 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 231715 | keep | 0 | Jan | 2022 | 0.15782 | 0.00041206 | Sustained | FALSE | FALSE | Not_TMED_Event | 605
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 372 | 006:23 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 CARGA POR EL 1423-04 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 142476 | keep | 0 | Jan | 2022 | 0.09704 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 732 | 006:23 | T | LINEA DE TRANSMISION 38KV | DISSPARO DE LINEA 3200 CARGA POR EL 1423-04 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 280356 | keep | 0 | Jan | 2022 | 0.19095 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 721 | 006:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 276143 | keep | 0 | Jan | 2022 | 0.18808 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 325 | 006:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 124475 | keep | 0 | Jan | 2022 | 0.084779 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 600 | 006:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 229800 | keep | 0 | Jan | 2022 | 0.15652 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 267 | 006:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 LLEVA LA CARGA DEL 1422-04 Y 1422-03 Y 90% DEL 1422-02 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 102261 | keep | 0 | Jan | 2022 | 0.06965 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 13:57 | 621 | 006:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 383 | 2022-01-27 | 237843 | keep | 0 | Jan | 2022 | 0.16199 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 08:58 | 2203 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-27 | 185052 | keep | 0 | Jan | 2022 | 0.12604 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 08:58 | 246 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-27 | 20664 | keep | 0 | Jan | 2022 | 0.014074 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2022-01-27 07:34 | 2022-01-27 08:58 | 9 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 1424-08 LLEVA 100% CARGA 1348-07 80 % 1348-06 | S22012700197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-27 | 756 | keep | 0 | Jan | 2022 | 0.00051491 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-27 07:38 | 2022-01-27 12:36 | 1 | 004:58 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REQUIERE DESGANCHE | M22012700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-01-27 | 298 | keep | 0 | Jan | 2022 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-27 07:46 | 2022-01-27 07:47 | 600 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE LA CARGA 1206-03 | S22012700175 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-27 | 600 | keep | 0 | Jan | 2022 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-01-27 07:46 | 2022-01-27 07:47 | 3718 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE LA CARGA 1206-03 | S22012700175 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-27 | 3718 | keep | 0 | Jan | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2022-01-27 07:48 | 2022-01-27 09:10 | 60 | 001:22 | P | DESGANCHE | 3 X 65 EN C/L | R22012700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-01-27 | 4920 | keep | 0 | Jan | 2022 | 0.003351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-27 07:58 | 2022-01-27 07:59 | 2201 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A22012700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-27 | 2201 | keep | 0 | Jan | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-01-27 07:58 | 2022-01-27 07:59 | 1986 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A22012700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-27 | 1986 | keep | 0 | Jan | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-01-27 07:58 | 2022-01-27 07:59 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A22012700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-27 | 199 | keep | 0 | Jan | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2022-01-27 07:58 | 2022-01-27 07:59 | 24 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A22012700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-27 | 24 | keep | 0 | Jan | 2022 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2022-01-27 08:02 | 2022-01-27 11:38 | 20 | 003:36 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | B22012700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2022-01-27 | 4320 | keep | 0 | Jan | 2022 | 0.0029423 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-27 08:09 | 2022-01-27 08:11 | 600 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE LA CARGA 1206-03 | S22012700229 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-01-27 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-01-27 08:09 | 2022-01-27 08:11 | 3718 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE LA CARGA 1206-03 | S22012700229 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-01-27 | 7436 | keep | 0 | Jan | 2022 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-01-27 08:16 | 2022-01-27 09:58 | 3718 | 001:42 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE 1206-03 SE CERRO POR SCADA ABRIENDO MACHETES N/O | S22012700241 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 102 | 2022-01-27 | 379236 | keep | 0 | Jan | 2022 | 0.2583 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2022-01-27 08:27 | 2022-01-27 09:53 | 25 | 001:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-01-27 | 2150 | keep | 0 | Jan | 2022 | 0.0014644 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-01-27 08:31 | 2022-01-27 10:54 | 6 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22012700008 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2022-01-27 | 858 | keep | 0 | Jan | 2022 | 0.00058438 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-27 08:33 | 2022-01-27 12:05 | 48 | 003:32 | P | NO SE REPORTO CAUSA | 1X65 EN CORTE DE LINEA PRINCIPAL Y 1X30 EN OTRO CORTE DE LINEA | B22012700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2022-01-27 | 10176 | keep | 0 | Jan | 2022 | 0.0069308 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CANOVANAS | 2022-01-27 08:36 | 2022-01-27 12:25 | 1 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | R22012700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-01-27 | 229 | keep | 0 | Jan | 2022 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-27 08:40 | 2022-01-27 08:41 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22012700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 1192 | keep | 0 | Jan | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CAGUAS | 2022-01-27 09:01 | 2022-01-27 09:48 | 39 | 000:47 | P | DESGANCHE | 1 X 10 Y 1 X 20 EN TRANSFORMADORES | C22012700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-01-27 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2022-01-27 09:01 | 2022-01-27 12:14 | 2 | 003:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | C22012700017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 193 | 2022-01-27 | 386 | keep | 0 | Jan | 2022 | 0.0002629 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-27 09:02 | 2022-01-27 13:00 | 1000 | 003:58 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 ALIMENTADOR 1424-08 LLEVA CARGA 100% 1348-07 Y 80% 1348-06 | S22012700197 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 238 | 2022-01-27 | 238000 | keep | 0 | Jan | 2022 | 0.1621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-27 09:02 | 2022-01-27 13:00 | 278 | 003:58 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 ALIMENTADOR 1424-08 LLEVA CARGA 100% 1348-07 Y 80% 1348-06 | S22012700197 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 238 | 2022-01-27 | 66164 | keep | 0 | Jan | 2022 | 0.045064 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-27 09:02 | 2022-01-27 13:00 | 2203 | 003:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700197 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 238 | 2022-01-27 | 524314 | keep | 0 | Jan | 2022 | 0.35711 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-27 09:02 | 2022-01-27 13:00 | 246 | 003:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700197 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 238 | 2022-01-27 | 58548 | keep | 0 | Jan | 2022 | 0.039877 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-27 09:02 | 2022-01-27 13:00 | 9 | 003:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22012700197 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 238 | 2022-01-27 | 2142 | keep | 0 | Jan | 2022 | 0.0014589 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-27 09:20 | 2022-01-27 10:05 | 10 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012600146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-01-27 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-27 09:34 | 2022-01-27 14:25 | 120 | 004:51 | P | NO SE REPORTO CAUSA | 3X80 EN CORTE DE LINEA | B22012700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2022-01-27 | 34920 | keep | 0 | Jan | 2022 | 0.023784 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2022-01-27 09:39 | 2022-01-27 09:40 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 1310 | keep | 0 | Jan | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-01-27 09:43 | 2022-01-27 12:47 | 1 | 003:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | B22012700018 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2022-01-27 | 184 | keep | 0 | Jan | 2022 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-27 09:52 | 2022-01-27 14:30 | 15 | 004:38 | P | ESTRUCTURA AVERIADA | SE REMPLAZARON DOS POSTES Y UN XMR. SIN ORDENES DE TRABAJO. SE REALIZO INFORME DE INCIDENTE | B22012700020 | New_Event | Defective Pole | Include | Include | Equipment | 278 | 2022-01-27 | 4170 | keep | 0 | Jan | 2022 | 0.0028402 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-27 09:58 | 2022-01-27 10:58 | 600 | 001:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO MACHETES N/O SE REMPLAZO AISLADOR PARTIDO | S22012700241 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-01-27 | 36000 | keep | 0 | Jan | 2022 | 0.024519 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
HUMACAO | 2022-01-27 09:59 | 2022-01-27 11:22 | 3 | 001:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22012700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-01-27 | 249 | keep | 0 | Jan | 2022 | 0.00016959 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-01-27 10:15 | 2022-01-27 16:33 | 1 | 006:18 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | A22012700008 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 378 | 2022-01-27 | 378 | keep | 0 | Jan | 2022 | 0.00025745 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-27 10:22 | 2022-01-27 17:29 | 12 | 007:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR | M22012700024 | New_Event | Cutout Failure | Include | Include | Equipment | 427 | 2022-01-27 | 5124 | keep | 0 | Jan | 2022 | 0.0034899 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-27 10:29 | 2022-01-27 11:47 | 40 | 001:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-01-27 | 3120 | keep | 0 | Jan | 2022 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-27 10:43 | 2022-01-27 22:00 | 24 | 011:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO 4 POSTES PARTIDOS IMPACTADOS POR DIGGER | R22012700034 | New_Event |  |  | Include | Wildlife | 677 | 2022-01-27 | 16248 | keep | 0 | Jan | 2022 | 0.011066 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2022-01-27 11:05 | 2022-01-27 13:15 | 1 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2X30 EN CORTE DE LINEA CRUCE POR AVE | B22012700030 | New_Event |  |  | Include | Wildlife | 130 | 2022-01-27 | 130 | keep | 0 | Jan | 2022 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-27 11:24 | 2022-01-27 11:25 | 2873 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 2873 | keep | 0 | Jan | 2022 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
BAYAMON | 2022-01-27 11:43 | 2022-01-27 13:38 | 25 | 001:55 | P | NO SE REPORTO CAUSA | 2X50 EN CORTE DE LINEA | B22012700038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-01-27 | 2875 | keep | 0 | Jan | 2022 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-27 11:49 | 2022-01-27 17:30 | 43 | 005:41 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING EN PM | S22012700395 | New_Event | Service Transformer Failure | Include | Include | Equipment | 341 | 2022-01-27 | 14663 | keep | 0 | Jan | 2022 | 0.0099869 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2022-01-27 12:05 | 2022-01-27 12:06 | 4634 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C22012700033 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-27 | 4634 | keep | 0 | Jan | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-01-27 12:06 | 2022-01-27 18:07 | 1500 | 006:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE REPARO PUENTE ABIERTO Y PEGADO A POSTE DE METAL | C22012700114 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 361 | 2022-01-27 | 541500 | keep | 0 | Jan | 2022 | 0.36881 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2022-01-27 12:22 | 2022-01-27 12:23 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 215 | keep | 0 | Jan | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-01-27 12:23 | 2022-01-27 17:37 | 30 | 005:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22012700046 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 314 | 2022-01-27 | 9420 | keep | 0 | Jan | 2022 | 0.0064159 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-27 12:25 | 2022-01-27 12:51 | 6197 | 000:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA | C22012700000 | New_Event | Wire Down | Include | Include | Equipment | 26 | 2022-01-27 | 161122 | keep | 0 | Jan | 2022 | 0.10974 | 0.0042207 | Sustained | FALSE | FALSE | Not_TMED_Event | 6197
HUMACAO | 2022-01-27 12:47 | 2022-01-27 12:58 | 1593 | 000:11 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONA FUERA | C22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-01-27 | 17523 | keep | 0 | Jan | 2022 | 0.011935 | 0.001085 | Sustained | FALSE | FALSE | Not_TMED_Event | 1593
CAGUAS | 2022-01-27 12:51 | 2022-01-27 15:12 | 2000 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO REPORTADO POR RAUL SUAREZ | C22012700000 | Partial_restoration | Wire Down | Include | Include | Equipment | 141 | 2022-01-27 | 282000 | keep | 0 | Jan | 2022 | 0.19207 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-27 12:59 | 2022-01-27 14:09 | 90 | 001:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22012700090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-01-27 | 6300 | keep | 0 | Jan | 2022 | 0.0042909 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-01-27 13:05 | 2022-01-27 15:25 | 8 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22012700038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2022-01-27 | 1120 | keep | 0 | Jan | 2022 | 0.00076283 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-01-27 13:05 | 2022-01-27 16:04 | 12 | 002:59 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO PISTOLA | B22012700045 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 179 | 2022-01-27 | 2148 | keep | 0 | Jan | 2022 | 0.001463 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-27 13:06 | 2022-01-27 15:45 | 4 | 002:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS EN PEDESTAL Y BAJANTE SECUNDARIO EN TRANSFORMADOR AEREO | S22012700422 | New_Event | Secondary Wire Down | Include | Include | Equipment | 159 | 2022-01-27 | 636 | keep | 0 | Jan | 2022 | 0.00043318 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-01-27 13:08 | 2022-01-27 16:58 | 100 | 003:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P22012700062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-01-27 | 23000 | keep | 0 | Jan | 2022 | 0.015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-27 13:10 | 2022-01-27 15:40 | 12 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012700011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2022-01-27 | 1800 | keep | 0 | Jan | 2022 | 0.001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-01-27 13:21 | 2022-01-27 15:00 | 5 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22012700040 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2022-01-27 | 495 | keep | 0 | Jan | 2022 | 0.00033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-01-27 13:31 | 2022-01-27 22:20 | 150 | 008:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M22012700106 | New_Event | Cutout Failure | Include | Include | Equipment | 529 | 2022-01-27 | 79350 | keep | 0 | Jan | 2022 | 0.054045 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-01-27 13:37 | 2022-01-27 14:51 | 1 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTES SECUNDARIOS | P22012700061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2022-01-27 | 74 | keep | 0 | Jan | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-27 13:38 | 2022-01-27 13:39 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1717-05 | B22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 4533 | keep | 0 | Jan | 2022 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2022-01-27 13:38 | 2022-01-27 13:39 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1717-01 EL CUAL LLEVA TRANSFERIDA LA CARGA DEL 1717-05 | B22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 341 | keep | 0 | Jan | 2022 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
VEGA BAJA | 2022-01-27 13:42 | 2022-01-27 13:43 | 30 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN CORTE DE LINEA CRUCE POR AVE | B22012700028 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-27 | 30 | keep | 0 | Jan | 2022 | 2.0433e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-01-27 13:50 | 2022-01-27 17:28 | 90 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA Y 2 X 80 EN RISER CRUCE POR CULEBRA | R22012700038 | New_Event |  |  | Include | Wildlife | 218 | 2022-01-27 | 19620 | keep | 0 | Jan | 2022 | 0.013363 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-01-27 13:53 | 2022-01-27 14:31 | 15 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22012700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2022-01-27 | 570 | keep | 0 | Jan | 2022 | 0.00038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-27 14:00 | 2022-01-27 16:08 | 10 | 002:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 37.5 KVA X 50 KVA | A22012700013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 128 | 2022-01-27 | 1280 | keep | 0 | Jan | 2022 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-27 14:02 | 2022-01-27 15:08 | 30 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22012700445 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-01-27 | 1980 | keep | 0 | Jan | 2022 | 0.0013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-27 14:07 | 2022-01-27 14:08 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BARRANQUITAS | 2022-01-27 14:09 | 2022-01-27 15:28 | 2 | 001:19 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C22012700112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-01-27 | 158 | keep | 0 | Jan | 2022 | 0.00010761 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-01-27 14:18 | 2022-01-27 15:41 | 1 | 001:23 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C22012700112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-01-27 | 83 | keep | 0 | Jan | 2022 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-27 14:30 | 2022-01-27 16:18 | 8 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012700014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2022-01-27 | 864 | keep | 0 | Jan | 2022 | 0.00058847 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-01-27 14:32 | 2022-01-27 21:40 | 1 | 007:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN T-42 CRUCE POR IGUANA | R22012700040 | New_Event |  |  | Include | Wildlife | 428 | 2022-01-27 | 428 | keep | 0 | Jan | 2022 | 0.00029151 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-27 14:43 | 2022-01-27 19:24 | 6 | 004:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN XMR SE REPARO SECUNDARIA | S22012700449 | New_Event | Secondary Wire Down | Include | Include | Equipment | 281 | 2022-01-27 | 1686 | keep | 0 | Jan | 2022 | 0.0011483 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-27 14:48 | 2022-01-27 18:10 | 11 | 003:22 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR REPARO SECUNDARIA | R22012700041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 202 | 2022-01-27 | 2222 | keep | 0 | Jan | 2022 | 0.0015134 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-01-27 15:06 | 2022-01-27 16:47 | 5 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y REEMPLAZO BAJANTE SECUNDARIO AVERIADO | R22012700042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2022-01-27 | 505 | keep | 0 | Jan | 2022 | 0.00034395 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-01-27 15:10 | 2022-01-27 16:00 | 15 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22012700020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-01-27 | 750 | keep | 0 | Jan | 2022 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-27 15:12 | 2022-01-27 15:57 | 6197 | 000:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO REPORTADO POR RAUL SUAREZ | C22012700000 | Additional_clients | Wire Down | Include | Include | Equipment | 45 | 2022-01-27 | 278865 | keep | 0 | Jan | 2022 | 0.18993 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-27 15:19 | 2022-01-27 19:28 | 1 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE CERRO C/L | S22012700454 | New_Event | Wire Down | Include | Include | Equipment | 249 | 2022-01-27 | 249 | keep | 0 | Jan | 2022 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-27 15:40 | 2022-01-27 16:19 | 50 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R22012700043 | New_Event |  |  | Include | Wildlife | 39 | 2022-01-27 | 1950 | keep | 0 | Jan | 2022 | 0.0013281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-27 15:53 | 2022-01-27 18:29 | 2067 | 002:36 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA PRIMARIA | M22012700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-01-27 | 322452 | keep | 0 | Jan | 2022 | 0.21962 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
CAGUAS | 2022-01-27 15:57 | 2022-01-27 20:06 | 2000 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PERSONAL LEVANTANDO CONDUCTOR DEL SUELO | C22012700000 | Partial_restoration | Wire Down | Include | Include | Equipment | 249 | 2022-01-27 | 498000 | keep | 0 | Jan | 2022 | 0.33919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-27 15:57 | 2022-01-27 18:30 | 50 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA EN CORTE DE LINEA | P22012700070 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-01-27 | 7650 | keep | 0 | Jan | 2022 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-27 16:04 | 2022-01-27 18:43 | 50 | 002:39 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22012700460 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-01-27 | 7950 | keep | 0 | Jan | 2022 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-01-27 16:36 | 2022-01-27 18:25 | 25 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22012700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-01-27 | 2725 | keep | 0 | Jan | 2022 | 0.001856 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-27 16:41 | 2022-01-27 17:51 | 2 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES | C22012700179 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-01-27 | 140 | keep | 0 | Jan | 2022 | 9.5353e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-27 16:55 | 2022-01-27 16:57 | 500 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR PARTE POR 1620-5 | S22012700000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-27 | 1000 | keep | 0 | Jan | 2022 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-01-27 16:55 | 2022-01-27 16:57 | 1615 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR | S22012700000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-27 | 3230 | keep | 0 | Jan | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CAGUAS | 2022-01-27 16:55 | 2022-01-27 17:49 | 4 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES | C22012700192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-27 | 216 | keep | 0 | Jan | 2022 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-27 16:57 | 2022-01-27 19:13 | 600 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO EN MACHETE | R22012700074 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 136 | 2022-01-27 | 81600 | keep | 0 | Jan | 2022 | 0.055577 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CANOVANAS | 2022-01-27 17:31 | 2022-01-27 17:32 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 1648 | keep | 0 | Jan | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
UTUADO | 2022-01-27 17:41 | 2022-01-27 18:39 | 100 | 000:58 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE CORTE DE LINEA | A22012700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-01-27 | 5800 | keep | 0 | Jan | 2022 | 0.0039504 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-27 17:44 | 2022-01-27 19:10 | 19 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22012700206 | New_Event |  |  | Include | Wildlife | 86 | 2022-01-27 | 1634 | keep | 0 | Jan | 2022 | 0.0011129 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2022-01-27 17:48 | 2022-01-27 18:44 | 100 | 000:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P22012700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-01-27 | 5600 | keep | 0 | Jan | 2022 | 0.0038141 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-27 17:52 | 2022-01-27 20:00 | 8 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR | M22012700079 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-01-27 | 1024 | keep | 0 | Jan | 2022 | 0.00069744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-27 18:17 | 2022-01-27 22:30 | 1000 | 004:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | M22012700089 | New_Event | Wire Down | Include | Include | Equipment | 253 | 2022-01-27 | 253000 | keep | 0 | Jan | 2022 | 0.17232 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
ARECIBO | 2022-01-27 18:22 | 2022-01-27 22:28 | 30 | 004:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER LLUVIA Y FUERTES VIENTOS | A22012700031 | New_Event | Bad Weather | Include | Include | Weather | 246 | 2022-01-27 | 7380 | keep | 0 | Jan | 2022 | 0.0050265 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-27 18:31 | 2022-01-27 18:32 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22012700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 1026 | keep | 0 | Jan | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
MAYAGÃœEZ | 2022-01-27 19:10 | 2022-01-27 22:05 | 6 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22012700041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2022-01-27 | 1050 | keep | 0 | Jan | 2022 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-27 19:13 | 2022-01-27 19:14 | 1615 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA QUE PERSONAL CERRARA MACHETE | S22012700508 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-01-27 | 1615 | keep | 0 | Jan | 2022 | 0.0011 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-27 19:19 | 2022-01-27 21:13 | 35 | 001:54 | P | DESGANCHE | 2 X 15 EN PROVISIONAL SE REALIZO DESGANCHE | B22012700063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-01-27 | 3990 | keep | 0 | Jan | 2022 | 0.0027176 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-01-27 19:47 | 2022-01-27 19:48 | 1097 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22012700122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-27 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2022-01-27 19:48 | 2022-01-28 00:01 | 250 | 004:13 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMA | M22012700126 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 253 | 2022-01-27 | 63250 | keep | 0 | Jan | 2022 | 0.043079 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2022-01-27 20:06 | 2022-01-27 20:07 | 6197 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA ABRIR MACHETES PARA CERRAR PUENTES EN TRONCAL | C22012700000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-01-27 | 6197 | keep | 0 | Jan | 2022 | 0.0042207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-27 20:07 | 2022-01-27 21:46 | 600 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON PUENTES ABIERTOS | C22012700001 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 99 | 2022-01-27 | 59400 | keep | 0 | Jan | 2022 | 0.040457 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-01-27 20:27 | 2022-01-27 20:29 | 300 | 000:02 | P | ERROR HUMANO | DISPARO AL CERRAR MACHETE CALLE ANA OTERO RAMOS ANTONINI PARTE POR 1335-5 | S22012700000 | New_Event | Human Error | Include | Include | Other | 2 | 2022-01-27 | 600 | keep | 0 | Jan | 2022 | 0.00040866 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-01-27 20:27 | 2022-01-27 20:29 | 314 | 000:02 | T | ERROR HUMANO | DISPARO AL CERRAR MACHETE CALLE ANA OTERO RES. ANTONINI CONTRA 1301-2 PARA NORMALIZAR CARGAS | S22012700000 | New_Event | Human Error | Include | Include | Other | 2 | 2022-01-27 | 628 | keep | 0 | Jan | 2022 | 0.00042773 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
UTUADO | 2022-01-27 20:55 | 2022-01-28 10:26 | 100 | 013:31 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA INFORMA EL JOURNEYMAN QUE EL SECTOR REQUIERE DESGANCHE | A22012700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 811 | 2022-01-27 | 81100 | keep | 0 | Jan | 2022 | 0.055237 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-27 20:58 | 2022-01-27 20:59 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22012700159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-27 | 1192 | keep | 0 | Jan | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CAGUAS | 2022-01-27 21:16 | 2022-01-27 21:18 | 817 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22012700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-27 | 1634 | keep | 0 | Jan | 2022 | 0.0011129 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
MAYAGÃœEZ | 2022-01-27 22:30 | 2022-01-27 23:05 | 3000 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR PUENTE ABIERTO | M22012700089 | Additional_clients | Wire Down | Include | Include | Equipment | 35 | 2022-01-27 | 105000 | keep | 0 | Jan | 2022 | 0.071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-27 23:35 | 2022-01-28 09:28 | 3 | 009:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22012700247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 593 | 2022-01-27 | 1779 | keep | 0 | Jan | 2022 | 0.0012117 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-01-28 00:04 | 2022-01-28 11:13 | 200 | 011:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22012800001 | New_Event |  |  | Include | Wildlife | 669 | 2022-01-28 | 133800 | keep | 0 | Jan | 2022 | 0.091131 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-01-28 00:58 | 2022-01-28 09:40 | 100 | 008:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INDICA FOREMAN QUE EL SECTOR REQUIERE DESGANCHE | A22012800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 522 | 2022-01-28 | 52200 | keep | 0 | Jan | 2022 | 0.035553 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-28 02:05 | 2022-01-28 16:22 | 125 | 014:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | C22012800010 | New_Event | Cutout Failure | Include | Include | Equipment | 857 | 2022-01-28 | 107125 | keep | 0 | Jan | 2022 | 0.072962 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-01-28 03:17 | 2022-01-28 15:12 | 100 | 011:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22012800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2022-01-28 | 71500 | keep | 0 | Jan | 2022 | 0.048698 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-28 06:39 | 2022-01-28 06:40 | 837 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1401-7 | S22012800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 837 | keep | 0 | Jan | 2022 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-01-28 06:39 | 2022-01-28 06:40 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1401-6 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22012800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 908 | keep | 0 | Jan | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
CANOVANAS | 2022-01-28 07:19 | 2022-01-28 10:00 | 130 | 002:41 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | R22012800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-01-28 | 20930 | keep | 0 | Jan | 2022 | 0.014255 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2022-01-28 07:44 | 2022-01-28 20:06 | 1 | 012:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22012800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 742 | 2022-01-28 | 742 | keep | 0 | Jan | 2022 | 0.00050537 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-28 07:52 | 2022-01-28 11:14 | 1 | 003:22 | P | OTRAS CAUSAS | 3 X 40 EN RISER PROBLEMA DEL CLIENTE | C22012800056 | New_Event | Other Causes | Include | Include | Other | 202 | 2022-01-28 | 202 | keep | 0 | Jan | 2022 | 0.00013758 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-28 08:40 | 2022-01-28 12:30 | 39 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 20 EN TRANSFORMADORES SE REEMPLAZARON CAJAS QUEMADAS | C22012800040 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2022-01-28 | 8970 | keep | 0 | Jan | 2022 | 0.0061094 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
UTUADO | 2022-01-28 08:57 | 2022-01-28 09:01 | 1479 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR SE VERIFICO CON EL PERSONAL DE DESGANCHE TRABAJANDO EN EL ALIMENTADOR E INDICARON QUE NO TUVIERON CONTACTO CON LAS LINEAS | A22012800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-28 | 5916 | keep | 0 | Jan | 2022 | 0.0040294 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
BAYAMON | 2022-01-28 09:16 | 2022-01-28 09:17 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1713-03 | B22012800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 5252 | keep | 0 | Jan | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
MAYAGÃœEZ | 2022-01-28 09:32 | 2022-01-28 11:39 | 40 | 002:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22012800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-01-28 | 5080 | keep | 0 | Jan | 2022 | 0.00346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-28 09:33 | 2022-01-28 11:39 | 185 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA EXCAVADORA TRABAJANDO CERCA DE LAS LINEAS CAUSO LA INTERRUPCION | A22012800027 | New_Event |  |  | Include | Wildlife | 126 | 2022-01-28 | 23310 | keep | 0 | Jan | 2022 | 0.015876 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
BAYAMON | 2022-01-28 09:37 | 2022-01-28 09:41 | 514 | 000:04 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR 1520-5 QUE LLEVA A SU VEZ LA CARGA DEL 1520-01 Y 1520-4. PERSONAL COMPAÃ‘IA WRIGHT TREE SERVICE EN LABORES DE PODA EN LINEA 6800 CAYO RAMA SOBRE ALIMENTADOR | S22012800000 | New_Event | Human Error | Include | Include | Other | 4 | 2022-01-28 | 2056 | keep | 0 | Jan | 2022 | 0.0014003 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-01-28 09:37 | 2022-01-28 09:41 | 681 | 000:04 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR 1520-5 QUE LLEVA A SU VEZ LA CARGA DEL 1520-01 Y 1520-04. PERSONAL COMPAÃ‘IA WRIGHT TREE SERVICE EN LABORES DE PODA EN LINEA 6800 CAYO RAMA SOBRE ALIMENTADOR | S22012800000 | New_Event | Human Error | Include | Include | Other | 4 | 2022-01-28 | 2724 | keep | 0 | Jan | 2022 | 0.0018553 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
BAYAMON | 2022-01-28 09:37 | 2022-01-28 09:41 | 68 | 000:04 | T | ERROR HUMANO | DISPARO CON R/R OFF LLAVE CARGA 1520-1 Y 4 PERSONAL COMPAÃ‘IA WRIGHT TREE SERVICIO DESGANCHANDO EN L-6800 CAYO RAMA SOBRE ALIMENTADOR Y DISPARO SE VERIFICO PERSONAL FUERA | S22012800000 | New_Event | Human Error | Include | Include | Other | 4 | 2022-01-28 | 272 | keep | 0 | Jan | 2022 | 0.00018526 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
CAGUAS | 2022-01-28 09:37 | 2022-01-28 13:24 | 6 | 003:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON BAJANTES SECUNDARIOS QUEMADOS | C22012800056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 227 | 2022-01-28 | 1362 | keep | 0 | Jan | 2022 | 0.00092765 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-01-28 09:48 | 2022-01-28 13:59 | 20 | 004:11 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE RETIRO CARGA EN DOS TRANSFORMADORES PARA REMPLAZAR POSTE SECUNDARIO | P22012800011 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 251 | 2022-01-28 | 5020 | keep | 0 | Jan | 2022 | 0.0034191 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-01-28 10:09 | 2022-01-28 13:01 | 10 | 002:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A22012800035 | New_Event |  |  | Include | Wildlife | 172 | 2022-01-28 | 1720 | keep | 0 | Jan | 2022 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-28 10:11 | 2022-01-28 15:40 | 1 | 005:29 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA PARARRAYO DEFECTUOSO | P22012800014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 329 | 2022-01-28 | 329 | keep | 0 | Jan | 2022 | 0.00022408 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-28 10:50 | 2022-01-28 10:51 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9207-08 LLEVANDO CARGA 9207-09 | B22012800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 1859 | keep | 0 | Jan | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-01-28 10:50 | 2022-01-28 10:51 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9207-08 LLEVANDO CARGA 9207-09 | B22012800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 7 | keep | 0 | Jan | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-01-28 10:51 | 2022-01-28 15:00 | 65 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22012800024 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-01-28 | 16185 | keep | 0 | Jan | 2022 | 0.011024 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-01-28 10:52 | 2022-01-28 11:07 | 10 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONEXIONES | P22012800016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-01-28 | 150 | keep | 0 | Jan | 2022 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-28 11:01 | 2022-01-28 12:36 | 10 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE | S22012800026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2022-01-28 | 950 | keep | 0 | Jan | 2022 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-28 11:10 | 2022-01-28 14:25 | 1 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22012800038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-01-28 | 195 | keep | 0 | Jan | 2022 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-28 11:17 | 2022-01-28 15:06 | 70 | 003:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE Y SE RETIRO PENCA | C22012800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2022-01-28 | 16030 | keep | 0 | Jan | 2022 | 0.010918 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-01-28 11:20 | 2022-01-28 17:30 | 14 | 006:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TANSFORMADOR PARA REEMPLAZAR SECUNDARIA | C22012800067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 370 | 2022-01-28 | 5180 | keep | 0 | Jan | 2022 | 0.0035281 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-01-28 11:31 | 2022-01-28 12:02 | 1879 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-01-28 | 58249 | keep | 0 | Jan | 2022 | 0.039673 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
ARECIBO | 2022-01-28 11:31 | 2022-01-28 12:02 | 2777 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-01-28 | 86087 | keep | 0 | Jan | 2022 | 0.058633 | 0.0018914 | Sustained | FALSE | FALSE | Not_TMED_Event | 2777
ARECIBO | 2022-01-28 11:31 | 2022-01-28 12:02 | 2 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-01-28 | 62 | keep | 0 | Jan | 2022 | 4.2228e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-01-28 11:31 | 2022-01-28 12:02 | 2839 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-01-28 | 88009 | keep | 0 | Jan | 2022 | 0.059943 | 0.0019336 | Sustained | FALSE | FALSE | Not_TMED_Event | 2839
ARECIBO | 2022-01-28 11:31 | 2022-01-28 12:02 | 1160 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-01-28 | 35960 | keep | 0 | Jan | 2022 | 0.024492 | 0.00079007 | Sustained | FALSE | FALSE | Not_TMED_Event | 1160
ARECIBO | 2022-01-28 11:31 | 2022-01-28 12:02 | 1860 | 000:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2022-01-28 | 57660 | keep | 0 | Jan | 2022 | 0.039272 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-01-28 11:43 | 2022-01-28 15:47 | 60 | 004:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22012800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2022-01-28 | 14640 | keep | 0 | Jan | 2022 | 0.0099712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-28 12:07 | 2022-01-28 20:02 | 6 | 007:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22012800069 | New_Event | Cutout Failure | Include | Include | Equipment | 475 | 2022-01-28 | 2850 | keep | 0 | Jan | 2022 | 0.0019411 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-28 12:10 | 2022-01-28 13:37 | 1879 | 001:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 87 | 2022-01-28 | 163473 | keep | 0 | Jan | 2022 | 0.11134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-28 12:10 | 2022-01-28 13:37 | 2777 | 001:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 87 | 2022-01-28 | 241599 | keep | 0 | Jan | 2022 | 0.16455 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-28 12:10 | 2022-01-28 13:37 | 2 | 001:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 87 | 2022-01-28 | 174 | keep | 0 | Jan | 2022 | 0.00011851 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-28 12:10 | 2022-01-28 13:37 | 2839 | 001:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 87 | 2022-01-28 | 246993 | keep | 0 | Jan | 2022 | 0.16823 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-28 12:10 | 2022-01-28 13:37 | 1160 | 001:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 87 | 2022-01-28 | 100920 | keep | 0 | Jan | 2022 | 0.068736 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-28 12:10 | 2022-01-28 13:37 | 1860 | 001:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | A22012800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 87 | 2022-01-28 | 161820 | keep | 0 | Jan | 2022 | 0.11021 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-28 12:12 | 2022-01-28 12:22 | 1348 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | R22012800000 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2022-01-28 | 13480 | keep | 0 | Jan | 2022 | 0.0091812 | 0.00091812 | Sustained | FALSE | FALSE | Not_TMED_Event | 1348
CANOVANAS | 2022-01-28 12:22 | 2022-01-28 15:58 | 150 | 003:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y CERRO MACHETES | R22012800032 | Partial_restoration | Wire Down | Include | Include | Equipment | 216 | 2022-01-28 | 32400 | keep | 0 | Jan | 2022 | 0.022067 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-28 12:31 | 2022-01-28 13:25 | 30 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22012800019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-28 | 1620 | keep | 0 | Jan | 2022 | 0.0011034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-01-28 13:11 | 2022-01-28 15:55 | 50 | 002:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22012800027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-01-28 | 8200 | keep | 0 | Jan | 2022 | 0.005585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-28 13:32 | 2022-01-28 18:39 | 11 | 005:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR LAGARTO | C22012800084 | New_Event |  |  | Include | Wildlife | 307 | 2022-01-28 | 3377 | keep | 0 | Jan | 2022 | 0.0023001 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-01-28 13:33 | 2022-01-28 17:08 | 60 | 003:35 | P | DESGANCHE | 1 X 50 1 X 40 Y 1 X 25 EN CORTES DE LINEA | R22012800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-01-28 | 12900 | keep | 0 | Jan | 2022 | 0.0087861 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-01-28 13:47 | 2022-01-28 17:33 | 20 | 003:46 | P | ESTRUCTURA AVERIADA | SE RELOCALIZO TRANSFORMADOR A POSTE PRIMARIO CERCANO AL POSTE PARTIDO | C22012800086 | New_Event | Defective Pole | Include | Include | Equipment | 226 | 2022-01-28 | 4520 | keep | 0 | Jan | 2022 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-28 14:11 | 2022-01-28 14:49 | 11 | 000:38 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR PEDESTAL AVERIADO | C22012800089 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 38 | 2022-01-28 | 418 | keep | 0 | Jan | 2022 | 0.0002847 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-01-28 14:11 | 2022-01-29 02:10 | 15 | 011:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REPARO CONECTORES QUEMADOS | M22012800025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 719 | 2022-01-28 | 10785 | keep | 0 | Jan | 2022 | 0.0073456 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-01-28 14:40 | 2022-01-28 17:30 | 10 | 002:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22012800021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 170 | 2022-01-28 | 1700 | keep | 0 | Jan | 2022 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-28 14:45 | 2022-01-28 15:09 | 6 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22012800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-01-28 | 144 | keep | 0 | Jan | 2022 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-28 14:49 | 2022-01-28 18:04 | 9 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | C22012800075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-01-28 | 1755 | keep | 0 | Jan | 2022 | 0.0011953 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-28 14:52 | 2022-01-28 14:53 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22012800029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 6285 | keep | 0 | Jan | 2022 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
ARECIBO | 2022-01-28 14:55 | 2022-01-28 19:00 | 65 | 004:05 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | A22012800037 | New_Event | Defective Pole | Include | Include | Equipment | 245 | 2022-01-28 | 15925 | keep | 0 | Jan | 2022 | 0.010846 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-01-28 15:08 | 2022-01-28 23:40 | 150 | 008:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR ALAMBRE PARTIDO | M22012800116 | New_Event | Wire Down | Include | Include | Equipment | 512 | 2022-01-28 | 76800 | keep | 0 | Jan | 2022 | 0.052308 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-01-28 15:13 | 2022-01-28 15:38 | 10 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22012800032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-01-28 | 250 | keep | 0 | Jan | 2022 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-28 15:16 | 2022-01-28 15:17 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22012800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 1478 | keep | 0 | Jan | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
SAN JUAN | 2022-01-28 15:18 | 2022-01-28 16:37 | 35 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22012800041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-01-28 | 2765 | keep | 0 | Jan | 2022 | 0.0018832 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-01-28 15:30 | 2022-01-28 18:03 | 284 | 002:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | C22012800102 | New_Event |  |  | Include | Wildlife | 153 | 2022-01-28 | 43452 | keep | 0 | Jan | 2022 | 0.029595 | 0.00019343 | Sustained | FALSE | FALSE | Not_TMED_Event | 284
CANOVANAS | 2022-01-28 15:31 | 2022-01-28 16:47 | 30 | 001:16 | P | DESGANCHE | 1 X 30 EN C/L | R22012800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-01-28 | 2280 | keep | 0 | Jan | 2022 | 0.0015529 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-28 16:03 | 2022-01-28 21:15 | 12 | 005:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A22012800122 | New_Event |  |  | Include | Wildlife | 312 | 2022-01-28 | 3744 | keep | 0 | Jan | 2022 | 0.00255 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-28 16:06 | 2022-01-28 16:41 | 6 | 000:35 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE REALIZO DESGANCHE Y SE AJUSTO TAPS DEL 3 @ 2 | B22012800036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 35 | 2022-01-28 | 210 | keep | 0 | Jan | 2022 | 0.00014303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-28 16:13 | 2022-01-28 16:14 | 8 | 000:01 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | R22012800011 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2022-01-28 | 8 | keep | 0 | Jan | 2022 | 5.4488e-06 | 5.4488e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-28 16:22 | 2022-01-28 19:40 | 100 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22012800060 | New_Event |  |  | Include | Wildlife | 198 | 2022-01-28 | 19800 | keep | 0 | Jan | 2022 | 0.013486 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-28 16:25 | 2022-01-28 16:26 | 2076 | 000:01 | P | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1718-03 QUE LLEVA 40% DEL 1710-05 | B22012800000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-28 | 2076 | keep | 0 | Jan | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-01-28 16:25 | 2022-01-28 16:26 | 2605 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1718-03 LLEVANDO 40% DEL 1710-05 | B22012800000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-28 | 2605 | keep | 0 | Jan | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-01-28 16:26 | 2022-01-28 19:55 | 600 | 003:29 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO Y SE CERRO MACHETES | B22012800062 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 209 | 2022-01-28 | 125400 | keep | 0 | Jan | 2022 | 0.085409 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2022-01-28 16:27 | 2022-01-28 18:40 | 6 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S22012800048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2022-01-28 | 798 | keep | 0 | Jan | 2022 | 0.00054351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-28 16:28 | 2022-01-28 20:10 | 100 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | M22012800062 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2022-01-28 | 22200 | keep | 0 | Jan | 2022 | 0.01512 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-28 16:45 | 2022-01-28 18:56 | 10 | 002:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50KVA POR UNO DE IGUAL CAPACIDAD | B22012800049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 131 | 2022-01-28 | 1310 | keep | 0 | Jan | 2022 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-28 16:51 | 2022-01-28 17:20 | 6 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR SE REPARO SECUNDARIA | B22012800055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-01-28 | 174 | keep | 0 | Jan | 2022 | 0.00011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-01-28 17:17 | 2022-01-28 17:18 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22012800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-28 | 2113 | keep | 0 | Jan | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2022-01-28 17:20 | 2022-01-29 12:00 | 60 | 018:40 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN CORTE DE LINEA SE REPARO AVERIA SOTERRADA | M22012800085 | New_Event | UG Cable Fault | Include | Include | Equipment | 1120 | 2022-01-28 | 67200 | keep | 0 | Jan | 2022 | 0.04577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-28 17:37 | 2022-01-28 18:44 | 14 | 001:07 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR DE 37.5KVA A 2.4KV AVERIADO SE TRANSFIEREN LAS CARGAS A TRANSFORMADOR EXISTENTE DE 50KVA A 13KV (14 CLIENTES SEGUN OMS) | P22012800041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 67 | 2022-01-28 | 938 | keep | 0 | Jan | 2022 | 0.00063887 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-01-28 17:49 | 2022-01-28 18:15 | 100 | 000:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22012800112 | New_Event | Cutout Failure | Include | Include | Equipment | 26 | 2022-01-28 | 2600 | keep | 0 | Jan | 2022 | 0.0017708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-28 17:51 | 2022-01-29 11:50 | 10 | 017:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 50KVA X 50KVA | R22012800035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1079 | 2022-01-28 | 10790 | keep | 0 | Jan | 2022 | 0.007349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-28 18:12 | 2022-01-28 20:58 | 45 | 002:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA JOURNEYMAN INFORMA SECTOR REQUIERE DESGANCHE | A22012800128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-01-28 | 7470 | keep | 0 | Jan | 2022 | 0.0050878 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-01-28 18:27 | 2022-01-28 18:28 | 2379 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | P22012800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-28 | 2379 | keep | 0 | Jan | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-01-28 18:28 | 2022-01-28 20:00 | 200 | 001:32 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P22012800046 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-01-28 | 18400 | keep | 0 | Jan | 2022 | 0.012532 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-01-28 18:36 | 2022-01-28 19:00 | 1979 | 000:24 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE COLOCA RR EN OFF Y SE CERRO MANUAL ELECTRICAMENTE | P22012800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-01-28 | 47496 | keep | 0 | Jan | 2022 | 0.032349 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
HUMACAO | 2022-01-28 18:58 | 2022-01-29 08:52 | 40 | 013:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22012800125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 834 | 2022-01-28 | 33360 | keep | 0 | Jan | 2022 | 0.022721 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-28 19:12 | 2022-01-28 21:05 | 80 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA CAJA QUEMADA | S22012800051 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-01-28 | 9040 | keep | 0 | Jan | 2022 | 0.0061571 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-01-28 19:44 | 2022-01-29 10:15 | 10 | 014:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22012800127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 871 | 2022-01-28 | 8710 | keep | 0 | Jan | 2022 | 0.0059323 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-28 20:24 | 2022-01-28 21:16 | 1798 | 000:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR POR LINEA PRIMARIA ENERGIZADA EN EL SUELO A PETICION DEL ING LUIS FENEQUE SE SECCIONALIZO PARA CERRAR EL INTERRUPTOR | A22012800139 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2022-01-28 | 93496 | keep | 0 | Jan | 2022 | 0.06368 | 0.0012246 | Sustained | FALSE | FALSE | Not_TMED_Event | 1798
ARECIBO | 2022-01-28 20:56 | 2022-01-28 22:38 | 40 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA CAJA DEFECTUOSA | A22012800147 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-01-28 | 4080 | keep | 0 | Jan | 2022 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-28 21:08 | 2022-01-29 12:10 | 80 | 015:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M22012800134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 902 | 2022-01-28 | 72160 | keep | 0 | Jan | 2022 | 0.049148 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-28 21:16 | 2022-01-28 23:20 | 716 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO SE ABRIO PUENTES PARA SECCIONALIZAR OTRO ALAMBRE PARTIDO EN TERMINAL DE LINEA | A22012800155 | Partial_restoration | Wire Down | Include | Include | Equipment | 124 | 2022-01-28 | 88784 | keep | 0 | Jan | 2022 | 0.06047 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-28 21:40 | 2022-01-29 09:56 | 10 | 012:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE RETIRO IGUANA CRUZADA CON BUSHING PRIMARIO DEL TRANSFORMADOR | P22012800078 | New_Event |  |  | Include | Wildlife | 736 | 2022-01-28 | 7360 | keep | 0 | Jan | 2022 | 0.0050129 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-28 22:43 | 2022-01-29 03:19 | 100 | 004:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22012800144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-01-28 | 27600 | keep | 0 | Jan | 2022 | 0.018798 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-28 23:16 | 2022-01-29 02:49 | 25 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22012800131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-01-28 | 5325 | keep | 0 | Jan | 2022 | 0.0036268 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-28 23:20 | 2022-01-29 12:14 | 1 | 012:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22012900008 | Partial_restoration | Wire Down | Include | Include | Equipment | 774 | 2022-01-28 | 774 | keep | 0 | Jan | 2022 | 0.00052717 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-29 00:39 | 2022-01-29 00:40 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22012900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
ARECIBO | 2022-01-29 01:01 | 2022-01-29 01:02 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
HUMACAO | 2022-01-29 03:01 | 2022-01-29 03:02 | 676 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22012900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 676 | keep | 0 | Jan | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-01-29 03:02 | 2022-01-29 09:58 | 250 | 006:56 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | C22012900003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 416 | 2022-01-29 | 104000 | keep | 0 | Jan | 2022 | 0.070834 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-01-29 04:00 | 2022-01-29 09:04 | 40 | 005:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA PRINCIPAL Y 1 X 50 EN CORTE DE LINEA INTERMEDIO | S22012900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2022-01-29 | 12160 | keep | 0 | Jan | 2022 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-29 04:14 | 2022-01-29 04:15 | 2770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 2770 | keep | 0 | Jan | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
MAYAGÃœEZ | 2022-01-29 05:00 | 2022-01-29 08:09 | 1 | 003:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REMPLAZO CONECTOR SECUNDARIO | M22012900004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 189 | 2022-01-29 | 189 | keep | 0 | Jan | 2022 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-29 06:17 | 2022-01-29 09:40 | 30 | 003:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22012900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-01-29 | 6090 | keep | 0 | Jan | 2022 | 0.0041479 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-29 06:19 | 2022-01-29 06:20 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 2354 | keep | 0 | Jan | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2022-01-29 06:52 | 2022-01-29 09:11 | 7 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22012900005 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2022-01-29 | 973 | keep | 0 | Jan | 2022 | 0.00066271 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-29 07:00 | 2022-01-29 09:42 | 30 | 002:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22012900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-01-29 | 4860 | keep | 0 | Jan | 2022 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-29 07:03 | 2022-01-29 09:08 | 85 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L NO CAUSA | C22012900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-01-29 | 10625 | keep | 0 | Jan | 2022 | 0.0072366 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2022-01-29 07:16 | 2022-01-29 15:40 | 10 | 008:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | C22012900010 | New_Event | Cutout Failure | Include | Include | Equipment | 504 | 2022-01-29 | 5040 | keep | 0 | Jan | 2022 | 0.0034327 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-29 07:22 | 2022-01-29 09:53 | 80 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22012900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-01-29 | 12080 | keep | 0 | Jan | 2022 | 0.0082276 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-01-29 07:39 | 2022-01-29 11:55 | 10 | 004:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22012900007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 256 | 2022-01-29 | 2560 | keep | 0 | Jan | 2022 | 0.0017436 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-29 08:21 | 2022-01-29 08:22 | 31 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO Y SE CERRO POR CONTROL | B22012900004 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-29 | 31 | keep | 0 | Jan | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2022-01-29 08:22 | 2022-01-29 12:29 | 25 | 004:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN RISER SE RETIRO AVE | B22012900011 | 1st_after_momentary |  |  | Include | Wildlife | 247 | 2022-01-29 | 6175 | keep | 0 | Jan | 2022 | 0.0042058 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-29 08:29 | 2022-01-29 09:22 | 12 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22012900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-01-29 | 636 | keep | 0 | Jan | 2022 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-01-29 08:33 | 2022-01-29 11:05 | 65 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22012900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-01-29 | 9880 | keep | 0 | Jan | 2022 | 0.0067292 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-01-29 08:35 | 2022-01-29 11:00 | 20 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22012900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-01-29 | 2900 | keep | 0 | Jan | 2022 | 0.0019752 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-01-29 08:40 | 2022-01-29 12:56 | 12 | 004:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22012900002 | New_Event | Cutout Failure | Include | Include | Equipment | 256 | 2022-01-29 | 3072 | keep | 0 | Jan | 2022 | 0.0020923 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-29 08:41 | 2022-01-29 11:23 | 1541 | 002:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENERGIZO SUBESTACION POR LINEA 13700 | A22012900003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-01-29 | 249642 | keep | 0 | Jan | 2022 | 0.17003 | 0.0010496 | Sustained | FALSE | FALSE | Not_TMED_Event | 1541
ARECIBO | 2022-01-29 08:41 | 2022-01-29 11:23 | 307 | 002:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENERGIZO SUBESTACION POR LINEA 13700 | A22012900003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-01-29 | 49734 | keep | 0 | Jan | 2022 | 0.033874 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
ARECIBO | 2022-01-29 08:41 | 2022-01-29 11:23 | 1277 | 002:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENERGIZO SUBESTACION POR LINEA 13700 | A22012900003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-01-29 | 206874 | keep | 0 | Jan | 2022 | 0.1409 | 0.00086976 | Sustained | FALSE | FALSE | Not_TMED_Event | 1277
ARECIBO | 2022-01-29 08:41 | 2022-01-29 11:23 | 1644 | 002:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENERGIZO SUBESTACION POR LINEA 13700 | A22012900003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-01-29 | 266328 | keep | 0 | Jan | 2022 | 0.18139 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
ARECIBO | 2022-01-29 08:41 | 2022-01-29 11:23 | 1831 | 002:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 SE ENERGIZO SUBESTACION POR LINEA 13700 | A22012900003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 162 | 2022-01-29 | 296622 | keep | 0 | Jan | 2022 | 0.20203 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
BAYAMON | 2022-01-29 08:53 | 2022-01-29 17:49 | 360 | 008:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE RETEZO LINEA Y SE ENDEREZO POSTE PRIMARIO | B22012900010 | New_Event | Wire Down | Include | Include | Equipment | 536 | 2022-01-29 | 192960 | keep | 0 | Jan | 2022 | 0.13142 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
CAGUAS | 2022-01-29 09:30 | 2022-01-29 13:00 | 45 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22012900030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-01-29 | 9450 | keep | 0 | Jan | 2022 | 0.0064364 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-01-29 09:54 | 2022-01-29 12:20 | 15 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22012900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2022-01-29 | 2190 | keep | 0 | Jan | 2022 | 0.0014916 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-29 10:08 | 2022-01-29 10:50 | 457 | 000:42 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE PATRULLO Y EN UN PRINCIPIO NO SE ENCONTRO CAUSA | S22012900021 | New_Event |  |  | Include | Wildlife | 42 | 2022-01-29 | 19194 | keep | 0 | Jan | 2022 | 0.013073 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
CAGUAS | 2022-01-29 10:15 | 2022-01-29 11:56 | 13 | 001:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 15KVA POR UNO DE 37.5KVA | C22012900032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 101 | 2022-01-29 | 1313 | keep | 0 | Jan | 2022 | 0.00089428 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-01-29 10:33 | 2022-01-29 13:00 | 5 | 002:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22012900014 | New_Event |  |  | Include | Wildlife | 147 | 2022-01-29 | 735 | keep | 0 | Jan | 2022 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-01-29 10:50 | 2022-01-29 12:03 | 309 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | LUEGO DE ALIMENTADOR EN SERVICIO SE ABRIO MACHETES PARA RETIRAR IGUANA QUE CRUZO CONDUCTOR SPACER Y REALIZAR DESGANCHE | S22012900021 | Partial_restoration |  |  | Include | Wildlife | 73 | 2022-01-29 | 22557 | keep | 0 | Jan | 2022 | 0.015363 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-29 11:03 | 2022-01-29 12:33 | 10 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | C22012900035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-01-29 | 900 | keep | 0 | Jan | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-29 11:11 | 2022-01-29 12:47 | 30 | 001:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S22012900028 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2022-01-29 | 2880 | keep | 0 | Jan | 2022 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-29 11:36 | 2022-01-29 12:59 | 10 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22012900020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-01-29 | 830 | keep | 0 | Jan | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-29 11:38 | 2022-01-29 11:39 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO | C22012900000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-29 | 2450 | keep | 0 | Jan | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-01-29 11:39 | 2022-01-29 13:41 | 80 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L SE RETIRO PAJARO | C22012900037 | 1st_after_momentary |  |  | Include | Wildlife | 122 | 2022-01-29 | 9760 | keep | 0 | Jan | 2022 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-01-29 11:55 | 2022-01-29 12:49 | 15 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | P22012900011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-29 | 810 | keep | 0 | Jan | 2022 | 0.00055169 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-01-29 11:57 | 2022-01-29 11:58 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22012900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 2484 | keep | 0 | Jan | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
FAJARDO | 2022-01-29 12:05 | 2022-01-29 12:39 | 10 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22012900004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2022-01-29 | 340 | keep | 0 | Jan | 2022 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-29 12:10 | 2022-01-29 12:18 | 14 | 000:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | P22012900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 8 | 2022-01-29 | 112 | keep | 0 | Jan | 2022 | 7.6283e-05 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-01-29 12:27 | 2022-01-29 14:36 | 1 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA Y 1 X 30 EN RISER CRUCE POR PALOMA | C22012900039 | New_Event |  |  | Include | Wildlife | 129 | 2022-01-29 | 129 | keep | 0 | Jan | 2022 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-29 12:33 | 2022-01-29 13:40 | 40 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | B22012900025 | New_Event | Wire Down | Include | Include | Equipment | 67 | 2022-01-29 | 2680 | keep | 0 | Jan | 2022 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-29 13:31 | 2022-01-29 18:14 | 30 | 004:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A22012900088 | New_Event | Wire Down | Include | Include | Equipment | 283 | 2022-01-29 | 8490 | keep | 0 | Jan | 2022 | 0.0057825 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-01-29 13:50 | 2022-01-29 15:09 | 20 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR NEUTRAL SECUNDARIO | R22012900025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2022-01-29 | 1580 | keep | 0 | Jan | 2022 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-01-29 14:11 | 2022-01-29 15:03 | 4 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22012900043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-01-29 | 208 | keep | 0 | Jan | 2022 | 0.00014167 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-29 14:17 | 2022-01-29 14:19 | 860 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE ALIMENTADOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA | S22012900033 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-29 | 1720 | keep | 0 | Jan | 2022 | 0.0011715 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
SAN JUAN | 2022-01-29 14:17 | 2022-01-29 14:19 | 2435 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE ALIMENTADOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA | S22012900033 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-29 | 4870 | keep | 0 | Jan | 2022 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-01-29 14:19 | 2022-01-29 15:01 | 287 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PARTIDO | S22012900033 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 42 | 2022-01-29 | 12054 | keep | 0 | Jan | 2022 | 0.0082099 | 0.00019547 | Sustained | FALSE | FALSE | Not_TMED_Event | 287
BAYAMON | 2022-01-29 14:23 | 2022-01-29 17:21 | 60 | 002:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22012900038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-01-29 | 10680 | keep | 0 | Jan | 2022 | 0.0072741 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-29 14:25 | 2022-01-29 14:26 | 837 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 SE CERRO POR SCADA | S22012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 837 | keep | 0 | Jan | 2022 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-01-29 14:25 | 2022-01-29 14:26 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 SE CERRO POR SCADA | S22012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 908 | keep | 0 | Jan | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
HUMACAO | 2022-01-29 14:35 | 2022-01-29 16:55 | 8 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER CRUCE POR CHANGO | C22012900044 | New_Event |  |  | Include | Wildlife | 140 | 2022-01-29 | 1120 | keep | 0 | Jan | 2022 | 0.00076283 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-01-29 14:49 | 2022-01-29 16:20 | 4 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C22012900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-01-29 | 364 | keep | 0 | Jan | 2022 | 0.00024792 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-29 14:51 | 2022-01-29 16:07 | 25 | 001:16 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA DIVIDIR CARGA SECTOR CON PROBLEMAS DE VOLTAJE | B22012900030 | New_Event | Other Causes | Include | Include | Other | 76 | 2022-01-29 | 1900 | keep | 0 | Jan | 2022 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-29 15:01 | 2022-01-29 17:02 | 860 | 002:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1303-02 QUE ESTA LLEVANDO 20% DEL 1204-02 PARA ABRIR AMARRE ENTRE 1204-02 Y 1303-02 Y LEVANTAR CONDUCTOR PRIMARIO PARTIDO EN CAMINO LOS GONZALEZ | S22012900033 | Additional_clients | Wire Down | Include | Include | Equipment | 121 | 2022-01-29 | 104060 | keep | 0 | Jan | 2022 | 0.070875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-29 15:01 | 2022-01-29 15:02 | 2435 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 PARA ABRIR MACHETES N/O ENTRE 1204-02 Y 1303-02 PARA SECCIONALIZAR CONDUCTOR EN EL SUELO DEL 1204-02 | S22012900033 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-01-29 | 2435 | keep | 0 | Jan | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
VEGA BAJA | 2022-01-29 15:04 | 2022-01-29 19:14 | 40 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22012900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2022-01-29 | 10000 | keep | 0 | Jan | 2022 | 0.006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-01-29 16:28 | 2022-01-29 17:53 | 29 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | C22012900050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2022-01-29 | 2465 | keep | 0 | Jan | 2022 | 0.0016789 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2022-01-29 16:35 | 2022-01-29 17:35 | 9 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | C22012900052 | New_Event |  |  | Include | Wildlife | 60 | 2022-01-29 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-01-29 16:35 | 2022-01-29 18:14 | 10 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BARRAS EN PEDESTAL SECUNDARIO | P22012900004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2022-01-29 | 990 | keep | 0 | Jan | 2022 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-29 16:55 | 2022-01-29 18:55 | 1 | 002:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE RISER | A22012900091 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2022-01-29 | 120 | keep | 0 | Jan | 2022 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-01-29 17:14 | 2022-01-29 17:15 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22012900035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 4132 | keep | 0 | Jan | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2022-01-29 17:20 | 2022-01-29 18:40 | 12 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y 3 TOMAS | R22012900008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2022-01-29 | 960 | keep | 0 | Jan | 2022 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-29 17:31 | 2022-01-29 18:20 | 15 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22012800034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2022-01-29 | 735 | keep | 0 | Jan | 2022 | 0.00050061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-29 17:37 | 2022-01-29 18:04 | 25 | 000:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CAMION PARTE TOMA SECUNDARIA | P22012900039 | New_Event |  |  | Include | Wildlife | 27 | 2022-01-29 | 675 | keep | 0 | Jan | 2022 | 0.00045974 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-29 17:48 | 2022-01-29 18:04 | 15 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B22012900040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2022-01-29 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-29 18:41 | 2022-01-29 18:42 | 1812 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 1812 | keep | 0 | Jan | 2022 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-01-29 19:25 | 2022-01-29 19:26 | 30 | 000:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22012900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-29 | 30 | keep | 0 | Jan | 2022 | 2.0433e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-01-29 19:31 | 2022-01-29 21:15 | 60 | 001:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A22012900097 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2022-01-29 | 6240 | keep | 0 | Jan | 2022 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-29 19:37 | 2022-01-30 11:48 | 12 | 016:11 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA DEL SU - 5 @ T - 46 | C22012900056 | New_Event | UG Cable Fault | Include | Include | Equipment | 971 | 2022-01-29 | 11652 | keep | 0 | Jan | 2022 | 0.0079361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-29 20:06 | 2022-01-30 01:05 | 300 | 004:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | M22012900035 | New_Event | Wire Down | Include | Include | Equipment | 299 | 2022-01-29 | 89700 | keep | 0 | Jan | 2022 | 0.061094 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-01-29 20:19 | 2022-01-29 20:20 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22012900039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2022-01-29 21:09 | 2022-01-29 21:10 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22012900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-29 | 312 | keep | 0 | Jan | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
BAYAMON | 2022-01-29 21:20 | 2022-01-29 22:26 | 15 | 001:06 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE SECUNDARIO | S22012900055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 66 | 2022-01-29 | 990 | keep | 0 | Jan | 2022 | 0.00067428 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-01-29 21:24 | 2022-01-30 11:28 | 6 | 014:04 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMA | R22012900012 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 844 | 2022-01-29 | 5064 | keep | 0 | Jan | 2022 | 0.0034491 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-29 23:07 | 2022-01-30 15:01 | 12 | 015:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5KVA | S22012900064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 954 | 2022-01-29 | 11448 | keep | 0 | Jan | 2022 | 0.0077972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:52 | 693 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2800 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-01-29 | 2079 | keep | 0 | Jan | 2022 | 0.001416 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:52 | 47 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2800 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-01-29 | 141 | keep | 0 | Jan | 2022 | 9.6034e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:52 | 1256 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2800 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-01-29 | 3768 | keep | 0 | Jan | 2022 | 0.0025664 | 0.00085546 | Momentary | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:52 | 558 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2800 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-01-29 | 1674 | keep | 0 | Jan | 2022 | 0.0011402 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 1192 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA VICTORIA 38KV | M22012900057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-29 | 9536 | keep | 0 | Jan | 2022 | 0.0064949 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 3041 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA VICTORIA 38KV | M22012900057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-29 | 24328 | keep | 0 | Jan | 2022 | 0.01657 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 390 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA VICTORIA 38KV | M22012900057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-29 | 3120 | keep | 0 | Jan | 2022 | 0.002125 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 650 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA VICTORIA 38KV | M22012900057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-29 | 5200 | keep | 0 | Jan | 2022 | 0.0035417 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 569 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 4552 | keep | 0 | Jan | 2022 | 0.0031003 | 0.00038754 | Sustained | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 1245 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 9960 | keep | 0 | Jan | 2022 | 0.0067837 | 0.00084796 | Sustained | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 1155 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 9240 | keep | 0 | Jan | 2022 | 0.0062933 | 0.00078667 | Sustained | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 867 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 6936 | keep | 0 | Jan | 2022 | 0.0047241 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 257 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 2056 | keep | 0 | Jan | 2022 | 0.0014003 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 1336 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 10688 | keep | 0 | Jan | 2022 | 0.0072795 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 3315 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 26520 | keep | 0 | Jan | 2022 | 0.018063 | 0.0022578 | Sustained | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:57 | 1718 | 000:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38KV Y LINEA 2500 | M22012900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2022-01-29 | 13744 | keep | 0 | Jan | 2022 | 0.009361 | 0.0011701 | Sustained | FALSE | FALSE | Not_TMED_Event | 1718
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:58 | 154 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV Y LINEA 15900 | M22012900053 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-01-29 | 1386 | keep | 0 | Jan | 2022 | 0.000944 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:58 | 1261 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV Y LINEA 15900 | M22012900053 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-01-29 | 11349 | keep | 0 | Jan | 2022 | 0.0077298 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:58 | 3894 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV Y LINEA 15900 | M22012900053 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-01-29 | 35046 | keep | 0 | Jan | 2022 | 0.02387 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:58 | 997 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV Y LINEA 15900 | M22012900053 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-01-29 | 8973 | keep | 0 | Jan | 2022 | 0.0061115 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2022-01-29 23:49 | 2022-01-29 23:58 | 1497 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV Y LINEA 15900 | M22012900053 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-01-29 | 13473 | keep | 0 | Jan | 2022 | 0.0091764 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
AGUADILLA | 2022-01-29 23:57 | 2022-01-30 08:17 | 150 | 008:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M22012900037 | New_Event |  |  | Include | Wildlife | 500 | 2022-01-29 | 75000 | keep | 0 | Jan | 2022 | 0.051082 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-01-30 01:15 | 2022-01-30 09:28 | 8 | 008:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR RATON CRUZO FASE | P22013000001 | New_Event |  |  | Include | Wildlife | 493 | 2022-01-30 | 3944 | keep | 0 | Jan | 2022 | 0.0026862 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-01-30 06:10 | 2022-01-30 12:32 | 90 | 006:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C22013000010 | New_Event | Cutout Failure | Include | Include | Equipment | 382 | 2022-01-30 | 34380 | keep | 0 | Jan | 2022 | 0.023416 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-01-30 07:12 | 2022-01-30 09:31 | 7621 | 002:19 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR 3 VECES QUEDO FUERA TIENE RISER DE SALIDA AVERIADO SE TRANSFIRIO 5027 CLIENTES AL 1646-03 Y 2594 CLIENTES AL 2402-03 | R22013000002 | New_Event | UG Cable Fault | Include | Include | Equipment | 139 | 2022-01-30 | 1059319 | keep | 0 | Jan | 2022 | 0.7215 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
HUMACAO | 2022-01-30 07:16 | 2022-01-30 10:41 | 90 | 003:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C22013000016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 205 | 2022-01-30 | 18450 | keep | 0 | Jan | 2022 | 0.012566 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-01-30 08:17 | 2022-01-30 09:51 | 125 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA PALOMA CRUZO FASE | P22013000005 | New_Event |  |  | Include | Wildlife | 94 | 2022-01-30 | 11750 | keep | 0 | Jan | 2022 | 0.0080029 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-01-30 08:37 | 2022-01-30 10:59 | 30 | 002:22 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE RELOCALIZO SECUNDARIA POR POSTE SECUNDARIO PARTIDO | B22013000004 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 142 | 2022-01-30 | 4260 | keep | 0 | Jan | 2022 | 0.0029015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-01-30 09:31 | 2022-01-30 10:27 | 2594 | 000:56 | P | CABLE SOTERRADO AVERIADO | SE CERRO N/O DEL 2404-06 CON 2402-03 RISER DE SALIDA AVERIADO DEL 2404-06 | R22013000002 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 56 | 2022-01-30 | 145264 | keep | 0 | Jan | 2022 | 0.098939 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-30 09:42 | 2022-01-30 11:30 | 1 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER NO SE INFORMO CAUSA | M22013000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-01-30 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-30 10:07 | 2022-01-30 10:58 | 1569 | 000:51 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES EN CARR 183 FTE BERTOS EQUIPMENT AND REPAIR | C22013000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-01-30 | 80019 | keep | 0 | Jan | 2022 | 0.054501 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
SAN JUAN | 2022-01-30 10:15 | 2022-01-30 11:34 | 1483 | 001:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR PARTIDO AVE. DE DIEGO FTE. VENUS GARDEN SU 30% DE SU CARGA POR 1336-8 | S22013000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 79 | 2022-01-30 | 117157 | keep | 0 | Jan | 2022 | 0.079795 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-30 10:15 | 2022-01-30 11:34 | 2500 | 001:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR PARTIDO Y SE CERRO SU-2 CARR.181 INT.PR-3 SU CARGA POR 1336-8 | S22013000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 79 | 2022-01-30 | 197500 | keep | 0 | Jan | 2022 | 0.13452 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
SAN JUAN | 2022-01-30 10:15 | 2022-01-30 11:09 | 5290 | 000:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECERRO SE ABRIO MACHETE CARR181 INT.PR-3 N/O CONTRA 1204-5 Y SE PROBO POR CONTROL QUEDO EN SERVICIO 1336-8 Y 9 QUEDO FUERA PARTE DEL 1204-5 Y 1204-4 | S22013000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 54 | 2022-01-30 | 285660 | keep | 0 | Jan | 2022 | 0.19456 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-30 10:15 | 2022-01-30 11:09 | 207 | 000:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE SECCIONALIZO SE ENCONTRO AISLADOR PARTIDO AVE. VENUS GARDEN SU CARGA POR 1336-8 | S22013000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 54 | 2022-01-30 | 11178 | keep | 0 | Jan | 2022 | 0.0076133 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
FAJARDO | 2022-01-30 10:15 | 2022-01-30 13:59 | 30 | 003:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TANSFORMADOR | R22013000077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-01-30 | 6720 | keep | 0 | Jan | 2022 | 0.004577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-30 10:24 | 2022-01-30 12:20 | 50 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA PERSONAL NO ENCONTRO CAUSA | A22013000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-01-30 | 5800 | keep | 0 | Jan | 2022 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-30 10:36 | 2022-01-30 14:05 | 16 | 003:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | R22013000080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 209 | 2022-01-30 | 3344 | keep | 0 | Jan | 2022 | 0.0022776 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-01-30 10:58 | 2022-01-30 11:44 | 157 | 000:46 | P | NO SE REPORTO CAUSA | SE PATRULLO ALIMENTADOR NO SE ENCONTRO CAUSA Y CERRARON MACHETES EN CARR 183 FTE BERTOS EQUIPMENT AND REPAIR | C22013000029 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-01-30 | 7222 | keep | 0 | Jan | 2022 | 0.0049189 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-30 11:00 | 2022-01-30 12:05 | 6 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | P22013000012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-01-30 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-01-30 11:15 | 2022-01-30 11:51 | 3 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22013000009 | New_Event | Wire Down | Include | Include | Equipment | 36 | 2022-01-30 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-01-30 11:18 | 2022-01-30 12:59 | 46 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER HACIA T-6 NO CAUSA | R22013000087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-01-30 | 4646 | keep | 0 | Jan | 2022 | 0.0031644 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
CAGUAS | 2022-01-30 11:26 | 2022-01-30 12:15 | 1 | 000:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETEZAR Y FIJAR LINEA PRIMARIA. | C22013000034 | New_Event | Wire Down | Include | Include | Equipment | 49 | 2022-01-30 | 49 | keep | 0 | Jan | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-30 11:29 | 2022-01-30 11:30 | 7000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 1206-03 LLEVA 70% CARGA DEL 1204-05 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 7000 | keep | 0 | Jan | 2022 | 0.0047677 | 0.0047677 | Momentary | FALSE | FALSE | Not_TMED_Event | 7000
CAGUAS | 2022-01-30 11:30 | 2022-01-30 15:58 | 1 | 004:28 | P | DESGANCHE | 1 X 40 EN C/L | C22013000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-01-30 | 268 | keep | 0 | Jan | 2022 | 0.00018253 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-30 11:34 | 2022-01-30 12:24 | 800 | 000:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR PARTIDO AVE. DE DIEGO FTE. VENUS GARDEN SU CARGA POR 1336-8 | S22013000010 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 50 | 2022-01-30 | 40000 | keep | 0 | Jan | 2022 | 0.027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-30 11:38 | 2022-01-30 11:39 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22013000054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 3701 | keep | 0 | Jan | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2022-01-30 11:46 | 2022-01-30 11:47 | 718 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 90% DEL 1901-5 | S22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 718 | keep | 0 | Jan | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2022-01-30 11:46 | 2022-01-30 11:47 | 540 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1330-1 | S22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2022-01-30 11:48 | 2022-01-30 11:49 | 1153 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22013000056 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-30 | 1153 | keep | 0 | Jan | 2022 | 0.0007853 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-30 11:49 | 2022-01-30 12:30 | 12 | 000:41 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA DEL SU - 5 @ T - 46 | C22012900056 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 41 | 2022-01-30 | 492 | keep | 0 | Jan | 2022 | 0.0003351 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-30 11:50 | 2022-01-30 14:14 | 50 | 002:24 | P | NO SE REPORTO CAUSA | 1 X 25 Y 1 X 30 EN DISTINTOS CORTES DE LINEA INFORMARON QUE NO SE ENCONTRO CAUSA PARA LOS FUSIBLES FUNDIDOS | A22013000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-01-30 | 7200 | keep | 0 | Jan | 2022 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-30 12:13 | 2022-01-30 13:53 | 10 | 001:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR 37 KVA | B22013000011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2022-01-30 | 1000 | keep | 0 | Jan | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-30 12:28 | 2022-01-30 13:42 | 20 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22013000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-01-30 | 1480 | keep | 0 | Jan | 2022 | 0.001008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-30 12:30 | 2022-01-30 12:31 | 1153 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO INTERRUPTOR EN SERVICIO | C22013000068 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-30 | 1153 | keep | 0 | Jan | 2022 | 0.0007853 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-30 12:31 | 2022-01-30 13:43 | 12 | 001:12 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA DEL SU - 5 @ T - 46 | C22012900056 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 72 | 2022-01-30 | 864 | keep | 0 | Jan | 2022 | 0.00058847 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-30 12:35 | 2022-01-30 16:34 | 1 | 003:59 | P | PARARRAYOS DEFECTUOSO | 2 X 10 EN BANCO DE TRANSFORMADORES REMPLAZO PARARRAYO | C22013000069 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 239 | 2022-01-30 | 239 | keep | 0 | Jan | 2022 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-30 13:07 | 2022-01-30 16:00 | 4 | 002:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22013000019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 173 | 2022-01-30 | 692 | keep | 0 | Jan | 2022 | 0.00047132 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-30 13:22 | 2022-01-30 14:07 | 15 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22013000013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-01-30 | 675 | keep | 0 | Jan | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-30 13:43 | 2022-01-30 13:44 | 1153 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22013000082 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-30 | 1153 | keep | 0 | Jan | 2022 | 0.0007853 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-30 13:44 | 2022-01-30 13:46 | 12 | 000:02 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA DEL SU - 5 @ T - 46 | C22012900056 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 2 | 2022-01-30 | 24 | keep | 0 | Jan | 2022 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-30 13:46 | 2022-01-30 13:47 | 1153 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22013000083 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-30 | 1153 | keep | 0 | Jan | 2022 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2022-01-30 13:47 | 2022-01-30 14:13 | 1153 | 000:26 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR POR MACHETE Y CAMPANA QUEMADOS | C22013000085 | New_Event | Switch Failure | Include | Include | Equipment | 26 | 2022-01-30 | 29978 | keep | 0 | Jan | 2022 | 0.020418 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
SAN JUAN | 2022-01-30 13:50 | 2022-01-30 13:52 | 726 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1346-4 | S22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-30 | 1452 | keep | 0 | Jan | 2022 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-01-30 13:50 | 2022-01-30 13:52 | 3932 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-3 | S22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-30 | 7864 | keep | 0 | Jan | 2022 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
CANOVANAS | 2022-01-30 13:55 | 2022-01-31 11:52 | 11 | 021:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA PEDESTAL AVERIADA | R22013000094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1317 | 2022-01-30 | 14487 | keep | 0 | Jan | 2022 | 0.009867 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-01-30 14:00 | 2022-01-30 18:08 | 60 | 004:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22013000308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2022-01-30 | 14880 | keep | 0 | Jan | 2022 | 0.010135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-30 14:11 | 2022-01-30 15:00 | 1 | 000:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22013000015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-01-30 | 49 | keep | 0 | Jan | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-30 14:13 | 2022-01-30 15:02 | 12 | 000:49 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA DEL SU - 5 @ T - 46 | C22012900056 | New_Event | UG Cable Fault | Include | Include | Equipment | 49 | 2022-01-30 | 588 | keep | 0 | Jan | 2022 | 0.00040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-30 14:13 | 2022-01-30 15:02 | 12 | 000:49 | P | DESCONECTIVO DEFECTUOSO | SE HIZO BY PASS EN EL SU - 3A POR MACHETE Y CAMPANA QUEMADOS | C22013000105 | Partial_restoration | Switch Failure | Include | Include | Equipment | 49 | 2022-01-30 | 588 | keep | 0 | Jan | 2022 | 0.00040048 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-30 14:37 | 2022-01-30 18:12 | 156 | 003:35 | P | DESGANCHE | DESGANCHO, RETIRO REPTIL Y CERRO PUENTE | C22013000138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-01-30 | 33540 | keep | 0 | Jan | 2022 | 0.022844 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
CAGUAS | 2022-01-30 15:02 | 2022-01-30 15:33 | 1153 | 000:31 | T | DESCONECTIVO DEFECTUOSO | DISPARO | C22013000105 | Additional_clients | Switch Failure | Include | Include | Equipment | 31 | 2022-01-30 | 35743 | keep | 0 | Jan | 2022 | 0.024344 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-30 15:25 | 2022-01-30 16:20 | 12 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA LEVANTAR SECUNDARIA | S22013000292 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-01-30 | 660 | keep | 0 | Jan | 2022 | 0.00044952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-30 15:33 | 2022-01-30 17:01 | 12 | 001:28 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA DEL SU - 5 @ T - 46 | C22012900056 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 88 | 2022-01-30 | 1056 | keep | 0 | Jan | 2022 | 0.00071924 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-30 15:33 | 2022-01-30 18:04 | 12 | 002:31 | P | DESCONECTIVO DEFECTUOSO | SE HIZO BY PASS EN EL SU - 3A POR MACHETE Y CAMPANA QUEMADOS | C22013000105 | Partial_restoration | Switch Failure | Include | Include | Equipment | 151 | 2022-01-30 | 1812 | keep | 0 | Jan | 2022 | 0.0012341 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-30 15:34 | 2022-01-30 17:51 | 16 | 002:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA SE DEJO CLIENTE CON PROA FUERA | R22013000080 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 137 | 2022-01-30 | 2192 | keep | 0 | Jan | 2022 | 0.001493 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-30 15:57 | 2022-01-30 19:21 | 1483 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ENCONTRO PUENTE ABIERTO RAMAL 8 FTE. MALL OF SAN JUAN Y AISLADOR PARTIDO CALLE ANA OTERO RES. RAMOS ANTONINI 30% DE SU CARGA POR 1336-8 | S22013000292 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2022-01-30 | 302532 | keep | 0 | Jan | 2022 | 0.20605 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-30 15:57 | 2022-01-30 19:22 | 2500 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ENCONTRO PUENTE ABIERTO RAMAL 8 FTE. MALL OF SAN JUAN Y AISLADOR PARTIDO CALLE ANA OTERO RES. RAMOS ANTONINI SU CARGA POR 1336-8 | S22013000292 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2022-01-30 | 512500 | keep | 0 | Jan | 2022 | 0.34906 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
SAN JUAN | 2022-01-30 15:57 | 2022-01-30 19:22 | 5290 | 003:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ENCONTRO PUENTE ABIERTO RAMAL 8 FTE. MALL OF SAN JUAN Y AISLADOR PARTIDO CALLE ANA OTERO RES. RAMOS ANTONINI | S22013000292 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2022-01-30 | 1084450 | keep | 0 | Jan | 2022 | 0.73861 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-30 15:57 | 2022-01-30 19:22 | 207 | 003:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ENCONTRO PUENTE ABIERTO RAMAL 8 FTE. MALL OF SAN JUAN Y AISLADOR PARTIDO CALLE ANA OTERO RES. RAMOS ANTONINI SU CARGA POR 1336-8 | S22013000292 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2022-01-30 | 42435 | keep | 0 | Jan | 2022 | 0.028902 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-01-30 16:01 | 2022-01-30 16:02 | 870 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1303-04 | S22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 870 | keep | 0 | Jan | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2022-01-30 16:17 | 2022-01-30 16:58 | 99 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R22013000097 | New_Event |  |  | Include | Wildlife | 41 | 2022-01-30 | 4059 | keep | 0 | Jan | 2022 | 0.0027646 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
HUMACAO | 2022-01-30 16:54 | 2022-01-30 18:09 | 200 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN LA SALIDA DEL CONVERTIDOR | C22013000130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-01-30 | 15000 | keep | 0 | Jan | 2022 | 0.010216 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-01-30 17:01 | 2022-01-30 18:45 | 14 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE REPORTO CAUSA | M22013000026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-01-30 | 1456 | keep | 0 | Jan | 2022 | 0.00099167 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2022-01-30 17:26 | 2022-01-30 18:35 | 12 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22013000028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2022-01-30 | 828 | keep | 0 | Jan | 2022 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-30 17:32 | 2022-01-30 18:25 | 6 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22013000135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-01-30 | 318 | keep | 0 | Jan | 2022 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-30 17:36 | 2022-01-30 18:12 | 1569 | 000:36 | T | DESGANCHE | DISPARO | C22013000138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-01-30 | 56484 | keep | 0 | Jan | 2022 | 0.038471 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2022-01-30 18:11 | 2022-01-30 20:13 | 50 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | C22013000144 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-01-30 | 6100 | keep | 0 | Jan | 2022 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-30 18:12 | 2022-01-30 20:15 | 156 | 002:03 | P | DESGANCHE | DESGANCHO, RETIRO REPTIL Y CERRO PUENTE | C22013000138 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-01-30 | 19188 | keep | 0 | Jan | 2022 | 0.013069 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-30 18:18 | 2022-01-30 21:46 | 80 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22013000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-01-30 | 16640 | keep | 0 | Jan | 2022 | 0.011333 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-01-30 18:25 | 2022-01-30 23:07 | 4 | 004:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C22013000146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 282 | 2022-01-30 | 1128 | keep | 0 | Jan | 2022 | 0.00076828 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-01-30 18:34 | 2022-01-31 11:54 | 1 | 017:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | R22013000099 | New_Event | Cutout Failure | Include | Include | Equipment | 1040 | 2022-01-30 | 1040 | keep | 0 | Jan | 2022 | 0.00070834 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-30 18:56 | 2022-01-31 09:35 | 1 | 014:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22013000152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 879 | 2022-01-30 | 879 | keep | 0 | Jan | 2022 | 0.00059868 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-30 19:34 | 2022-01-30 22:42 | 57 | 003:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22013000024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-01-30 | 10716 | keep | 0 | Jan | 2022 | 0.0072986 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2022-01-30 19:37 | 2022-01-30 19:38 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1303-5 | S22013000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 225 | keep | 0 | Jan | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
BAYAMON | 2022-01-30 19:45 | 2022-01-30 19:47 | 1984 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1911-7 SE PROBO QUEDO EN SERVICIO | S22013000678 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-30 | 3968 | keep | 0 | Jan | 2022 | 0.0027026 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-01-30 19:45 | 2022-01-30 19:47 | 577 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1529-12 | S22013000678 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-30 | 1154 | keep | 0 | Jan | 2022 | 0.00078598 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
MAYAGÃœEZ | 2022-01-30 20:10 | 2022-01-31 10:19 | 12 | 014:09 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR PERSONAL NO ENCONTRO CAUSA | M22013000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 849 | 2022-01-30 | 10188 | keep | 0 | Jan | 2022 | 0.006939 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-01-30 20:12 | 2022-01-30 23:18 | 20 | 003:06 | P | DESGANCHE | 1 X 20 EN C/L | R22013000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-01-30 | 3720 | keep | 0 | Jan | 2022 | 0.0025337 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-30 20:15 | 2022-01-30 20:41 | 1569 | 000:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL BKR PARA CERRAR PUENTE EN EL TRONCAL | C22013000101 | New_Event | Wire Down | Include | Include | Equipment | 26 | 2022-01-30 | 40794 | keep | 0 | Jan | 2022 | 0.027785 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
HUMACAO | 2022-01-30 20:30 | 2022-01-31 11:06 | 8 | 014:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REGULARLO Y SE REEMPLAZO BAJANTE SECUNDARIO | C22013000174 | New_Event | Secondary Wire Down | Include | Include | Equipment | 876 | 2022-01-30 | 7008 | keep | 0 | Jan | 2022 | 0.0047731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 1076 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 27976 | keep | 0 | Jan | 2022 | 0.019054 | 0.00073286 | Sustained | FALSE | FALSE | Not_TMED_Event | 1076
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 595 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 15470 | keep | 0 | Jan | 2022 | 0.010537 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 1007 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 13 KV | P22013000075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 26182 | keep | 0 | Jan | 2022 | 0.017832 | 0.00068586 | Sustained | FALSE | FALSE | Not_TMED_Event | 1007
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 9 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 234 | keep | 0 | Jan | 2022 | 0.00015938 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 3744 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 97344 | keep | 0 | Jan | 2022 | 0.066301 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 2379 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 61854 | keep | 0 | Jan | 2022 | 0.042128 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 778 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 20228 | keep | 0 | Jan | 2022 | 0.013777 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 1746 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 45396 | keep | 0 | Jan | 2022 | 0.030919 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2022-01-30 20:54 | 2022-01-30 21:20 | 11 | 000:26 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4600 DEJO FUERA DE SERVICIO BARRA DE RAMBLA 38KV | P22013000090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 26 | 2022-01-30 | 286 | keep | 0 | Jan | 2022 | 0.00019479 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-01-30 21:37 | 2022-01-31 12:12 | 12 | 014:35 | P | TRANSFORMADOR AVERIADO | REEMPLAZAR XMR AVERIADA 50KVA X 50KVA | R22013000105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 875 | 2022-01-30 | 10500 | keep | 0 | Jan | 2022 | 0.0071515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-30 21:45 | 2022-01-30 21:46 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22013000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-30 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2022-01-31 00:36 | 2022-01-31 04:20 | 150 | 003:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M22013100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-01-31 | 33600 | keep | 0 | Jan | 2022 | 0.022885 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-01-31 00:59 | 2022-01-31 09:59 | 10 | 009:00 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B22013100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 540 | 2022-01-31 | 5400 | keep | 0 | Jan | 2022 | 0.0036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-31 00:59 | 2022-01-31 09:59 | 10 | 009:00 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | B22013100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 540 | 2022-01-31 | 5400 | keep | 0 | Jan | 2022 | 0.0036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-31 01:44 | 2022-01-31 13:08 | 10 | 011:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | A22013100001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 684 | 2022-01-31 | 6840 | keep | 0 | Jan | 2022 | 0.0046587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-31 02:31 | 2022-01-31 02:32 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22013100002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
CAGUAS | 2022-01-31 03:10 | 2022-01-31 16:54 | 10 | 013:44 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL SU#5 AL T-46 SE CONSTRUYO AEREO PROVISIONAL DEL T-40 AL T-46 | C22013000004 | New_Event | UG Cable Fault | Include | Include | Equipment | 824 | 2022-01-31 | 8240 | keep | 0 | Jan | 2022 | 0.0056122 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-31 03:34 | 2022-01-31 03:35 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 3458 | keep | 0 | Jan | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-01-31 05:03 | 2022-01-31 10:48 | 1 | 005:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 Y 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y PARARRAYO | C22013100001 | New_Event | Cutout Failure | Include | Include | Equipment | 345 | 2022-01-31 | 345 | keep | 0 | Jan | 2022 | 0.00023498 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-31 07:07 | 2022-01-31 07:08 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
MAYAGÃœEZ | 2022-01-31 07:11 | 2022-01-31 17:15 | 7 | 010:04 | P | OTRAS CAUSAS | AVERIA SOTERRADA EN FID 19476105 SE DEJO ABIERTO Y CON TAG Y SE CERRO EL N/O EN FID 119476182 INFORMO EL JOURNEYMAN QUE LA AVERIA ES PRIVADA | M22013100010 | New_Event | Other Causes | Include | Include | Other | 604 | 2022-01-31 | 4228 | keep | 0 | Jan | 2022 | 0.0028797 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-01-31 07:26 | 2022-01-31 13:13 | 30 | 005:47 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22013100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2022-01-31 | 10410 | keep | 0 | Jan | 2022 | 0.0070902 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-31 07:35 | 2022-01-31 11:05 | 60 | 003:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22013100007 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2022-01-31 | 12600 | keep | 0 | Jan | 2022 | 0.0085818 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-01-31 07:37 | 2022-01-31 11:15 | 10 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO CAUSA | C22013100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-01-31 | 2180 | keep | 0 | Jan | 2022 | 0.0014848 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-31 07:47 | 2022-01-31 07:48 | 1986 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR RAMA SOBRE LAS LINEAS | A22013100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-31 | 1986 | keep | 0 | Jan | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-01-31 07:48 | 2022-01-31 10:39 | 6 | 002:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22013100009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-01-31 | 1026 | keep | 0 | Jan | 2022 | 0.0006988 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-01-31 07:49 | 2022-01-31 07:50 | 2565 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22013100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2565 | keep | 0 | Jan | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-01-31 07:55 | 2022-01-31 11:47 | 38 | 003:52 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | C22013100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-01-31 | 8816 | keep | 0 | Jan | 2022 | 0.0060045 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-31 07:55 | 2022-01-31 07:56 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-31 07:57 | 2022-01-31 07:58 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P220131000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-31 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
VEGA BAJA | 2022-01-31 07:57 | 2022-01-31 09:06 | 15 | 001:09 | P | PARARRAYOS DEFECTUOSO | 1X30 EN CORTE DE LINEA Y SE ELIMINO PARARRAYO DEFECTUOSO | B22013100005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 69 | 2022-01-31 | 1035 | keep | 0 | Jan | 2022 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-31 08:15 | 2022-01-31 08:16 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22013100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2999 | keep | 0 | Jan | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
HUMACAO | 2022-01-31 08:31 | 2022-01-31 16:14 | 6 | 007:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPPARAR BAJANTE SECUNDARIO | C22013100009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 463 | 2022-01-31 | 2778 | keep | 0 | Jan | 2022 | 0.0018921 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-01-31 08:38 | 2022-01-31 11:03 | 90 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | R22013100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-01-31 | 13050 | keep | 0 | Jan | 2022 | 0.0088883 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-01-31 08:59 | 2022-01-31 09:00 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2354 | keep | 0 | Jan | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2022-01-31 09:01 | 2022-01-31 10:21 | 828 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 60% DE LA CARGA POR EL 1206-04 | S22013100005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2022-01-31 | 66240 | keep | 0 | Jan | 2022 | 0.045116 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-01-31 09:01 | 2022-01-31 10:21 | 1977 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 40% DE LA CARGA POR EL 1206-04 | S22013100005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2022-01-31 | 158160 | keep | 0 | Jan | 2022 | 0.10772 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-01-31 09:01 | 2022-01-31 10:21 | 1799 | 001:20 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y CRUCETA LLEVA 40% DEL 1204-04 60% DEL 1204-03 | S22013100005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2022-01-31 | 143920 | keep | 0 | Jan | 2022 | 0.098023 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
HUMACAO | 2022-01-31 09:23 | 2022-01-31 09:24 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22013100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2354 | keep | 0 | Jan | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
ARECIBO | 2022-01-31 09:25 | 2022-01-31 12:00 | 7 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22013100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2022-01-31 | 1085 | keep | 0 | Jan | 2022 | 0.00073899 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-01-31 09:32 | 2022-01-31 14:31 | 50 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22013100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-01-31 | 14950 | keep | 0 | Jan | 2022 | 0.010182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-01-31 09:47 | 2022-01-31 16:58 | 1 | 007:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA POR OTRO DE 25KVA | A22013100017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 431 | 2022-01-31 | 431 | keep | 0 | Jan | 2022 | 0.00029355 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-31 09:58 | 2022-01-31 17:23 | 9 | 007:25 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C22013100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 445 | 2022-01-31 | 4005 | keep | 0 | Jan | 2022 | 0.0027278 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-01-31 10:09 | 2022-01-31 11:14 | 1 | 001:05 | P | NO SE REPORTO CAUSA | 2X15 EN BANCO DE TRANSFORMADORES BOMBA DE AUTORIDAD DE ACUEDUCTOS Y ALCANTARILLADOS | B22013100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-01-31 | 65 | keep | 0 | Jan | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-31 10:28 | 2022-01-31 12:11 | 7 | 001:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA X 75KVA | A22013100024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 103 | 2022-01-31 | 721 | keep | 0 | Jan | 2022 | 0.00049107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-01-31 10:32 | 2022-01-31 11:08 | 10 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22013000081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-01-31 | 360 | keep | 0 | Jan | 2022 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-31 10:41 | 2022-01-31 20:01 | 100 | 009:20 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | S22013100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 560 | 2022-01-31 | 56000 | keep | 0 | Jan | 2022 | 0.038141 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-31 10:46 | 2022-01-31 14:40 | 10 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 20 EN XMR SE REPARO BAJANTE SECUNDARIO | C22013100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2022-01-31 | 2340 | keep | 0 | Jan | 2022 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-31 10:50 | 2022-01-31 12:10 | 1 | 001:20 | P | OTRAS CAUSAS | 1 X 10 EN XMR FUSIBLE CORROIDO | R22013100011 | New_Event | Other Causes | Include | Include | Other | 80 | 2022-01-31 | 80 | keep | 0 | Jan | 2022 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-01-31 11:20 | 2022-01-31 11:32 | 40 | 000:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | P22013100059 | New_Event |  |  | Include | Wildlife | 12 | 2022-01-31 | 480 | keep | 0 | Jan | 2022 | 0.00032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-31 11:24 | 2022-01-31 12:06 | 1 | 000:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN C/L CRUCE POR AVE | C22013100034 | New_Event |  |  | Include | Wildlife | 42 | 2022-01-31 | 42 | keep | 0 | Jan | 2022 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-31 11:29 | 2022-01-31 11:30 | 3406 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 3406 | keep | 0 | Jan | 2022 | 0.0023198 | 0.0023198 | Momentary | FALSE | FALSE | Not_TMED_Event | 3406
PONCE | 2022-01-31 11:34 | 2022-01-31 17:22 | 10 | 005:48 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE CAJA DE TRANSFORMADOR PARA CAMBIAR POSTE SECUNDARIO | P22013100060 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 348 | 2022-01-31 | 3480 | keep | 0 | Jan | 2022 | 0.0023702 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-31 12:10 | 2022-01-31 12:25 | 5 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22013100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-01-31 | 75 | keep | 0 | Jan | 2022 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-01-31 12:14 | 2022-01-31 12:17 | 4882 | 0:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR PUENTE PRIMARIO ABIERTO | M22013100032 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-01-31 | 14646 | keep | 0 | Jan | 2022 | 0.0099753 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-01-31 12:17 | 2022-01-31 17:17 | 60 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M22013100033 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 300 | 2022-01-31 | 18000 | keep | 0 | Jan | 2022 | 0.01226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-01-31 12:19 | 2022-01-31 12:42 | 15 | 000:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO HOT CLAMP DEFECTUOSO EN BAJANTE PRIMARIO DE TRANSFORMADOR | P22013100065 | New_Event | Wire Down | Include | Include | Equipment | 23 | 2022-01-31 | 345 | keep | 0 | Jan | 2022 | 0.00023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-31 12:31 | 2022-01-31 12:32 | 154 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 1342-04 LLEVA 25% DEL 1203-03 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 154 | keep | 0 | Jan | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-01-31 12:31 | 2022-01-31 12:32 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1342-04 LLEVA 25% DEL 1203-03 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
CANOVANAS | 2022-01-31 12:52 | 2022-01-31 16:02 | 50 | 003:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R22013100018 | New_Event | Wire Down | Include | Include | Equipment | 190 | 2022-01-31 | 9500 | keep | 0 | Jan | 2022 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-31 13:06 | 2022-01-31 15:35 | 20 | 002:29 | P | DESGANCHE | 1X40 EN CORTE DE LINEA | B22013100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-01-31 | 2980 | keep | 0 | Jan | 2022 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-01-31 13:18 | 2022-01-31 14:54 | 130 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 65 EN CORTES DE LINEA CRUCE X AVE | R22013100022 | New_Event |  |  | Include | Wildlife | 96 | 2022-01-31 | 12480 | keep | 0 | Jan | 2022 | 0.0085001 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
FAJARDO | 2022-01-31 13:23 | 2022-01-31 14:21 | 12 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22013100023 | New_Event |  |  | Include | Wildlife | 58 | 2022-01-31 | 696 | keep | 0 | Jan | 2022 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-31 13:26 | 2022-01-31 13:27 | 1105 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22013100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 1105 | keep | 0 | Jan | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2022-01-31 13:46 | 2022-01-31 15:30 | 1 | 001:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO NEUTRAL PARTIDO | A22013100032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 104 | 2022-01-31 | 104 | keep | 0 | Jan | 2022 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-31 13:55 | 2022-01-31 15:06 | 8 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LE REPARO LINEA SECUNDARIA | B22013100028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-01-31 | 568 | keep | 0 | Jan | 2022 | 0.00038686 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-01-31 14:23 | 2022-02-01 11:44 | 10 | 021:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO DE XMR AVERIADO | C22013100049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1281 | 2022-01-31 | 12810 | keep | 0 | Jan | 2022 | 0.0087248 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-31 14:36 | 2022-01-31 21:36 | 3 | 007:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02, 1707-03, 1707-04, 1707-05 SE SECCIONALIZO ALIMENTADOR SE REPARO NEUTRAL SOBRE LINEA PRIMARIA - NO HUBO INTERRUPCION PARCIAL ALGUNA | B22013100031 | New_Event | Wire Down | Include | Include | Equipment | 420 | 2022-01-31 | 1260 | keep | 0 | Jan | 2022 | 0.00085818 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-31 14:36 | 2022-01-31 21:36 | 61 | 007:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02, 1707-03, 1707-04, 1707-05 SE SECCIONALIZO ALIMENTADOR SE REPARO NEUTRAL SOBRE LINEA PRIMARIA - NO HUBO INTERRUPCION PARCIAL ALGUNA | B22013100031 | New_Event | Wire Down | Include | Include | Equipment | 420 | 2022-01-31 | 25620 | keep | 0 | Jan | 2022 | 0.01745 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-01-31 14:36 | 2022-01-31 19:41 | 1501 | 005:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02, 1707-03, 1707-04, 1707-05 SE SECCIONALIZO ALIMENTADOR | B22013100031 | New_Event | Wire Down | Include | Include | Equipment | 305 | 2022-01-31 | 457805 | keep | 0 | Jan | 2022 | 0.31181 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-01-31 14:36 | 2022-01-31 21:36 | 546 | 007:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02, 1707-03, 1707-04, 1707-05 SE SECCIONALIZO ALIMENTADOR SE REPARO NEUTRAL SOBRE LINEA PRIMARIA | B22013100031 | New_Event | Wire Down | Include | Include | Equipment | 420 | 2022-01-31 | 229320 | keep | 0 | Jan | 2022 | 0.15619 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
CAGUAS | 2022-01-31 14:39 | 2022-01-31 17:43 | 8 | 003:04 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 37.5 KVA | C22013000102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 184 | 2022-01-31 | 1472 | keep | 0 | Jan | 2022 | 0.0010026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-01-31 14:43 | 2022-01-31 17:47 | 1812 | 003:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO INTERRUPTOR POR CONTROL | B22013100033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 184 | 2022-01-31 | 333408 | keep | 0 | Jan | 2022 | 0.22708 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
MAYAGÃœEZ | 2022-01-31 14:50 | 2022-01-31 18:53 | 4 | 004:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | M22013100050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 243 | 2022-01-31 | 972 | keep | 0 | Jan | 2022 | 0.00066202 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-31 14:58 | 2022-01-31 20:02 | 40 | 005:04 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | S22013100059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-01-31 | 12160 | keep | 0 | Jan | 2022 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-31 15:16 | 2022-01-31 19:52 | 30 | 004:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C22013100053 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2022-01-31 | 8280 | keep | 0 | Jan | 2022 | 0.0056395 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-01-31 15:17 | 2022-01-31 16:31 | 1 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22013100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-01-31 | 74 | keep | 0 | Jan | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-31 15:34 | 2022-01-31 19:39 | 50 | 004:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100AMP EN CORTE DE LINEA | M22013100057 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2022-01-31 | 12250 | keep | 0 | Jan | 2022 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-31 15:41 | 2022-01-31 16:57 | 1512 | 001:16 | P | DESGANCHE | SE ABRIO MACHETE HACIA CAMINO LOS GUANOS Y SE CERRO BKR. 100% CARGA 1346-6 Y 90% 1303-1 | S22013100166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-01-31 | 114912 | keep | 0 | Jan | 2022 | 0.078266 | 0.0010298 | Sustained | FALSE | FALSE | Not_TMED_Event | 1512
SAN JUAN | 2022-01-31 15:41 | 2022-01-31 18:17 | 225 | 002:36 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE CONTRA 1303-5 | S22013100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-01-31 | 35100 | keep | 0 | Jan | 2022 | 0.023906 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-31 15:41 | 2022-01-31 17:50 | 870 | 002:09 | T | DESGANCHE | SE ABRIO MACHETE CAMINO LOS MATOS Y SE CERRO INTERRUPTOR 40% EN SERVICIO Y FUERA EL 1303-4 | S22013100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-01-31 | 112230 | keep | 0 | Jan | 2022 | 0.076439 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-01-31 15:41 | 2022-01-31 16:57 | 1598 | 001:16 | T | DESGANCHE | SE ABRIO MACHETE HACIA CAMINO LOS GUANOS Y SE CERRO BKR. 100% CARGA 1346-6 Y 90% 1303-1 | S22013100166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-01-31 | 121448 | keep | 0 | Jan | 2022 | 0.082718 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2022-01-31 15:54 | 2022-01-31 16:57 | 7 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO Y CONECTORES | C22013100058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-01-31 | 441 | keep | 0 | Jan | 2022 | 0.00030036 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-31 16:08 | 2022-01-31 16:12 | 552 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 30% POR 1529-15 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-31 | 2208 | keep | 0 | Jan | 2022 | 0.0015039 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
BAYAMON | 2022-01-31 16:08 | 2022-01-31 16:12 | 1802 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERCIO LLEVA 30% 1346-2 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-31 | 7208 | keep | 0 | Jan | 2022 | 0.0049093 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-01-31 16:16 | 2022-01-31 19:35 | 1483 | 003:19 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRO MACHETE QUEDO EN SERVICIO 30% DE SU CARGA POR 1336-8 MAL TIEMPO | S22013100000 | New_Event | Bad Weather | Include | Include | Weather | 199 | 2022-01-31 | 295117 | keep | 0 | Jan | 2022 | 0.201 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-31 16:16 | 2022-01-31 17:47 | 2500 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | SE ABRIO MACHETE CARR.181 EXPRESO TRUJILLO Y SE CERRO SU-2 CARR.181 INT. PR-3 MAL TIEMPO | S22013100000 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2022-01-31 | 227500 | keep | 0 | Jan | 2022 | 0.15495 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
SAN JUAN | 2022-01-31 16:16 | 2022-01-31 17:13 | 5290 | 000:57 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE ABRIO N/O SU-2 1336-8 Y 1204-5 SE PROBO QUEDO EN SERVICIO 1336-8 Y 9 QUEDO FUERA PARTE 1204-4 Y 5 MAL TIEMPO | S22013100000 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2022-01-31 | 301530 | keep | 0 | Jan | 2022 | 0.20537 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-31 16:16 | 2022-01-31 17:13 | 207 | 000:57 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE ABRIO N/O SU-2 1336-8 Y 1204-5 SE PROBO QUEDO EN SERVICIO 1336-8 Y 9 QUEDO FUERA PARTE 1204-4 Y 5 MAL TIEMPO | S22013100000 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2022-01-31 | 11799 | keep | 0 | Jan | 2022 | 0.0080362 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-01-31 16:18 | 2022-01-31 22:43 | 1290 | 006:25 | S | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR DE PORTATIL #8 | S22013100486 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2022-01-31 | 496650 | keep | 0 | Jan | 2022 | 0.33827 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 16:39 | 137 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-01-31 | 822 | keep | 0 | Jan | 2022 | 0.00055986 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 16:39 | 457 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-01-31 | 2742 | keep | 0 | Jan | 2022 | 0.0018676 | 0.00031126 | Sustained | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 16:39 | 1225 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-01-31 | 7350 | keep | 0 | Jan | 2022 | 0.0050061 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 16:39 | 1452 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-01-31 | 8712 | keep | 0 | Jan | 2022 | 0.0059337 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 16:39 | 616 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-01-31 | 3696 | keep | 0 | Jan | 2022 | 0.0025173 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 20:12 | 7000 | 003:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO MACHETE 70% DE SU CARGA POR 1206-3 | S22013100401 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 219 | 2022-01-31 | 1533000 | keep | 0 | Jan | 2022 | 1.0441 | 0.0047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 7000
SAN JUAN | 2022-01-31 16:33 | 2022-01-31 18:52 | 3406 | 002:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETE PARA SECCIONALIZAR AISLADOR PARTIDO DEL 1204-5 Y SE CERRO INTERRUPTOR | S22013100401 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 139 | 2022-01-31 | 473434 | keep | 0 | Jan | 2022 | 0.32245 | 0.0023198 | Sustained | FALSE | FALSE | Not_TMED_Event | 3406
SAN JUAN | 2022-01-31 16:34 | 2022-01-31 20:21 | 727 | 003:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO N/O CONTRA 1620-2 | S22013100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 227 | 2022-01-31 | 165029 | keep | 0 | Jan | 2022 | 0.1124 | 0.00049516 | Sustained | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2022-01-31 16:34 | 2022-01-31 19:14 | 3718 | 002:40 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE ABRIO N/O CONTRA 1206-3 Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO QUEDO FUERA CARGA 1206-3 | S22013100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2022-01-31 | 594880 | keep | 0 | Jan | 2022 | 0.40517 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-01-31 16:49 | 2022-01-31 16:50 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1911-7 | S22013100532 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 1984 | keep | 0 | Jan | 2022 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-01-31 16:49 | 2022-01-31 16:50 | 577 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1529-12 | S22013100532 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 577 | keep | 0 | Jan | 2022 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
ARECIBO | 2022-01-31 16:55 | 2022-01-31 18:52 | 150 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR FUERTES VIENTOS | A22013100045 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2022-01-31 | 17550 | keep | 0 | Jan | 2022 | 0.011953 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-01-31 16:57 | 2022-01-31 19:53 | 168 | 002:56 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S22013100166 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-01-31 | 29568 | keep | 0 | Jan | 2022 | 0.020139 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-31 16:57 | 2022-01-31 21:55 | 18 | 004:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE SECCIONALIZO LINEA SECUNDARIA ROTA | M22013100064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 298 | 2022-01-31 | 5364 | keep | 0 | Jan | 2022 | 0.0036534 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-01-31 16:58 | 2022-02-01 11:32 | 36 | 018:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22013100596 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1114 | 2022-01-31 | 40104 | keep | 0 | Jan | 2022 | 0.027315 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-01-31 17:12 | 2022-01-31 18:39 | 23 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22013100057 | New_Event |  |  | Include | Wildlife | 87 | 2022-01-31 | 2001 | keep | 0 | Jan | 2022 | 0.0013629 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2022-01-31 17:24 | 2022-01-31 17:25 | 1702 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | C22013100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-01-31 | 1702 | keep | 0 | Jan | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-01-31 17:25 | 2022-01-31 20:50 | 84 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO | C22013100071 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 205 | 2022-01-31 | 17220 | keep | 0 | Jan | 2022 | 0.011728 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
HUMACAO | 2022-01-31 17:45 | 2022-01-31 18:32 | 6 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO | C22013100059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2022-01-31 | 282 | keep | 0 | Jan | 2022 | 0.00019207 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-31 17:47 | 2022-01-31 18:07 | 181 | 000:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO MACHETES | B22013100033 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 20 | 2022-01-31 | 3620 | keep | 0 | Jan | 2022 | 0.0024656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-31 17:50 | 2022-01-31 18:17 | 522 | 000:27 | P | DESGANCHE | SE REALIZE DESGANCHE Y SE CERRO MACHETE 100% EN SERVICIO 1303-5 Y 1303-4 | S22013100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 27 | 2022-01-31 | 14094 | keep | 0 | Jan | 2022 | 0.0095994 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-31 17:52 | 2022-01-31 17:53 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 4176 | keep | 0 | Jan | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-01-31 17:53 | 2022-01-31 17:54 | 3941 | 000:01 | T | DESGANCHE | RECERRO | B22013100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-31 | 3941 | keep | 0 | Jan | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-01-31 17:55 | 2022-01-31 17:57 | 948 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO PRO CONTROL QUEDO EN SERVICIO | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-31 | 1896 | keep | 0 | Jan | 2022 | 0.0012914 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
BAYAMON | 2022-01-31 18:07 | 2022-01-31 18:08 | 1812 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL | B22013100033 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-31 | 1812 | keep | 0 | Jan | 2022 | 0.0012341 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-31 18:08 | 2022-01-31 18:47 | 1268 | 000:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR | B22013100033 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 39 | 2022-01-31 | 49452 | keep | 0 | Jan | 2022 | 0.033682 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
CAGUAS | 2022-01-31 18:15 | 2022-01-31 19:14 | 7 | 000:59 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA RETIRAR ARBOL Y LEVANTAR SECUNDARIA | C22013100065 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 59 | 2022-01-31 | 413 | keep | 0 | Jan | 2022 | 0.00028129 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-31 18:32 | 2022-01-31 21:39 | 100 | 003:07 | P | DESGANCHE | 2 X 50 EN RISER Y 1 RBA DE 50 AMP EN SU - 3A | R22013100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-01-31 | 18700 | keep | 0 | Jan | 2022 | 0.012736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-31 18:39 | 2022-02-01 01:30 | 45 | 006:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22013100215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 411 | 2022-01-31 | 18495 | keep | 0 | Jan | 2022 | 0.012597 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-01-31 18:40 | 2022-01-31 18:55 | 1356 | 000:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22013100991 | New_Event | Wire Down | Include | Include | Equipment | 15 | 2022-01-31 | 20340 | keep | 0 | Jan | 2022 | 0.013853 | 0.00092357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1356
BAYAMON | 2022-01-31 18:40 | 2022-01-31 19:48 | 2466 | 001:08 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE REPORTO CAUSA | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-01-31 | 167688 | keep | 0 | Jan | 2022 | 0.11421 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2022-01-31 18:47 | 2022-01-31 21:41 | 181 | 002:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO MACHETES | B22013100033 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2022-01-31 | 31494 | keep | 0 | Jan | 2022 | 0.02145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-31 18:52 | 2022-02-01 03:43 | 44 | 008:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR ENDEREZO PARARRAYO Y REPARO BAJANTE PRIMARIO | R22013100088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 531 | 2022-01-31 | 23364 | keep | 0 | Jan | 2022 | 0.015913 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2022-01-31 18:55 | 2022-02-01 01:05 | 25 | 006:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE REMPLAZO CAJA QUEMADA | S22013101301 | Partial_restoration | Wire Down | Include | Include | Equipment | 370 | 2022-01-31 | 9250 | keep | 0 | Jan | 2022 | 0.0063001 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-31 18:55 | 2022-01-31 20:35 | 15 | 001:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA | B22013100233 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2022-01-31 | 1500 | keep | 0 | Jan | 2022 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-31 18:58 | 2022-01-31 23:54 | 100 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P22013100101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-01-31 | 29600 | keep | 0 | Jan | 2022 | 0.02016 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-01-31 19:01 | 2022-01-31 21:11 | 30 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR CONTACTO DE AVE | P22013100104 | New_Event |  |  | Include | Wildlife | 130 | 2022-01-31 | 3900 | keep | 0 | Jan | 2022 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-31 19:08 | 2022-01-31 19:11 | 1 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 3 | keep | 0 | Jan | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-31 19:08 | 2022-01-31 19:11 | 1964 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 5892 | keep | 0 | Jan | 2022 | 0.004013 | 0.0013377 | Momentary | FALSE | FALSE | Not_TMED_Event | 1964
BAYAMON | 2022-01-31 19:08 | 2022-01-31 19:11 | 733 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 2199 | keep | 0 | Jan | 2022 | 0.0014977 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-01-31 19:08 | 2022-01-31 19:11 | 10 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 30 | keep | 0 | Jan | 2022 | 2.0433e-05 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-31 19:08 | 2022-01-31 19:11 | 1825 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 5475 | keep | 0 | Jan | 2022 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-01-31 19:08 | 2022-01-31 19:11 | 4398 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 13194 | keep | 0 | Jan | 2022 | 0.0089864 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-01-31 19:08 | 2022-01-31 19:11 | 2782 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S22013100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-01-31 | 8346 | keep | 0 | Jan | 2022 | 0.0056844 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-01-31 19:20 | 2022-01-31 20:29 | 225 | 001:09 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-5 MAL TIEMPO | S22013100000 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-01-31 | 15525 | keep | 0 | Jan | 2022 | 0.010574 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-31 19:20 | 2022-01-31 20:29 | 870 | 001:09 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO MAL TIEMPO SE PROBO QUEDO EN SERVICIO LLEVA 1303-4 MAL TIEMPO | S22013100000 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-01-31 | 60030 | keep | 0 | Jan | 2022 | 0.040886 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2022-01-31 19:38 | 2022-01-31 19:39 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-01-31 19:38 | 2022-02-01 00:16 | 1834 | 004:38 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | B22013100275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-01-31 | 509852 | keep | 0 | Jan | 2022 | 0.34726 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
SAN JUAN | 2022-01-31 19:53 | 2022-01-31 20:04 | 1512 | 000:11 | P | DESGANCHE | AL CERRAR MACHETE CAMINO LOS GUANOS DISPARO BKR. SU CARGA POR 1303-4 | S22013100166 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 11 | 2022-01-31 | 16632 | keep | 0 | Jan | 2022 | 0.011328 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-31 19:53 | 2022-01-31 20:04 | 1598 | 000:11 | T | DESGANCHE | DISPARO AL CERRAR MACHETE CAMINO LOS GUANOS SU CARGA POR 1303-04 | S22013100166 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 11 | 2022-01-31 | 17578 | keep | 0 | Jan | 2022 | 0.011972 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-31 19:56 | 2022-02-01 17:24 | 100 | 021:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-1 | B22013100295 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1288 | 2022-01-31 | 128800 | keep | 0 | Jan | 2022 | 0.087725 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-31 19:58 | 2022-01-31 22:26 | 343 | 002:28 | S | PROTECCION DEFECTUOSA | SE ARREGLO PRESSURE RELEASE DE SUBESTACION | S22013101261 | New_Event | Protection Miscoordination | Include | Include | Other | 148 | 2022-01-31 | 50764 | keep | 0 | Jan | 2022 | 0.034575 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
BAYAMON | 2022-01-31 19:58 | 2022-01-31 22:26 | 996 | 002:28 | S | PROTECCION DEFECTUOSA | SE ARREGLO PRESSURE RELEASE DE SUBESTACION | S22013101261 | New_Event | Protection Miscoordination | Include | Include | Other | 148 | 2022-01-31 | 147408 | keep | 0 | Jan | 2022 | 0.1004 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
BAYAMON | 2022-01-31 19:58 | 2022-02-01 08:34 | 169 | 012:36 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | CARGA ESTABA POR EL 1116-05 Y SE NORMALIZO POR SU INTERRUPTOR | S22013101261 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 756 | 2022-01-31 | 127764 | keep | 0 | Jan | 2022 | 0.087019 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-01-31 19:58 | 2022-02-01 09:34 | 5 | 013:36 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO HACIA SU#27 | S22013101261 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 816 | 2022-01-31 | 4080 | keep | 0 | Jan | 2022 | 0.0027789 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-31 19:58 | 2022-02-01 08:34 | 466 | 012:36 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON OPERACIONES DE CAMPO Y ENTRA UN 50% EN SERVICIO LA CARGA DEL 1117-08 A TRAVEZ DE INTERRUPTOR DISPONIBLE 1116-4 | S22013101261 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 756 | 2022-01-31 | 352296 | keep | 0 | Jan | 2022 | 0.23995 | 0.00031739 | Sustained | FALSE | FALSE | Not_TMED_Event | 466
AGUADILLA | 2022-01-31 20:00 | 2022-01-31 22:41 | 25 | 002:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22013100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-01-31 | 4025 | keep | 0 | Jan | 2022 | 0.0027414 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-31 20:04 | 2022-01-31 22:15 | 168 | 002:11 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S22013100166 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-01-31 | 22008 | keep | 0 | Jan | 2022 | 0.01499 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-31 20:29 | 2022-02-01 09:37 | 50 | 013:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22013100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 788 | 2022-01-31 | 39400 | keep | 0 | Jan | 2022 | 0.026835 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-31 20:31 | 2022-01-31 20:50 | 60 | 000:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22013100339 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-01-31 | 1140 | keep | 0 | Jan | 2022 | 0.00077645 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-31 20:37 | 2022-01-31 20:38 | 154 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 25% POR 1342-4 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 154 | keep | 0 | Jan | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-01-31 20:37 | 2022-01-31 20:38 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1342-04 LLEVA 25% DEL 1203-03 | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
VEGA BAJA | 2022-01-31 20:58 | 2022-01-31 20:59 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2610 | keep | 0 | Jan | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
HUMACAO | 2022-01-31 21:01 | 2022-01-31 21:02 | 2873 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22013100097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2873 | keep | 0 | Jan | 2022 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
BAYAMON | 2022-01-31 21:08 | 2022-02-01 08:40 | 125 | 011:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L SE REMPLAZO CAJAS PRIMARIAS | S22013101426 | New_Event | Cutout Failure | Include | Include | Equipment | 692 | 2022-01-31 | 86500 | keep | 0 | Jan | 2022 | 0.058915 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-01-31 21:11 | 2022-02-01 12:55 | 50 | 015:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22013101430 | New_Event | Vegetation Contact | Include | Include | Vegetation | 944 | 2022-01-31 | 47200 | keep | 0 | Jan | 2022 | 0.032148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-31 21:15 | 2022-02-01 14:54 | 50 | 017:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22013101440 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1059 | 2022-01-31 | 52950 | keep | 0 | Jan | 2022 | 0.036064 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-31 21:17 | 2022-02-01 00:55 | 10 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22013100394 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-01-31 | 2180 | keep | 0 | Jan | 2022 | 0.0014848 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-31 21:19 | 2022-02-01 09:40 | 25 | 012:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L SE REMPLAZO AISLADOR PARTIDO | B22013100399 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 741 | 2022-01-31 | 18525 | keep | 0 | Jan | 2022 | 0.012617 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-31 21:21 | 2022-02-01 16:11 | 60 | 018:50 | P | DESGANCHE | 1 X 65 EN C/L Y 1 X 80 EN C/L SE REALIZO DESGANCHE | S22013101452 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1130 | 2022-01-31 | 67800 | keep | 0 | Jan | 2022 | 0.046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-31 21:21 | 2022-02-01 11:15 | 60 | 013:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | A22013100052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 834 | 2022-01-31 | 50040 | keep | 0 | Jan | 2022 | 0.034082 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-01-31 21:29 | 2022-02-01 09:46 | 60 | 012:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22013100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 737 | 2022-01-31 | 44220 | keep | 0 | Jan | 2022 | 0.030118 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-31 21:33 | 2022-01-31 21:36 | 1501 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | INTERRUPTOR PROVISIONAL 6 LLEVA LA CARGA DEL 1707-02, 1707-03, 1707-04, 1707-05 SE SECCIONALIZO ALIMENTADOR SE REPARO NEUTRAL SOBRE LINEA PRIMARIA - SE ABRIO MOMENTANEAMENTE EL BREAKER PARA CERRAR MACHETES | B22013100031 | Partial_restoration | Wire Down | Include | Include | Equipment | 3 | 2022-01-31 | 4503 | keep | 0 | Jan | 2022 | 0.003067 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-31 22:11 | 2022-02-01 13:32 | 200 | 015:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 1 X 80 SE RETEZO LINEAS | S22013101501 | New_Event | Wire Down | Include | Include | Equipment | 921 | 2022-01-31 | 184200 | keep | 0 | Jan | 2022 | 0.12546 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-01-31 22:26 | 2022-01-31 22:27 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22013100149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2708 | keep | 0 | Jan | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-01-31 22:30 | 2022-02-01 06:10 | 60 | 007:40 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE RETIRO PARARAYO | R22013100147 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 460 | 2022-01-31 | 27600 | keep | 0 | Jan | 2022 | 0.018798 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-31 22:32 | 2022-02-01 01:07 | 946 | 002:35 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA CARGA POR 1525-05 | S22013101510 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-01-31 | 146630 | keep | 0 | Jan | 2022 | 0.099869 | 0.00064432 | Sustained | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2022-01-31 22:32 | 2022-02-01 01:07 | 937 | 002:35 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA LLEVA 1525-02 | S22013101510 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-01-31 | 145235 | keep | 0 | Jan | 2022 | 0.098919 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2022-01-31 22:39 | 2022-02-01 13:30 | 69 | 014:51 | P | PARARRAYOS DEFECTUOSO | 3 X 65 EN C/L SE REMPLAZARON 2 PARARRAYOS | B22013100468 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 891 | 2022-01-31 | 61479 | keep | 0 | Jan | 2022 | 0.041873 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2022-01-31 22:55 | 2022-01-31 22:56 | 824 | 000:01 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1119-04 | B22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 824 | keep | 0 | Jan | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-01-31 22:55 | 2022-01-31 22:56 | 2720 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-31 | 2720 | keep | 0 | Jan | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-01-31 22:58 | 2022-02-01 00:46 | 60 | 001:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA AVERIADA | R22013100151 | New_Event | Cutout Failure | Include | Include | Equipment | 108 | 2022-01-31 | 6480 | keep | 0 | Jan | 2022 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-31 23:05 | 2022-02-01 14:06 | 50 | 015:01 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN RISER SE REMPLAZO TERMINACION | B22013100476 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 901 | 2022-01-31 | 45050 | keep | 0 | Jan | 2022 | 0.030683 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-31 23:16 | 2022-02-01 09:36 | 32 | 010:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22013100481 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 620 | 2022-01-31 | 19840 | keep | 0 | Jan | 2022 | 0.013513 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2022-01-31 23:32 | 2022-01-31 23:34 | 4027 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22013100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-31 | 8054 | keep | 0 | Jan | 2022 | 0.0054855 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-01-31 23:49 | 2022-02-01 07:21 | 60 | 007:32 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 50 EN C/L | B22013100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 452 | 2022-01-31 | 27120 | keep | 0 | Jan | 2022 | 0.018471 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-31 23:59 | 2022-02-01 13:01 | 95 | 013:02 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEAS SE RETIRO ARBOL SOBRE LINEA Y ENDEREZO POSTE PRIMARIO | C22013100102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 782 | 2022-01-31 | 74290 | keep | 0 | Jan | 2022 | 0.050599 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2022-02-01 00:16 | 2022-02-01 01:40 | 1000 | 001:24 | P | DESGANCHE | SE CERRARON MACHETES PREVIAMENTE ABIERTOS | B22013100275 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-02-01 | 84000 | keep | 0 | Feb | 2022 | 0.057212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-01 00:29 | 2022-02-01 03:44 | 3438 | 003:15 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO POR SCADA | B22020100003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 195 | 2022-02-01 | 670410 | keep | 0 | Feb | 2022 | 0.45661 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2022-02-01 01:07 | 2022-02-01 14:33 | 13 | 013:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO Y PARA CERRARLO SE ESTABLECIO GOI SJ-220201-01A | S22020100080 | New_Event | Wire Down | Include | Include | Equipment | 806 | 2022-02-01 | 10478 | keep | 0 | Feb | 2022 | 0.0071365 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2022-02-01 01:08 | 2022-02-01 10:53 | 50 | 009:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22020100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 585 | 2022-02-01 | 29250 | keep | 0 | Feb | 2022 | 0.019922 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-01 01:24 | 2022-02-01 09:24 | 15 | 008:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A22020100001 | New_Event | Wire Down | Include | Include | Equipment | 480 | 2022-02-01 | 7200 | keep | 0 | Feb | 2022 | 0.0049039 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-01 01:30 | 2022-02-01 11:51 | 80 | 010:21 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO CRUZADO Y CAJA PRIMARIA EN TRANSFORMADOR | P22020100001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 621 | 2022-02-01 | 49680 | keep | 0 | Feb | 2022 | 0.033837 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-01 01:40 | 2022-02-01 02:29 | 600 | 000:49 | P | DESGANCHE | SE PATRULLO Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | B22013100275 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-02-01 | 29400 | keep | 0 | Feb | 2022 | 0.020024 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-01 01:50 | 2022-02-01 19:48 | 10 | 017:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 37.5 X 37.5 KVA | S22020100023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1078 | 2022-02-01 | 10780 | keep | 0 | Feb | 2022 | 0.0073422 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-01 02:09 | 2022-02-01 09:16 | 30 | 007:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO AVE | R22020100004 | New_Event |  |  | Include | Wildlife | 427 | 2022-02-01 | 12810 | keep | 0 | Feb | 2022 | 0.0087248 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-01 02:38 | 2022-02-01 10:51 | 86 | 008:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | S22020100031 | New_Event | Wire Down | Include | Include | Equipment | 493 | 2022-02-01 | 42398 | keep | 0 | Feb | 2022 | 0.028877 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
PONCE | 2022-02-01 02:43 | 2022-02-01 09:06 | 100 | 006:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P22020100030 | New_Event |  |  | Include | Wildlife | 383 | 2022-02-01 | 38300 | keep | 0 | Feb | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-01 02:48 | 2022-02-01 10:31 | 30 | 007:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22020100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2022-02-01 | 13890 | keep | 0 | Feb | 2022 | 0.0094604 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-01 02:52 | 2022-02-01 07:10 | 70 | 004:18 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE ELIMINO PARARRAYO CRUZADO | A22020100004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 258 | 2022-02-01 | 18060 | keep | 0 | Feb | 2022 | 0.012301 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-02-01 02:56 | 2022-02-01 13:02 | 26 | 010:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L SE REPARO LINEA PRIMARIA | B22020100041 | New_Event | Wire Down | Include | Include | Equipment | 606 | 2022-02-01 | 15756 | keep | 0 | Feb | 2022 | 0.010731 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2022-02-01 03:08 | 2022-02-01 13:29 | 32 | 010:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22020100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 621 | 2022-02-01 | 19872 | keep | 0 | Feb | 2022 | 0.013535 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
PONCE | 2022-02-01 03:43 | 2022-02-01 07:43 | 50 | 004:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22050100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-02-01 | 12000 | keep | 0 | Feb | 2022 | 0.0081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-01 03:51 | 2022-02-01 03:52 | 1200 | 000:01 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 30% POR EL 1336-08 | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 1200 | keep | 0 | Feb | 2022 | 0.00081731 | 0.00081731 | Momentary | FALSE | FALSE | Not_TMED_Event | 1200
SAN JUAN | 2022-02-01 03:51 | 2022-02-01 03:52 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1336-09 Y 305 DEL 1204-04 | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 5290 | keep | 0 | Feb | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-02-01 03:51 | 2022-02-01 03:52 | 207 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1336-08 | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 207 | keep | 0 | Feb | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
FAJARDO | 2022-02-01 04:07 | 2022-02-01 12:25 | 125 | 008:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22020100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 498 | 2022-02-01 | 62250 | keep | 0 | Feb | 2022 | 0.042398 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-02-01 04:10 | 2022-02-01 11:10 | 60 | 007:00 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B22020100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2022-02-01 | 25200 | keep | 0 | Feb | 2022 | 0.017164 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-01 04:11 | 2022-02-01 16:32 | 40 | 012:21 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | S22020100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 741 | 2022-02-01 | 29640 | keep | 0 | Feb | 2022 | 0.020188 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-01 05:05 | 2022-02-01 11:30 | 45 | 006:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER | S22020100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2022-02-01 | 17325 | keep | 0 | Feb | 2022 | 0.0118 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-02-01 05:10 | 2022-02-01 09:03 | 25 | 003:53 | P | DESGANCHE | SE RETIRO PALMA ENCIMA DE LA LINEA Y SE CERRO C/L | B22020100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-02-01 | 5825 | keep | 0 | Feb | 2022 | 0.0039674 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-01 06:16 | 2022-02-01 12:38 | 50 | 006:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INFORMA EL UT2 TRAINED QUE EL SECTOR REQUIERE DESGANCHE | M22020100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2022-02-01 | 19100 | keep | 0 | Feb | 2022 | 0.013009 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-01 06:38 | 2022-02-01 09:40 | 20 | 003:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22020100002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 182 | 2022-02-01 | 3640 | keep | 0 | Feb | 2022 | 0.0024792 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-01 06:53 | 2022-02-01 12:45 | 12 | 005:52 | P | NO SE REPORTO CAUSA | 1 X 12 NX | S22020100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 352 | 2022-02-01 | 4224 | keep | 0 | Feb | 2022 | 0.0028769 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-01 07:02 | 2022-02-01 21:00 | 10 | 013:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPALZO CAJA AVERIADA | S22020100065 | New_Event | Cutout Failure | Include | Include | Equipment | 838 | 2022-02-01 | 8380 | keep | 0 | Feb | 2022 | 0.0057076 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-01 07:04 | 2022-02-01 07:05 | 422 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1907-04 Y SE CERRO POR SCADA LLEVANDO PARTE DEL 1346-03 | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 422 | keep | 0 | Feb | 2022 | 0.00028742 | 0.00028742 | Momentary | FALSE | FALSE | Not_TMED_Event | 422
BAYAMON | 2022-02-01 07:04 | 2022-02-01 07:05 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1907-4 Y SE CERRO POR SCADA LLEVA PARTE DEL 1346-03 | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2466 | keep | 0 | Feb | 2022 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
HUMACAO | 2022-02-01 07:05 | 2022-02-01 12:00 | 9 | 004:55 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR DE 25KVA X 25KVA | C22020100006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 295 | 2022-02-01 | 2655 | keep | 0 | Feb | 2022 | 0.0018083 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-02-01 07:19 | 2022-02-01 12:50 | 8 | 005:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CORTE DE LINEA PARA REPARAR SECUNDARIA AVERIADA Y REALIZAR DESGANCHE | C22020100007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 331 | 2022-02-01 | 2648 | keep | 0 | Feb | 2022 | 0.0018035 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-01 07:22 | 2022-02-01 11:01 | 75 | 003:39 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | C22020100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-02-01 | 16425 | keep | 0 | Feb | 2022 | 0.011187 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-02-01 07:43 | 2022-02-01 07:44 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2039 | keep | 0 | Feb | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2022-02-01 07:44 | 2022-02-01 10:15 | 50 | 002:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22020100031 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-02-01 | 7550 | keep | 0 | Feb | 2022 | 0.0051423 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-01 07:46 | 2022-02-01 09:52 | 1 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA HACIA BOMBAS AAA | S22020100093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-02-01 | 126 | keep | 0 | Feb | 2022 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-01 07:53 | 2022-02-01 18:36 | 10 | 010:43 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22020100102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 643 | 2022-02-01 | 6430 | keep | 0 | Feb | 2022 | 0.0043794 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-01 07:58 | 2022-02-01 20:37 | 300 | 012:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO CAJA PRIMARIA AVERIADA | A22020100139 | New_Event | Wire Down | Include | Include | Equipment | 759 | 2022-02-01 | 227700 | keep | 0 | Feb | 2022 | 0.15509 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-02-01 08:04 | 2022-02-01 11:13 | 50 | 003:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A22020100008 | New_Event | Cutout Failure | Include | Include | Equipment | 189 | 2022-02-01 | 9450 | keep | 0 | Feb | 2022 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-01 08:10 | 2022-02-01 16:15 | 40 | 008:05 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO BAMBUA | S22020100120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2022-02-01 | 19400 | keep | 0 | Feb | 2022 | 0.013213 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-01 08:14 | 2022-02-01 15:23 | 7 | 007:09 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR EL JOURNEYMAN NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22020100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 429 | 2022-02-01 | 3003 | keep | 0 | Feb | 2022 | 0.0020453 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-01 08:16 | 2022-02-01 08:17 | 418 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 418 | keep | 0 | Feb | 2022 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
AGUADILLA | 2022-02-01 08:19 | 2022-02-01 12:25 | 25 | 004:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | M22020100007 | New_Event | Wire Down | Include | Include | Equipment | 246 | 2022-02-01 | 6150 | keep | 0 | Feb | 2022 | 0.0041887 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-02-01 08:22 | 2022-02-01 10:50 | 40 | 002:28 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PARTIDO DE PROVISIONAL AEREO | R22020100013 | New_Event | Defective Pole | Include | Include | Equipment | 148 | 2022-02-01 | 5920 | keep | 0 | Feb | 2022 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-01 08:30 | 2022-02-01 10:15 | 75 | 001:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22020100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-02-01 | 7875 | keep | 0 | Feb | 2022 | 0.0053636 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-01 08:34 | 2022-02-01 09:34 | 187 | 001:00 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON OPERACIONES DE CAMPO Y ENTRA UN 60% EN SERVICIO CARGAS DEL 1117-08 A TRAVEZ DEL INTERRUPTOR 1116-05 | S22013101261 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 60 | 2022-02-01 | 11220 | keep | 0 | Feb | 2022 | 0.0076419 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
ARECIBO | 2022-02-01 08:34 | 2022-02-01 16:49 | 100 | 008:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22020100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2022-02-01 | 49500 | keep | 0 | Feb | 2022 | 0.033714 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-01 08:40 | 2022-02-01 08:41 | 2402 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | S22020100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-01 | 2402 | keep | 0 | Feb | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-02-01 08:41 | 2022-02-01 13:10 | 125 | 004:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L SE REMPLAZO CAJAS PRIMARIAS | S22013101426 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 269 | 2022-02-01 | 33625 | keep | 0 | Feb | 2022 | 0.022902 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-02-01 08:51 | 2022-02-01 14:34 | 15 | 005:43 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22020100071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 343 | 2022-02-01 | 5145 | keep | 0 | Feb | 2022 | 0.0035042 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-01 08:53 | 2022-02-01 11:05 | 5 | 002:12 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR | C22020100015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 132 | 2022-02-01 | 660 | keep | 0 | Feb | 2022 | 0.00044952 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-02-01 09:00 | 2022-02-01 10:48 | 15 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS | A22020100013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2022-02-01 | 1620 | keep | 0 | Feb | 2022 | 0.0011034 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-01 09:02 | 2022-02-01 11:31 | 35 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020100015 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-02-01 | 5215 | keep | 0 | Feb | 2022 | 0.0035519 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-02-01 09:03 | 2022-02-01 13:35 | 10 | 004:32 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN TRANSFORMADOR POR PARARRAYO AVERIADO | M22020100021 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 272 | 2022-02-01 | 2720 | keep | 0 | Feb | 2022 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-01 09:06 | 2022-02-01 16:04 | 12 | 006:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15KVA X 37.5KVA | M22020100022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 418 | 2022-02-01 | 5016 | keep | 0 | Feb | 2022 | 0.0034164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-01 09:11 | 2022-02-01 15:46 | 12 | 006:35 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO EL SU - 3A | C22020100012 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 395 | 2022-02-01 | 4740 | keep | 0 | Feb | 2022 | 0.0032284 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-01 09:11 | 2022-02-01 15:11 | 1 | 006:00 | P | DESGANCHE | 2 X 40 EN RISER SE REALIZO DESGANCHE | B22020100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2022-02-01 | 360 | keep | 0 | Feb | 2022 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-01 09:18 | 2022-02-01 15:17 | 70 | 005:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | M22020100030 | New_Event | Bad Weather | Include | Include | Weather | 359 | 2022-02-01 | 25130 | keep | 0 | Feb | 2022 | 0.017116 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-02-01 09:23 | 2022-02-01 11:39 | 1 | 002:16 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C22020100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-02-01 | 136 | keep | 0 | Feb | 2022 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-02-01 09:29 | 2022-02-01 18:11 | 1 | 008:42 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | C22020100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 522 | 2022-02-01 | 522 | keep | 0 | Feb | 2022 | 0.00035553 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-02-01 09:30 | 2022-02-01 09:52 | 6 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO CONECTORES SECUNDARIOS | A22013100051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2022-02-01 | 132 | keep | 0 | Feb | 2022 | 8.9905e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-01 09:34 | 2022-02-01 10:40 | 87 | 001:06 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON OPERACIONES DE CAMPO Y DISPARA 1116-05 LLEVANDO UN 20% DEL 1117-08 | S22013101261 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 66 | 2022-02-01 | 5742 | keep | 0 | Feb | 2022 | 0.0039109 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-01 09:40 | 2022-02-01 10:46 | 12 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22020100049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2022-02-01 | 792 | keep | 0 | Feb | 2022 | 0.00053943 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-01 09:41 | 2022-02-01 11:10 | 1 | 001:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | R22020100035 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2022-02-01 | 89 | keep | 0 | Feb | 2022 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-01 09:47 | 2022-02-01 14:00 | 30 | 004:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22020100192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2022-02-01 | 7590 | keep | 0 | Feb | 2022 | 0.0051695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-01 09:54 | 2022-02-01 11:55 | 27 | 002:01 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN SU-1JC SE SECCIONALIZO SU-5JC | R22020100037 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 121 | 2022-02-01 | 3267 | keep | 0 | Feb | 2022 | 0.0022251 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BARRANQUITAS | 2022-02-01 10:06 | 2022-02-01 10:07 | 1364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 1364 | keep | 0 | Feb | 2022 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
AGUADILLA | 2022-02-01 10:20 | 2022-02-01 11:25 | 6 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22020100039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-02-01 | 390 | keep | 0 | Feb | 2022 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-01 10:31 | 2022-02-01 14:24 | 5 | 003:53 | P | ESTRUCTURA AVERIADA | SE ABRIO MONTURA DE TRANSFORMADOR Y SE REEMPLAZO POSTE SECUNDARIO PARTIDO | M22020100046 | New_Event | Defective Pole | Include | Include | Equipment | 233 | 2022-02-01 | 1165 | keep | 0 | Feb | 2022 | 0.00079348 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-01 10:40 | 2022-02-01 13:28 | 20 | 002:48 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ELIMINO TOMA ABANDONADA AVERIADA Y SE REPUSO 2 X 80 EN SU-21 | S22013101261 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 168 | 2022-02-01 | 3360 | keep | 0 | Feb | 2022 | 0.0022885 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-01 11:06 | 2022-02-01 11:30 | 50 | 000:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO | S22020100056 | New_Event | Cutout Failure | Include | Include | Equipment | 24 | 2022-02-01 | 1200 | keep | 0 | Feb | 2022 | 0.00081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-01 11:31 | 2022-02-01 11:59 | 1310 | 000:28 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO POR SCADA | S22020100237 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2022-02-01 | 36680 | keep | 0 | Feb | 2022 | 0.024983 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2022-02-01 11:51 | 2022-02-01 15:36 | 5 | 003:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA | C22020100040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 225 | 2022-02-01 | 1125 | keep | 0 | Feb | 2022 | 0.00076623 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-02-01 11:52 | 2022-02-01 13:08 | 45 | 001:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22020100041 | New_Event |  |  | Include | Wildlife | 76 | 2022-02-01 | 3420 | keep | 0 | Feb | 2022 | 0.0023293 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-02-01 11:55 | 2022-02-01 13:37 | 2 | 001:42 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO MACHETE QUEMADO EN SU-5JC | R22020100046 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 102 | 2022-02-01 | 204 | keep | 0 | Feb | 2022 | 0.00013894 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-02-01 12:10 | 2022-02-01 15:03 | 8 | 002:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIO Y INSTALO VARILLA DE GROUND | C22020100043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 173 | 2022-02-01 | 1384 | keep | 0 | Feb | 2022 | 0.00094264 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-01 12:13 | 2022-02-01 18:13 | 40 | 006:00 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020100255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2022-02-01 | 14400 | keep | 0 | Feb | 2022 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-02-01 12:18 | 2022-02-01 13:36 | 1 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE XMR | C22020100044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2022-02-01 | 78 | keep | 0 | Feb | 2022 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-02-01 12:20 | 2022-02-01 14:10 | 10 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO MONTURA DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22020100063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2022-02-01 | 1100 | keep | 0 | Feb | 2022 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-02-01 12:22 | 2022-02-01 13:59 | 40 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE DESENRREDO LINEA PRIMARIA | P22020100059 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2022-02-01 | 3880 | keep | 0 | Feb | 2022 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-01 12:37 | 2022-02-01 16:13 | 40 | 003:36 | P | DESGANCHE | 1 X 40 EN C/L | C22020100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-02-01 | 8640 | keep | 0 | Feb | 2022 | 0.0058847 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-01 12:40 | 2022-02-01 16:59 | 30 | 004:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE REMPLAZO AISLADOR | C22020100046 | New_Event |  |  | Include | Wildlife | 259 | 2022-02-01 | 7770 | keep | 0 | Feb | 2022 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-01 12:46 | 2022-02-01 14:36 | 50 | 001:50 | P | DESGANCHE | 1 X 80 EN C/L RAMA | S22020100267 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-02-01 | 5500 | keep | 0 | Feb | 2022 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-01 12:48 | 2022-02-01 14:26 | 25 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA SE RETIRO GLOBO DE LA LINEA | R22020100051 | New_Event |  |  | Include | Wildlife | 98 | 2022-02-01 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-02-01 12:56 | 2022-02-01 14:06 | 9 | 001:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | P22020100057 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2022-02-01 | 630 | keep | 0 | Feb | 2022 | 0.00042909 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-02-01 13:05 | 2022-02-01 13:06 | 5 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON OPERACIONES DE CAMPO Y DISPARA 1116-05 LLEVANDO UN 20% DEL 1117-08 | S22013101261 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2022-02-01 | 5 | keep | 0 | Feb | 2022 | 3.4055e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-01 13:17 | 2022-02-01 17:26 | 2 | 004:09 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22020100117 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 249 | 2022-02-01 | 498 | keep | 0 | Feb | 2022 | 0.00033919 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-01 13:28 | 2022-02-01 16:14 | 6 | 002:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO SU-27 CONTAMINADO MEDIANTE GOI SJ-220201-07A | S22013101261 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 166 | 2022-02-01 | 996 | keep | 0 | Feb | 2022 | 0.00067837 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-01 13:35 | 2022-02-01 16:58 | 40 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020100120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-02-01 | 8120 | keep | 0 | Feb | 2022 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-01 13:37 | 2022-02-01 18:45 | 13 | 005:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A22020100031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 308 | 2022-02-01 | 4004 | keep | 0 | Feb | 2022 | 0.0027271 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-02-01 13:41 | 2022-02-01 13:42 | 418 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 418 | keep | 0 | Feb | 2022 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2022-02-01 13:52 | 2022-02-02 11:12 | 10 | 021:20 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 20 EN SU-1A Y SE REALIZO TERMINACION EN CAJA SECA | S22020100280 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1280 | 2022-02-01 | 12800 | keep | 0 | Feb | 2022 | 0.008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-01 13:57 | 2022-02-01 13:58 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 4176 | keep | 0 | Feb | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-02-01 13:58 | 2022-02-01 16:06 | 75 | 002:08 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA | B22020100127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 128 | 2022-02-01 | 9600 | keep | 0 | Feb | 2022 | 0.0065385 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2022-02-01 14:14 | 2022-02-01 15:09 | 15 | 000:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO PENCA Y CHANGO DE LA LINEA | R22020100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-02-01 | 825 | keep | 0 | Feb | 2022 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-02-01 14:14 | 2022-02-01 14:15 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 551 | keep | 0 | Feb | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2022-02-01 14:15 | 2022-02-01 18:47 | 1 | 004:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER REMPLAZO CAJA QUEMADA | C22020100053 | New_Event | Cutout Failure | Include | Include | Equipment | 272 | 2022-02-01 | 272 | keep | 0 | Feb | 2022 | 0.00018526 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-01 14:25 | 2022-02-01 17:44 | 6 | 003:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZARON BARRAS EN PEDESTAL SOTERRADO AUNQUE EL EVENTO ES DEL DIA 31 NO HABIA CLIENTES FUERA | M22013100065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 199 | 2022-02-01 | 1194 | keep | 0 | Feb | 2022 | 0.00081323 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-01 14:26 | 2022-02-01 17:24 | 80 | 002:58 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN RISER SE REPARO TERMINACION EN RISER DE AEREO PROVISIONAL | S22020100293 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 178 | 2022-02-01 | 14240 | keep | 0 | Feb | 2022 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-02-01 14:26 | 2022-02-01 14:27 | 9 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR | P22020100057 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-01 | 9 | keep | 0 | Feb | 2022 | 6.1299e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-01 14:33 | 2022-02-01 15:58 | 37 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA CERRAR PUENTE MEDIANTE GOI SJ-220201-01A | S22020100080 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2022-02-01 | 3145 | keep | 0 | Feb | 2022 | 0.002142 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2022-02-01 15:03 | 2022-02-01 19:26 | 1 | 004:23 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO RAMA | S22020100298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2022-02-01 | 263 | keep | 0 | Feb | 2022 | 0.00017913 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-01 15:12 | 2022-02-01 15:17 | 763 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18800 DE SABANA LLANA A CAROLINA PUEBLO | R22020100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-02-01 | 3815 | keep | 0 | Feb | 2022 | 0.0025984 | 0.00051968 | Momentary | FALSE | FALSE | Not_TMED_Event | 763
SAN JUAN | 2022-02-01 15:12 | 2022-02-01 15:17 | 27 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18800 DE SABANA LLANA A CAROLINA PUEBLO | R22020100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-02-01 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2022-02-01 15:12 | 2022-02-01 15:17 | 1259 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18800 DE SABANA LLANA A CAROLINA PUEBLO | R22020100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-02-01 | 6295 | keep | 0 | Feb | 2022 | 0.0042875 | 0.0008575 | Momentary | FALSE | FALSE | Not_TMED_Event | 1259
SAN JUAN | 2022-02-01 15:12 | 2022-02-01 15:17 | 1051 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18800 DE SABANA LLANA A CAROLINA PUEBLO | R22020100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-02-01 | 5255 | keep | 0 | Feb | 2022 | 0.0035792 | 0.00071583 | Momentary | FALSE | FALSE | Not_TMED_Event | 1051
SAN JUAN | 2022-02-01 15:12 | 2022-02-01 15:17 | 188 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18800 DE SABANA LLANA A CAROLINA PUEBLO | R22020100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-02-01 | 940 | keep | 0 | Feb | 2022 | 0.00064023 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
CANOVANAS | 2022-02-01 15:15 | 2022-02-01 19:00 | 13 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R22020100060 | New_Event |  |  | Include | Wildlife | 225 | 2022-02-01 | 2925 | keep | 0 | Feb | 2022 | 0.0019922 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2022-02-01 15:15 | 2022-02-01 16:00 | 14 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R22020100053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-02-01 | 630 | keep | 0 | Feb | 2022 | 0.00042909 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-02-01 15:33 | 2022-02-01 17:18 | 12 | 001:45 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO ARBOL CAIDO SOBRE LAS LINEAS | A22020100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-02-01 | 1260 | keep | 0 | Feb | 2022 | 0.00085818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-01 15:34 | 2022-02-01 18:39 | 10 | 003:05 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA DESGANCHE Y REPARAR SECUNDARIA | M22020100086 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 185 | 2022-02-01 | 1850 | keep | 0 | Feb | 2022 | 0.00126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-01 15:45 | 2022-02-01 20:10 | 67 | 004:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22020100307 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 265 | 2022-02-01 | 17755 | keep | 0 | Feb | 2022 | 0.012093 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
PONCE | 2022-02-01 15:57 | 2022-02-01 17:29 | 75 | 001:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | P22020100067 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2022-02-01 | 6900 | keep | 0 | Feb | 2022 | 0.0046996 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-01 15:59 | 2022-02-01 19:22 | 15 | 003:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA | B22020100142 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2022-02-01 | 3045 | keep | 0 | Feb | 2022 | 0.0020739 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-02-01 16:00 | 2022-02-01 16:47 | 60 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22020100050 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2022-02-01 | 2820 | keep | 0 | Feb | 2022 | 0.0019207 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-01 16:05 | 2022-02-01 17:02 | 60 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | M22020100090 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2022-02-01 | 3420 | keep | 0 | Feb | 2022 | 0.0023293 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-01 16:14 | 2022-02-01 16:18 | 87 | 000:04 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DANDO SERVICIO EN SU-27 MEDIANTE GOI SJ-220201-07A DISPARO 1116-05 LLEVANDO UN 20% DEL 1117-08. SE ABRIO NUEVAMENTE EN VS-27 Y SE ESTABLECIO GOI SJ-220201-07C | S22013101261 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 4 | 2022-02-01 | 348 | keep | 0 | Feb | 2022 | 0.00023702 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-01 16:14 | 2022-02-01 17:27 | 25 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22020100143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-02-01 | 1825 | keep | 0 | Feb | 2022 | 0.001243 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-01 16:18 | 2022-02-01 17:10 | 6 | 000:52 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO SU-27 CONTAMINADO MEDIANTE GOI SJ-220201-07A | S22013101261 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 52 | 2022-02-01 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-01 16:19 | 2022-02-01 16:38 | 40 | 000:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | B22020100286 | New_Event | Bad Weather | Include | Include | Weather | 19 | 2022-02-01 | 760 | keep | 0 | Feb | 2022 | 0.00051763 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-01 16:23 | 2022-02-01 16:24 | 5 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO INTERRUPTOR AL CERRAR EN MH-27 DESPUES DE DARLE RELEASE AL GOI SJ-220131-07A. SE ABRIO NUEVAMENTE EN VS-27 Y SE ESTABLECIO GOI 220131-07C. LLEVANDO UN 20% DEL 1117-08 | S22013101261 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2022-02-01 | 5 | keep | 0 | Feb | 2022 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-02-01 16:25 | 2022-02-01 18:56 | 4 | 002:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X RATA | C22020100068 | New_Event |  |  | Include | Wildlife | 151 | 2022-02-01 | 604 | keep | 0 | Feb | 2022 | 0.00041138 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-02-01 16:25 | 2022-02-01 19:09 | 40 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22020100067 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2022-02-01 | 6560 | keep | 0 | Feb | 2022 | 0.004468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-01 16:26 | 2022-02-01 17:23 | 75 | 000:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22020100054 | New_Event |  |  | Include | Wildlife | 57 | 2022-02-01 | 4275 | keep | 0 | Feb | 2022 | 0.0029117 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2022-02-01 16:31 | 2022-02-01 19:07 | 6 | 002:36 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO SE LE PASO LA CARGA AL TRANSFORMADOR DE 50 KVA CERCANO | R22020100065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 156 | 2022-02-01 | 936 | keep | 0 | Feb | 2022 | 0.00063751 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-01 16:37 | 2022-02-01 17:28 | 45 | 000:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22020100318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-02-01 | 2295 | keep | 0 | Feb | 2022 | 0.0015631 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-02-01 16:42 | 2022-02-01 17:49 | 80 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER HACIA SU-1 | S22020100321 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-02-01 | 5360 | keep | 0 | Feb | 2022 | 0.0036507 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-02-01 16:42 | 2022-02-01 16:43 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020100070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-02-01 16:46 | 2022-02-01 16:47 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020100071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
MAYAGÃœEZ | 2022-02-01 16:51 | 2022-02-01 16:52 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22020100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 1287 | keep | 0 | Feb | 2022 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
ARECIBO | 2022-02-01 16:53 | 2022-02-01 17:36 | 1105 | 000:43 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR ARBOL CAIDO SOBRE LAS LINEAS PRIMARIAS | A22020100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-02-01 | 47515 | keep | 0 | Feb | 2022 | 0.032362 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
MAYAGÃœEZ | 2022-02-01 16:55 | 2022-02-01 16:56 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22020100097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 470 | keep | 0 | Feb | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-02-01 16:55 | 2022-02-01 16:56 | 2483 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22020100097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2483 | keep | 0 | Feb | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
ARECIBO | 2022-02-01 16:55 | 2022-02-01 18:00 | 50 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22020100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-02-01 | 3250 | keep | 0 | Feb | 2022 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-01 17:04 | 2022-02-02 09:07 | 1 | 016:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22020100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 963 | 2022-02-01 | 963 | keep | 0 | Feb | 2022 | 0.00065589 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-01 17:05 | 2022-02-01 17:11 | 470 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | M22020100098 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-02-01 | 2820 | keep | 0 | Feb | 2022 | 0.0019207 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-02-01 17:05 | 2022-02-01 17:11 | 2483 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | M22020100098 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-02-01 | 14898 | keep | 0 | Feb | 2022 | 0.010147 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
BAYAMON | 2022-02-01 17:10 | 2022-02-01 20:24 | 4 | 003:14 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPALZARON 3 MACHETES EN SU-3 QUE SE SIRVEN DEL MH-18 MEDIANTE GOI SJ-220201-07B | S22013101261 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 194 | 2022-02-01 | 776 | keep | 0 | Feb | 2022 | 0.00052853 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-01 17:10 | 2022-02-01 20:01 | 115 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | M22020100100 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2022-02-01 | 19665 | keep | 0 | Feb | 2022 | 0.013394 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
MAYAGÃœEZ | 2022-02-01 17:14 | 2022-02-01 19:06 | 120 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR LLUVIAS | M22020100101 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2022-02-01 | 13440 | keep | 0 | Feb | 2022 | 0.0091539 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2022-02-01 17:21 | 2022-02-01 18:04 | 30 | 000:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020100146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-02-01 | 1290 | keep | 0 | Feb | 2022 | 0.00087861 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-01 17:26 | 2022-02-02 02:30 | 10 | 009:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22020100105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 544 | 2022-02-01 | 5440 | keep | 0 | Feb | 2022 | 0.0037052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-01 17:28 | 2022-02-01 19:15 | 60 | 001:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-02-01 | 6420 | keep | 0 | Feb | 2022 | 0.0043726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-01 17:33 | 2022-02-01 18:17 | 30 | 000:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020100109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-02-01 | 1320 | keep | 0 | Feb | 2022 | 0.00089905 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-01 17:36 | 2022-02-01 18:54 | 552 | 001:18 | P | DESGANCHE | SE RETIRO ARBOL CAIDO SOBRE LAS LINEAS Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22020100057 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-02-01 | 43056 | keep | 0 | Feb | 2022 | 0.029325 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-01 17:37 | 2022-02-02 17:07 | 60 | 023:30 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DEGANCHE | B22020100149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1410 | 2022-02-01 | 84600 | keep | 0 | Feb | 2022 | 0.057621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-01 17:47 | 2022-02-01 19:20 | 25 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S22020100328 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-02-01 | 2325 | keep | 0 | Feb | 2022 | 0.0015835 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-01 17:48 | 2022-02-01 17:50 | 125 | 000:02 | T | DESGANCHE | DISPARO | C22020100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-02-01 | 250 | keep | 0 | Feb | 2022 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-02-01 17:52 | 2022-02-01 21:01 | 125 | 003:09 | T | DESGANCHE | SE REALIZO DESGANCHE | C22020100079 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-02-01 | 23625 | keep | 0 | Feb | 2022 | 0.016091 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-02-01 17:53 | 2022-02-01 18:55 | 40 | 001:02 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22020100331 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-02-01 | 2480 | keep | 0 | Feb | 2022 | 0.0016891 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-02-01 17:58 | 2022-02-01 21:23 | 30 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEA AVERIADA SIGUE AL DIA SIGUIENTE | A22020100068 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2022-02-01 | 6150 | keep | 0 | Feb | 2022 | 0.0041887 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-01 18:02 | 2022-02-01 18:03 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 25% 9405-05 | B22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 3597 | keep | 0 | Feb | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-02-01 18:02 | 2022-02-01 18:03 | 877 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1719-15 25% DE LA CARGA TRANSFERIDA | B22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 877 | keep | 0 | Feb | 2022 | 0.00059732 | 0.00059732 | Momentary | FALSE | FALSE | Not_TMED_Event | 877
BAYAMON | 2022-02-01 18:03 | 2022-02-01 20:17 | 40 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020100158 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-02-01 | 5360 | keep | 0 | Feb | 2022 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-01 18:13 | 2022-02-01 18:14 | 2201 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020100070 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-01 | 2201 | keep | 0 | Feb | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-02-01 18:14 | 2022-02-01 20:30 | 200 | 002:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA Y FUERTE VIENTO | A22020100071 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 136 | 2022-02-01 | 27200 | keep | 0 | Feb | 2022 | 0.018526 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-02-01 18:18 | 2022-02-01 19:14 | 1879 | 000:56 | T | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO EL ALIMENTADOR | C22020100098 | New_Event | Bad Weather | Include | Include | Weather | 56 | 2022-02-01 | 105224 | keep | 0 | Feb | 2022 | 0.071668 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2022-02-01 18:18 | 2022-02-01 19:14 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22020100013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-02-01 | 560 | keep | 0 | Feb | 2022 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-01 18:24 | 2022-02-01 18:26 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL | B22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-01 | 4468 | keep | 0 | Feb | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2022-02-01 18:29 | 2022-02-01 18:30 | 2694 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2694 | keep | 0 | Feb | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2022-02-01 18:31 | 2022-02-02 12:40 | 20 | 018:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | A22020100080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1089 | 2022-02-01 | 21780 | keep | 0 | Feb | 2022 | 0.014834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-01 18:34 | 2022-02-02 00:26 | 15 | 005:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER Y 1 X 80 EN C/L | S22020100337 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 352 | 2022-02-01 | 5280 | keep | 0 | Feb | 2022 | 0.0035962 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-01 18:37 | 2022-02-01 18:39 | 232 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22020100087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-01 | 464 | keep | 0 | Feb | 2022 | 0.00031603 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2022-02-01 18:38 | 2022-02-01 18:39 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 3431 | keep | 0 | Feb | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
VEGA BAJA | 2022-02-01 18:50 | 2022-02-01 22:51 | 50 | 004:01 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22020100171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-02-01 | 12050 | keep | 0 | Feb | 2022 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-01 18:54 | 2022-02-02 09:36 | 90 | 014:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22020100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 882 | 2022-02-01 | 79380 | keep | 0 | Feb | 2022 | 0.054065 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-02-01 19:00 | 2022-02-01 19:01 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22020100120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 990 | keep | 0 | Feb | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2022-02-01 19:01 | 2022-02-02 11:43 | 35 | 016:42 | P | HERRAJE ROTO O PODRIDO | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CRUCETA CON TRANSFORMADOR | S22020100349 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1002 | 2022-02-01 | 35070 | keep | 0 | Feb | 2022 | 0.023886 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-02-01 19:05 | 2022-02-01 20:18 | 90 | 001:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22020100068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-02-01 | 6570 | keep | 0 | Feb | 2022 | 0.0044748 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-02-01 19:08 | 2022-02-02 09:20 | 25 | 014:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA JOURNEYMAN INFORMA SECTOR REQUIERE DESGANCHE | A22020100101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 852 | 2022-02-01 | 21300 | keep | 0 | Feb | 2022 | 0.014507 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-01 19:12 | 2022-02-02 01:01 | 650 | 005:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO | S22020100359 | New_Event | Wire Down | Include | Include | Equipment | 349 | 2022-02-01 | 226850 | keep | 0 | Feb | 2022 | 0.15451 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
BAYAMON | 2022-02-01 19:12 | 2022-02-01 19:56 | 125 | 000:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN C/L SE REMPLAZARON DOS CAJA | B22020100359 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2022-02-01 | 5500 | keep | 0 | Feb | 2022 | 0.003746 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-02-01 19:14 | 2022-02-01 21:29 | 934 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | SE SECCIONALIZO EL ALIMENTADOR | C22020100171 | Partial_restoration | Bad Weather | Include | Include | Weather | 135 | 2022-02-01 | 126090 | keep | 0 | Feb | 2022 | 0.085879 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-01 19:23 | 2022-02-02 07:43 | 100 | 012:20 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B22020200181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 740 | 2022-02-01 | 74000 | keep | 0 | Feb | 2022 | 0.050401 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-02-01 19:42 | 2022-02-01 19:43 | 1394 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R22020100071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-01 | 1394 | keep | 0 | Feb | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2022-02-01 19:43 | 2022-02-01 22:14 | 200 | 002:31 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTES DE LINEA | R22020100077 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-02-01 | 30200 | keep | 0 | Feb | 2022 | 0.020569 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-01 19:56 | 2022-02-01 20:01 | 760 | 000:05 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 50% DE LA CARGA TRANSFERIDA AL 1909-07 SE VERIFICO PERSONAL FUERA DE LA LINEA | B22020100190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-01 | 3800 | keep | 0 | Feb | 2022 | 0.0025882 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
BAYAMON | 2022-02-01 19:56 | 2022-02-01 20:01 | 2364 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE BREAKER | B22020100359 | Additional_clients | Cutout Failure | Include | Include | Equipment | 5 | 2022-02-01 | 11820 | keep | 0 | Feb | 2022 | 0.0080505 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-01 19:56 | 2022-02-01 20:01 | 2364 | 000:05 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIA AL 1709-03 DISPARO Y SE CERRO POR CONTROL SE VERIFICO PERSONAL FUERA | B22020100190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-01 | 11820 | keep | 0 | Feb | 2022 | 0.0080505 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
ARECIBO | 2022-02-01 19:58 | 2022-02-02 08:40 | 100 | 012:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020100126 | New_Event | Bad Weather | Include | Include | Weather | 762 | 2022-02-01 | 76200 | keep | 0 | Feb | 2022 | 0.051899 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-01 20:01 | 2022-02-01 22:53 | 125 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN C/L SE REMPLAZARON DOS CAJA | B22020100359 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 172 | 2022-02-01 | 21500 | keep | 0 | Feb | 2022 | 0.014644 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-01 20:07 | 2022-02-02 12:11 | 30 | 016:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO CORTE DE LINEA ABIERTO PARA REPARAR Y SECCIONALIZAR CONDUCTOR SAFADO DE GRAPA QUEMANDO. | C22020100164 | New_Event | Wire Down | Include | Include | Equipment | 964 | 2022-02-01 | 28920 | keep | 0 | Feb | 2022 | 0.019697 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-01 20:37 | 2022-02-01 20:38 | 1066 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR SIGUE PARCIAL AL OTRO DIA | A22020100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-01 | 1066 | keep | 0 | Feb | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2022-02-01 20:37 | 2022-02-02 11:15 | 15 | 014:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22020100134 | New_Event | Bad Weather | Include | Include | Weather | 878 | 2022-02-01 | 13170 | keep | 0 | Feb | 2022 | 0.00897 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-01 20:38 | 2022-02-02 10:18 | 300 | 013:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO CAJA PRIMARIA AVERIADA | A22020100139 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 820 | 2022-02-01 | 246000 | keep | 0 | Feb | 2022 | 0.16755 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-02-01 20:38 | 2022-02-01 20:40 | 1834 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL | B22020100224 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-01 | 3668 | keep | 0 | Feb | 2022 | 0.0024983 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-02-01 20:41 | 2022-02-01 20:42 | 1834 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B22020100000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-01 | 1834 | keep | 0 | Feb | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-02-01 20:41 | 2022-02-01 20:42 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 2324 | keep | 0 | Feb | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
BAYAMON | 2022-02-01 20:41 | 2022-02-01 20:43 | 1180 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22020100227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-01 | 2360 | keep | 0 | Feb | 2022 | 0.0016074 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
ARECIBO | 2022-02-01 20:49 | 2022-02-02 09:53 | 125 | 013:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020100142 | New_Event | Bad Weather | Include | Include | Weather | 784 | 2022-02-01 | 98000 | keep | 0 | Feb | 2022 | 0.066747 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-02-01 21:03 | 2022-02-01 21:04 | 1834 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B22020100000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-01 | 1834 | keep | 0 | Feb | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
ARECIBO | 2022-02-01 21:09 | 2022-02-02 00:59 | 100 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN CORTES DE LINEAS DISTINTOS MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020100148 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2022-02-01 | 23000 | keep | 0 | Feb | 2022 | 0.015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-01 21:13 | 2022-02-01 21:15 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22020100260 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-01 | 4468 | keep | 0 | Feb | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2022-02-01 21:26 | 2022-02-02 11:00 | 6 | 013:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR AVE CRUZO LINEAS | B22020200270 | New_Event |  |  | Include | Wildlife | 814 | 2022-02-01 | 4884 | keep | 0 | Feb | 2022 | 0.0033265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-01 21:29 | 2022-02-01 23:05 | 567 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO TRAMO A TRAMO LLUVIAS Y VIENTOS DURANTE LA TARDE | C22020100098 | Partial_restoration | Bad Weather | Include | Include | Weather | 96 | 2022-02-01 | 54432 | keep | 0 | Feb | 2022 | 0.037073 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-01 21:29 | 2022-02-02 11:36 | 9 | 014:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA | C22020100186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 847 | 2022-02-01 | 7623 | keep | 0 | Feb | 2022 | 0.005192 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-02-01 21:30 | 2022-02-02 03:13 | 1834 | 005:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERRO POR SCADA | B22020100277 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 343 | 2022-02-01 | 629062 | keep | 0 | Feb | 2022 | 0.42845 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
CAGUAS | 2022-02-01 21:36 | 2022-02-02 15:32 | 30 | 017:56 | P | DESGANCHE | 1 X 65 EN C/L | C22020100416 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1076 | 2022-02-01 | 32280 | keep | 0 | Feb | 2022 | 0.021986 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-01 22:30 | 2022-02-02 09:12 | 5809 | 010:42 | T | BREAKER DEFECTUOSO O NO OPERA | SE SECCIONALIZO BREAKER 1710-01 POR CABLERIA QUEMADA Y SE CERRO N/O CONTRA 1716-03 | B22020100526 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 642 | 2022-02-01 | 3729378 | keep | 0 | Feb | 2022 | 2.5401 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-02-01 22:30 | 2022-02-01 23:47 | 3941 | 001:17 | T | BREAKER DEFECTUOSO O NO OPERA | SE ENCONTRO SUBESTACION FUERA DE SERVICIO SE CERRO EN LA SUBESTACION POR PERSONAL DE CDS EN INSPECCION SE ENCONTRO CABLES DEL 1710-01 QUEMADOS | B22020100526 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 77 | 2022-02-01 | 303457 | keep | 0 | Feb | 2022 | 0.20668 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-02-01 22:30 | 2022-02-01 23:47 | 3871 | 001:17 | T | BREAKER DEFECTUOSO O NO OPERA | SE ENCONTRO SUBESTACION FUERA DE SERVICIO SE CERRO EN LA SUBESTACION POR PERSONAL DE CDS EN INSPECCION SE ENCONTRO CABLES DEL 1710-01 QUEMADOS | B22020100526 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 77 | 2022-02-01 | 298067 | keep | 0 | Feb | 2022 | 0.20301 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2022-02-01 22:30 | 2022-02-02 03:23 | 5191 | 004:53 | T | BREAKER DEFECTUOSO O NO OPERA | SE ENCONTRO SUBESTACION FUERA DE SERVICIO SE CERRO B/I CONTRA EL 1710-04 Y SE SECCIONALIZO BREAKER 1710-01 POR CABLERIA QUEMADA Y SE CERRO N/O CONTRA EL BREAKER 1716-03 | B22020100526 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 293 | 2022-02-01 | 1520963 | keep | 0 | Feb | 2022 | 1.0359 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2022-02-01 22:30 | 2022-02-02 09:57 | 3597 | 011:27 | T | BREAKER DEFECTUOSO O NO OPERA | SE VERIFICO BKR POR PERSONAL DE CONSERVACION Y SE REALIZO UN DESGANCHE EN EGIDA DE CARR. 167 CON CARR. 829 Y SE CERRO BKR EN EL CAMPO SUB. SIN RTU | B22020200338 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 687 | 2022-02-01 | 2471139 | keep | 0 | Feb | 2022 | 1.6831 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-02-01 22:30 | 2022-02-02 03:16 | 492 | 004:46 | T | BREAKER DEFECTUOSO O NO OPERA | SE ENCONTRO SUBESTACION FUERA DE SERVICIO SE CERRO EN LA SUBESTACION | B22020100338 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 286 | 2022-02-01 | 140712 | keep | 0 | Feb | 2022 | 0.095838 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2022-02-01 22:30 | 2022-02-02 00:11 | 4028 | 001:41 | T | BREAKER DEFECTUOSO O NO OPERA | SE ENCONTRO SUBESTACION FUERA DE SERVICIO Y SE CERRO EN LA SUBESTACION POR PERSONAL DE CDS DURANTE LA INSPECCION SE ENCONTRO CABLES QUEMADOS DEL BREAKER 1710-01 | B22020100338 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 101 | 2022-02-01 | 406828 | keep | 0 | Feb | 2022 | 0.27709 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2022-02-01 22:30 | 2022-02-02 00:09 | 2617 | 001:39 | T | BREAKER DEFECTUOSO O NO OPERA | SE ENCONTRO SUBESTACION FUERA DE SERVICIO SE CERRO EN LA SUBESTACION POR PERSONAL DE CDS | B22020100338 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 99 | 2022-02-01 | 259083 | keep | 0 | Feb | 2022 | 0.17646 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
CAGUAS | 2022-02-01 23:05 | 2022-02-01 23:07 | 350 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO TRAMO A TRAMO LLUVIAS Y VIENTOS DURANTE LA TARDE | C22020100098 | Partial_restoration | Bad Weather | Include | Include | Weather | 2 | 2022-02-01 | 700 | keep | 0 | Feb | 2022 | 0.00047677 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-01 23:08 | 2022-02-02 01:14 | 100 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R22020100085 | New_Event |  |  | Include | Wildlife | 126 | 2022-02-01 | 12600 | keep | 0 | Feb | 2022 | 0.0085818 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-01 23:36 | 2022-02-02 00:16 | 10 | 000:40 | P | DESGANCHE | SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | S22020100391 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-02-01 | 400 | keep | 0 | Feb | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-01 23:48 | 2022-02-01 23:49 | 1863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020100114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 1863 | keep | 0 | Feb | 2022 | 0.0012689 | 0.0012689 | Momentary | FALSE | FALSE | Not_TMED_Event | 1863
ARECIBO | 2022-02-01 23:57 | 2022-02-01 23:58 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22020100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-01 | 3431 | keep | 0 | Feb | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
VEGA BAJA | 2022-02-01 23:57 | 2022-02-02 | 3387 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22020100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-01 | 10161 | keep | 0 | Feb | 2022 | 0.0069206 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2022-02-02 00:07 | 2022-02-02 07:31 | 190 | 007:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020200001 | New_Event | Bad Weather | Include | Include | Weather | 444 | 2022-02-02 | 84360 | keep | 0 | Feb | 2022 | 0.057457 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
ARECIBO | 2022-02-02 00:58 | 2022-02-02 00:59 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22020200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1227 | keep | 0 | Feb | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2022-02-02 01:01 | 2022-02-02 01:37 | 766 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO EN SALIDA. LLEVA 1709-05 Y 50% POR 1909-07 | S22020100359 | Additional_clients | Wire Down | Include | Include | Equipment | 36 | 2022-02-02 | 27576 | keep | 0 | Feb | 2022 | 0.018782 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 01:01 | 2022-02-02 01:37 | 2364 | 000:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE Y SE CERRO POR SCADA CARGA POR EL 1709-03 | S22020100359 | New_Event | Wire Down | Include | Include | Equipment | 36 | 2022-02-02 | 85104 | keep | 0 | Feb | 2022 | 0.057964 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
ARECIBO | 2022-02-02 01:24 | 2022-02-02 09:40 | 70 | 008:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22020200005 | New_Event | Wire Down | Include | Include | Equipment | 496 | 2022-02-02 | 34720 | keep | 0 | Feb | 2022 | 0.023648 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-02-02 01:36 | 2022-02-02 02:44 | 1879 | 001:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZARON AISLADOR ROTO ABRIENDO MACHETES EN CARR 156 GARAJE TOTAL VALLE TOLIMA | C22020200003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 68 | 2022-02-02 | 127772 | keep | 0 | Feb | 2022 | 0.087025 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2022-02-02 01:42 | 2022-02-02 12:54 | 800 | 011:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIAS Y SE REALIZO DESGANCHE | B2202200147 | New_Event | Wire Down | Include | Include | Equipment | 672 | 2022-02-02 | 537600 | keep | 0 | Feb | 2022 | 0.36616 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2022-02-02 01:50 | 2022-02-02 04:20 | 343 | 002:30 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR | S22020200013 | New_Event | Protection Miscoordination | Include | Include | Other | 150 | 2022-02-02 | 51450 | keep | 0 | Feb | 2022 | 0.035042 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
BAYAMON | 2022-02-02 01:50 | 2022-02-02 04:20 | 996 | 002:30 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR | S22020200013 | New_Event | Protection Miscoordination | Include | Include | Other | 150 | 2022-02-02 | 149400 | keep | 0 | Feb | 2022 | 0.10176 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
BAYAMON | 2022-02-02 01:50 | 2022-02-02 08:25 | 169 | 006:35 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1116-04 LLEVANDO LA CARGA PARCIAL DEL 1117-08 UN 80% | S22020100259 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 395 | 2022-02-02 | 66755 | keep | 0 | Feb | 2022 | 0.045467 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-02-02 01:50 | 2022-02-02 08:25 | 372 | 006:35 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1116-04 LLEVANDO LA CARGA PARCIAL DEL 1117-08 UN 80% | S22020100259 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 395 | 2022-02-02 | 146940 | keep | 0 | Feb | 2022 | 0.10008 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
BAYAMON | 2022-02-02 01:53 | 2022-02-02 02:28 | 35 | 000:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S22020200014 | New_Event | Cutout Failure | Include | Include | Equipment | 35 | 2022-02-02 | 1225 | keep | 0 | Feb | 2022 | 0.00083434 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-02-02 02:44 | 2022-02-02 11:48 | 934 | 009:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES ROTOS, REALIZO DESGANCHE Y CERRO MACHETES EN CARR 156 GARAJE TOTAL VALLE TOLIMA | C22020200003 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 544 | 2022-02-02 | 508096 | keep | 0 | Feb | 2022 | 0.34606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-02 03:12 | 2022-02-02 12:00 | 20 | 008:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO 2 CAJAS | R22020200005 | New_Event | Cutout Failure | Include | Include | Equipment | 528 | 2022-02-02 | 10560 | keep | 0 | Feb | 2022 | 0.0071924 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-02 03:13 | 2022-02-02 03:14 | 900 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALIMENTADOR DISPARO Y SE DEJO FUERA | B22020100277 | Partial_restoration | Wire Down | Include | Include | Equipment | 1 | 2022-02-02 | 900 | keep | 0 | Feb | 2022 | 0.00061299 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 03:14 | 2022-02-02 05:46 | 1834 | 002:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESGANCHO Y SE REPARO CONDUCTOR SE CERRO POR SCADA | B22020100277 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 152 | 2022-02-02 | 278768 | keep | 0 | Feb | 2022 | 0.18987 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
ARECIBO | 2022-02-02 03:28 | 2022-02-02 10:25 | 100 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020200007 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2022-02-02 | 41700 | keep | 0 | Feb | 2022 | 0.028402 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-02 04:21 | 2022-02-02 04:26 | 343 | 000:05 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR | S22020200013 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 5 | 2022-02-02 | 1715 | keep | 0 | Feb | 2022 | 0.0011681 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 04:21 | 2022-02-02 04:26 | 996 | 000:05 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR | S22020200013 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 5 | 2022-02-02 | 4980 | keep | 0 | Feb | 2022 | 0.0033919 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 04:21 | 2022-02-02 04:26 | 5 | 000:05 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR | S22020200013 | New_Event | Protection Miscoordination | Include | Include | Other | 5 | 2022-02-02 | 25 | keep | 0 | Feb | 2022 | 1.7027e-05 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-02 04:33 | 2022-02-02 04:52 | 343 | 000:19 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR PERSONAL DE CDS ELIMINO RELAY RLS CON HUMEDAD DEL TRANSFORMADOR | S22020200013 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 19 | 2022-02-02 | 6517 | keep | 0 | Feb | 2022 | 0.0044387 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 04:33 | 2022-02-02 04:52 | 996 | 000:19 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR PERSONAL DE CDS ELIMINO RELAY RLS CON HUMEDAD DEL TRANSOFRMADOR | S22020200013 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 19 | 2022-02-02 | 18924 | keep | 0 | Feb | 2022 | 0.012889 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 04:33 | 2022-02-02 04:52 | 5 | 000:19 | S | PROTECCION DEFECTUOSA | SE TRANSFIRIO A LA 1117-00 SE CERRO TIE BKR PERSONAL DE CDS ELIMINO RELAY RLS CON HUMEDAD DEL TRANSOFRMADOR | S22020200013 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 19 | 2022-02-02 | 95 | keep | 0 | Feb | 2022 | 6.4704e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-02 04:56 | 2022-02-02 16:38 | 80 | 011:42 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA DE T-34 @ T-35. SE REEMPLAZO SMU-20 EN SU-1 @ T-35 Y SE CERRO N/O EN SU-2 HASTA T-34. TODOS EN SERVICIO | S22020200028 | New_Event | UG Cable Fault | Include | Include | Equipment | 702 | 2022-02-02 | 56160 | keep | 0 | Feb | 2022 | 0.03825 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-02 04:59 | 2022-02-02 05:00 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 3511 | keep | 0 | Feb | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
VEGA BAJA | 2022-02-02 05:20 | 2022-02-02 11:31 | 300 | 006:11 | P | NO SE REPORTO CAUSA | 3 X 100 EN C/L | B22020200244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2022-02-02 | 111300 | keep | 0 | Feb | 2022 | 0.075806 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-02-02 05:27 | 2022-02-02 05:28 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 3511 | keep | 0 | Feb | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2022-02-02 05:46 | 2022-02-02 06:10 | 900 | 000:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MACHETES LUEGO DE CERRADO INTERRUPTOR | B22020100277 | Partial_restoration | Wire Down | Include | Include | Equipment | 24 | 2022-02-02 | 21600 | keep | 0 | Feb | 2022 | 0.014712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-02 05:57 | 2022-02-02 10:40 | 1 | 004:43 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN SU SE ELIMINO PARARAYO | R22020200014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 283 | 2022-02-02 | 283 | keep | 0 | Feb | 2022 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-02 06:00 | 2022-02-02 06:01 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1478 | keep | 0 | Feb | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
BARRANQUITAS | 2022-02-02 06:11 | 2022-02-02 10:37 | 1 | 004:26 | P | DESGANCHE | 1 X 40 EN RISER | C22020200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-02-02 | 266 | keep | 0 | Feb | 2022 | 0.00018117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-02 06:22 | 2022-02-02 06:23 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 3511 | keep | 0 | Feb | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
HUMACAO | 2022-02-02 06:53 | 2022-02-02 06:54 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22020200023 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-02 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
UTUADO | 2022-02-02 06:53 | 2022-02-02 08:58 | 5 | 002:05 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22020200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-02-02 | 625 | keep | 0 | Feb | 2022 | 0.00042568 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-02-02 06:54 | 2022-02-02 12:09 | 60 | 005:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22020200028 | 1st_after_momentary |  |  | Include | Wildlife | 315 | 2022-02-02 | 18900 | keep | 0 | Feb | 2022 | 0.012873 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-02 06:59 | 2022-02-02 09:19 | 75 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22020200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-02-02 | 10500 | keep | 0 | Feb | 2022 | 0.0071515 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-02 07:10 | 2022-02-02 10:50 | 12 | 003:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22020200050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 220 | 2022-02-02 | 2640 | keep | 0 | Feb | 2022 | 0.0017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-02-02 07:16 | 2022-02-02 14:41 | 4 | 007:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA PARTIDA | A22020200016 | New_Event | Wire Down | Include | Include | Equipment | 445 | 2022-02-02 | 1780 | keep | 0 | Feb | 2022 | 0.0012123 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-02 07:32 | 2022-02-02 11:29 | 60 | 003:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INFORMA FOREMAN REQUIERE DESGANCHE | M22020200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-02-02 | 14220 | keep | 0 | Feb | 2022 | 0.0096852 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-02 07:44 | 2022-02-02 12:30 | 75 | 004:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2022-02-02 | 21450 | keep | 0 | Feb | 2022 | 0.014609 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-02 07:59 | 2022-02-02 08:00 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 3438 | keep | 0 | Feb | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
ARECIBO | 2022-02-02 08:06 | 2022-02-02 10:10 | 1 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020200023 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2022-02-02 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-02 08:10 | 2022-02-02 09:24 | 30 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22020200024 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2022-02-02 | 2220 | keep | 0 | Feb | 2022 | 0.001512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-02 08:15 | 2022-02-02 08:16 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1370 | keep | 0 | Feb | 2022 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
FAJARDO | 2022-02-02 08:30 | 2022-02-02 11:41 | 15 | 003:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA | R22020200017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 191 | 2022-02-02 | 2865 | keep | 0 | Feb | 2022 | 0.0019513 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-02 08:34 | 2022-02-02 14:40 | 1 | 006:06 | P | NO SE REPORTO CAUSA | SE REEMPLAZO EN SU UN SMU-20 | S22020200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 366 | 2022-02-02 | 366 | keep | 0 | Feb | 2022 | 0.00024928 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-02 08:35 | 2022-02-02 16:06 | 10 | 007:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25 X 25KVA | S22020200085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 451 | 2022-02-02 | 4510 | keep | 0 | Feb | 2022 | 0.0030717 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-02 08:35 | 2022-02-02 12:02 | 6 | 003:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020200431 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2022-02-02 | 1242 | keep | 0 | Feb | 2022 | 0.00084592 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-02-02 08:37 | 2022-02-02 13:47 | 60 | 005:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22020200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-02-02 | 18600 | keep | 0 | Feb | 2022 | 0.012668 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-02 08:43 | 2022-02-02 08:44 | 3 | 000:01 | T | DESGANCHE | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVANDO 1707-03, 1707-04, 1707-05 | B22020200438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-02 | 3 | keep | 0 | Feb | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-02-02 08:43 | 2022-02-02 08:44 | 61 | 000:01 | T | DESGANCHE | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVANDO 1707-03 | B22020200438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-02 | 61 | keep | 0 | Feb | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-02-02 08:43 | 2022-02-02 08:44 | 1501 | 000:01 | T | DESGANCHE | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVANDO 1707-04 | B22020200438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-02 | 1501 | keep | 0 | Feb | 2022 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-02-02 08:43 | 2022-02-02 08:44 | 546 | 000:01 | T | DESGANCHE | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVANDO 1707-04 | B22020200438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-02 | 546 | keep | 0 | Feb | 2022 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2022-02-02 08:44 | 2022-02-02 12:53 | 50 | 004:09 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B22020200538 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-02-02 | 12450 | keep | 0 | Feb | 2022 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-02 08:50 | 2022-02-02 09:20 | 65 | 000:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22020200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-02-02 | 1950 | keep | 0 | Feb | 2022 | 0.0013281 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-02-02 08:57 | 2022-02-02 12:40 | 50 | 003:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22020200055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-02-02 | 11150 | keep | 0 | Feb | 2022 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-02 09:00 | 2022-02-02 12:39 | 6 | 003:39 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR SE REMPLAZO POSTE Y SE REPARO SECUNDARIA | B22020200458 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 219 | 2022-02-02 | 1314 | keep | 0 | Feb | 2022 | 0.00089496 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-02-02 09:01 | 2022-02-02 11:58 | 25 | 002:57 | P | NO SE REPORTO CAUSA | 1X50 EN CORTE DE LINEA | R22020200025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-02-02 | 4425 | keep | 0 | Feb | 2022 | 0.0030138 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-02-02 09:07 | 2022-02-02 14:47 | 80 | 005:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22020200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2022-02-02 | 27200 | keep | 0 | Feb | 2022 | 0.018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-02 09:12 | 2022-02-02 09:51 | 3485 | 000:39 | P | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO MACHETES EN AVE HOSTOS Y SE CERRO EN CARR. 831 BO. MINILLAS CARGA AL 1716-03 | B22020100526 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 39 | 2022-02-02 | 135915 | keep | 0 | Feb | 2022 | 0.092571 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-02 09:14 | 2022-02-02 17:15 | 20 | 008:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L RETEZO LINEAS | C22020200066 | New_Event | Wire Down | Include | Include | Equipment | 481 | 2022-02-02 | 9620 | keep | 0 | Feb | 2022 | 0.0065521 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-02 09:17 | 2022-02-02 13:27 | 65 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 65 EN C/L | B22020200589 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2022-02-02 | 16250 | keep | 0 | Feb | 2022 | 0.011068 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-02-02 09:18 | 2022-02-02 13:10 | 10 | 003:52 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-02-02 | 2320 | keep | 0 | Feb | 2022 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-02 09:24 | 2022-02-02 09:25 | 1227 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | A22020200032 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2022-02-02 | 1227 | keep | 0 | Feb | 2022 | 0.0008357 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-02 09:25 | 2022-02-02 11:50 | 30 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22020200024 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 145 | 2022-02-02 | 4350 | keep | 0 | Feb | 2022 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-02 09:29 | 2022-02-02 09:45 | 2891 | 000:16 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO EN EL CAMPO | R22020200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2022-02-02 | 46256 | keep | 0 | Feb | 2022 | 0.031505 | 0.001969 | Sustained | FALSE | FALSE | Not_TMED_Event | 2891
SAN JUAN | 2022-02-02 09:29 | 2022-02-02 09:30 | 1474 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | R22020200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1474 | keep | 0 | Feb | 2022 | 0.0010039 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
CANOVANAS | 2022-02-02 09:32 | 2022-02-02 09:33 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 2708 | keep | 0 | Feb | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 2100 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 98700 | keep | 0 | Feb | 2022 | 0.067224 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 922 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 43334 | keep | 0 | Feb | 2022 | 0.029515 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 1676 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 78772 | keep | 0 | Feb | 2022 | 0.053651 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 2844 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 133668 | keep | 0 | Feb | 2022 | 0.091041 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:37 | 2775 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-02-02 | 155400 | keep | 0 | Feb | 2022 | 0.10584 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 1457 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 68479 | keep | 0 | Feb | 2022 | 0.046641 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 1086 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 51042 | keep | 0 | Feb | 2022 | 0.034764 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:28 | 2134 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-02-02 | 100298 | keep | 0 | Feb | 2022 | 0.068313 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:55 | 1464 | 001:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2022-02-02 | 108336 | keep | 0 | Feb | 2022 | 0.073787 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:55 | 1833 | 001:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2022-02-02 | 135642 | keep | 0 | Feb | 2022 | 0.092385 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:55 | 1565 | 001:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2022-02-02 | 115810 | keep | 0 | Feb | 2022 | 0.078878 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-02 09:41 | 2022-02-02 10:55 | 977 | 001:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 FASE SOBRE ALIMENTADOR 4201-01 | P22020200086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2022-02-02 | 72298 | keep | 0 | Feb | 2022 | 0.049242 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
BAYAMON | 2022-02-02 09:51 | 2022-02-02 10:36 | 2906 | 000:45 | P | BREAKER DEFECTUOSO O NO OPERA | SE PATRULLO NO SE ENCONTRO NADA ADICIONAL Y SE CERRO MACHETES EN AVE. HOSTOS | B22020100526 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 45 | 2022-02-02 | 130770 | keep | 0 | Feb | 2022 | 0.089067 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-02 10:02 | 2022-02-02 12:49 | 5 | 002:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA | R22020100065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 167 | 2022-02-02 | 835 | keep | 0 | Feb | 2022 | 0.00056871 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-02 10:08 | 2022-02-02 14:36 | 200 | 004:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 Y 1 X 65 EN C/L SE REMPLAZARON 2 AISLADORES Y SE LLEVO LINEAS A SU SITIO | B22020200521 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 268 | 2022-02-02 | 53600 | keep | 0 | Feb | 2022 | 0.036507 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-02 10:08 | 2022-02-02 14:55 | 50 | 004:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE RETEZO LINEAS | B22020200522 | New_Event | Wire Down | Include | Include | Equipment | 287 | 2022-02-02 | 14350 | keep | 0 | Feb | 2022 | 0.0097737 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-02 10:16 | 2022-02-02 10:23 | 343 | 000:07 | S | ERROR HUMANO | PERSONAL DE OPERACIONES CONSERVACION OCASIONO DISPARO ACCIDENTAL EN TRABAJOS DE DIAGNOSTICO AL TRANSFORMADOR 1116-00. LUEGO LOS INTERRUPTORES 1116-04 Y 1116-03 DIERON PROBLES DE MECANISMO Y BOBINA DE CLOSE QUEMADAS | S22020200000 | New_Event | Human Error | Include | Include | Other | 7 | 2022-02-02 | 2401 | keep | 0 | Feb | 2022 | 0.0016353 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
BAYAMON | 2022-02-02 10:16 | 2022-02-02 12:41 | 996 | 002:25 | S | ERROR HUMANO | PERSONAL DE OPERACIONES CONSERVACION OCASIONO DISPARO ACCIDENTAL EN TRABAJOS DE DIAGNOSTICO AL TRANSFORMADOR 1116-00. LUEGO LOS INTERRUPTORES 1116-04 Y 1116-03 DIERON PROBLES DE MECANISMO Y BOBINA DE CLOSE QUEMADAS | S22020200000 | New_Event | Human Error | Include | Include | Other | 145 | 2022-02-02 | 144420 | keep | 0 | Feb | 2022 | 0.098364 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
BAYAMON | 2022-02-02 10:16 | 2022-02-02 10:54 | 169 | 000:38 | S | ERROR HUMANO | PERSONAL DE OPERACIONES CONSERVACION OCASIONO DISPARO ACCIDENTAL EN TRABAJOS DE DIAGNOSTICO AL TRANSFORMADOR 1116-00. LUEGO LOS INTERRUPTORES 1116-04 Y 1116-03 DIERON PROBLES DE MECANISMO Y BOBINA DE CLOSE QUEMADAS. CARGA TRANSFERIDA AL 1116-05 | S22020200000 | New_Event | Human Error | Include | Include | Other | 38 | 2022-02-02 | 6422 | keep | 0 | Feb | 2022 | 0.004374 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-02-02 10:16 | 2022-02-02 10:23 | 5 | 000:07 | S | ERROR HUMANO | PERSONAL DE OPERACIONES CONSERVACION OCASIONO DISPARO ACCIDENTAL EN TRABAJOS DE DIAGNOSTICO AL TRANSFORMADOR 1116-00. LUEGO LOS INTERRUPTORES 1116-04 Y 1116-03 DIERON PROBLES DE MECANISMO Y BOBINA DE CLOSE QUEMADAS | S22020200000 | New_Event | Human Error | Include | Include | Other | 7 | 2022-02-02 | 35 | keep | 0 | Feb | 2022 | 2.3838e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-02 10:16 | 2022-02-02 10:54 | 372 | 000:38 | P | ERROR HUMANO | PERSONAL DE OPERACIONES CONSERVACION OCASIONO DISPARO ACCIDENTAL EN TRABAJOS DE DIAGNOSTICO AL TRANSFORMADOR 1116-00. LUEGO LOS INTERRUPTORES 1116-04 Y 1116-03 DIERON PROBLES DE MECANISMO Y BOBINA DE CLOSE QUEMADAS. CARGA TRANSFERIDA AL 1116-05 | S22020200000 | New_Event | Human Error | Include | Include | Other | 38 | 2022-02-02 | 14136 | keep | 0 | Feb | 2022 | 0.009628 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
BAYAMON | 2022-02-02 10:18 | 2022-02-02 11:26 | 6 | 001:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22020200270 | New_Event | Secondary Wire Down | Include | Include | Equipment | 68 | 2022-02-02 | 408 | keep | 0 | Feb | 2022 | 0.00027789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-02 10:20 | 2022-02-02 16:25 | 30 | 006:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2022-02-02 | 10950 | keep | 0 | Feb | 2022 | 0.007458 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-02 10:21 | 2022-02-02 11:05 | 36 | 000:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL | B22020200528 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2022-02-02 | 1584 | keep | 0 | Feb | 2022 | 0.0010789 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-02 10:27 | 2022-02-02 10:28 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1681 | keep | 0 | Feb | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-02 10:27 | 2022-02-02 10:28 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1598 | keep | 0 | Feb | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
GUAYAMA | 2022-02-02 10:37 | 2022-02-02 14:38 | 463 | 004:01 | P | LINEA DE TRANSMISION 38KV | SE ABREN MACHETES PARA SECCIONALIZAR ALIMENTADOR PARA LEVANTAR TRAMO DE LINEA 3700 QUE CAYO SOBRE EL ALIMENTADOR | P22020200129 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 241 | 2022-02-02 | 111583 | keep | 0 | Feb | 2022 | 0.075999 | 0.00031535 | Sustained | FALSE | FALSE | Not_TMED_Event | 463
MAYAGÃœEZ | 2022-02-02 10:45 | 2022-02-02 12:45 | 12 | 002:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIO | M22020200015 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 120 | 2022-02-02 | 1440 | keep | 0 | Feb | 2022 | 0.00098078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-02-02 10:51 | 2022-02-02 13:49 | 1 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A22020200040 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2022-02-02 | 178 | keep | 0 | Feb | 2022 | 0.00012123 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-02 10:54 | 2022-02-02 18:09 | 20 | 007:15 | P | DESGANCHE | 1 X 40 EN C/L | C22020200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2022-02-02 | 8700 | keep | 0 | Feb | 2022 | 0.0059255 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-02 11:00 | 2022-02-02 18:15 | 42 | 007:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE IMPACTADO POR CAMION MEDIANTE GOI SJ-220202-02 | S22020200131 | New_Event |  |  | Include | Wildlife | 435 | 2022-02-02 | 18270 | keep | 0 | Feb | 2022 | 0.012444 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
PONCE | 2022-02-02 11:00 | 2022-02-02 11:41 | 15 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZO DE BAJANTES SECUNDARIOS | P22020200115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2022-02-02 | 615 | keep | 0 | Feb | 2022 | 0.00041887 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-02 11:19 | 2022-02-02 14:45 | 35 | 003:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | A22020200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-02-02 | 7210 | keep | 0 | Feb | 2022 | 0.0049107 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-02-02 11:41 | 2022-02-02 15:12 | 30 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22020200548 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-02-02 | 6330 | keep | 0 | Feb | 2022 | 0.0043113 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-02 11:58 | 2022-02-02 15:15 | 10 | 003:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE CAMBIO CAJA EN MONTURA DE TRANSFORMADOR | A22020200048 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2022-02-02 | 1970 | keep | 0 | Feb | 2022 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-02 12:13 | 2022-02-02 13:43 | 11 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22020200112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-02-02 | 990 | keep | 0 | Feb | 2022 | 0.00067428 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-02-02 12:30 | 2022-02-02 14:45 | 1 | 002:15 | P | NO SE REPORTO CAUSA | 1X10 EN TRANSFORMADOR | R22020200040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-02-02 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-02 12:31 | 2022-02-02 15:46 | 10 | 003:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE VOLVIO A CERRAR LUEGO DE REALIZAR DESGANCHE SECUNDARIO | R22020200041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 195 | 2022-02-02 | 1950 | keep | 0 | Feb | 2022 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-02-02 12:36 | 2022-02-02 13:57 | 1 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO VIENTOS FUERTES | M22020200029 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2022-02-02 | 81 | keep | 0 | Feb | 2022 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-02 12:49 | 2022-02-02 12:50 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL LLEVA PARTE DE LA CARGA DEL 1336-06 | R22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 2000 | keep | 0 | Feb | 2022 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
CAGUAS | 2022-02-02 12:49 | 2022-02-02 15:38 | 1 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | C22020200114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-02 | 169 | keep | 0 | Feb | 2022 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-02 13:07 | 2022-02-02 16:40 | 10 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | B22020200581 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-02-02 | 2130 | keep | 0 | Feb | 2022 | 0.0014507 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-02 13:15 | 2022-02-02 16:56 | 15 | 003:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50KVA POR LA MISMA CAPACIDAD | M22020200031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 221 | 2022-02-02 | 3315 | keep | 0 | Feb | 2022 | 0.0022578 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-02-02 13:16 | 2022-02-02 18:20 | 60 | 005:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22020200583 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2022-02-02 | 18240 | keep | 0 | Feb | 2022 | 0.012423 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-02-02 13:18 | 2022-02-02 15:02 | 7 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22020200124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-02-02 | 728 | keep | 0 | Feb | 2022 | 0.00049584 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-02-02 13:21 | 2022-02-02 14:32 | 42 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22020200125 | New_Event |  |  | Include | Wildlife | 71 | 2022-02-02 | 2982 | keep | 0 | Feb | 2022 | 0.002031 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2022-02-02 13:23 | 2022-02-02 13:40 | 10 | 000:17 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA ELIMINAR TOMA | S22020200161 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 17 | 2022-02-02 | 170 | keep | 0 | Feb | 2022 | 0.00011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-02 13:29 | 2022-02-02 13:39 | 6 | 000:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020200589 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-02-02 | 60 | keep | 0 | Feb | 2022 | 4.0866e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-02 13:38 | 2022-02-02 14:46 | 36 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 40 C/L | B22020200592 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-02-02 | 2448 | keep | 0 | Feb | 2022 | 0.0016673 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
GUAYAMA | 2022-02-02 13:51 | 2022-02-02 16:20 | 149 | 002:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22020200136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-02-02 | 22201 | keep | 0 | Feb | 2022 | 0.015121 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
AGUADILLA | 2022-02-02 13:53 | 2022-02-02 16:45 | 90 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR LIINEA PRIMARIA ROTA | M22020200033 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2022-02-02 | 15480 | keep | 0 | Feb | 2022 | 0.010543 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-02-02 13:55 | 2022-02-02 15:13 | 15 | 001:18 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 37.5 KVA A 2.4 KV POR OTRO 37.5 KVA A 4160 VOLTS | P22020200135 | New_Event | Service Transformer Failure | Include | Include | Equipment | 78 | 2022-02-02 | 1170 | keep | 0 | Feb | 2022 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-02 13:58 | 2022-02-02 14:58 | 59 | 001:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1117-09 AL REEMPLAZAR FUSIBLE EN MH-9. SE ENCONTRO AVERIA AISLADORES EN SU-2. SE ESTABLECIO GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-02-02 | 3540 | keep | 0 | Feb | 2022 | 0.0024111 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2022-02-02 13:58 | 2022-02-02 14:58 | 134 | 001:00 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1117-09 AL REEMPLAZAR FUSIBLE EN MH-9. SE ENCONTRO AVERIA AISLADORES EN SU-2. SE ESTABLECIO GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-02-02 | 8040 | keep | 0 | Feb | 2022 | 0.005476 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2022-02-02 13:58 | 2022-02-02 14:58 | 35 | 001:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1117-09 AL REEMPLAZAR FUSIBLE EN MH-9. SE ENCONTRO AVERIA AISLADORES EN SU-2. SE ESTABLECIO GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-02-02 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-02-02 13:58 | 2022-02-02 14:58 | 316 | 001:00 | T | AISLADOR ROTO, PARTIDO O SAFADO | AL REEMPLAZAR FUSIBLE EN MH-9 DISPARO ALIMENTADOR 1117-09 Y SE AVERIO AISLADORES EN SU-2 QUEDANDO 90% FUERA. SE ESTABLECIO GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL 1115-03, 30% 1115-04 Y 50% DEL 1115-02. | S22020200166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-02-02 | 18960 | keep | 0 | Feb | 2022 | 0.012914 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
MAYAGÃœEZ | 2022-02-02 14:08 | 2022-02-02 16:52 | 3 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y VIENTO | M22020200034 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2022-02-02 | 492 | keep | 0 | Feb | 2022 | 0.0003351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-02-02 14:12 | 2022-02-02 14:18 | 12 | 000:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE PRIMARIO | P22020200128 | New_Event | Wire Down | Include | Include | Equipment | 6 | 2022-02-02 | 72 | keep | 0 | Feb | 2022 | 4.9039e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-02 14:17 | 2022-02-02 16:38 | 82 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO FASES | P22020200139 | New_Event |  |  | Include | Wildlife | 141 | 2022-02-02 | 11562 | keep | 0 | Feb | 2022 | 0.0078748 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
CAGUAS | 2022-02-02 14:19 | 2022-02-02 16:16 | 20 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22020200138 | New_Event |  |  | Include | Wildlife | 117 | 2022-02-02 | 2340 | keep | 0 | Feb | 2022 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-02 14:26 | 2022-02-02 16:36 | 10 | 002:10 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22020200601 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-02-02 | 1300 | keep | 0 | Feb | 2022 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-02 14:28 | 2022-02-02 19:46 | 4 | 005:18 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 KVA X 50 KVA LA NOTA DEL DIA 1 PERO NO HABIA CLIENTES SIN SERVICIO LA INTERRUPCION FUE DEL DIA 2 | A22020100033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 318 | 2022-02-02 | 1272 | keep | 0 | Feb | 2022 | 0.00086635 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-02 14:30 | 2022-02-02 16:04 | 8 | 001:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR PEDESTAL SECUNDARIO AVERIADO | M22020200035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 94 | 2022-02-02 | 752 | keep | 0 | Feb | 2022 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-02 14:58 | 2022-02-02 17:24 | 285 | 002:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | AISLADORES AVERIADOS EN SU-2. 90% DEL 1117-09 FUERA. SE ESTABLECIO GOI SJ-220202-03 PARA REPARAR AVERIA. | S22020200166 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2022-02-02 | 41610 | keep | 0 | Feb | 2022 | 0.02834 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-02 15:05 | 2022-02-02 15:06 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020200143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 4035 | keep | 0 | Feb | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
ARECIBO | 2022-02-02 15:13 | 2022-02-02 16:35 | 30 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 50 RISER Y 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22020200071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-02-02 | 2460 | keep | 0 | Feb | 2022 | 0.0016755 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-02 15:24 | 2022-02-02 19:17 | 50 | 003:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-02-02 | 11650 | keep | 0 | Feb | 2022 | 0.0079348 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-02 15:37 | 2022-02-02 16:15 | 6 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 25 Y 1 X 20 EN BANCO DE XMR | B22020200609 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 38 | 2022-02-02 | 228 | keep | 0 | Feb | 2022 | 0.00015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 15:51 | 2022-02-02 19:45 | 6 | 003:54 | P | NO SE REPORTO CAUSA | 1 X 40 SMU-20 | S22020200183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2022-02-02 | 1404 | keep | 0 | Feb | 2022 | 0.00095626 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-02 16:24 | 2022-02-02 20:33 | 10 | 004:09 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA | M22020200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-02-02 | 2490 | keep | 0 | Feb | 2022 | 0.0016959 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-02 16:40 | 2022-02-02 17:27 | 1 | 000:47 | P | NO SE REPORTO CAUSA | 2 X 10 EN BANCO DE TRANSFORMADORES NO CAUSA | C22020200148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-02-02 | 47 | keep | 0 | Feb | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-02-02 16:45 | 2022-02-03 14:46 | 2 | 022:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | M22020200033 | Partial_restoration | Wire Down | Include | Include | Equipment | 1321 | 2022-02-02 | 2642 | keep | 0 | Feb | 2022 | 0.0017995 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-02 17:13 | 2022-02-02 18:44 | 30 | 001:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22020200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-02-02 | 2730 | keep | 0 | Feb | 2022 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-02 17:24 | 2022-02-02 17:26 | 59 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO 1117-09 PARA CERRAR EN SU-1 POR SEGURIDAD MEDIANTE GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-02-02 | 118 | keep | 0 | Feb | 2022 | 8.0369e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 17:24 | 2022-02-02 17:26 | 134 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO 1117-09 PARA CERRAR EN SU-1 POR SEGURIDAD MEDIANTE GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-02-02 | 268 | keep | 0 | Feb | 2022 | 0.00018253 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 17:24 | 2022-02-02 17:26 | 35 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO 1117-09 PARA CERRAR EN SU-1 POR SEGURIDAD MEDIANTE GOI SJ-220202-03. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-02-02 | 70 | keep | 0 | Feb | 2022 | 4.7677e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 17:24 | 2022-02-02 17:26 | 316 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO 1117-09 PARA CERRAR EN SU-1 POR SEGURIDAD MEDIANTE GOI SJ-220202-03. SE REEMPLAZARON DOS AISLADORES EN SU-2. LLEVANDO LA CARGA TOTAL DEL 1115-03, 50% DEL 1115-02 Y 30% DEL 1115-04 | S22020200166 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-02-02 | 632 | keep | 0 | Feb | 2022 | 0.00043045 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 17:24 | 2022-02-02 21:41 | 4 | 004:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR PALOMA | B22020200613 | New_Event |  |  | Include | Wildlife | 257 | 2022-02-02 | 1028 | keep | 0 | Feb | 2022 | 0.00070017 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-02-02 17:34 | 2022-02-02 18:34 | 10 | 001:00 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE Y REPARAR SECUNDARIA | S22020100308 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 60 | 2022-02-02 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-02 17:45 | 2022-02-02 21:22 | 60 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | S22020200193 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2022-02-02 | 13020 | keep | 0 | Feb | 2022 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-02 17:48 | 2022-02-02 23:24 | 1 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA | S22020200194 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2022-02-02 | 336 | keep | 0 | Feb | 2022 | 0.00022885 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-02 18:26 | 2022-02-03 09:21 | 9 | 014:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR AVE | C22020300155 | New_Event |  |  | Include | Wildlife | 895 | 2022-02-02 | 8055 | keep | 0 | Feb | 2022 | 0.0054862 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-02-02 19:29 | 2022-02-02 21:50 | 60 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN TRANSCLOSURE | S22020200209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2022-02-02 | 8460 | keep | 0 | Feb | 2022 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-02 19:35 | 2022-02-02 21:33 | 30 | 001:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22020200618 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-02-02 | 3540 | keep | 0 | Feb | 2022 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-02 19:50 | 2022-02-02 19:51 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 990 | keep | 0 | Feb | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CAGUAS | 2022-02-02 19:52 | 2022-02-03 10:36 | 4 | 014:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO FASE ABIERTA EN SECUNDARIA | C22020200158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 884 | 2022-02-02 | 3536 | keep | 0 | Feb | 2022 | 0.0024084 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-02-02 21:01 | 2022-02-02 22:55 | 35 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO MACHETES PARA SECCIONALIZAR | M22020200054 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2022-02-02 | 3990 | keep | 0 | Feb | 2022 | 0.0027176 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-02-02 21:08 | 2022-02-02 21:09 | 1192 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22020200055 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-02 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
VEGA BAJA | 2022-02-02 21:09 | 2022-02-02 21:10 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 2926 | keep | 0 | Feb | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2022-02-02 21:15 | 2022-02-02 21:16 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA PARTE DEL 9202-03 | B22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-02 21:15 | 2022-02-02 21:16 | 390 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 9202-02 QUE LLEVA PARTE DEL 9202-03 | B22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 390 | keep | 0 | Feb | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-02-02 21:48 | 2022-02-03 01:14 | 15 | 003:26 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | S22020200019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2022-02-02 | 3090 | keep | 0 | Feb | 2022 | 0.0021046 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-02 21:55 | 2022-02-02 21:56 | 1066 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S22020200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-02 | 1066 | keep | 0 | Feb | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2022-02-02 21:55 | 2022-02-02 23:10 | 353 | 001:15 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S22020200221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-02-02 | 26475 | keep | 0 | Feb | 2022 | 0.018032 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
AGUADILLA | 2022-02-02 21:57 | 2022-02-02 21:58 | 1192 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22020200000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-02-02 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-02-02 21:58 | 2022-02-03 00:47 | 1000 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22020200071 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 169 | 2022-02-02 | 169000 | keep | 0 | Feb | 2022 | 0.11511 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-02-02 22:20 | 2022-02-03 00:30 | 35 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22020200238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-02-02 | 4550 | keep | 0 | Feb | 2022 | 0.003099 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-02-02 22:32 | 2022-02-03 10:52 | 25 | 012:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L SE LEVANTO CONDUCTOR | B22020200621 | New_Event | Wire Down | Include | Include | Equipment | 740 | 2022-02-02 | 18500 | keep | 0 | Feb | 2022 | 0.0126 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-02 22:51 | 2022-02-02 23:26 | 7 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22020200186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-02-02 | 245 | keep | 0 | Feb | 2022 | 0.00016687 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-02-02 22:55 | 2022-02-02 23:26 | 820 | 000:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA ABRIENDO PUENTES Y SE CERRO MACHETES | M22020200054 | Additional_clients | Wire Down | Include | Include | Equipment | 31 | 2022-02-02 | 25420 | keep | 0 | Feb | 2022 | 0.017313 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-02 23:05 | 2022-02-03 09:13 | 80 | 010:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22020200097 | New_Event | Bad Weather | Include | Include | Weather | 608 | 2022-02-02 | 48640 | keep | 0 | Feb | 2022 | 0.033128 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-02 23:10 | 2022-02-02 23:30 | 50 | 000:20 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S22020200221 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-02-02 | 1000 | keep | 0 | Feb | 2022 | 0.0006811 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-02 23:15 | 2022-02-04 18:45 | 15 | 043:30 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO A PM-16 POR AVERIA SOTERRADA | A22020200028 | New_Event | UG Cable Fault | Include | Include | Equipment | 2610 | 2022-02-02 | 39150 | keep | 0 | Feb | 2022 | 0.026665 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-02 23:15 | 2022-02-03 19:00 | 10 | 019:45 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO SE SECCIONALIZO | A22020200098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1185 | 2022-02-02 | 11850 | keep | 0 | Feb | 2022 | 0.008071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-02-02 23:26 | 2022-02-03 05:30 | 60 | 006:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | M22020200088 | Partial_restoration | Wire Down | Include | Include | Equipment | 364 | 2022-02-02 | 21840 | keep | 0 | Feb | 2022 | 0.014875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-02 23:30 | 2022-02-03 00:37 | 125 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE A EN SALIDA DE ALIMENTADOR | S22020200221 | New_Event | Wire Down | Include | Include | Equipment | 67 | 2022-02-02 | 8375 | keep | 0 | Feb | 2022 | 0.0057042 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2022-02-03 00:04 | 2022-02-03 09:55 | 20 | 009:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22020300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 591 | 2022-02-03 | 11820 | keep | 0 | Feb | 2022 | 0.0080505 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-03 01:29 | 2022-02-03 11:40 | 30 | 010:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 611 | 2022-02-03 | 18330 | keep | 0 | Feb | 2022 | 0.012484 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-03 03:08 | 2022-02-03 09:05 | 45 | 005:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 357 | 2022-02-03 | 16065 | keep | 0 | Feb | 2022 | 0.010942 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-02-03 03:40 | 2022-02-03 03:41 | 651 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 651 | keep | 0 | Feb | 2022 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CANOVANAS | 2022-02-03 03:57 | 2022-02-03 03:58 | 2106 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR CONTROL | R22020300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-03 | 2106 | keep | 0 | Feb | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2022-02-03 04:30 | 2022-02-03 04:31 | 2179 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R22020300003 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-02-03 | 2179 | keep | 0 | Feb | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2022-02-03 04:31 | 2022-02-03 04:41 | 232 | 000:10 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO EN CARRTERA 190 FRENTE NATIONAL | R22020300005 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 10 | 2022-02-03 | 2320 | keep | 0 | Feb | 2022 | 0.0015801 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
BAYAMON | 2022-02-03 04:40 | 2022-02-03 04:42 | 343 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-03 | 686 | keep | 0 | Feb | 2022 | 0.00046723 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2022-02-03 04:41 | 2022-02-03 04:42 | 2179 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R22020300006 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-02-03 | 2179 | keep | 0 | Feb | 2022 | 0.0014841 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-03 04:42 | 2022-02-03 09:18 | 232 | 004:36 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO EN CARRTERA 190 FRENTE NATIONAL | R22020300005 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 276 | 2022-02-03 | 64032 | keep | 0 | Feb | 2022 | 0.043612 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
BAYAMON | 2022-02-03 05:46 | 2022-02-03 07:27 | 12 | 001:41 | P | DESGANCHE | 2 X 15 EN XMR SE REALIZO DEGANCHE | B22020300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-02-03 | 1212 | keep | 0 | Feb | 2022 | 0.00082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-03 06:00 | 2022-02-03 11:12 | 1 | 005:12 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DEGANCHE | B22020300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-02-03 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-03 06:00 | 2022-02-03 10:00 | 20 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22020300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2022-02-03 | 4800 | keep | 0 | Feb | 2022 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-03 06:08 | 2022-02-03 09:20 | 766 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA. LLEVA 1709-05 | B22020300008 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2022-02-03 | 147072 | keep | 0 | Feb | 2022 | 0.10017 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-02-03 06:08 | 2022-02-03 09:20 | 2364 | 003:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO 1709-05 QUE ESTA ATRAVES DEL 1709-03 Y SE CERRO POR SCADA EL 1709-03 | B22020300008 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2022-02-03 | 453888 | keep | 0 | Feb | 2022 | 0.30914 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
SAN JUAN | 2022-02-03 06:09 | 2022-02-03 08:38 | 40 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22020300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-02-03 | 5960 | keep | 0 | Feb | 2022 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-03 06:16 | 2022-02-03 08:09 | 50 | 001:53 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA Y SE REPORTA AVERIA SOTERRADA DESDE SU-47 | S22020300008 | New_Event | UG Cable Fault | Include | Include | Equipment | 113 | 2022-02-03 | 5650 | keep | 0 | Feb | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-02-03 06:25 | 2022-02-03 12:50 | 300 | 006:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE MASIVO TERMINO DE REPARAR A LAS 16:30 | P22020300001 | New_Event | Wire Down | Include | Include | Equipment | 385 | 2022-02-03 | 115500 | keep | 0 | Feb | 2022 | 0.078667 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-02-03 06:27 | 2022-02-03 09:39 | 50 | 003:12 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO 1 X 20 EN XMR 1 X 40 EN SU-11 | B22020300011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 192 | 2022-02-03 | 9600 | keep | 0 | Feb | 2022 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-02-03 06:50 | 2022-02-03 12:01 | 60 | 005:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 1 XX 80 Y 1 X 50 EN DIFERENTES CORTES DE LINEA SE REMPLAZO CAJA PRIMARIA | R22020300021 | New_Event | Cutout Failure | Include | Include | Equipment | 311 | 2022-02-03 | 18660 | keep | 0 | Feb | 2022 | 0.012709 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-03 06:50 | 2022-02-03 19:30 | 500 | 012:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA MISMO EVENTO SITUACIONES DIFERENTES | A22020300002 | New_Event | Wire Down | Include | Include | Equipment | 760 | 2022-02-03 | 380000 | keep | 0 | Feb | 2022 | 0.25882 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-02-03 06:50 | 2022-02-03 12:55 | 20 | 006:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA MISMO EVENTO SITUACIONES DIFERENTES | A22020300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2022-02-03 | 7300 | keep | 0 | Feb | 2022 | 0.004972 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-03 06:51 | 2022-02-03 13:01 | 1 | 006:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22020300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 370 | 2022-02-03 | 370 | keep | 0 | Feb | 2022 | 0.00025201 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-03 06:56 | 2022-02-03 06:57 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 2147 | keep | 0 | Feb | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
AGUADILLA | 2022-02-03 07:23 | 2022-02-03 12:35 | 50 | 005:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-02-03 | 15600 | keep | 0 | Feb | 2022 | 0.010625 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-03 07:29 | 2022-02-03 14:45 | 16 | 007:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M22020300007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 436 | 2022-02-03 | 6976 | keep | 0 | Feb | 2022 | 0.0047513 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-02-03 07:30 | 2022-02-03 12:39 | 50 | 005:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S22020300021 | New_Event | Cutout Failure | Include | Include | Equipment | 309 | 2022-02-03 | 15450 | keep | 0 | Feb | 2022 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-03 07:33 | 2022-02-03 10:50 | 40 | 003:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22020300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-02-03 | 7880 | keep | 0 | Feb | 2022 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-02-03 07:53 | 2022-02-03 07:54 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 1894 | keep | 0 | Feb | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
FAJARDO | 2022-02-03 08:00 | 2022-02-03 09:46 | 30 | 001:46 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | R22020300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-02-03 | 3180 | keep | 0 | Feb | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-03 08:02 | 2022-02-03 10:05 | 80 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 1 X 40 EN DIFERENTES CORTES DE LINEAS SE CREO DESPEJO PARA QUE AVES NO CRUCEN LAS FASES | A22020300005 | New_Event |  |  | Include | Wildlife | 123 | 2022-02-03 | 9840 | keep | 0 | Feb | 2022 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-02-03 08:06 | 2022-02-03 11:07 | 12 | 003:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y REEMPLAZAR BAJANTE SECUNDARIO DE XMR | C22020200037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 181 | 2022-02-03 | 2172 | keep | 0 | Feb | 2022 | 0.0014793 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-03 08:06 | 2022-02-03 08:07 | 5069 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22020300007 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-03 | 5069 | keep | 0 | Feb | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-02-03 08:07 | 2022-02-03 16:45 | 50 | 008:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22020300058 | 1st_after_momentary |  |  | Include | Wildlife | 518 | 2022-02-03 | 25900 | keep | 0 | Feb | 2022 | 0.01764 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-03 08:09 | 2022-02-03 12:56 | 50 | 004:47 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN SU-47 Y SE REEMPLAZO PARARRAYO AVERIADO | S22020300008 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 287 | 2022-02-03 | 14350 | keep | 0 | Feb | 2022 | 0.0097737 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-03 08:32 | 2022-02-03 08:36 | 2466 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-03 | 9864 | keep | 0 | Feb | 2022 | 0.0067183 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2022-02-03 08:40 | 2022-02-03 12:04 | 30 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN C.L SE RETEZO LINEAS Y SE REALIZO DESGANCHE | B22020300034 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2022-02-03 | 6120 | keep | 0 | Feb | 2022 | 0.0041683 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-03 08:55 | 2022-02-03 11:13 | 6 | 002:18 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE PARTIDO | A22020300003 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 138 | 2022-02-03 | 828 | keep | 0 | Feb | 2022 | 0.00056395 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-03 09:18 | 2022-02-03 09:19 | 2179 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION ANGEL PANNEL PARA CERRAR MACHETES EN CARRETERA 190 FRENTE NATIONAL POR ESTAR INCOMODO | R22020300005 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-02-03 | 2179 | keep | 0 | Feb | 2022 | 0.0014841 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-03 09:19 | 2022-02-03 10:09 | 60 | 000:50 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO OTRO MACHETE QUEMADO EN CARRETERA 190 EN ESQUINA CALLE A CERRANDO MACHETES EN CARRETERA 190 FRENTE NATIONAL | R22020300005 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 50 | 2022-02-03 | 3000 | keep | 0 | Feb | 2022 | 0.0020433 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-03 09:20 | 2022-02-03 09:55 | 100 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO N/OS DE T-2 @ T-3 Y DE T-12 @ T-13 | B22020300008 | Partial_restoration | Wire Down | Include | Include | Equipment | 35 | 2022-02-03 | 3500 | keep | 0 | Feb | 2022 | 0.0023838 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-03 09:24 | 2022-02-03 09:25 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 1227 | keep | 0 | Feb | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2022-02-03 09:31 | 2022-02-03 14:51 | 80 | 005:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22020300058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2022-02-03 | 25600 | keep | 0 | Feb | 2022 | 0.017436 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-02-03 09:40 | 2022-02-03 12:08 | 60 | 002:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22020300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-02-03 | 8880 | keep | 0 | Feb | 2022 | 0.0060481 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-03 09:55 | 2022-02-03 12:09 | 20 | 002:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS NO HABIAN CLIENTES SIN SERVICIO ANTES DE ABRIR EL TRANSFORMADOR | M22013000015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 134 | 2022-02-03 | 2680 | keep | 0 | Feb | 2022 | 0.0018253 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-03 10:01 | 2022-02-03 11:38 | 20 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22020300031 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2022-02-03 | 1940 | keep | 0 | Feb | 2022 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-03 10:27 | 2022-02-03 15:32 | 10 | 005:05 | P | TRANSFORMADOR AVERIADO | SE REEMPALZO XMR 25 X 25KVA | C22020300020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 305 | 2022-02-03 | 3050 | keep | 0 | Feb | 2022 | 0.0020773 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-03 10:36 | 2022-02-03 14:46 | 60 | 004:10 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22020300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-02-03 | 15000 | keep | 0 | Feb | 2022 | 0.010216 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-03 10:42 | 2022-02-03 10:43 | 225 | 000:01 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR A CAUSA DE CONTRATISTA WRIGHT TREE SERVICE EN LABORES DE PODA. CARGA POR EL 1303-05 | S22020300000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-03 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-02-03 10:42 | 2022-02-03 10:43 | 870 | 000:01 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR A CAUSA DE CONTRATISTA WRIGHT TREE SERVICE EN LABORES DE PODA. ADEMAS LLEVA LA CARGA DEL 1303-04 | S22020300000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-03 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-02-03 10:45 | 2022-02-03 11:46 | 6 | 001:01 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO SECUNDARIA Y SE REALIZO SECUNDARIA | B22020300022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 61 | 2022-02-03 | 366 | keep | 0 | Feb | 2022 | 0.00024928 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-03 10:46 | 2022-02-03 16:00 | 200 | 005:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-02-03 | 62800 | keep | 0 | Feb | 2022 | 0.042773 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-02-03 10:55 | 2022-02-03 13:13 | 15 | 002:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA EN TRANSFORMADOR PARA REMPLAZAR BARRAS EN PEDESTAL SECUNDARIO | P22020300022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 138 | 2022-02-03 | 2070 | keep | 0 | Feb | 2022 | 0.0014099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-03 11:02 | 2022-02-03 11:32 | 7 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO ABIERTO | C22020300025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-02-03 | 210 | keep | 0 | Feb | 2022 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-02-03 11:15 | 2022-02-03 11:50 | 1 | 000:35 | P | HERRAJE ROTO O PODRIDO | SE ABRE CAJAS EN TRANSFORMADOR PARA FIJAR TRANSFORMADOR EN CRUCETA | P22020300024 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 35 | 2022-02-03 | 35 | keep | 0 | Feb | 2022 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-03 11:16 | 2022-02-03 11:17 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22020300035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 4304 | keep | 0 | Feb | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
VEGA BAJA | 2022-02-03 11:29 | 2022-02-03 11:52 | 60 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22020300054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-02-03 | 1380 | keep | 0 | Feb | 2022 | 0.00093991 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-03 11:32 | 2022-02-03 15:51 | 162 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L SE LEVANTO CONDUCTOR | C22020300029 | New_Event | Wire Down | Include | Include | Equipment | 259 | 2022-02-03 | 41958 | keep | 0 | Feb | 2022 | 0.028577 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
BARRANQUITAS | 2022-02-03 11:34 | 2022-02-03 13:08 | 12 | 001:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR CONECTORES EN SECUNDARIA | C22020300030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 94 | 2022-02-03 | 1128 | keep | 0 | Feb | 2022 | 0.00076828 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-03 11:49 | 2022-02-03 18:16 | 40 | 006:27 | P | DESGANCHE | 1 X 50 EN C/L. SE DESGANCHO ARBOL Y RETEZO LINEA | C22020300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2022-02-03 | 15480 | keep | 0 | Feb | 2022 | 0.010543 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-03 12:03 | 2022-02-03 15:00 | 10 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22020300033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2022-02-03 | 1770 | keep | 0 | Feb | 2022 | 0.0012055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-03 12:06 | 2022-02-03 14:43 | 10 | 002:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C22020300034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 157 | 2022-02-03 | 1570 | keep | 0 | Feb | 2022 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-02-03 12:10 | 2022-02-03 14:55 | 15 | 002:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA POR 75 KVA | R22020300089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2022-02-03 | 2475 | keep | 0 | Feb | 2022 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-03 12:24 | 2022-02-03 13:40 | 10 | 001:16 | P | DESGANCHE | 1 X 50 EN RISER SE RETIRO ENREDADERA | A22020300044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-02-03 | 760 | keep | 0 | Feb | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-03 12:40 | 2022-02-03 17:10 | 80 | 004:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22020300041 | New_Event | Bad Weather | Include | Include | Weather | 270 | 2022-02-03 | 21600 | keep | 0 | Feb | 2022 | 0.014712 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-02-03 12:45 | 2022-02-03 12:46 | 3744 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO LINEAS ARIADAS | P22020300033 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-03 | 3744 | keep | 0 | Feb | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
CAGUAS | 2022-02-03 12:48 | 2022-02-03 15:08 | 10 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR AVE | C22020300036 | New_Event |  |  | Include | Wildlife | 140 | 2022-02-03 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-03 12:49 | 2022-02-03 14:01 | 3744 | 001:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE RETEZO LINEAS PRIMARIA EN BO TIBES Y SE COLOCO INTERRUPTOR EN SERVICIO | P22020300034 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 72 | 2022-02-03 | 269568 | keep | 0 | Feb | 2022 | 0.1836 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
MAYAGÃœEZ | 2022-02-03 12:50 | 2022-02-03 16:28 | 281 | 003:38 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 218 | 2022-02-03 | 61258 | keep | 0 | Feb | 2022 | 0.041723 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-02-03 12:50 | 2022-02-03 16:28 | 1252 | 003:38 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 218 | 2022-02-03 | 272936 | keep | 0 | Feb | 2022 | 0.1859 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-02-03 12:50 | 2022-02-03 17:21 | 595 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2022-02-03 | 161245 | keep | 0 | Feb | 2022 | 0.10982 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-02-03 12:50 | 2022-02-03 17:21 | 51 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2022-02-03 | 13821 | keep | 0 | Feb | 2022 | 0.0094134 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-02-03 12:50 | 2022-02-03 17:21 | 721 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2022-02-03 | 195391 | keep | 0 | Feb | 2022 | 0.13308 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-02-03 12:50 | 2022-02-03 16:32 | 1382 | 003:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 222 | 2022-02-03 | 306804 | keep | 0 | Feb | 2022 | 0.20896 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-02-03 12:50 | 2022-02-03 16:32 | 654 | 003:42 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 222 | 2022-02-03 | 145188 | keep | 0 | Feb | 2022 | 0.098887 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
PONCE | 2022-02-03 12:59 | 2022-02-03 14:42 | 60 | 001:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-02-03 | 6180 | keep | 0 | Feb | 2022 | 0.0042092 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-03 13:00 | 2022-02-03 15:03 | 100 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA APARENTE | A22020300045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-02-03 | 12300 | keep | 0 | Feb | 2022 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-03 13:13 | 2022-02-03 14:21 | 30 | 001:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-02-03 | 2040 | keep | 0 | Feb | 2022 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-03 13:17 | 2022-02-03 15:48 | 40 | 002:31 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-02-03 | 6040 | keep | 0 | Feb | 2022 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-03 13:19 | 2022-02-03 13:24 | 36 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO CARGA 1620-01 | R22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-03 | 180 | keep | 0 | Feb | 2022 | 0.0001226 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-03 13:19 | 2022-02-03 13:24 | 172 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO CARGA 1620-01 | R22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-03 | 860 | keep | 0 | Feb | 2022 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2022-02-03 13:19 | 2022-02-03 13:45 | 12 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22020300056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-02-03 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-03 13:26 | 2022-02-03 13:27 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO CARGA 1620-01 | R22020300000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-03 13:26 | 2022-02-03 13:27 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO CARGA 1620-01 | R22020300000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 172 | keep | 0 | Feb | 2022 | 0.00011715 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-03 13:32 | 2022-02-03 16:24 | 36 | 002:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L RAYOS | B22020300060 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2022-02-03 | 6192 | keep | 0 | Feb | 2022 | 0.0042173 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-02-03 13:32 | 2022-02-03 18:58 | 5 | 005:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22020300055 | New_Event | Bad Weather | Include | Include | Weather | 326 | 2022-02-03 | 1630 | keep | 0 | Feb | 2022 | 0.0011102 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-02-03 13:51 | 2022-02-03 15:59 | 50 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 200 AMP | A22020300061 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-02-03 | 6400 | keep | 0 | Feb | 2022 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-03 13:56 | 2022-02-03 13:58 | 974 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 NO AFECTO 6301 | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-03 | 1948 | keep | 0 | Feb | 2022 | 0.0013268 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
AGUADILLA | 2022-02-03 13:56 | 2022-02-03 23:14 | 100 | 009:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22020300060 | New_Event | Bad Weather | Include | Include | Weather | 558 | 2022-02-03 | 55800 | keep | 0 | Feb | 2022 | 0.038005 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-03 14:01 | 2022-02-03 15:06 | 30 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22020300064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-02-03 | 1950 | keep | 0 | Feb | 2022 | 0.0013281 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-03 14:03 | 2022-02-03 16:23 | 30 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE LLEVO LINEA A SU AISLADOR | B22020300067 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2022-02-03 | 4200 | keep | 0 | Feb | 2022 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-03 14:12 | 2022-02-04 10:29 | 10 | 020:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | P22020300060 | New_Event | Cutout Failure | Include | Include | Equipment | 1217 | 2022-02-03 | 12170 | keep | 0 | Feb | 2022 | 0.0082889 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-03 14:13 | 2022-02-03 14:17 | 343 | 000:04 | S | ERROR HUMANO | DISPARO 0020 LOCKOUT RADY RIVERA INSPECCIONANDO ALARMA LTC HIGH, SE REMONTO LOCKOUT Y SE CERRO TIE BKR Y SE RESTABLECIO SERVICIO | S22020300000 | New_Event | Human Error | Include | Include | Other | 4 | 2022-02-03 | 1372 | keep | 0 | Feb | 2022 | 0.00093446 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
BAYAMON | 2022-02-03 14:13 | 2022-02-03 14:17 | 996 | 000:04 | S | NO SE REPORTO CAUSA | DISPARO 0020 LOCKOUT RADY RIVERA INSPECCIONANDO ALARMA LTC HIGHT, SE REMONTO LOCKOUT Y SE CERRO TIE BKR Y SE RESTABLECIO SERVICIO | S22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-03 | 3984 | keep | 0 | Feb | 2022 | 0.0027135 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
BAYAMON | 2022-02-03 14:13 | 2022-02-03 14:17 | 169 | 000:04 | S | NO SE REPORTO CAUSA | DISPARO 0020 LOCKOUT RADY RIVERA INSPECCIONANDO ALARMA LTC HIGHT, SE REMONTO LOCKOUT Y SE CERRO TIE BKR Y SE RESTABLECIO SERVICIO | S22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-03 | 676 | keep | 0 | Feb | 2022 | 0.00046042 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-02-03 14:13 | 2022-02-03 14:16 | 5 | 000:03 | S | ERROR HUMANO | DISPARO 0020 LOCKOUT RADY RIVERA INSPECCIONANDO ALARMA LTC HIGH, SE REMONTO LOCKOUT Y SE CERRO TIE BKR Y SE RESTABLECIO SERVICIO | S22020300000 | New_Event | Human Error | Include | Include | Other | 3 | 2022-02-03 | 15 | keep | 0 | Feb | 2022 | 1.0216e-05 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-03 14:13 | 2022-02-03 14:16 | 5 | 000:03 | T | ERROR HUMANO | DISPARO 0020 LOCKOUT RADY RIVERA INSPECCIONANDO ALARMA LTC HIGH, SE REMONTO LOCKOUT Y SE CERRO TIE BKR Y SE RESTABLECIO SERVICIO | S22020300000 | New_Event | Human Error | Include | Include | Other | 3 | 2022-02-03 | 15 | keep | 0 | Feb | 2022 | 1.0216e-05 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-03 14:13 | 2022-02-03 14:21 | 727 | 000:08 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO PARTE POR 1620-5 | S22020300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-03 | 5816 | keep | 0 | Feb | 2022 | 0.0039613 | 0.00049516 | Sustained | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2022-02-03 14:13 | 2022-02-03 14:21 | 1615 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA PARCIAL 1206-3 SE PROBO QUEDO EN SERVICIO | S22020300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-03 | 12920 | keep | 0 | Feb | 2022 | 0.0087998 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
HUMACAO | 2022-02-03 14:13 | 2022-02-03 16:48 | 5630 | 002:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO PUENTE ABIERTO MEDIANTE GOI CG-20203-01. SE CERRO INTERRUPTOR PARA PODER DARLE VOLTAJE AL PB 2603-08F Y PODER CERRARLO. 90% CONTINUA FUERA | C22020300046 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2022-02-03 | 872650 | keep | 0 | Feb | 2022 | 0.59436 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
YAUCO | 2022-02-03 14:16 | 2022-02-03 16:00 | 125 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEA CAMION MUEVE ESTRUCTURA Y CAUSA CRUCE DE FASES PRIMARIAS | P22020300062 | New_Event |  |  | Include | Wildlife | 104 | 2022-02-03 | 13000 | keep | 0 | Feb | 2022 | 0.0088542 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-02-03 14:30 | 2022-02-03 15:15 | 1 | 000:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020300040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-02-03 | 45 | keep | 0 | Feb | 2022 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-03 14:31 | 2022-02-03 14:32 | 4641 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-03 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-02-03 14:32 | 2022-02-03 20:32 | 12 | 006:00 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22020300067 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 360 | 2022-02-03 | 4320 | keep | 0 | Feb | 2022 | 0.0029423 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-03 14:34 | 2022-02-03 14:35 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 888 | keep | 0 | Feb | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-02-03 14:34 | 2022-02-03 14:35 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 393 | keep | 0 | Feb | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-02-03 14:34 | 2022-02-03 14:35 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 4 | keep | 0 | Feb | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-03 14:34 | 2022-02-03 14:36 | 372 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-03 | 744 | keep | 0 | Feb | 2022 | 0.00050674 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-02-03 14:34 | 2022-02-03 14:35 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 2530 | keep | 0 | Feb | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-02-03 14:34 | 2022-02-03 14:35 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 MAL TIEMPO DESCARGAS ELECTRICAS | M22020300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 199 | keep | 0 | Feb | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
CAGUAS | 2022-02-03 14:44 | 2022-02-03 17:32 | 30 | 002:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO | C22020300056 | New_Event | Wire Down | Include | Include | Equipment | 168 | 2022-02-03 | 5040 | keep | 0 | Feb | 2022 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-02-03 14:45 | 2022-02-03 16:38 | 5 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22020300036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2022-02-03 | 565 | keep | 0 | Feb | 2022 | 0.00038482 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-03 14:51 | 2022-02-03 19:40 | 2 | 004:49 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22020300106 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 289 | 2022-02-03 | 578 | keep | 0 | Feb | 2022 | 0.00039367 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-02-03 14:53 | 2022-02-03 19:56 | 100 | 005:03 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L, 1 X 80 EN RISER SE RETIRO ENREDADERA Y SE REEMPLAZARON DOS PARARRAYOS | C22020300059 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 303 | 2022-02-03 | 30300 | keep | 0 | Feb | 2022 | 0.020637 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-03 14:57 | 2022-02-03 17:01 | 100 | 002:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-02-03 | 12400 | keep | 0 | Feb | 2022 | 0.0084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-03 15:00 | 2022-02-03 20:45 | 10 | 005:45 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-02-03 | 3450 | keep | 0 | Feb | 2022 | 0.0023498 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-03 15:20 | 2022-02-03 18:24 | 230 | 003:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO MACHETES | B22020300071 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2022-02-03 | 42320 | keep | 0 | Feb | 2022 | 0.028824 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
PONCE | 2022-02-03 15:25 | 2022-02-04 09:13 | 15 | 017:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P22020300073 | New_Event | Bad Weather | Include | Include | Weather | 1068 | 2022-02-03 | 16020 | keep | 0 | Feb | 2022 | 0.010911 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-02-03 15:34 | 2022-02-03 15:35 | 1047 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22020300091 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-03 | 1047 | keep | 0 | Feb | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
SAN JUAN | 2022-02-03 15:35 | 2022-02-03 17:35 | 12 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BARRA PEDESTAL | S22020300110 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2022-02-03 | 1440 | keep | 0 | Feb | 2022 | 0.00098078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-03 15:48 | 2022-02-03 17:33 | 10 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22020300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-02-03 | 1050 | keep | 0 | Feb | 2022 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-03 15:59 | 2022-02-03 16:00 | 1863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 1863 | keep | 0 | Feb | 2022 | 0.0012689 | 0.0012689 | Momentary | FALSE | FALSE | Not_TMED_Event | 1863
PONCE | 2022-02-03 15:59 | 2022-02-03 16:00 | 708 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 708 | keep | 0 | Feb | 2022 | 0.00048222 | 0.00048222 | Momentary | FALSE | FALSE | Not_TMED_Event | 708
YAUCO | 2022-02-03 15:59 | 2022-02-03 16:00 | 502 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 502 | keep | 0 | Feb | 2022 | 0.00034191 | 0.00034191 | Momentary | FALSE | FALSE | Not_TMED_Event | 502
YAUCO | 2022-02-03 15:59 | 2022-02-03 16:00 | 2747 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 2747 | keep | 0 | Feb | 2022 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2022-02-03 15:59 | 2022-02-03 16:00 | 1587 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 1587 | keep | 0 | Feb | 2022 | 0.0010809 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
YAUCO | 2022-02-03 15:59 | 2022-02-03 16:00 | 2671 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 2671 | keep | 0 | Feb | 2022 | 0.0018192 | 0.0018192 | Momentary | FALSE | FALSE | Not_TMED_Event | 2671
YAUCO | 2022-02-03 15:59 | 2022-02-03 16:00 | 508 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 508 | keep | 0 | Feb | 2022 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2022-02-03 15:59 | 2022-02-03 16:00 | 64 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 500 | P22020300087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-03 | 64 | keep | 0 | Feb | 2022 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2022-02-03 16:04 | 2022-02-03 18:27 | 100 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 50 EN C/L RAYOS | B22020300116 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2022-02-03 | 14300 | keep | 0 | Feb | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-03 16:12 | 2022-02-03 20:23 | 10 | 004:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR AVE | C22020300103 | New_Event |  |  | Include | Wildlife | 251 | 2022-02-03 | 2510 | keep | 0 | Feb | 2022 | 0.0017095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-03 16:18 | 2022-02-03 20:04 | 100 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P22020300091 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2022-02-03 | 22600 | keep | 0 | Feb | 2022 | 0.015393 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-03 16:25 | 2022-02-03 16:50 | 10 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO DE TOMA SOTERRADA | R22020300100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-02-03 | 250 | keep | 0 | Feb | 2022 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-03 16:29 | 2022-02-03 19:18 | 12 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22020300119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-03 | 2028 | keep | 0 | Feb | 2022 | 0.0013813 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-03 16:31 | 2022-02-03 17:30 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S220S0300120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-02-03 | 708 | keep | 0 | Feb | 2022 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-03 16:38 | 2022-02-03 16:39 | 3342 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 3342 | keep | 0 | Feb | 2022 | 0.0022762 | 0.0022762 | Momentary | FALSE | FALSE | Not_TMED_Event | 3342
HUMACAO | 2022-02-03 16:48 | 2022-02-03 17:05 | 5120 | 000:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO PUENTE ABIERTO MEDIANTE GOI CG-20203-01. SE CERRO PB 2603-08F Y SE DIO SERVICIO TOTAL | C22020300046 | Partial_restoration | Wire Down | Include | Include | Equipment | 17 | 2022-02-03 | 87040 | keep | 0 | Feb | 2022 | 0.059283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-03 16:55 | 2022-02-03 18:08 | 25 | 001:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-02-03 | 1825 | keep | 0 | Feb | 2022 | 0.001243 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-02-03 17:00 | 2022-02-03 19:40 | 12 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN C/L RAYOS | B22020300077 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2022-02-03 | 1920 | keep | 0 | Feb | 2022 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-03 17:17 | 2022-02-03 19:15 | 15 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22020300120 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2022-02-03 | 1770 | keep | 0 | Feb | 2022 | 0.0012055 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-03 17:22 | 2022-02-03 18:02 | 10 | 000:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERAS SOBRE LAS LINEAS | M22020300121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-02-03 | 400 | keep | 0 | Feb | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-03 17:29 | 2022-02-03 21:01 | 25 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L SE REPARO LINEAS AVERIADAS POR CAMION | B22020300080 | New_Event |  |  | Include | Wildlife | 212 | 2022-02-03 | 5300 | keep | 0 | Feb | 2022 | 0.0036098 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-03 17:32 | 2022-02-03 19:00 | 60 | 001:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SEA BRIO C/L TOTAL Y SE CERRO PUENTE ABIERTO (NO FUNDIO FUSIBLE) | C22020300056 | Additional_clients | Wire Down | Include | Include | Equipment | 88 | 2022-02-03 | 5280 | keep | 0 | Feb | 2022 | 0.0035962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-03 17:35 | 2022-02-03 19:40 | 80 | 002:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-02-03 | 10000 | keep | 0 | Feb | 2022 | 0.006811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-02-03 17:49 | 2022-02-03 19:26 | 350 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 1 X 80 EN OTRO C/L | C22020300146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-02-03 | 33950 | keep | 0 | Feb | 2022 | 0.023123 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
UTUADO | 2022-02-03 17:52 | 2022-02-03 19:56 | 25 | 002:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020300127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-02-03 | 3100 | keep | 0 | Feb | 2022 | 0.0021114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-02-03 18:04 | 2022-02-03 18:05 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22020300123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 2163 | keep | 0 | Feb | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
SAN JUAN | 2022-02-03 18:19 | 2022-02-03 21:56 | 12 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22020300135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-02-03 | 2604 | keep | 0 | Feb | 2022 | 0.0017736 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-02-03 18:26 | 2022-02-03 20:05 | 50 | 001:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMP | A22020300131 | New_Event | Cutout Failure | Include | Include | Equipment | 99 | 2022-02-03 | 4950 | keep | 0 | Feb | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-02-03 18:37 | 2022-02-03 20:48 | 10 | 002:11 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | R22020300103 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2022-02-03 | 1310 | keep | 0 | Feb | 2022 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-03 18:41 | 2022-02-03 19:49 | 500 | 001:08 | P | NO SE REPORTO CAUSA | DISPARO SECUNDARIO PORTATIL#8 SE RESETEO BANDERA Y SE CERRO LLEVA CARGA 20% DEL 1348-6 Y 20% 1336-8 | S22020300138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-02-03 | 34000 | keep | 0 | Feb | 2022 | 0.023157 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-02-03 18:41 | 2022-02-03 19:49 | 250 | 001:08 | P | NO SE REPORTO CAUSA | DISPARO SECUNDARIO PORTATIL#8 SE RESETEO BANDERA Y SE CERRO LLEVA CARGA 20% DEL 1348-6 Y 20% 1336-8 | S22020300138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-02-03 | 17000 | keep | 0 | Feb | 2022 | 0.011579 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-02-03 18:41 | 2022-02-03 19:49 | 1290 | 001:08 | T | NO SE REPORTO CAUSA | DISPARO SECUNDARIO PORTATIL#8 SE RESETEO BANDERA Y SE CERRO LLEVA CARGA 20% DEL 1348-6 Y 20% 1336-8 | S22020300138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-02-03 | 87720 | keep | 0 | Feb | 2022 | 0.059746 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-02-03 18:53 | 2022-02-03 20:17 | 12 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRO PORTAFUSIBLES QUE SE ABRIO AL VEHICULO IMPACTAR POSTE | B22020300085 | New_Event |  |  | Include | Wildlife | 84 | 2022-02-03 | 1008 | keep | 0 | Feb | 2022 | 0.00068654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-02-03 18:59 | 2022-02-03 21:09 | 40 | 002:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE MASIVO | A22020300135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-02-03 | 5200 | keep | 0 | Feb | 2022 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-03 19:26 | 2022-02-04 07:30 | 30 | 012:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22020300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 724 | 2022-02-03 | 21720 | keep | 0 | Feb | 2022 | 0.014793 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-03 19:39 | 2022-02-03 19:40 | 316 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020300138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 316 | keep | 0 | Feb | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
MAYAGÃœEZ | 2022-02-03 19:45 | 2022-02-03 19:46 | 3630 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22020300133 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-03 | 3630 | keep | 0 | Feb | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-02-03 19:46 | 2022-02-03 23:09 | 20 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22020300137 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 203 | 2022-02-03 | 4060 | keep | 0 | Feb | 2022 | 0.0027652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-03 19:46 | 2022-02-03 21:00 | 100 | 001:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE FIJO TREE WIRE DE CAJA PRIMARIA | A22020300140 | New_Event | Wire Down | Include | Include | Equipment | 74 | 2022-02-03 | 7400 | keep | 0 | Feb | 2022 | 0.0050401 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-03 20:28 | 2022-02-03 20:30 | 2524 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22020300107 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-02-03 | 5048 | keep | 0 | Feb | 2022 | 0.0034382 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-02-03 20:30 | 2022-02-03 22:28 | 99 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO | R22020300114 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 118 | 2022-02-03 | 11682 | keep | 0 | Feb | 2022 | 0.0079566 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
MAYAGÃœEZ | 2022-02-03 20:51 | 2022-02-04 09:38 | 100 | 012:47 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA POSTE EN MALAS CONDICIONES SE REFIRIO A TECNICA | M22020300135 | New_Event | Defective Pole | Include | Include | Equipment | 767 | 2022-02-03 | 76700 | keep | 0 | Feb | 2022 | 0.05224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-03 21:13 | 2022-02-04 12:02 | 136 | 014:49 | P | PARARRAYOS DEFECTUOSO | 1 X 80 Y 1 X 100 EN CORTES DE LINEA SE RETEZO LINEA Y REEMPLAZO PARARRAYOS | C22020300171 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 889 | 2022-02-03 | 120904 | keep | 0 | Feb | 2022 | 0.082347 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
VEGA BAJA | 2022-02-03 21:51 | 2022-02-03 21:52 | 538 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 538 | keep | 0 | Feb | 2022 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
HUMACAO | 2022-02-03 22:11 | 2022-02-04 10:49 | 454 | 012:38 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRO PB-G MAL TIEMPO | C22020300174 | New_Event | Bad Weather | Include | Include | Weather | 758 | 2022-02-03 | 344132 | keep | 0 | Feb | 2022 | 0.23439 | 0.00030922 | Sustained | FALSE | FALSE | Not_TMED_Event | 454
PONCE | 2022-02-03 22:22 | 2022-02-03 22:23 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P222020300XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-03 | 2379 | keep | 0 | Feb | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
VEGA BAJA | 2022-02-03 22:54 | 2022-02-04 09:30 | 40 | 010:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LLEVO CONDUCTOR A AISLADOR | B22020300101 | New_Event | Wire Down | Include | Include | Equipment | 636 | 2022-02-03 | 25440 | keep | 0 | Feb | 2022 | 0.017327 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-03 23:01 | 2022-02-04 00:26 | 14 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE CON AVE | R22020300136 | New_Event |  |  | Include | Wildlife | 85 | 2022-02-03 | 1190 | keep | 0 | Feb | 2022 | 0.0008105 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-02-04 00:29 | 2022-02-04 00:30 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22020400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2022-02-04 00:44 | 2022-02-04 00:45 | 2720 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR CAJA PRIMARIA QUEMADA | A22020400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-04 | 2720 | keep | 0 | Feb | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-02-04 00:45 | 2022-02-04 00:46 | 2720 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR CAJA PRIMARIA QUEMADA | A22020400001 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-04 | 2720 | keep | 0 | Feb | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-02-04 00:46 | 2022-02-04 13:11 | 75 | 012:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CONVERTIDOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22020400022 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 745 | 2022-02-04 | 55875 | keep | 0 | Feb | 2022 | 0.038056 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-02-04 00:48 | 2022-02-04 09:54 | 55 | 009:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22020400002 | New_Event |  |  | Include | Wildlife | 546 | 2022-02-04 | 30030 | keep | 0 | Feb | 2022 | 0.020453 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2022-02-04 00:51 | 2022-02-04 00:52 | 4188 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | R22020400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-04 | 4188 | keep | 0 | Feb | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CAGUAS | 2022-02-04 01:53 | 2022-02-04 01:54 | 725 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIAS | C22020400003 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-04 | 725 | keep | 0 | Feb | 2022 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
HUMACAO | 2022-02-04 02:53 | 2022-02-04 02:54 | 776 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C22020400004 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-04 | 776 | keep | 0 | Feb | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
CANOVANAS | 2022-02-04 04:29 | 2022-02-04 11:02 | 20 | 006:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L SE RETIRO AVE | R22020400003 | New_Event |  |  | Include | Wildlife | 393 | 2022-02-04 | 7860 | keep | 0 | Feb | 2022 | 0.0053534 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-04 04:40 | 2022-02-04 10:46 | 35 | 006:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA | C22020400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2022-02-04 | 12810 | keep | 0 | Feb | 2022 | 0.0087248 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-02-04 04:44 | 2022-02-04 04:45 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 281 | keep | 0 | Feb | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-02-04 04:44 | 2022-02-04 04:45 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1252 | keep | 0 | Feb | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-02-04 04:44 | 2022-02-04 04:45 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 595 | keep | 0 | Feb | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-02-04 04:44 | 2022-02-04 04:45 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 51 | keep | 0 | Feb | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-02-04 04:44 | 2022-02-04 04:45 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 721 | keep | 0 | Feb | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-02-04 04:44 | 2022-02-04 04:45 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1382 | keep | 0 | Feb | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-02-04 04:44 | 2022-02-04 04:45 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 654 | keep | 0 | Feb | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
CAGUAS | 2022-02-04 04:56 | 2022-02-04 04:57 | 3005 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL | C22020400007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-04 | 3005 | keep | 0 | Feb | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2022-02-04 05:02 | 2022-02-04 05:08 | 3005 | 000:06 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL | C22020400007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 6 | 2022-02-04 | 18030 | keep | 0 | Feb | 2022 | 0.01228 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
BARRANQUITAS | 2022-02-04 05:03 | 2022-02-04 13:55 | 456 | 008:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | C22020400009 | New_Event | Bad Weather | Include | Include | Weather | 532 | 2022-02-04 | 242592 | keep | 0 | Feb | 2022 | 0.16523 | 0.00031058 | Sustained | FALSE | FALSE | Not_TMED_Event | 456
CAGUAS | 2022-02-04 05:09 | 2022-02-04 06:06 | 3005 | 000:57 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR SE ABRIO MACHETES SOLO 1% EN SERVICIO CERRADO POR CONTROL | C22020400010 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 57 | 2022-02-04 | 171285 | keep | 0 | Feb | 2022 | 0.11666 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-04 05:43 | 2022-02-04 13:46 | 30 | 008:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR PRIMARIO NO FUNDIO | B22020400007 | New_Event | Wire Down | Include | Include | Equipment | 483 | 2022-02-04 | 14490 | keep | 0 | Feb | 2022 | 0.0098691 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-04 05:50 | 2022-02-04 10:22 | 8 | 004:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER UT2 TRAINED INFORMA NO SE DETERMINO CAUSA | A22020400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2022-02-04 | 2176 | keep | 0 | Feb | 2022 | 0.0014821 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-04 05:58 | 2022-02-04 09:55 | 29 | 003:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22020400020 | New_Event |  |  | Include | Wildlife | 237 | 2022-02-04 | 6873 | keep | 0 | Feb | 2022 | 0.0046812 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CAGUAS | 2022-02-04 06:06 | 2022-02-04 08:26 | 2985 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE DE LINEA A RISER CERRARON MACHETES | C22020400010 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 140 | 2022-02-04 | 417900 | keep | 0 | Feb | 2022 | 0.28463 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-04 06:09 | 2022-02-04 12:42 | 200 | 006:33 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22020400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 393 | 2022-02-04 | 78600 | keep | 0 | Feb | 2022 | 0.053534 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-02-04 06:28 | 2022-02-04 16:43 | 75 | 010:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADORES AVERIADO | C22020400029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 615 | 2022-02-04 | 46125 | keep | 0 | Feb | 2022 | 0.031416 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-02-04 06:45 | 2022-02-04 14:02 | 1 | 007:17 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA XMR Y 1 X 25 EN CORTE DE LINEA | B22020400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 437 | 2022-02-04 | 437 | keep | 0 | Feb | 2022 | 0.00029764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-04 07:05 | 2022-02-04 07:06 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22020400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 778 | keep | 0 | Feb | 2022 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
ARECIBO | 2022-02-04 07:10 | 2022-02-04 10:35 | 150 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22020400012 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2022-02-04 | 30750 | keep | 0 | Feb | 2022 | 0.020944 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-02-04 07:12 | 2022-02-04 09:22 | 1 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER UT2 TRAINED INFORMA NO SE ENCONTRO CAUSA | A22020400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-02-04 | 130 | keep | 0 | Feb | 2022 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-02-04 07:40 | 2022-02-04 15:32 | 60 | 007:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR MONOFASICO DEL SUELO | C22020400046 | New_Event | Wire Down | Include | Include | Equipment | 472 | 2022-02-04 | 28320 | keep | 0 | Feb | 2022 | 0.019289 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-02-04 08:06 | 2022-02-04 14:52 | 30 | 006:46 | P | DESCONECTIVO DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO MACHETES Y SE REALIZO DESGANCHE | B22020400015 | New_Event | Switch Failure | Include | Include | Equipment | 406 | 2022-02-04 | 12180 | keep | 0 | Feb | 2022 | 0.0082957 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-04 08:07 | 2022-02-04 12:29 | 39 | 004:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22020400059 | New_Event | Bad Weather | Include | Include | Weather | 262 | 2022-02-04 | 10218 | keep | 0 | Feb | 2022 | 0.0069594 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
PONCE | 2022-02-04 08:07 | 2022-02-04 12:52 | 25 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 18 NX EN PM DESCARGAS ELECTRICAS | P22020400006 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2022-02-04 | 7125 | keep | 0 | Feb | 2022 | 0.0048528 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-02-04 08:08 | 2022-02-04 09:55 | 100 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 1 X 65 Y 1 X 50 EN C/L SE RETIRO CHANGO | R22020400006 | New_Event |  |  | Include | Wildlife | 107 | 2022-02-04 | 10700 | keep | 0 | Feb | 2022 | 0.0072877 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-04 08:11 | 2022-02-04 10:40 | 40 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22020400021 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-02-04 | 5960 | keep | 0 | Feb | 2022 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-04 08:26 | 2022-02-04 08:37 | 2960 | 000:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE RAPARO PUENTE DE LINEA A RISER CERRARON MACHETES | C22020400010 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 11 | 2022-02-04 | 32560 | keep | 0 | Feb | 2022 | 0.022176 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-04 08:30 | 2022-02-04 10:12 | 6 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 12 NX EN T-373 | R22020400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-02-04 | 612 | keep | 0 | Feb | 2022 | 0.00041683 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-04 08:30 | 2022-02-04 11:33 | 1058 | 003:03 | P | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL #8 QUE LLEVA A SU VEZ LA CARGA DEL 1348-08, 20% 1348-06 Y 20% 1336-08 | S22020400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-02-04 | 193614 | keep | 0 | Feb | 2022 | 0.13187 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-02-04 08:30 | 2022-02-04 11:33 | 250 | 003:03 | P | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL #8 QUE LLEVA A SU VEZ LA CARGA DEL 1348-08, 20% 1348-06 Y 20% 1336-08 | S22020400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-02-04 | 45750 | keep | 0 | Feb | 2022 | 0.03116 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-02-04 08:30 | 2022-02-04 11:33 | 1290 | 003:03 | T | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL #8 QUE LLEVA A SU VEZ LA CARGA DEL 1348-08, 20% 1348-06 Y 20% 1336-08 | S22020400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-02-04 | 236070 | keep | 0 | Feb | 2022 | 0.16079 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
UTUADO | 2022-02-04 08:31 | 2022-02-04 17:09 | 15 | 008:38 | P | ESTRUCTURA AVERIADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | A22020400025 | New_Event | Defective Pole | Include | Include | Equipment | 518 | 2022-02-04 | 7770 | keep | 0 | Feb | 2022 | 0.0052921 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-04 08:32 | 2022-02-04 08:33 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22020400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2379 | keep | 0 | Feb | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-02-04 08:35 | 2022-02-04 11:32 | 40 | 002:57 | P | PROTECCION DEFECTUOSA | 1 X 80 EN RISER COORDINACION DE FUSIBLE ERRONEA SE TOMO AMPERAJE EN LA LINEA | P22020400009 | New_Event | Protection Miscoordination | Include | Include | Other | 177 | 2022-02-04 | 7080 | keep | 0 | Feb | 2022 | 0.0048222 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-02-04 08:38 | 2022-02-04 08:39 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2106 | keep | 0 | Feb | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
BAYAMON | 2022-02-04 08:47 | 2022-02-04 08:49 | 900 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1708-03 LLEVANDO PARTE 1708-02 | B22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-04 | 1800 | keep | 0 | Feb | 2022 | 0.001226 | 0.00061299 | Momentary | FALSE | FALSE | Not_TMED_Event | 900
BAYAMON | 2022-02-04 08:47 | 2022-02-04 08:49 | 1498 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1708-03 LLEVANDO PARTE 1708-02 | B22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-04 | 2996 | keep | 0 | Feb | 2022 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
FAJARDO | 2022-02-04 09:06 | 2022-02-04 09:07 | 1394 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 1394 | keep | 0 | Feb | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
ARECIBO | 2022-02-04 09:13 | 2022-02-04 15:26 | 7 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22020400028 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2022-02-04 | 2611 | keep | 0 | Feb | 2022 | 0.0017783 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-02-04 09:21 | 2022-02-04 21:45 | 25 | 012:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020400029 | New_Event | Bad Weather | Include | Include | Weather | 744 | 2022-02-04 | 18600 | keep | 0 | Feb | 2022 | 0.012668 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-04 09:24 | 2022-02-04 10:14 | 16 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA LEVANTAR SECUNDARIA DEL SUELO | C22020300171 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-02-04 | 800 | keep | 0 | Feb | 2022 | 0.00054488 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-02-04 09:25 | 2022-02-04 11:25 | 1 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | M22020400008 | New_Event |  |  | Include | Wildlife | 120 | 2022-02-04 | 120 | keep | 0 | Feb | 2022 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-04 09:28 | 2022-02-04 12:47 | 10 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA FOREMAN INDICA NO SE ENCONTRO CAUSA | A22020400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-02-04 | 1990 | keep | 0 | Feb | 2022 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-04 09:29 | 2022-02-04 09:30 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | M22020400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 1287 | keep | 0 | Feb | 2022 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2022-02-04 09:35 | 2022-02-04 13:00 | 4 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22020300138 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-02-04 | 820 | keep | 0 | Feb | 2022 | 0.0005585 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-04 09:51 | 2022-02-04 14:20 | 50 | 004:29 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020400012 | New_Event | Bad Weather | Include | Include | Weather | 269 | 2022-02-04 | 13450 | keep | 0 | Feb | 2022 | 0.0091607 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-04 09:52 | 2022-02-04 12:04 | 15 | 002:12 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMA | M22020400013 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 132 | 2022-02-04 | 1980 | keep | 0 | Feb | 2022 | 0.0013486 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-04 10:12 | 2022-02-04 15:18 | 20 | 005:06 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-02-04 | 6120 | keep | 0 | Feb | 2022 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-04 10:14 | 2022-02-04 12:09 | 958 | 001:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE ALIMENTADOR 1346-03 CON SOLO EL 40% DE SU CARGA. SE SECCIONALIZO AVERIA AISLADOR PARTIDO Y SE CERRO AMARRE CONTRA EL 1908-03 | S22020400154 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 115 | 2022-02-04 | 110170 | keep | 0 | Feb | 2022 | 0.075036 | 0.00065249 | Sustained | FALSE | FALSE | Not_TMED_Event | 958
SAN JUAN | 2022-02-04 10:20 | 2022-02-04 10:22 | 382 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO EL 95% DEL 1336-10 | S22020400000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-04 | 764 | keep | 0 | Feb | 2022 | 0.00052036 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
SAN JUAN | 2022-02-04 10:20 | 2022-02-04 10:22 | 36 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1620-04 LLEVANDO EL 1620-01 Y 95% DEL 1336-10 | S22020400000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-04 | 72 | keep | 0 | Feb | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-04 10:20 | 2022-02-04 10:21 | 172 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA LLEVA 1620-01 Y 95% DEL 1336-10 | S22020400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-04 | 172 | keep | 0 | Feb | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-02-04 10:21 | 2022-02-04 15:34 | 3 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE DE LINEA A LINEA | R22020400020 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 313 | 2022-02-04 | 939 | keep | 0 | Feb | 2022 | 0.00063955 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-02-04 10:23 | 2022-02-04 19:10 | 30 | 008:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REEMPLAZO 2 CAJAS PRIMARIA AVERIADAS | C22020400096 | New_Event | Cutout Failure | Include | Include | Equipment | 527 | 2022-02-04 | 15810 | keep | 0 | Feb | 2022 | 0.010768 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-04 10:29 | 2022-02-04 10:30 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3000 DE JUNCOS A RIO BLANCO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1089 | keep | 0 | Feb | 2022 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-02-04 10:29 | 2022-02-04 10:30 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3000 DE JUNCOS A RIO BLANCO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 3896 | keep | 0 | Feb | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-02-04 10:29 | 2022-02-04 10:30 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 3000 DE JUNCOS A RIO BLANCO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1467 | keep | 0 | Feb | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
ARECIBO | 2022-02-04 10:33 | 2022-02-04 16:50 | 15 | 006:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22020400045 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2022-02-04 | 5655 | keep | 0 | Feb | 2022 | 0.0038516 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-02-04 10:38 | 2022-02-04 12:50 | 100 | 002:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M22020400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-02-04 | 13200 | keep | 0 | Feb | 2022 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-04 10:40 | 2022-02-04 10:41 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO 1907-05 | S22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-04 10:40 | 2022-02-04 10:41 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO 1907-05 | S22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-02-04 10:41 | 2022-02-05 09:08 | 68 | 022:27 | P | NO SE REPORTO CAUSA | 3 X 65 EN C/L | S22020400088 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1347 | 2022-02-04 | 91596 | keep | 0 | Feb | 2022 | 0.062386 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CAGUAS | 2022-02-04 10:42 | 2022-02-04 10:43 | 1378 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22020400104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 1378 | keep | 0 | Feb | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
ARECIBO | 2022-02-04 10:49 | 2022-02-04 12:24 | 25 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22020400047 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2022-02-04 | 2375 | keep | 0 | Feb | 2022 | 0.0016176 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-02-04 10:59 | 2022-02-04 16:44 | 55 | 005:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | C22020400108 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 345 | 2022-02-04 | 18975 | keep | 0 | Feb | 2022 | 0.012924 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
UTUADO | 2022-02-04 11:00 | 2022-02-04 13:15 | 1 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22020400048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2022-02-04 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-04 11:05 | 2022-02-04 12:55 | 110 | 001:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZO AISLADOR | R22020400018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2022-02-04 | 12100 | keep | 0 | Feb | 2022 | 0.0082413 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
ARECIBO | 2022-02-04 11:05 | 2022-02-04 17:40 | 40 | 006:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020400051 | New_Event | Bad Weather | Include | Include | Weather | 395 | 2022-02-04 | 15800 | keep | 0 | Feb | 2022 | 0.010761 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-04 11:07 | 2022-02-04 12:51 | 60 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X20 EN SU-20 Y 1 X 50 EN CORTE DE LINEA SE RETIRO UN GATO DEL SU 20 | B22020400054 | New_Event |  |  | Include | Wildlife | 104 | 2022-02-04 | 6240 | keep | 0 | Feb | 2022 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-02-04 11:07 | 2022-02-04 19:16 | 10 | 008:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22020400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 489 | 2022-02-04 | 4890 | keep | 0 | Feb | 2022 | 0.0033306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-04 11:18 | 2022-02-04 12:56 | 143 | 001:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE ELIMINO CAJA PRIMARIA VACANTE | C22020400115 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2022-02-04 | 14014 | keep | 0 | Feb | 2022 | 0.0095449 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
ARECIBO | 2022-02-04 11:25 | 2022-02-05 15:17 | 1 | 027:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 25 CORTE DE LINEA SE REPARO LINEA PARTIDA PARA BOMBAS DE AGUA | A22020400053 | New_Event | Wire Down | Include | Include | Equipment | 1672 | 2022-02-04 | 1672 | keep | 0 | Feb | 2022 | 0.0011388 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-04 11:35 | 2022-02-04 13:34 | 1084 | 001:59 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECERRO INTERRUPTOR 3 VECES SE DEJO FUERA SE SECCIONALIZO MH-1 CAJA SECA AVERIADA 6 CLIENTES FUERA | C22020400121 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 119 | 2022-02-04 | 128996 | keep | 0 | Feb | 2022 | 0.087859 | 0.00073831 | Sustained | FALSE | FALSE | Not_TMED_Event | 1084
SAN JUAN | 2022-02-04 11:44 | 2022-02-04 13:23 | 3432 | 001:39 | P | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL 22 QUE LLEVA LAS CARGA PARCIALES DE LOS ALIMENTADORES 1204-02 UN 80% Y 1204-03 UN 40% | S22020400260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-02-04 | 339768 | keep | 0 | Feb | 2022 | 0.23141 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-02-04 11:44 | 2022-02-04 13:23 | 552 | 001:39 | P | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL 22 QUE LLEVA LAS CARGA PARCIALES DE LOS ALIMENTADORES 1204-02 UN 80% Y 1204-03 UN 40% | S22020400260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-02-04 | 54648 | keep | 0 | Feb | 2022 | 0.037221 | 0.00037596 | Sustained | FALSE | FALSE | Not_TMED_Event | 552
BAYAMON | 2022-02-04 11:51 | 2022-02-04 14:22 | 30 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1X65 EN CORTE DE LINEA MAL TIEMPO | B22020400066 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2022-02-04 | 4530 | keep | 0 | Feb | 2022 | 0.0030854 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-04 11:57 | 2022-02-04 11:58 | 2228 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR 8007-04 VEHICULO IMPACTO POSTE Y CRUZO LINEAS EL CUAL LLEVA LA CARGA DEL 8007-03 | A22020400061 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-04 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-04 11:57 | 2022-02-04 11:58 | 438 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR VEHICULO IMPACTO POSTE Y CRUZO LINEAS LLEVA LA CARGA DEL 8007-03 | A22020400061 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-04 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-04 11:58 | 2022-02-04 16:25 | 150 | 004:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA VEHICULO IMPACTO POSTE Y CRUZO LINEAS | A22020400068 | 1st_after_momentary |  |  | Include | Wildlife | 267 | 2022-02-04 | 40050 | keep | 0 | Feb | 2022 | 0.027278 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-02-04 12:02 | 2022-02-04 13:18 | 150 | 001:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M22020400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-02-04 | 11400 | keep | 0 | Feb | 2022 | 0.0077645 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-02-04 12:03 | 2022-02-04 15:54 | 500 | 003:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | C22002040009 | New_Event | Wire Down | Include | Include | Equipment | 231 | 2022-02-04 | 115500 | keep | 0 | Feb | 2022 | 0.078667 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2022-02-04 12:07 | 2022-02-04 13:40 | 200 | 001:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22020400045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-02-04 | 18600 | keep | 0 | Feb | 2022 | 0.012668 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-02-04 12:08 | 2022-02-04 14:41 | 210 | 002:33 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | C22020400131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-02-04 | 32130 | keep | 0 | Feb | 2022 | 0.021884 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
SAN JUAN | 2022-02-04 12:09 | 2022-02-04 17:09 | 186 | 005:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO PIN POLE TOP Y SE REALIZO DESGANCHE MEDIANTE GOI SJ-220204-01 | S22020400154 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 300 | 2022-02-04 | 55800 | keep | 0 | Feb | 2022 | 0.038005 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-02-04 12:10 | 2022-02-04 16:27 | 80 | 004:17 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22020400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-02-04 | 20560 | keep | 0 | Feb | 2022 | 0.014003 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-04 12:14 | 2022-02-04 12:15 | 679 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-02 LLEVANDO 85% DE 1705-05 | B22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 679 | keep | 0 | Feb | 2022 | 0.00046246 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2022-02-04 12:14 | 2022-02-04 12:15 | 510 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-02 LLEVANDO 85% 1705-05 | B22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 510 | keep | 0 | Feb | 2022 | 0.00034736 | 0.00034736 | Momentary | FALSE | FALSE | Not_TMED_Event | 510
BAYAMON | 2022-02-04 12:28 | 2022-02-04 16:08 | 200 | 003:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO G.O.I. BY-220204-01 | B22020400045 | New_Event | Wire Down | Include | Include | Equipment | 220 | 2022-02-04 | 44000 | keep | 0 | Feb | 2022 | 0.029968 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-02-04 12:35 | 2022-02-04 13:53 | 100 | 001:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020400068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-02-04 | 7800 | keep | 0 | Feb | 2022 | 0.0053125 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-04 12:46 | 2022-02-04 12:49 | 2580 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-04 | 7740 | keep | 0 | Feb | 2022 | 0.0052717 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2022-02-04 12:46 | 2022-02-04 12:49 | 500 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-04 | 1500 | keep | 0 | Feb | 2022 | 0.0010216 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2022-02-04 12:47 | 2022-02-04 13:53 | 150 | 001:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN C/L NO CAUSA | R22020400024 | New_Event | Wire Down | Include | Include | Equipment | 66 | 2022-02-04 | 9900 | keep | 0 | Feb | 2022 | 0.0067428 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-04 12:51 | 2022-02-04 14:51 | 2617 | 002:00 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO GATO DE SU Y SE CERRO INTERRUPTOR EN SUBESTACION INTERRUPTOR OPERO AL HACER PRUEBA EN CORTE DE LINEA SUBESTACION TENIA RTU DOWN | B22020400141 | Additional_clients |  |  | Include | Wildlife | 120 | 2022-02-04 | 314040 | keep | 0 | Feb | 2022 | 0.21389 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-04 12:55 | 2022-02-04 12:56 | 2708 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R22020400000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-04 | 2708 | keep | 0 | Feb | 2022 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-04 12:56 | 2022-02-04 14:29 | 110 | 001:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZO AISLADOR | R22020400018 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 93 | 2022-02-04 | 10230 | keep | 0 | Feb | 2022 | 0.0069676 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
FAJARDO | 2022-02-04 13:02 | 2022-02-04 14:36 | 50 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | R22020400026 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-02-04 | 4700 | keep | 0 | Feb | 2022 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-04 13:04 | 2022-02-04 13:05 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2107 | keep | 0 | Feb | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
SAN JUAN | 2022-02-04 13:05 | 2022-02-04 13:08 | 553 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 Y SE CERRO POR SCADA. ADEMAS LLEVA EL 30% DEL 1346-02. | S22002040000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-04 | 1659 | keep | 0 | Feb | 2022 | 0.0011299 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-02-04 13:05 | 2022-02-04 13:08 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 Y SE CERRO POR SCADA. ADEMAS LLEVA EL 30% DEL 1346-02. | S22002040000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-04 | 5406 | keep | 0 | Feb | 2022 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-02-04 13:07 | 2022-02-04 18:31 | 100 | 005:24 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22020400200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 324 | 2022-02-04 | 32400 | keep | 0 | Feb | 2022 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-04 13:10 | 2022-02-04 13:11 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2402-03 LLEVA 2404-06 | R22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 4085 | keep | 0 | Feb | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-02-04 13:10 | 2022-02-04 13:11 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 2402-03 LLEVA 2404-06 | R22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 7621 | keep | 0 | Feb | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2022-02-04 13:11 | 2022-02-04 17:16 | 40 | 004:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L DESPEGO PUENTE DEL POSTE | R22020400040 | New_Event | Wire Down | Include | Include | Equipment | 245 | 2022-02-04 | 9800 | keep | 0 | Feb | 2022 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-02-04 13:11 | 2022-02-04 15:05 | 122 | 001:54 | P | DESGANCHE | 2 X 100 EN C/L | R22020400052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-02-04 | 13908 | keep | 0 | Feb | 2022 | 0.0094727 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
ARECIBO | 2022-02-04 13:11 | 2022-02-04 14:30 | 20 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020400075 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2022-02-04 | 1580 | keep | 0 | Feb | 2022 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-04 13:12 | 2022-02-04 19:06 | 60 | 005:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN C/L SE REPARO TERMINACION EN SU-27 | S22020400175 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 354 | 2022-02-04 | 21240 | keep | 0 | Feb | 2022 | 0.014466 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-04 13:12 | 2022-02-04 15:01 | 50 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22020400207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-02-04 | 5450 | keep | 0 | Feb | 2022 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-04 13:15 | 2022-02-04 13:16 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S22020400213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 3718 | keep | 0 | Feb | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2022-02-04 13:15 | 2022-02-04 16:21 | 20 | 003:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22020400150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-02-04 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-04 13:17 | 2022-02-04 14:35 | 40 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1X80 EN CORTE DE LINEA POR MAL TIEMPO Y FUERTES LLUVIAS CON TRUENOS EN EL AREA | B22020400087 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2022-02-04 | 3120 | keep | 0 | Feb | 2022 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-04 13:17 | 2022-02-04 20:00 | 8 | 006:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22020400078 | New_Event | Wire Down | Include | Include | Equipment | 403 | 2022-02-04 | 3224 | keep | 0 | Feb | 2022 | 0.0021959 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-04 13:19 | 2022-02-04 14:40 | 10 | 001:21 | P | ERROR HUMANO | 1 X 20 EN XMR. PERSONAL DE LOW VOLTAGE CRUZO LINEA Y FUNDIO FUSIBLE INFORMA JUAN C. RAMOS | S22020400219 | New_Event | Human Error | Include | Include | Other | 81 | 2022-02-04 | 810 | keep | 0 | Feb | 2022 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-04 13:19 | 2022-02-04 19:15 | 1243 | 005:56 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR SECCIONALIZANDO ALIMENTADOR 10% EN SERVICIO | B22020400214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 356 | 2022-02-04 | 442508 | keep | 0 | Feb | 2022 | 0.30139 | 0.0008466 | Sustained | FALSE | FALSE | Not_TMED_Event | 1243
ARECIBO | 2022-02-04 13:21 | 2022-02-04 17:53 | 50 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22020400080 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2022-02-04 | 13600 | keep | 0 | Feb | 2022 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-02-04 13:33 | 2022-02-04 14:49 | 65 | 001:16 | P | DESGANCHE | 2 X 40 EN C/L | R22020400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-02-04 | 4940 | keep | 0 | Feb | 2022 | 0.0033646 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-02-04 13:34 | 2022-02-04 19:13 | 6 | 005:39 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO CAJA SECA EN MH-1 SE CERRO MACHETE DE RISER HACIA MH-1 | C22020400159 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 339 | 2022-02-04 | 2034 | keep | 0 | Feb | 2022 | 0.0013853 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-04 13:34 | 2022-02-04 14:50 | 41 | 001:16 | P | HERRAJE ROTO O PODRIDO | 1 X 50 EN CORTE DE LINEA SE REPARO SOPORTE DE CRUCETA | C22020400156 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 76 | 2022-02-04 | 3116 | keep | 0 | Feb | 2022 | 0.0021223 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2022-02-04 13:41 | 2022-02-04 18:26 | 15 | 004:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22020400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-02-04 | 4275 | keep | 0 | Feb | 2022 | 0.0029117 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-02-04 13:45 | 2022-02-04 17:25 | 80 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES Y DESGANCHE | M22020400085 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2022-02-04 | 17600 | keep | 0 | Feb | 2022 | 0.011987 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-04 13:52 | 2022-02-04 13:53 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22020400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2858 | keep | 0 | Feb | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
MAYAGÃœEZ | 2022-02-04 13:53 | 2022-02-04 13:54 | 393 | 000:01 | T | DESGANCHE | CARGA POR 6007-05 RAMAS SOBRE LAS LINEAS | M22020400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-04 | 393 | keep | 0 | Feb | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-02-04 13:53 | 2022-02-04 13:54 | 4 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6007-04 POR RAMAS SOBRE ALIMENTADOR 6007-04 | M22020400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-04 | 4 | keep | 0 | Feb | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-04 13:53 | 2022-02-04 16:30 | 40 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1X80 EN CORTE DE LINEA POR MAL TIEMPO Y FUERTES LLUVIAS CON TRUENOS EN EL AREA | B22020400136 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2022-02-04 | 6280 | keep | 0 | Feb | 2022 | 0.0042773 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-04 13:53 | 2022-02-04 17:18 | 20 | 003:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020400179 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-02-04 | 4100 | keep | 0 | Feb | 2022 | 0.0027925 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-04 13:54 | 2022-02-04 16:29 | 150 | 002:35 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020400096 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-02-04 | 23250 | keep | 0 | Feb | 2022 | 0.015835 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-02-04 13:55 | 2022-02-04 17:14 | 60 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L LEVANTO CONDUCTOR | R22020400053 | New_Event | Wire Down | Include | Include | Equipment | 199 | 2022-02-04 | 11940 | keep | 0 | Feb | 2022 | 0.0081323 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-02-04 14:03 | 2022-02-04 19:00 | 80 | 004:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | C22020400165 | New_Event | Bad Weather | Include | Include | Weather | 297 | 2022-02-04 | 23760 | keep | 0 | Feb | 2022 | 0.016183 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-02-04 14:05 | 2022-02-04 14:06 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2410 | keep | 0 | Feb | 2022 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2022-02-04 14:05 | 2022-02-04 14:06 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2826 | keep | 0 | Feb | 2022 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BAYAMON | 2022-02-04 14:06 | 2022-02-04 16:48 | 30 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTES DE LINEA | B22020400127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-02-04 | 4860 | keep | 0 | Feb | 2022 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-04 14:08 | 2022-02-04 14:09 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020400098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 1417 | keep | 0 | Feb | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
YAUCO | 2022-02-04 14:13 | 2022-02-04 15:41 | 100 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P22020400057 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2022-02-04 | 8800 | keep | 0 | Feb | 2022 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-04 14:20 | 2022-02-04 16:46 | 60 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020400103 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2022-02-04 | 8760 | keep | 0 | Feb | 2022 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-02-04 14:22 | 2022-02-05 10:10 | 20 | 019:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZARON DOS XMR AVERIADOS DE 50KVA Y 25KVA | B22020400143 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1188 | 2022-02-04 | 23760 | keep | 0 | Feb | 2022 | 0.016183 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-04 14:23 | 2022-02-05 01:55 | 50 | 011:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA REPARAR PUENTE | S22020400249 | New_Event | Wire Down | Include | Include | Equipment | 692 | 2022-02-04 | 34600 | keep | 0 | Feb | 2022 | 0.023566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-04 14:27 | 2022-02-04 15:58 | 9 | 001:31 | P | PARARRAYOS DEFECTUOSO | 2 X 140 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C22020400166 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 91 | 2022-02-04 | 819 | keep | 0 | Feb | 2022 | 0.00055782 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-02-04 14:29 | 2022-02-04 14:54 | 1 | 000:25 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA POR MAL TIEMPO | P22020400059 | New_Event | Bad Weather | Include | Include | Weather | 25 | 2022-02-04 | 25 | keep | 0 | Feb | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-04 14:29 | 2022-02-04 14:46 | 4381 | 000:17 | T | DESGANCHE | DISPARO DE INTERRUPTOR BAMBUS SOBRE LINEAS | M22020400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-02-04 | 74477 | keep | 0 | Feb | 2022 | 0.050726 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
HUMACAO | 2022-02-04 14:32 | 2022-02-04 18:58 | 21 | 004:26 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22020400167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-02-04 | 5586 | keep | 0 | Feb | 2022 | 0.0038046 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-02-04 14:32 | 2022-02-05 11:10 | 1 | 020:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22020400110 | New_Event | Bad Weather | Include | Include | Weather | 1238 | 2022-02-04 | 1238 | keep | 0 | Feb | 2022 | 0.0008432 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-02-04 14:34 | 2022-02-04 15:12 | 27 | 000:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA LEVANTAR SECUNDARIA IMPACTADA POR CAMION Y SE DEJO TOMA AVERIADA FUERA | C22020400169 | New_Event |  |  | Include | Wildlife | 38 | 2022-02-04 | 1026 | keep | 0 | Feb | 2022 | 0.0006988 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-02-04 14:35 | 2022-02-04 16:18 | 50 | 001:43 | P | NO SE REPORTO CAUSA | 1X100 EN CORTE DE LINEA | B22020400155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-02-04 | 5150 | keep | 0 | Feb | 2022 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-02-04 14:40 | 2022-02-04 16:36 | 126 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L REMPLAZO CAJA AVERIADA | R22020400066 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2022-02-04 | 14616 | keep | 0 | Feb | 2022 | 0.0099549 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
BAYAMON | 2022-02-04 14:43 | 2022-02-04 14:51 | 4028 | 000:08 | T | ERROR HUMANO | PERSONAL EN SUBESTACION DISPARO INTERRUPTOR POR EQUIVOCACION AL INTENTAR CERRAR INTERRUPTOR 1719-19 | B22020400000 | New_Event | Human Error | Include | Include | Other | 8 | 2022-02-04 | 32224 | keep | 0 | Feb | 2022 | 0.021948 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
MAYAGÃœEZ | 2022-02-04 14:46 | 2022-02-05 00:37 | 10 | 009:51 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22020400175 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 591 | 2022-02-04 | 5910 | keep | 0 | Feb | 2022 | 0.0040253 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-04 14:47 | 2022-02-04 18:29 | 60 | 003:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020400128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-02-04 | 13320 | keep | 0 | Feb | 2022 | 0.0090722 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-02-04 14:49 | 2022-02-04 16:28 | 5 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR Y SE REMPLAZO PARARRAYO QUEMADO | M22020400130 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2022-02-04 | 495 | keep | 0 | Feb | 2022 | 0.00033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-02-04 14:50 | 2022-02-04 18:22 | 2 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22020400172 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2022-02-04 | 424 | keep | 0 | Feb | 2022 | 0.00028878 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-04 14:51 | 2022-02-04 16:16 | 60 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X20 EN SU-20 Y 1 X 50 EN CORTE DE LINEA SE RETIRO UN GATO DEL SU 20 | B22020400054 | Partial_restoration |  |  | Include | Wildlife | 85 | 2022-02-04 | 5100 | keep | 0 | Feb | 2022 | 0.0034736 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-04 15:10 | 2022-02-04 18:02 | 40 | 002:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020400137 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2022-02-04 | 6880 | keep | 0 | Feb | 2022 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-04 15:10 | 2022-02-04 19:05 | 25 | 003:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | B22020400181 | New_Event | Wire Down | Include | Include | Equipment | 235 | 2022-02-04 | 5875 | keep | 0 | Feb | 2022 | 0.0040014 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-04 15:18 | 2022-02-04 19:05 | 35 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22020400190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-02-04 | 7945 | keep | 0 | Feb | 2022 | 0.0054113 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-02-04 15:22 | 2022-02-05 09:50 | 65 | 018:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22020400262 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1108 | 2022-02-04 | 72020 | keep | 0 | Feb | 2022 | 0.049052 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-02-04 15:22 | 2022-02-05 15:15 | 6 | 023:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22020400140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1433 | 2022-02-04 | 8598 | keep | 0 | Feb | 2022 | 0.0058561 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-04 15:28 | 2022-02-04 19:20 | 18 | 003:52 | P | NO SE REPORTO CAUSA | SE CERRO PORTAFUSIBLE NO FUNDIO CLIENTE ALEGA PERSONAL DE LUMA TRABAJO EN EL AREA | C22020400182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-02-04 | 4176 | keep | 0 | Feb | 2022 | 0.0028443 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2022-02-04 15:30 | 2022-02-04 17:09 | 40 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P22020400067 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2022-02-04 | 3960 | keep | 0 | Feb | 2022 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-04 15:31 | 2022-02-04 18:43 | 30 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020400141 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2022-02-04 | 5760 | keep | 0 | Feb | 2022 | 0.0039231 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-04 15:32 | 2022-02-04 22:30 | 20 | 006:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22020400142 | New_Event | Bad Weather | Include | Include | Weather | 418 | 2022-02-04 | 8360 | keep | 0 | Feb | 2022 | 0.005694 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-04 15:33 | 2022-02-04 19:49 | 75 | 004:16 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020400143 | New_Event | Bad Weather | Include | Include | Weather | 256 | 2022-02-04 | 19200 | keep | 0 | Feb | 2022 | 0.013077 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-02-04 15:46 | 2022-02-04 16:01 | 3 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | P22020400066 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2022-02-04 | 45 | keep | 0 | Feb | 2022 | 3.0649e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-02-04 15:49 | 2022-02-04 17:14 | 100 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN C/L REPARO BAJANTE LINEA A CAJA | R22020400074 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2022-02-04 | 8500 | keep | 0 | Feb | 2022 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-02-04 15:49 | 2022-02-04 19:30 | 53 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C22020400189 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2022-02-04 | 11713 | keep | 0 | Feb | 2022 | 0.0079777 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
UTUADO | 2022-02-04 15:54 | 2022-02-04 18:23 | 20 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020400116 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-02-04 | 2980 | keep | 0 | Feb | 2022 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-04 16:03 | 2022-02-04 19:15 | 60 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22020400154 | New_Event |  |  | Include | Wildlife | 192 | 2022-02-04 | 11520 | keep | 0 | Feb | 2022 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-04 16:09 | 2022-02-04 16:10 | 30 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X65 EN C/L Y SE RETEZO LINEA | B22020400070 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-04 | 30 | keep | 0 | Feb | 2022 | 2.0433e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-02-04 16:11 | 2022-02-04 18:00 | 20 | 001:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R22020400077 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2022-02-04 | 2180 | keep | 0 | Feb | 2022 | 0.0014848 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-04 16:11 | 2022-02-04 19:46 | 125 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020400120 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2022-02-04 | 26875 | keep | 0 | Feb | 2022 | 0.018304 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-02-04 16:14 | 2022-02-04 16:15 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020400157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2825 | keep | 0 | Feb | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
ARECIBO | 2022-02-04 16:21 | 2022-02-04 18:30 | 50 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020400128 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2022-02-04 | 6450 | keep | 0 | Feb | 2022 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-04 16:22 | 2022-02-04 17:53 | 718 | 001:31 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES N/O CONTRA EL 1901-05 QUEDANDO EN SERVICIO. EL 90% DEL 1901-05 SE LE PASARA A LA REGION DE BAYAMON PARA QUE LO PATRULLE INFORMA VICTOR MARTINEZ | S22020400275 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-02-04 | 65338 | keep | 0 | Feb | 2022 | 0.044501 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2022-02-04 16:22 | 2022-02-04 22:15 | 558 | 005:53 | P | NO SE REPORTO CAUSA | SE ABRIO MACHETE ALTURAS DE SANTA MARIA Y SE CERRO N/O CARR.177 SAN FERNANDO 50% EN SERVICIO | S22020400275 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 353 | 2022-02-04 | 196974 | keep | 0 | Feb | 2022 | 0.13416 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
BARRANQUITAS | 2022-02-04 16:32 | 2022-02-04 17:07 | 8 | 000:35 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA AJUSTAR BUSHING SECUNDARIO | C22020400194 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 35 | 2022-02-04 | 280 | keep | 0 | Feb | 2022 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-02-04 16:40 | 2022-02-04 19:18 | 65 | 002:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P22020400082 | New_Event | Bad Weather | Include | Include | Weather | 158 | 2022-02-04 | 10270 | keep | 0 | Feb | 2022 | 0.0069949 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-02-04 16:43 | 2022-02-04 19:03 | 32 | 002:20 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO Y REPARO NEUTRAL | R22020400080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-02-04 | 4480 | keep | 0 | Feb | 2022 | 0.0030513 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2022-02-04 16:54 | 2022-02-04 17:44 | 10 | 000:50 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22020400215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2022-02-04 | 500 | keep | 0 | Feb | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-04 16:57 | 2022-02-05 17:00 | 15 | 024:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR EN MH-10 MEDIANTE GOI BY-220205-01 | B22020400219 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1443 | 2022-02-04 | 21645 | keep | 0 | Feb | 2022 | 0.014742 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-04 17:01 | 2022-02-04 17:02 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020400089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 1746 | keep | 0 | Feb | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2022-02-04 17:13 | 2022-02-04 19:29 | 511 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 1 X 65 EN CORTE DE LINEA SE ABRIO PUENTE EN PROVISIONAL | S22020400300 | New_Event | Wire Down | Include | Include | Equipment | 136 | 2022-02-04 | 69496 | keep | 0 | Feb | 2022 | 0.047333 | 0.00034804 | Sustained | FALSE | FALSE | Not_TMED_Event | 511
SAN JUAN | 2022-02-04 17:13 | 2022-02-04 17:14 | 382 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01 Y 95% DEL 1336-10 | S22020400302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 382 | keep | 0 | Feb | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
SAN JUAN | 2022-02-04 17:13 | 2022-02-04 17:14 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01 Y 95% DEL 1336-10 | S22020400302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-04 17:13 | 2022-02-04 17:14 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01 Y 95% DEL 1336-10 | S22020400302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 172 | keep | 0 | Feb | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-02-04 17:14 | 2022-02-04 20:35 | 100 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22020400214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-02-04 | 20100 | keep | 0 | Feb | 2022 | 0.01369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-04 17:17 | 2022-02-04 20:47 | 6 | 003:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA PRIMARIA A RISER | A22020400140 | New_Event | Wire Down | Include | Include | Equipment | 210 | 2022-02-04 | 1260 | keep | 0 | Feb | 2022 | 0.00085818 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-02-04 17:18 | 2022-02-06 09:30 | 7 | 040:12 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C22020400203 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2412 | 2022-02-04 | 16884 | keep | 0 | Feb | 2022 | 0.0115 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-02-04 17:23 | 2022-02-05 10:17 | 10 | 016:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE CERRO PUENTE DE CAJA AL TRANSFORMADOR | C22020400206 | New_Event | Wire Down | Include | Include | Equipment | 1014 | 2022-02-04 | 10140 | keep | 0 | Feb | 2022 | 0.0069063 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-04 17:28 | 2022-02-05 14:50 | 4 | 021:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO AFECTANDO DOS XMR'S | B22020400234 | New_Event | Wire Down | Include | Include | Equipment | 1282 | 2022-02-04 | 5128 | keep | 0 | Feb | 2022 | 0.0034927 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-04 17:32 | 2022-02-04 20:31 | 30 | 002:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22020400239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2022-02-04 | 5370 | keep | 0 | Feb | 2022 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-04 17:39 | 2022-02-04 19:30 | 40 | 001:51 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | B22020400244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-02-04 | 4440 | keep | 0 | Feb | 2022 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-04 17:44 | 2022-02-04 20:50 | 20 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020400247 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 186 | 2022-02-04 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-04 17:45 | 2022-02-04 21:13 | 10 | 003:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X REPTIL | R22020400089 | New_Event |  |  | Include | Wildlife | 208 | 2022-02-04 | 2080 | keep | 0 | Feb | 2022 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-04 17:54 | 2022-02-05 02:51 | 25 | 008:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A TRANSFORMADOR | S22020400324 | New_Event | Wire Down | Include | Include | Equipment | 537 | 2022-02-04 | 13425 | keep | 0 | Feb | 2022 | 0.0091437 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-02-04 17:55 | 2022-02-05 03:05 | 12 | 009:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | S22020400325 | New_Event | Cutout Failure | Include | Include | Equipment | 550 | 2022-02-04 | 6600 | keep | 0 | Feb | 2022 | 0.0044952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-04 18:03 | 2022-02-04 19:44 | 50 | 001:41 | P | DESGANCHE | 2 X 30 EN C/L | R22020400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-02-04 | 5050 | keep | 0 | Feb | 2022 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-04 18:04 | 2022-02-04 20:49 | 15 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA Y SE LEVANTO CONDUCTOR PRIMARIO | B22020400257 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2022-02-04 | 2475 | keep | 0 | Feb | 2022 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-04 18:10 | 2022-02-04 18:51 | 5809 | 000:41 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO 1710-01 ENTRANDO 50% EN SERVICIO Y SE IDENTIFICO AISLADOR AVERIADO. CARGA POR EL 1716-03 | B22020400337 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 41 | 2022-02-04 | 238169 | keep | 0 | Feb | 2022 | 0.16222 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-02-04 18:10 | 2022-02-04 18:38 | 1812 | 000:28 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1716-03 LLEVANDO LA CARGA DEL 1710-01. SE ABRIO MACHETES N/O CONTRA EL 1710-01 Y SE CERRO POR SCADA | B22020400337 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2022-02-04 | 50736 | keep | 0 | Feb | 2022 | 0.034556 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-02-04 18:12 | 2022-02-04 18:13 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 4431 | keep | 0 | Feb | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-02-04 18:19 | 2022-02-05 10:48 | 10 | 016:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020400265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 989 | 2022-02-04 | 9890 | keep | 0 | Feb | 2022 | 0.006736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-04 18:38 | 2022-02-05 10:29 | 163 | 015:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | C22020400215 | New_Event | Wire Down | Include | Include | Equipment | 951 | 2022-02-04 | 155013 | keep | 0 | Feb | 2022 | 0.10558 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
CANOVANAS | 2022-02-04 18:40 | 2022-02-04 21:45 | 80 | 003:05 | P | DESGANCHE | 1 X 65 EN C/L | R22020400096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-02-04 | 14800 | keep | 0 | Feb | 2022 | 0.01008 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-04 18:51 | 2022-02-04 19:11 | 2902 | 000:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO 50% DEL 1710-01 EN OPERACIONES PARA IDENTIFICAR AVERIA. CARGA POR EL 1716-03 | B22020400337 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 20 | 2022-02-04 | 58040 | keep | 0 | Feb | 2022 | 0.039531 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-04 18:59 | 2022-02-04 19:30 | 250 | 000:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X 80 RN RISER | S22020400344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-02-04 | 7750 | keep | 0 | Feb | 2022 | 0.0052785 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2022-02-04 19:00 | 2022-02-05 09:57 | 56 | 014:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C22020400225 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 897 | 2022-02-04 | 50232 | keep | 0 | Feb | 2022 | 0.034213 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
ARECIBO | 2022-02-04 19:00 | 2022-02-04 21:03 | 6 | 002:03 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA INFORMA JOURNEY LINEMAN QUE REQUIERE DESGANCHE | A22020400151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-02-04 | 738 | keep | 0 | Feb | 2022 | 0.00050265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-04 19:01 | 2022-02-05 03:25 | 120 | 008:24 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA | B22020400306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 504 | 2022-02-04 | 60480 | keep | 0 | Feb | 2022 | 0.041193 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-02-04 19:05 | 2022-02-05 08:33 | 8 | 013:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR POR CONTACTO DE AVE | P22020400099 | New_Event |  |  | Include | Wildlife | 808 | 2022-02-04 | 6464 | keep | 0 | Feb | 2022 | 0.0044026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-02-04 19:05 | 2022-02-04 19:06 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 18400 DE BARRANQUITAS AL ABANICO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2410 | keep | 0 | Feb | 2022 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2022-02-04 19:05 | 2022-02-04 19:06 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 18400 DE BARRANQUITAS AL ABANICO | C22020400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2826 | keep | 0 | Feb | 2022 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BAYAMON | 2022-02-04 19:06 | 2022-02-07 15:02 | 1 | 067:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE DE CAJA A EQUIPO DE MEDICION EN SUBESTACION DE CLIENTE | S22020400295 | New_Event | Wire Down | Include | Include | Equipment | 4076 | 2022-02-04 | 4076 | keep | 0 | Feb | 2022 | 0.0027761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-04 19:06 | 2022-02-04 20:08 | 25 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | B22020400181 | Partial_restoration | Wire Down | Include | Include | Equipment | 62 | 2022-02-04 | 1550 | keep | 0 | Feb | 2022 | 0.0010557 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-04 19:06 | 2022-02-04 20:08 | 35 | 001:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22020400190 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-02-04 | 2170 | keep | 0 | Feb | 2022 | 0.001478 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-04 19:08 | 2022-02-05 09:13 | 8 | 014:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22020400227 | New_Event | Bad Weather | Include | Include | Weather | 845 | 2022-02-04 | 6760 | keep | 0 | Feb | 2022 | 0.0046042 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-02-04 19:08 | 2022-02-04 20:47 | 40 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020400172 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2022-02-04 | 3960 | keep | 0 | Feb | 2022 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-04 19:11 | 2022-02-04 19:14 | 5809 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1716-03 LLEVANDO 50% DEL 1710-01 CUANDO SE REALIZABAN OPERACIONES PARA IDENTIFICAR AVERIA. GOI BY-220204-03 | B22020400337 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-02-04 | 17427 | keep | 0 | Feb | 2022 | 0.011869 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-04 19:11 | 2022-02-04 19:14 | 1812 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1716-03 LLEVANDO 50% DEL 1710-01 CUANDO SE REALIZABAN OPERACIONES PARA IDENTIFICAR AVERIA. | B22020400337 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-02-04 | 5436 | keep | 0 | Feb | 2022 | 0.0037024 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-04 19:14 | 2022-02-04 23:05 | 5809 | 003:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO MACHETE EN SERVICIO TOTAL SU CARGA POR 1716-3 | B22020400000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 231 | 2022-02-04 | 1341879 | keep | 0 | Feb | 2022 | 0.91395 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-02-04 19:15 | 2022-02-04 19:52 | 1078 | 000:37 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES ABRIENDO MACHETES EN OTRO PUNTO 12% EN SERVICIO | B22020400214 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-02-04 | 39886 | keep | 0 | Feb | 2022 | 0.027166 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-04 19:17 | 2022-02-06 10:57 | 45 | 039:40 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA Y 1 X 80 EN SU | S22020400353 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2380 | 2022-02-04 | 107100 | keep | 0 | Feb | 2022 | 0.072945 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
YAUCO | 2022-02-04 19:22 | 2022-02-04 20:11 | 5 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR MAL TIEMPO | P22020400106 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2022-02-04 | 245 | keep | 0 | Feb | 2022 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-04 19:29 | 2022-02-04 20:10 | 6244 | 000:41 | T | DESGANCHE | DISPARO 1336-07 DEBIDO A ARBOL QUE CAYO E HIZO CONTACTO CON ALIMENTADOR. SE RETIRO RAMA CON VARETA PEGADA A NEUTRAL Y SE CERRO BKR 1336-07 MEDIANTE SJ-220204-03 | S22020400035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2022-02-04 | 256004 | keep | 0 | Feb | 2022 | 0.17436 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
BARRANQUITAS | 2022-02-04 19:37 | 2022-02-04 22:44 | 100 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C22020400039 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2022-02-04 | 18700 | keep | 0 | Feb | 2022 | 0.012736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-04 19:49 | 2022-02-05 14:57 | 300 | 019:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22020400058 | New_Event | Wire Down | Include | Include | Equipment | 1148 | 2022-02-04 | 344400 | keep | 0 | Feb | 2022 | 0.23457 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-02-04 19:52 | 2022-02-04 20:41 | 1065 | 000:49 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES 100% EN SERVICIO NO SE ENCONTRO CAUSA | B22020400214 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-02-04 | 52185 | keep | 0 | Feb | 2022 | 0.035543 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-04 19:54 | 2022-02-04 20:09 | 60 | 000:15 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER | S22020400368 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-02-04 | 900 | keep | 0 | Feb | 2022 | 0.00061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-04 20:08 | 2022-02-05 12:18 | 39 | 016:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22020400252 | New_Event | Bad Weather | Include | Include | Weather | 970 | 2022-02-04 | 37830 | keep | 0 | Feb | 2022 | 0.025766 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-04 20:08 | 2022-02-04 20:09 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22020400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
BARRANQUITAS | 2022-02-04 20:08 | 2022-02-04 20:09 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C22020400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2410 | keep | 0 | Feb | 2022 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2022-02-04 20:08 | 2022-02-04 20:09 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C22020400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-04 | 2826 | keep | 0 | Feb | 2022 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
GUAYAMA | 2022-02-04 20:09 | 2022-02-04 21:51 | 50 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P22020400102 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2022-02-04 | 5100 | keep | 0 | Feb | 2022 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-04 20:09 | 2022-02-04 20:30 | 35 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22020400190 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-02-04 | 735 | keep | 0 | Feb | 2022 | 0.00050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-04 20:10 | 2022-02-04 23:01 | 511 | 002:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 1 X 65 EN CORTE DE LINEA SE ABRIO PUENTE EN PROVISIONAL | S22020400300 | Partial_restoration | Wire Down | Include | Include | Equipment | 171 | 2022-02-04 | 87381 | keep | 0 | Feb | 2022 | 0.059515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-04 20:14 | 2022-02-04 23:15 | 100 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22020400119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-02-04 | 18100 | keep | 0 | Feb | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-04 20:23 | 2022-02-04 22:27 | 50 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA | B22020400258 | New_Event | Wire Down | Include | Include | Equipment | 124 | 2022-02-04 | 6200 | keep | 0 | Feb | 2022 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-04 20:24 | 2022-02-05 08:17 | 4 | 011:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR SE RETIRO CULEBA | R22020400108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 713 | 2022-02-04 | 2852 | keep | 0 | Feb | 2022 | 0.0019425 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-04 20:32 | 2022-02-04 20:33 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-04 | 2324 | keep | 0 | Feb | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
UTUADO | 2022-02-04 20:39 | 2022-02-05 10:35 | 15 | 013:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | A22020400165 | New_Event | Wire Down | Include | Include | Equipment | 836 | 2022-02-04 | 12540 | keep | 0 | Feb | 2022 | 0.0085409 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-02-04 20:52 | 2022-02-05 09:53 | 31 | 013:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C22020400266 | New_Event | Bad Weather | Include | Include | Weather | 781 | 2022-02-04 | 24211 | keep | 0 | Feb | 2022 | 0.01649 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2022-02-04 20:54 | 2022-02-05 01:51 | 80 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 2 X 50 EN CORTE DE LINEA SE ABRIO PUENTE LINEA EN EL PISO | B22020400337 | New_Event | Wire Down | Include | Include | Equipment | 297 | 2022-02-04 | 23760 | keep | 0 | Feb | 2022 | 0.016183 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-02-04 21:00 | 2022-02-04 22:19 | 9 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22020400167 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2022-02-04 | 711 | keep | 0 | Feb | 2022 | 0.00048426 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-02-04 21:01 | 2022-02-04 21:08 | 1983 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 1711-04 | B22020400382 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-02-04 | 13881 | keep | 0 | Feb | 2022 | 0.0094543 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-02-04 21:01 | 2022-02-04 21:08 | 186 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 1711-04 | B22020400382 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-02-04 | 1302 | keep | 0 | Feb | 2022 | 0.00088679 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
VEGA BAJA | 2022-02-04 21:02 | 2022-02-05 07:27 | 10 | 010:25 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE RETIRO ENREDADERA | B22020400381 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 625 | 2022-02-04 | 6250 | keep | 0 | Feb | 2022 | 0.0042568 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-04 21:40 | 2022-02-05 04:37 | 40 | 006:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN SUM-20 EN SU-7 | S22020400399 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2022-02-04 | 16680 | keep | 0 | Feb | 2022 | 0.011361 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-04 21:44 | 2022-02-04 23:10 | 180 | 001:26 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | S22020400400 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2022-02-04 | 15480 | keep | 0 | Feb | 2022 | 0.010543 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2022-02-04 21:49 | 2022-02-04 21:51 | 1287 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020400177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-04 | 2574 | keep | 0 | Feb | 2022 | 0.0017531 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
BAYAMON | 2022-02-04 22:15 | 2022-02-04 22:56 | 279 | 000:41 | P | NO SE REPORTO CAUSA | SE ABRIO MACHETE CALLE CALIFORNIA Y SE CERRO ALTURAS DE SANTA MARIA 70% EN SERVICIO | S22020400275 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 41 | 2022-02-04 | 11439 | keep | 0 | Feb | 2022 | 0.0077911 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-04 22:16 | 2022-02-05 02:06 | 50 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22020400171 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2022-02-04 | 11500 | keep | 0 | Feb | 2022 | 0.0078326 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-04 22:28 | 2022-02-04 22:29 | 1709 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIAS | C22020400283 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-04 | 1709 | keep | 0 | Feb | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
BAYAMON | 2022-02-04 22:56 | 2022-02-04 23:19 | 167 | 000:23 | P | NO SE REPORTO CAUSA | SE CERRO MACHETE CALLE CALIFORNIA EN SERVICIO TOTAL | S22020400275 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-02-04 | 3841 | keep | 0 | Feb | 2022 | 0.0026161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-05 00:14 | 2022-02-05 08:22 | 50 | 008:08 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22020500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2022-02-05 | 24400 | keep | 0 | Feb | 2022 | 0.016619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-05 01:02 | 2022-02-05 16:15 | 8 | 015:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR 25 KVA | M22020500001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 913 | 2022-02-05 | 7304 | keep | 0 | Feb | 2022 | 0.0049747 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-05 01:27 | 2022-02-05 01:28 | 1834 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | B22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 1834 | keep | 0 | Feb | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-02-05 01:44 | 2022-02-05 01:47 | 5 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1117-8 | S22020400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-05 | 15 | keep | 0 | Feb | 2022 | 1.0216e-05 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-05 01:44 | 2022-02-05 01:47 | 466 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1116-5 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-05 | 1398 | keep | 0 | Feb | 2022 | 0.00095217 | 0.00031739 | Momentary | FALSE | FALSE | Not_TMED_Event | 466
VEGA BAJA | 2022-02-05 01:51 | 2022-02-05 09:38 | 35 | 007:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | B22020400377 | Partial_restoration | Wire Down | Include | Include | Equipment | 467 | 2022-02-05 | 16345 | keep | 0 | Feb | 2022 | 0.011133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-05 02:07 | 2022-02-05 02:08 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C22020500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-05 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-02-05 02:07 | 2022-02-05 02:08 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C22020500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-05 | 2280 | keep | 0 | Feb | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-02-05 02:07 | 2022-02-05 02:08 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C22020500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-05 | 1617 | keep | 0 | Feb | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2022-02-05 02:32 | 2022-02-05 02:34 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-05 | 2 | keep | 0 | Feb | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-05 02:49 | 2022-02-05 09:45 | 270 | 006:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | S22020500010 | New_Event | Wire Down | Include | Include | Equipment | 416 | 2022-02-05 | 112320 | keep | 0 | Feb | 2022 | 0.076501 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
SAN JUAN | 2022-02-05 03:23 | 2022-02-05 05:51 | 50 | 002:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22020500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-02-05 | 7400 | keep | 0 | Feb | 2022 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-05 03:24 | 2022-02-05 03:25 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C22020500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-05 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-02-05 03:24 | 2022-02-05 03:25 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C22020500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-05 | 2280 | keep | 0 | Feb | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-02-05 03:24 | 2022-02-05 03:25 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6500 | C22020500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-05 | 1617 | keep | 0 | Feb | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2022-02-05 03:30 | 2022-02-05 04:40 | 2635 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C22020500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-02-05 | 184450 | keep | 0 | Feb | 2022 | 0.12563 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-02-05 03:30 | 2022-02-05 04:40 | 2280 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C22020500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-02-05 | 159600 | keep | 0 | Feb | 2022 | 0.1087 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-02-05 03:30 | 2022-02-05 04:40 | 1617 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C22020500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-02-05 | 113190 | keep | 0 | Feb | 2022 | 0.077093 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2022-02-05 04:46 | 2022-02-05 04:47 | 4533 | 000:01 | T | ERROR HUMANO | SE ABRE A PETICION DE FORMAN VEHICULO IMPACTO PROVISIONAL NO ERA EL INDICADO | B22020500000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-05 | 4533 | keep | 0 | Feb | 2022 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2022-02-05 04:48 | 2022-02-05 04:56 | 4622 | 000:08 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE A PETICION FOREMAN PARA RETIRAR PELIGRO POSTE PROVISIONAL TUMBADO POR ACCIDENTE 99% EN SERVICIO | B22020500023 | New_Event |  |  | Include | Wildlife | 8 | 2022-02-05 | 36976 | keep | 0 | Feb | 2022 | 0.025184 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BARRANQUITAS | 2022-02-05 04:49 | 2022-02-05 14:04 | 2635 | 009:15 | S | LINEA DE TRANSMISION 38KV | SE REALIZO DESGANCHE EN LA LINEA 6500 CG-220205-01 | C22020500001 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 555 | 2022-02-05 | 1462425 | keep | 0 | Feb | 2022 | 0.99605 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-05 04:49 | 2022-02-05 14:04 | 2280 | 009:15 | S | LINEA DE TRANSMISION 38KV | SE REALIZO DESGANCHE EN LA LINEA 6500 CG-220205-01 | C22020500001 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 555 | 2022-02-05 | 1265400 | keep | 0 | Feb | 2022 | 0.86186 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-05 04:49 | 2022-02-05 14:04 | 1617 | 009:15 | S | LINEA DE TRANSMISION 38KV | SE REALIZO DESGANCHE EN LA LINEA 6500 CG-220205-01 | C22020500001 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 555 | 2022-02-05 | 897435 | keep | 0 | Feb | 2022 | 0.61124 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 04:56 | 2022-02-05 15:06 | 40 | 010:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN AEREO PROVISIONAL. SE INSTALO POSTE Y SE CONECTO AEREO PROVISIONAL NUEVAMENTE POR IMPACTO DE AUTO | B22020500031 | Partial_restoration |  |  | Include | Wildlife | 610 | 2022-02-05 | 24400 | keep | 0 | Feb | 2022 | 0.016619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-05 05:07 | 2022-02-05 18:53 | 30 | 013:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L LEVANTO CONDUCTOR | C22020500015 | New_Event | Wire Down | Include | Include | Equipment | 826 | 2022-02-05 | 24780 | keep | 0 | Feb | 2022 | 0.016878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-05 05:49 | 2022-02-05 18:18 | 50 | 012:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO PORTAFUSIBLES | S22020500022 | New_Event | Cutout Failure | Include | Include | Equipment | 749 | 2022-02-05 | 37450 | keep | 0 | Feb | 2022 | 0.025507 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-05 06:07 | 2022-02-05 10:58 | 30 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | R22020500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2022-02-05 | 8730 | keep | 0 | Feb | 2022 | 0.005946 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-02-05 06:12 | 2022-02-05 12:30 | 4 | 006:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN XMR SE REPARO SECUNDARIA | R22020500002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 378 | 2022-02-05 | 1512 | keep | 0 | Feb | 2022 | 0.0010298 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-02-05 06:20 | 2022-02-05 10:36 | 80 | 004:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22020500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2022-02-05 | 20480 | keep | 0 | Feb | 2022 | 0.013949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-02-05 06:26 | 2022-02-05 08:48 | 10 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE CERRO BAJANTE SECUNDARIO | B22020500042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2022-02-05 | 1420 | keep | 0 | Feb | 2022 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-05 06:30 | 2022-02-05 06:31 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1 | keep | 0 | Feb | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-05 06:46 | 2022-02-05 06:47 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2402-03 LLEVA CARGA DEL 2404-06 | R22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 4085 | keep | 0 | Feb | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-02-05 06:46 | 2022-02-05 06:47 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2402-03 LLEVA CARGA DEL 2404-06 | R22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 7621 | keep | 0 | Feb | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
PONCE | 2022-02-05 07:19 | 2022-02-05 17:54 | 50 | 010:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO | P22020500002 | New_Event | Wire Down | Include | Include | Equipment | 635 | 2022-02-05 | 31750 | keep | 0 | Feb | 2022 | 0.021625 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-05 07:34 | 2022-02-05 17:49 | 50 | 010:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN C/L SE REMPLAZO PISTOLA EN PM | S22020500035 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 615 | 2022-02-05 | 30750 | keep | 0 | Feb | 2022 | 0.020944 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-05 07:49 | 2022-02-05 10:07 | 10 | 002:18 | P | DESGANCHE | SE REALIZO DEGANCHE Y SE CERRO PORTAFUSIBLE. NO FUNDIO FUSIBLE Y SIMPLEMENTE ESTABA ABIERTO QUIZAS A CAUSA DE LA RAMA | B22020500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-02-05 | 1380 | keep | 0 | Feb | 2022 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-02-05 07:51 | 2022-02-05 14:36 | 1 | 006:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2022-02-05 | 405 | keep | 0 | Feb | 2022 | 0.00027584 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-05 07:55 | 2022-02-05 09:45 | 36 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L SE RETIRO PALOMA | R22020500007 | New_Event |  |  | Include | Wildlife | 110 | 2022-02-05 | 3960 | keep | 0 | Feb | 2022 | 0.0026971 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
FAJARDO | 2022-02-05 07:57 | 2022-02-05 09:48 | 6 | 001:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CONECTO BAJANTE SAFADO | R22020500008 | New_Event | Wire Down | Include | Include | Equipment | 111 | 2022-02-05 | 666 | keep | 0 | Feb | 2022 | 0.00045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-02-05 08:07 | 2022-02-05 18:13 | 29 | 010:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR SJ-220205-51 | R22020500010 | New_Event | Wire Down | Include | Include | Equipment | 606 | 2022-02-05 | 17574 | keep | 0 | Feb | 2022 | 0.01197 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2022-02-05 08:23 | 2022-02-05 10:26 | 50 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO | B22020500061 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2022-02-05 | 6150 | keep | 0 | Feb | 2022 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-05 08:37 | 2022-02-05 12:00 | 8 | 003:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A22020500016 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2022-02-05 | 1624 | keep | 0 | Feb | 2022 | 0.0011061 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-02-05 08:56 | 2022-02-05 09:50 | 5 | 000:54 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | B22020500068 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 54 | 2022-02-05 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-05 09:07 | 2022-02-05 09:08 | 485 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 QUE A SU VEZ LLEVA LA CARGA DEL 1420-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 485 | keep | 0 | Feb | 2022 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2022-02-05 09:07 | 2022-02-05 09:08 | 4 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 QUE A SU VEZ LLEVA LA CARGA DEL 1420-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 4 | keep | 0 | Feb | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-02-05 09:11 | 2022-02-05 09:39 | 25 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDADARIA | C22020400232 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-02-05 | 700 | keep | 0 | Feb | 2022 | 0.00047677 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-02-05 09:17 | 2022-02-05 12:10 | 50 | 002:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CAJA DE TRANSFORMADOR PARA CERRAR PUENTE PRIMARIO | P22020500011 | New_Event | Wire Down | Include | Include | Equipment | 173 | 2022-02-05 | 8650 | keep | 0 | Feb | 2022 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-05 09:19 | 2022-02-05 09:20 | 2201 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A22020500025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-05 | 2201 | keep | 0 | Feb | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
SAN JUAN | 2022-02-05 09:24 | 2022-02-05 18:04 | 36 | 008:40 | P | ESTRUCTURA AVERIADA | 2 X 50 EN C/L SE ABRIO PUENTES HACIA POSTE PARTIDO CON CONDUCTOR EN EL SUELO PENDIENTE A TRABAJAR MAÃ‘ANA PERSONAL DE CONSTRUCCION | S22020500068 | New_Event | Defective Pole | Include | Include | Equipment | 520 | 2022-02-05 | 18720 | keep | 0 | Feb | 2022 | 0.01275 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2022-02-05 09:25 | 2022-02-05 12:10 | 50 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA LINEA ARRIADA SE RETEZO LINEA PRIMARIA | A22020500027 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2022-02-05 | 8250 | keep | 0 | Feb | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-02-05 09:37 | 2022-02-05 11:14 | 60 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | R22020500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-02-05 | 5820 | keep | 0 | Feb | 2022 | 0.003964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-05 09:38 | 2022-02-05 14:40 | 80 | 005:02 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B22020500074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2022-02-05 | 24160 | keep | 0 | Feb | 2022 | 0.016455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-02-05 09:38 | 2022-02-05 13:44 | 84 | 004:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L PARA CERRAR PUENTE LUEGO DE HABER LEVANTADO CONDUCTOR | B22020400377 | Additional_clients | Wire Down | Include | Include | Equipment | 246 | 2022-02-05 | 20664 | keep | 0 | Feb | 2022 | 0.014074 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 09:45 | 2022-02-05 15:00 | 894 | 005:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR SE REALIZO DESGANCHE Y SE CERRO MACHETES | S22020500010 | Additional_clients | Wire Down | Include | Include | Equipment | 315 | 2022-02-05 | 281610 | keep | 0 | Feb | 2022 | 0.1918 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 09:52 | 2022-02-05 10:02 | 824 | 000:10 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR 1119-04 LLEVANDO 95% DE LA CARGA DEL 1115-05 | S22020500010 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2022-02-05 | 8240 | keep | 0 | Feb | 2022 | 0.0056122 | 0.00056122 | Sustained | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-02-05 09:52 | 2022-02-05 10:02 | 2720 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA 95% DE LA CARGA DEL 1115-05 | S22020500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-02-05 | 27200 | keep | 0 | Feb | 2022 | 0.018526 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-02-05 10:02 | 2022-02-05 10:03 | 2201 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A22020500041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-05 | 2201 | keep | 0 | Feb | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
BAYAMON | 2022-02-05 10:05 | 2022-02-07 17:59 | 50 | 055:54 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO | B22020500079 | New_Event | UG Cable Fault | Include | Include | Equipment | 3354 | 2022-02-05 | 167700 | keep | 0 | Feb | 2022 | 0.11422 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-05 10:08 | 2022-02-06 12:04 | 50 | 025:56 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL | B22020500370 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1556 | 2022-02-05 | 77800 | keep | 0 | Feb | 2022 | 0.052989 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-05 10:16 | 2022-02-05 13:08 | 70 | 002:52 | P | DESGANCHE | 1 X 140 Y 1 X 200 EN DIFERENTES CORTES DE LINEA POR DESGANCHE | P22020500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-02-05 | 12040 | keep | 0 | Feb | 2022 | 0.0082004 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-02-05 10:26 | 2022-02-05 11:50 | 150 | 001:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L PARA CERRAR PUENTE ABIERTO | B22020500061 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2022-02-05 | 12600 | keep | 0 | Feb | 2022 | 0.0085818 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-02-05 10:26 | 2022-02-05 15:31 | 25 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22020500110 | New_Event | Bad Weather | Include | Include | Weather | 305 | 2022-02-05 | 7625 | keep | 0 | Feb | 2022 | 0.0051934 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-02-05 10:28 | 2022-02-05 14:22 | 50 | 003:54 | P | DESGANCHE | 1 X 25 Y 1 X 30 EN CORTES DE LINEA | C22020500111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-02-05 | 11700 | keep | 0 | Feb | 2022 | 0.0079688 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-05 10:35 | 2022-02-05 13:16 | 80 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22020500115 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2022-02-05 | 12880 | keep | 0 | Feb | 2022 | 0.0087725 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-02-05 10:48 | 2022-02-05 10:49 | 2163 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P22020500023 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-05 | 2163 | keep | 0 | Feb | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
PONCE | 2022-02-05 10:49 | 2022-02-05 14:29 | 167 | 003:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y 1 X 100 EN DIFERENTES CORTES DE LINEA SE LEVANTO ALAMBRE PRIMARIO | P22020500035 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 220 | 2022-02-05 | 36740 | keep | 0 | Feb | 2022 | 0.025023 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
SAN JUAN | 2022-02-05 11:17 | 2022-02-05 12:18 | 2179 | 001:01 | T | DESGANCHE | SE SECCIONALIZO CARR. 190 Y SE CERRO POR SCADA | R22020500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-02-05 | 132919 | keep | 0 | Feb | 2022 | 0.090531 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2022-02-05 11:26 | 2022-02-05 11:27 | 513 | 000:01 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1118-10 Y SE CERRO POR SCADA. ADEMAS LLEVA EL 20% DEL 1111-01 | S22020500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-05 | 513 | keep | 0 | Feb | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-02-05 11:26 | 2022-02-05 11:27 | 2782 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1118-10 Y SE CERRO POR SCADA. ADEMAS LLEVA EL 20% DEL 1111-01 | S22020500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-05 | 2782 | keep | 0 | Feb | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-02-05 11:37 | 2022-02-05 11:38 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1909-08 LLEVANDO LA CARGA DEL 1907-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-05 11:37 | 2022-02-05 11:38 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1909-08 LLEVANDO LA CARGA DEL 1907-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-02-05 11:38 | 2022-02-05 16:56 | 80 | 005:18 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S22020500128 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 318 | 2022-02-05 | 25440 | keep | 0 | Feb | 2022 | 0.017327 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-02-05 11:42 | 2022-02-05 21:22 | 50 | 009:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P22020500030 | New_Event | Bad Weather | Include | Include | Weather | 580 | 2022-02-05 | 29000 | keep | 0 | Feb | 2022 | 0.019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-05 11:45 | 2022-02-05 19:27 | 80 | 007:42 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE DE ARBOL Y SE LEVANTO CONDUCTOR | B22020500102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 462 | 2022-02-05 | 36960 | keep | 0 | Feb | 2022 | 0.025173 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-05 11:48 | 2022-02-05 15:07 | 10 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA PERSONAL NO IDENTIFICO CAUSA | M22020500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-02-05 | 1990 | keep | 0 | Feb | 2022 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-05 11:57 | 2022-02-05 14:38 | 50 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22020500106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-02-05 | 8050 | keep | 0 | Feb | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-05 11:59 | 2022-02-05 15:34 | 10 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA Y BAJANTES SECUNDARIOS DE TRANSFORMADOR | P22020500031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2022-02-05 | 2150 | keep | 0 | Feb | 2022 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-05 12:07 | 2022-02-05 12:08 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1646-03 | R22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-02-05 12:18 | 2022-02-05 12:41 | 1060 | 000:23 | P | DESGANCHE | SE SECCIONALIZO FRENTE A FUNERARIA BORINQUEN Y SE CERRO EN CARR. 190 | R22020500038 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-02-05 | 24380 | keep | 0 | Feb | 2022 | 0.016605 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 12:19 | 2022-02-05 12:20 | 601 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 601 | keep | 0 | Feb | 2022 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
BAYAMON | 2022-02-05 12:29 | 2022-02-05 19:45 | 70 | 007:16 | P | DESGANCHE | 1 X 50 EN C/L | B22020500108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2022-02-05 | 30520 | keep | 0 | Feb | 2022 | 0.020787 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-02-05 12:30 | 2022-02-06 11:28 | 25 | 022:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22020500125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1378 | 2022-02-05 | 34450 | keep | 0 | Feb | 2022 | 0.023464 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-02-05 12:32 | 2022-02-05 13:30 | 30 | 000:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22020500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-02-05 | 1740 | keep | 0 | Feb | 2022 | 0.0011851 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-05 12:38 | 2022-02-05 14:29 | 40 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22002050014 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2022-02-05 | 4440 | keep | 0 | Feb | 2022 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-05 12:41 | 2022-02-05 13:31 | 545 | 000:50 | P | DESGANCHE | SE SECCIONALIZO EN CARR. 190 Y SE CERRO FRENTE A FUNERARIA BORINQUEN | R22020500038 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-02-05 | 27250 | keep | 0 | Feb | 2022 | 0.01856 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 12:45 | 2022-02-07 10:39 | 13 | 045:54 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020500156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2754 | 2022-02-05 | 35802 | keep | 0 | Feb | 2022 | 0.024385 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-02-05 12:53 | 2022-02-05 15:38 | 4 | 002:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA ZULFATADA | C22020500143 | New_Event | Secondary Wire Down | Include | Include | Equipment | 165 | 2022-02-05 | 660 | keep | 0 | Feb | 2022 | 0.00044952 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-02-05 13:02 | 2022-02-05 13:03 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1859 | keep | 0 | Feb | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-02-05 13:02 | 2022-02-05 13:03 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 7 | keep | 0 | Feb | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-02-05 13:15 | 2022-02-05 13:45 | 12 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22020500046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-02-05 | 360 | keep | 0 | Feb | 2022 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-05 13:18 | 2022-02-05 14:56 | 100 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M22020500015 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2022-02-05 | 9800 | keep | 0 | Feb | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-05 13:30 | 2022-02-05 18:42 | 50 | 005:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 1 X 40 EN DIFERENTES CORTES DE LINEA SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | C22020500155 | New_Event | Wire Down | Include | Include | Equipment | 312 | 2022-02-05 | 15600 | keep | 0 | Feb | 2022 | 0.010625 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-05 13:31 | 2022-02-05 14:30 | 218 | 000:59 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERR EN CARR. 190 | R22020500038 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-02-05 | 12862 | keep | 0 | Feb | 2022 | 0.0087602 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-05 13:33 | 2022-02-05 15:49 | 10 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22020500122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-02-05 | 1360 | keep | 0 | Feb | 2022 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-05 13:43 | 2022-02-05 13:44 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1646-03 | R22020500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
BAYAMON | 2022-02-05 13:45 | 2022-02-05 16:50 | 65 | 003:05 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | B22020500126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-02-05 | 12025 | keep | 0 | Feb | 2022 | 0.0081902 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-02-05 13:59 | 2022-02-05 14:01 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-05 | 1844 | keep | 0 | Feb | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-05 13:59 | 2022-02-05 14:01 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-05 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2022-02-05 14:09 | 2022-02-06 20:56 | 30 | 030:47 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO | B22020500130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1847 | 2022-02-05 | 55410 | keep | 0 | Feb | 2022 | 0.037739 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-02-05 14:14 | 2022-02-05 17:46 | 265 | 003:32 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C22020500178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-02-05 | 56180 | keep | 0 | Feb | 2022 | 0.038264 | 0.00018049 | Sustained | FALSE | FALSE | Not_TMED_Event | 265
FAJARDO | 2022-02-05 14:17 | 2022-02-05 19:59 | 30 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | R22020500096 | New_Event | Bad Weather | Include | Include | Weather | 342 | 2022-02-05 | 10260 | keep | 0 | Feb | 2022 | 0.006988 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-02-05 14:27 | 2022-02-05 15:54 | 10 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR DESCARGA ELECTRICA | P22020500040 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-02-05 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-05 14:29 | 2022-02-05 14:30 | 2163 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE SE LEVANTO ALAMBRE PRIMARIO | P22020500041 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-02-05 | 2163 | keep | 0 | Feb | 2022 | 0.0014732 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-05 14:30 | 2022-02-05 15:15 | 167 | 000:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y 1 X 100 EN DIFERENTES CORTES DE LINEA SE LEVANTO ALAMBRE PRIMARIO PARTIDO | P22020500035 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 45 | 2022-02-05 | 7515 | keep | 0 | Feb | 2022 | 0.0051184 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
CANOVANAS | 2022-02-05 14:48 | 2022-02-05 20:46 | 7 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | R22020500106 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2022-02-05 | 2506 | keep | 0 | Feb | 2022 | 0.0017068 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-05 14:50 | 2022-02-05 16:30 | 58 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L PARA ANCLAR LINEA DEBIDO AL MAL TIEMPO. SE LEVANTO CONDUCTOR | B22020400234 | Additional_clients | Wire Down | Include | Include | Equipment | 100 | 2022-02-05 | 5800 | keep | 0 | Feb | 2022 | 0.0039504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-05 15:01 | 2022-02-05 15:02 | 2926 | 000:01 | T | DESGANCHE | RECERRO | B22020500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-05 | 2926 | keep | 0 | Feb | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2022-02-05 15:04 | 2022-02-05 18:36 | 80 | 003:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22020500165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2022-02-05 | 16960 | keep | 0 | Feb | 2022 | 0.011551 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-05 15:07 | 2022-02-05 18:46 | 45 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22020500152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-02-05 | 9855 | keep | 0 | Feb | 2022 | 0.0067122 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-02-05 15:08 | 2022-02-05 15:09 | 2926 | 000:01 | T | DESGANCHE | RECERRO | B22020500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-05 | 2926 | keep | 0 | Feb | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
MAYAGÃœEZ | 2022-02-05 15:10 | 2022-02-05 16:08 | 50 | 000:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020500025 | New_Event | Bad Weather | Include | Include | Weather | 58 | 2022-02-05 | 2900 | keep | 0 | Feb | 2022 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-05 15:21 | 2022-02-05 17:18 | 10 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020500026 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2022-02-05 | 1170 | keep | 0 | Feb | 2022 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-05 15:24 | 2022-02-05 16:23 | 308 | 000:59 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR POR AISLADORES PARTIDOS SE SECCIONALIZO | A22020500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 59 | 2022-02-05 | 18172 | keep | 0 | Feb | 2022 | 0.012377 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-05 15:25 | 2022-02-05 15:26 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 325 | keep | 0 | Feb | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-02-05 15:26 | 2022-02-05 18:32 | 2926 | 003:06 | T | DESGANCHE | SE DESGANCHO BAMBUA CON VARETA MEDIANTE SF BY-220205-02 | B22020500164 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-02-05 | 544236 | keep | 0 | Feb | 2022 | 0.37068 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
CANOVANAS | 2022-02-05 15:29 | 2022-02-05 16:40 | 2106 | 001:11 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO EL ALIMENTADOR SUA2 AVERIADO | R22020500136 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 71 | 2022-02-05 | 149526 | keep | 0 | Feb | 2022 | 0.10184 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
VEGA BAJA | 2022-02-05 15:38 | 2022-02-05 15:51 | 10 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL ABIERTO | B22020500087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2022-02-05 | 130 | keep | 0 | Feb | 2022 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-05 15:42 | 2022-02-05 16:53 | 10 | 001:11 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR, SE DESGANCHO ARBOL Y SE REPARO SECUNDARIA | B22020500132 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 71 | 2022-02-05 | 710 | keep | 0 | Feb | 2022 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-05 15:46 | 2022-02-05 17:59 | 60 | 002:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020500074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-02-05 | 7980 | keep | 0 | Feb | 2022 | 0.0054351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-05 15:48 | 2022-02-05 15:49 | 1225 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1203-03 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1225 | keep | 0 | Feb | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-02-05 15:48 | 2022-02-05 15:49 | 616 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1203-01 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 616 | keep | 0 | Feb | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
CANOVANAS | 2022-02-05 16:00 | 2022-02-06 04:30 | 200 | 012:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | R22020500138 | New_Event | Bad Weather | Include | Include | Weather | 750 | 2022-02-05 | 150000 | keep | 0 | Feb | 2022 | 0.10216 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-02-05 16:02 | 2022-02-06 11:51 | 20 | 019:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22020500205 | New_Event | Bad Weather | Include | Include | Weather | 1189 | 2022-02-05 | 23780 | keep | 0 | Feb | 2022 | 0.016196 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-05 16:15 | 2022-02-05 16:16 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1526 | keep | 0 | Feb | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
CAGUAS | 2022-02-05 16:16 | 2022-02-06 09:14 | 30 | 016:58 | P | DESGANCHE | 1 X 50 EN C/L | C22020500208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1018 | 2022-02-05 | 30540 | keep | 0 | Feb | 2022 | 0.020801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-05 16:23 | 2022-02-05 17:26 | 250 | 001:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES PRIMARIOS PARTIDOS Y SE CERRARON MACHETES SOLIDOS | A22020500007 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 63 | 2022-02-05 | 15750 | keep | 0 | Feb | 2022 | 0.010727 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 16:25 | 2022-02-05 16:26 | 513 | 000:01 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1118-10 Y SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S22020500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-05 | 513 | keep | 0 | Feb | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-02-05 16:25 | 2022-02-05 16:26 | 2782 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1118-10 Y SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S22020500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-05 | 2782 | keep | 0 | Feb | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
VEGA BAJA | 2022-02-05 16:31 | 2022-02-05 20:27 | 652 | 003:56 | T | DESGANCHE | DISPARO Y SE DESGANCHO PENCAS SOBRE LINEA. SE CERRO EN EL CAMPO POR PROBLEMAS EN EL RTU | B22020500185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-02-05 | 153872 | keep | 0 | Feb | 2022 | 0.1048 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
BAYAMON | 2022-02-05 16:33 | 2022-02-05 18:36 | 45 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22020500187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-02-05 | 5535 | keep | 0 | Feb | 2022 | 0.0037699 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-02-05 16:40 | 2022-02-05 17:20 | 316 | 000:40 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO EL ALIMENTADOR SUA2 AVERIADO | R22020500136 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 40 | 2022-02-05 | 12640 | keep | 0 | Feb | 2022 | 0.008609 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-05 16:44 | 2022-02-06 12:48 | 105 | 020:04 | P | DESGANCHE | 2 X 50 Y 1 X 40 EN CORTES DE LINEA DEJO FUERA 1 XMR QUEMADO | C22020500217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1204 | 2022-02-05 | 126420 | keep | 0 | Feb | 2022 | 0.086104 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
HUMACAO | 2022-02-05 16:49 | 2022-02-05 18:48 | 60 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22020500220 | New_Event |  |  | Include | Wildlife | 119 | 2022-02-05 | 7140 | keep | 0 | Feb | 2022 | 0.004863 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-05 17:10 | 2022-02-06 20:00 | 36 | 026:50 | P | TRANSFORMADOR AVERIADO | SE REALIZO DESGANCHE Y SE REMPLAZO TRANSFORMADOR DE 75 KVA | S22020500183 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1610 | 2022-02-05 | 57960 | keep | 0 | Feb | 2022 | 0.039476 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2022-02-05 17:20 | 2022-02-05 17:58 | 1053 | 000:38 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO EL ALIMENTADOR SUA2 AVERIADO | R22020500136 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 38 | 2022-02-05 | 40014 | keep | 0 | Feb | 2022 | 0.027253 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 17:22 | 2022-02-05 19:50 | 70 | 002:28 | P | DESGANCHE | 1 X 80 EN C/L HAY QUE REALIZAR DESGANCHE | S22020500207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-02-05 | 10360 | keep | 0 | Feb | 2022 | 0.0070561 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-02-05 17:43 | 2022-02-05 19:50 | 2 | 002:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22020500085 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2022-02-05 | 254 | keep | 0 | Feb | 2022 | 0.000173 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-02-05 17:44 | 2022-02-05 19:15 | 100 | 001:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22020500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-02-05 | 9100 | keep | 0 | Feb | 2022 | 0.006198 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-05 17:48 | 2022-02-05 18:39 | 150 | 000:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE ABRIO PUENTES Y SE CERRO N/O CON EL 7801-01 SE DEJO TAG INSTALADO | M22020500034 | New_Event | Wire Down | Include | Include | Equipment | 51 | 2022-02-05 | 7650 | keep | 0 | Feb | 2022 | 0.0052104 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-02-05 17:48 | 2022-02-05 19:40 | 20 | 001:52 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | M22020500031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 112 | 2022-02-05 | 2240 | keep | 0 | Feb | 2022 | 0.0015257 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-05 17:58 | 2022-02-05 18:06 | 2106 | 000:08 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA SOTERRADA SUA2 AVERIADO | R22020500136 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 8 | 2022-02-05 | 16848 | keep | 0 | Feb | 2022 | 0.011475 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 18:04 | 2022-02-06 18:05 | 10 | 024:01 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y TRANSFORMADOR | S22020500182 | New_Event | Defective Pole | Include | Include | Equipment | 1441 | 2022-02-05 | 14410 | keep | 0 | Feb | 2022 | 0.0098146 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-05 18:09 | 2022-02-05 18:11 | 2106 | 000:02 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA SOTERRADA SUA2 AVERIADO | R22020500136 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2022-02-05 | 4212 | keep | 0 | Feb | 2022 | 0.0028688 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-05 18:11 | 2022-02-05 19:17 | 333 | 001:06 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 66 | 2022-02-05 | 21978 | keep | 0 | Feb | 2022 | 0.014969 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
VEGA BAJA | 2022-02-05 18:18 | 2022-02-05 18:19 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1859 | keep | 0 | Feb | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-02-05 18:18 | 2022-02-05 18:19 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 7 | keep | 0 | Feb | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-02-05 18:29 | 2022-02-05 18:30 | 380 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SUB PAQUE ESCORIAL 1620 POR LOCKOUT 95% DE LA CARGA POR EL 1620-04 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 380 | keep | 0 | Feb | 2022 | 0.00025882 | 0.00025882 | Momentary | FALSE | FALSE | Not_TMED_Event | 380
SAN JUAN | 2022-02-05 18:29 | 2022-02-05 18:30 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1620-04 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-05 18:29 | 2022-02-05 18:30 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01 Y 95% DEL 1336-10 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 172 | keep | 0 | Feb | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 828 | 002:49 | P | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 139932 | keep | 0 | Feb | 2022 | 0.095307 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 1977 | 002:49 | P | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES 40% DE LA CARGA POR EL 1206-04 | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 334113 | keep | 0 | Feb | 2022 | 0.22756 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 1000 | 002:49 | P | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 169000 | keep | 0 | Feb | 2022 | 0.11511 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 500 | 002:49 | S | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 84500 | keep | 0 | Feb | 2022 | 0.057553 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 733 | 002:49 | S | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 123877 | keep | 0 | Feb | 2022 | 0.084372 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 3000 | 002:49 | S | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 507000 | keep | 0 | Feb | 2022 | 0.34532 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 1799 | 002:49 | S | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES LLEVANDO 40% DEL 1204-04, 60% DEL 1206-03 Y 20% DEL 1303-02 | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 304031 | keep | 0 | Feb | 2022 | 0.20707 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-02-05 18:30 | 2022-02-05 21:19 | 827 | 002:49 | P | NO SE REPORTO CAUSA | DISPARO DE 0060 OCASIONADO POR BACK UP INDICA JUAN TORRES DE SUBESTACIONES 20% DE LA CARGA POR EL 1206-04 | S22020500224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-05 | 139763 | keep | 0 | Feb | 2022 | 0.095192 | 0.00056327 | Sustained | FALSE | FALSE | Not_TMED_Event | 827
SAN JUAN | 2022-02-05 18:32 | 2022-02-05 18:33 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA 30% DEL 1204-04 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1483 | keep | 0 | Feb | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-02-05 18:32 | 2022-02-05 18:33 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA PARTE DEL 1204-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 300 | keep | 0 | Feb | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-02-05 18:32 | 2022-02-05 18:33 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA 30% DEL 1204-04 LLEVA 1336-09 Y PARTE DEL 1204-05 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 5290 | keep | 0 | Feb | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-02-05 18:32 | 2022-02-05 18:33 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 Y SE CERRO POR SCADA LLEVA 1336-09 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 207 | keep | 0 | Feb | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-02-05 18:33 | 2022-02-06 11:13 | 5 | 016:40 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR Y SE TRANSFIRIO CARGA AL 1116-03. LLEVA CARGA 1117-08 | S22020500000 | New_Event | Switch Failure | Include | Include | Equipment | 1000 | 2022-02-05 | 5000 | keep | 0 | Feb | 2022 | 0.0034055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-05 18:33 | 2022-02-06 11:13 | 466 | 016:40 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO Y SE TRANSFIRIO LA CARGA AL 1116-03 | S22020500000 | New_Event | Switch Failure | Include | Include | Equipment | 1000 | 2022-02-05 | 466000 | keep | 0 | Feb | 2022 | 0.31739 | 0.00031739 | Sustained | FALSE | FALSE | Not_TMED_Event | 466
BAYAMON | 2022-02-05 18:50 | 2022-02-05 18:51 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 199 | keep | 0 | Feb | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2022-02-05 18:52 | 2022-02-05 20:25 | 1295 | 001:33 | T | NO SE REPORTO CAUSA | DISPARO DIO FAIL TO OPERATE SE CERRO EN EL CAMPO PERO LA INDICACION POR SCADA SE QUEDO ERRONEA ABIERTO EN SCADA CERRADO EN EL CAMPO | S22020500257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-02-05 | 120435 | keep | 0 | Feb | 2022 | 0.082028 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
VEGA BAJA | 2022-02-05 19:03 | 2022-02-05 19:04 | 31 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 31 | keep | 0 | Feb | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2022-02-05 19:05 | 2022-02-06 21:04 | 8 | 025:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO T-18 AVERIADO DE 75 KVA X 100 KVA | R22020500201 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1559 | 2022-02-05 | 12472 | keep | 0 | Feb | 2022 | 0.0084946 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-02-05 19:05 | 2022-02-06 15:25 | 90 | 020:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ENREDADERA | R22020600031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1220 | 2022-02-05 | 109800 | keep | 0 | Feb | 2022 | 0.074784 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-02-05 19:10 | 2022-02-05 19:11 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 2324 | keep | 0 | Feb | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
PONCE | 2022-02-05 19:11 | 2022-02-05 20:26 | 50 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | P22020500062 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-02-05 | 3750 | keep | 0 | Feb | 2022 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-05 19:13 | 2022-02-05 23:56 | 225 | 004:43 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO SU-18 A RISER CALLE ROSALES Y SE CERRO MACHETE CALLE DEL VALLE 20% DE LA CARGA POR EL 1118-10 ENTRO EN SERVICIO 10%. | S22020500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 283 | 2022-02-05 | 63675 | keep | 0 | Feb | 2022 | 0.043369 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-02-05 19:13 | 2022-02-05 21:54 | 2782 | 002:41 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO MACHETE CALLE DEL VALLE Y SE CERRO INTERRUPTOR 90% EN SERVICIO SE DEJO FUERA EL 20% QUE LLEVA DEL 1111-1 | S22020500000 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 161 | 2022-02-05 | 447902 | keep | 0 | Feb | 2022 | 0.30506 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-02-05 19:16 | 2022-02-05 19:17 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 2324 | keep | 0 | Feb | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
CANOVANAS | 2022-02-05 19:17 | 2022-02-05 19:36 | 300 | 000:19 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 19 | 2022-02-05 | 5700 | keep | 0 | Feb | 2022 | 0.0038822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 3941 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500274 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 370454 | keep | 0 | Feb | 2022 | 0.25231 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 3871 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500274 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 363874 | keep | 0 | Feb | 2022 | 0.24783 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 5191 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500274 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 487954 | keep | 0 | Feb | 2022 | 0.33234 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 3597 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500251 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 338118 | keep | 0 | Feb | 2022 | 0.23029 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 492 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500251 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 46248 | keep | 0 | Feb | 2022 | 0.031499 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 4028 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500251 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 378632 | keep | 0 | Feb | 2022 | 0.25788 | 0.0027435 | Sustained | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2022-02-05 19:23 | 2022-02-05 20:57 | 2617 | 001:34 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500251 | New_Event | Protection Miscoordination | Include | Include | Other | 94 | 2022-02-05 | 245998 | keep | 0 | Feb | 2022 | 0.16755 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
FAJARDO | 2022-02-05 19:31 | 2022-02-05 19:32 | 1376 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22020500205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1376 | keep | 0 | Feb | 2022 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
CANOVANAS | 2022-02-05 19:36 | 2022-02-05 20:17 | 270 | 000:41 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 41 | 2022-02-05 | 11070 | keep | 0 | Feb | 2022 | 0.0075397 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-05 19:42 | 2022-02-05 19:43 | 2141 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C22020500238 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 2141 | keep | 0 | Feb | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:35 | 700 | 002:40 | P | NO SE REPORTO CAUSA | DISPARO SUB PARQUE ESCORIAL 1620 SE REMONTO LOCKOUT Y SE ENERGIZO PARTE POR 1620-5 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2022-02-05 | 112000 | keep | 0 | Feb | 2022 | 0.076283 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:36 | 380 | 002:41 | P | NO SE REPORTO CAUSA | DISPARO SUB PAQUE ESCORIAL 1620 POR LOCKOUT 95% DE LA CARGA POR EL 1620-04 | S22020500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-02-05 | 61180 | keep | 0 | Feb | 2022 | 0.041669 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:36 | 36 | 002:41 | T | NO SE REPORTO CAUSA | DISPARO POR LOCKOUT CARGA POR EL 1620-04 | S22020500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-02-05 | 5796 | keep | 0 | Feb | 2022 | 0.0039476 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:33 | 3718 | 002:38 | S | NO SE REPORTO CAUSA | DISPARO POR LOCKOUT SE REMONTO LOCKOUT Y SE ENERGIZO SE DEJO FUERA CARGA 1620-1 Y 95% 1336-10 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-02-05 | 587444 | keep | 0 | Feb | 2022 | 0.40011 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:36 | 1073 | 002:41 | S | NO SE REPORTO CAUSA | DISPARO POR LOCKOUT SE REMONTO LOCKOUT Y SE ENERGIZO | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-02-05 | 172753 | keep | 0 | Feb | 2022 | 0.11766 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:47 | 172 | 002:52 | S | NO SE REPORTO CAUSA | DISPARO POR LOCKOUT SE REMONTO LOCKOUT Y SE ENERGIZO LLEVANDO CARGA DEL 16201-01 Y 95% DEL 1336-10 | S22020500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 172 | 2022-02-05 | 29584 | keep | 0 | Feb | 2022 | 0.02015 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-02-05 19:55 | 2022-02-05 22:35 | 1615 | 002:40 | S | NO SE REPORTO CAUSA | DISPARO POR LOCKOUT SE REMONTO LOCKOUT Y SE ENERGIZO PARTE DEL 1206-03 | S22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2022-02-05 | 258400 | keep | 0 | Feb | 2022 | 0.176 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
ARECIBO | 2022-02-05 19:58 | 2022-02-05 19:59 | 3431 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A22020500092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-05 | 3431 | keep | 0 | Feb | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-02-05 19:59 | 2022-02-05 22:16 | 200 | 002:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZARON TRES AISLADORES PARTIDOS | A22020500093 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 137 | 2022-02-05 | 27400 | keep | 0 | Feb | 2022 | 0.018662 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-02-05 20:07 | 2022-02-05 20:08 | 76 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22020500209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 76 | keep | 0 | Feb | 2022 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
CANOVANAS | 2022-02-05 20:17 | 2022-02-05 20:40 | 160 | 000:23 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 23 | 2022-02-05 | 3680 | keep | 0 | Feb | 2022 | 0.0025064 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-05 20:40 | 2022-02-05 20:44 | 115 | 000:04 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 4 | 2022-02-05 | 460 | keep | 0 | Feb | 2022 | 0.0003133 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-05 20:44 | 2022-02-05 21:02 | 100 | 000:18 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 18 | 2022-02-05 | 1800 | keep | 0 | Feb | 2022 | 0.001226 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-05 21:02 | 2022-02-05 21:04 | 95 | 000:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2022-02-05 | 190 | keep | 0 | Feb | 2022 | 0.00012941 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-05 21:04 | 2022-02-05 21:15 | 85 | 000:11 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 11 | 2022-02-05 | 935 | keep | 0 | Feb | 2022 | 0.00063682 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-02-05 21:06 | 2022-02-06 00:41 | 3941 | 003:35 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500274 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 215 | 2022-02-05 | 847315 | keep | 0 | Feb | 2022 | 0.5771 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 21:06 | 2022-02-06 00:42 | 3871 | 003:36 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | B22020500274 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 216 | 2022-02-05 | 836136 | keep | 0 | Feb | 2022 | 0.56949 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 21:06 | 2022-02-06 00:42 | 5191 | 003:36 | S | PROTECCION DEFECTUOSA | EN SERVICIO SUBESTACION 1710-00. DETERMINARON QUE BANCO DE BATERIA DE 48V ESTA BIEN PERO EL DE 125V QUE SUPLE A 1719-00 NO FUNCION Y NO TIENE PROTECCION. SF BY-220205-04 | B22020500274 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 216 | 2022-02-05 | 1121256 | keep | 0 | Feb | 2022 | 0.76368 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 21:06 | 2022-02-06 06:14 | 3597 | 009:08 | S | DESCONECTIVO DEFECTUOSO | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 QUEDO FUERA DE SERVICIO SE PATRULLO SE CERRO POR CONTROL Y QUEDO EN SERVICIO | B22020500078 | New_Event | Switch Failure | Include | Include | Equipment | 548 | 2022-02-05 | 1971156 | keep | 0 | Feb | 2022 | 1.3425 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-02-05 21:06 | 2022-02-06 00:51 | 492 | 003:45 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 SE CERRO EN EL CAMPO | S22020500000 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 225 | 2022-02-05 | 110700 | keep | 0 | Feb | 2022 | 0.075397 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 21:06 | 2022-02-06 00:43 | 4028 | 003:37 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | S22020500000 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 217 | 2022-02-05 | 874076 | keep | 0 | Feb | 2022 | 0.59533 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 21:06 | 2022-02-06 00:43 | 2617 | 003:37 | S | PROTECCION DEFECTUOSA | DISPARO LINEA 36100 PROBLEMAS CON EL BANCO DE BATERIAS Y NINGUNA DE LAS DOS SUBESTACIONES TIENE PROTECCION 1710 Y 1719. BY-220205-04 | S22020500000 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 217 | 2022-02-05 | 567889 | keep | 0 | Feb | 2022 | 0.38679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-05 21:09 | 2022-02-05 21:10 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22020500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-05 | 1498 | keep | 0 | Feb | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
CANOVANAS | 2022-02-05 21:15 | 2022-02-05 21:17 | 75 | 000:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2022-02-05 | 150 | keep | 0 | Feb | 2022 | 0.00010216 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-05 21:17 | 2022-02-06 00:37 | 15 | 003:20 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO | R22020500128 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 200 | 2022-02-05 | 3000 | keep | 0 | Feb | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-05 21:40 | 2022-02-06 09:57 | 30 | 012:17 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN CORTE DE LINEA TRANSFORMADOR AVERIADO CAUSO QUE FUNDIERA EL CORTE DE LINEA | A22020500098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 737 | 2022-02-05 | 22110 | keep | 0 | Feb | 2022 | 0.015059 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-05 21:54 | 2022-02-05 23:18 | 278 | 001:24 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | ALIMENTADOR SECCIONALIZADO | S22020500000 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 84 | 2022-02-05 | 23352 | keep | 0 | Feb | 2022 | 0.015905 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 22:04 | 2022-02-05 22:05 | 1225 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO LLEVA 1203-3 | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 1225 | keep | 0 | Feb | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-02-05 22:04 | 2022-02-05 22:05 | 616 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO CARGA POR EL 1203-01 | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 616 | keep | 0 | Feb | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-02-05 22:05 | 2022-02-06 05:22 | 100 | 007:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22020500590 | New_Event | Vegetation Contact | Include | Include | Vegetation | 437 | 2022-02-05 | 43700 | keep | 0 | Feb | 2022 | 0.029764 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-05 22:08 | 2022-02-05 22:40 | 50 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | A22020500108 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2022-02-05 | 1600 | keep | 0 | Feb | 2022 | 0.0010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-05 22:16 | 2022-02-05 22:17 | 3431 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR POR AISLADORES PARTIDOS | A22020500111 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-05 | 3431 | keep | 0 | Feb | 2022 | 0.0023368 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-05 22:17 | 2022-02-05 23:43 | 200 | 001:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZARON TRES AISLADORES PARTIDOS | A22020500093 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 86 | 2022-02-05 | 17200 | keep | 0 | Feb | 2022 | 0.011715 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-02-05 22:17 | 2022-02-06 11:09 | 75 | 012:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22020500390 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 772 | 2022-02-05 | 57900 | keep | 0 | Feb | 2022 | 0.039435 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-05 22:38 | 2022-02-05 22:39 | 767 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECERRO 50% DE SU CARGA POR EL 1909-07 LLEVA CARGA 1709-5 MAL TIEMPO | B22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 767 | keep | 0 | Feb | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-02-05 22:38 | 2022-02-05 22:39 | 2364 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO SU CARGA POR 1709-3 MAL TIEMPO | B22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 2364 | keep | 0 | Feb | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
SAN JUAN | 2022-02-05 22:40 | 2022-02-06 01:38 | 380 | 002:58 | P | NO SE REPORTO CAUSA | DISPARO 95% DE SU CARGA POR EL 1620-03 | S22020500000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 178 | 2022-02-05 | 67640 | keep | 0 | Feb | 2022 | 0.046069 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 22:40 | 2022-02-06 01:38 | 36 | 002:58 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PATRULLO Y SE CERRO POR CONTROL SU CARGA POR 1620-3 Y LLEVA 95% 1336- MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2022-02-05 | 6408 | keep | 0 | Feb | 2022 | 0.0043645 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-05 22:40 | 2022-02-05 22:46 | 1073 | 000:06 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE ABRIO MACHETES DE BARRA DE INSPECCION Y SE DEJO FUERA CARGA 1620-1 Y 95% 1336-10 MAL TIEMPO | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 6 | 2022-02-05 | 6438 | keep | 0 | Feb | 2022 | 0.0043849 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
BAYAMON | 2022-02-05 22:46 | 2022-02-06 19:36 | 50 | 020:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22020500441 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1250 | 2022-02-05 | 62500 | keep | 0 | Feb | 2022 | 0.042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-05 22:49 | 2022-02-05 22:50 | 767 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECERRO 50% DE SU CARGA POR EL 1909-07 LLEVA CARGA 1709-5 MAL TIEMPO | B22020500000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 767 | keep | 0 | Feb | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-02-05 22:49 | 2022-02-05 22:50 | 1533 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO CARGA POR EL 1709-03 MAL TIEMPO | B22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 1533 | keep | 0 | Feb | 2022 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2022-02-05 22:55 | 2022-02-06 09:05 | 200 | 010:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN RISER SE REMPLAZO CAJA | S22020500529 | New_Event | Cutout Failure | Include | Include | Equipment | 610 | 2022-02-05 | 122000 | keep | 0 | Feb | 2022 | 0.083094 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-02-05 22:57 | 2022-02-06 11:05 | 20 | 012:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22020500039 | New_Event | Bad Weather | Include | Include | Weather | 728 | 2022-02-05 | 14560 | keep | 0 | Feb | 2022 | 0.0099167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-05 23:00 | 2022-02-06 19:54 | 75 | 020:54 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-21 1 X 20 EN SU-17 1 X 20 EN SU-18 | B22020500494 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1254 | 2022-02-05 | 94050 | keep | 0 | Feb | 2022 | 0.064057 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-02-05 23:18 | 2022-02-05 23:20 | 2782 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | AL CERRAR MACHETE CALLE DEL VALLE DISPARO 90% EN SERVICIO CONTINUA FUERA 20% 1111-1 | S22020500000 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2022-02-05 | 5564 | keep | 0 | Feb | 2022 | 0.0037896 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-05 23:20 | 2022-02-05 23:47 | 278 | 000:27 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO SU-18 A RISER Y SE CERO MACHETE BCO. POPULAR 100% 1118-10 Y 10% 1111-1 | S22020500000 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 27 | 2022-02-05 | 7506 | keep | 0 | Feb | 2022 | 0.0051123 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
CANOVANAS | 2022-02-05 23:30 | 2022-02-06 14:27 | 7 | 014:57 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | R22020500305 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 897 | 2022-02-05 | 6279 | keep | 0 | Feb | 2022 | 0.0042766 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-05 23:35 | 2022-02-05 23:36 | 271 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 271 | keep | 0 | Feb | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2022-02-05 23:41 | 2022-02-05 23:42 | 1382 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 1382 | keep | 0 | Feb | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
SAN JUAN | 2022-02-05 23:43 | 2022-02-05 23:44 | 828 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE 60% DE LA CARGA POR EL 1206-04 MAL TIEMPO | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 828 | keep | 0 | Feb | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-02-05 23:43 | 2022-02-05 23:44 | 1977 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE 40% DE LA CARGA POR EL 1206-04 MAL TIEMPO | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 1977 | keep | 0 | Feb | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-02-05 23:43 | 2022-02-05 23:44 | 1799 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLEVANDO 40% DEL 1204-04, 60% DEL 1206-03 Y 20% DEL 1303-02 MAL TIEMPO | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 1799 | keep | 0 | Feb | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-02-05 23:43 | 2022-02-05 23:44 | 827 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | RECIERRE 20% DE LA CARGA POR EL 1206-04 MAL TIEMPO | S22020500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-05 | 827 | keep | 0 | Feb | 2022 | 0.00056327 | 0.00056327 | Momentary | FALSE | FALSE | Not_TMED_Event | 827
VEGA BAJA | 2022-02-05 23:51 | 2022-02-06 13:55 | 50 | 014:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B22020500529 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 844 | 2022-02-05 | 42200 | keep | 0 | Feb | 2022 | 0.028742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-05 23:56 | 2022-02-06 00:19 | 112 | 000:23 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO RISER HACIA SU-10 | S22020500000 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 23 | 2022-02-05 | 2576 | keep | 0 | Feb | 2022 | 0.0017545 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-06 00:01 | 2022-02-06 09:13 | 45 | 009:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22020600001 | New_Event | Bad Weather | Include | Include | Weather | 552 | 2022-02-06 | 24840 | keep | 0 | Feb | 2022 | 0.016918 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-02-06 00:03 | 2022-02-06 08:19 | 570 | 008:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER MAL TIEMPO | R22020600001 | New_Event | Bad Weather | Include | Include | Weather | 496 | 2022-02-06 | 282720 | keep | 0 | Feb | 2022 | 0.19256 | 0.00038822 | Sustained | FALSE | FALSE | Not_TMED_Event | 570
PONCE | 2022-02-06 00:17 | 2022-02-06 03:01 | 607 | 002:44 | T | DESGANCHE | DISPARO DE ALIMENTADOR POR ARBOL SOBRE LINEA | P22020600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-02-06 | 99548 | keep | 0 | Feb | 2022 | 0.067802 | 0.00041342 | Sustained | FALSE | FALSE | Not_TMED_Event | 607
PONCE | 2022-02-06 00:17 | 2022-02-06 03:01 | 462 | 002:44 | T | DESGANCHE | DISPARO DE ALIMENTADOR POR ARBOL SOBRE LINEA | P22020600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-02-06 | 75768 | keep | 0 | Feb | 2022 | 0.051605 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
ARECIBO | 2022-02-06 00:25 | 2022-02-07 11:35 | 7 | 035:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA Y DESCARGAS ELECTRICAS | A22020600002 | New_Event | Bad Weather | Include | Include | Weather | 2110 | 2022-02-06 | 14770 | keep | 0 | Feb | 2022 | 0.01006 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-02-06 00:37 | 2022-02-06 01:34 | 2106 | 000:57 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO | R22020600000 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 57 | 2022-02-06 | 120042 | keep | 0 | Feb | 2022 | 0.08176 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-06 00:39 | 2022-02-06 00:52 | 2216 | 000:13 | T | NO SE REPORTO CAUSA | RECERRO 1 VEZ QUEDO FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO | B22020600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-02-06 | 28808 | keep | 0 | Feb | 2022 | 0.019621 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
FAJARDO | 2022-02-06 01:07 | 2022-02-06 10:23 | 27 | 009:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22020600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2022-02-06 | 15012 | keep | 0 | Feb | 2022 | 0.010225 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
ARECIBO | 2022-02-06 01:08 | 2022-02-06 01:18 | 30 | 000:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A22020500119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-02-06 | 300 | keep | 0 | Feb | 2022 | 0.00020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-06 01:12 | 2022-02-06 05:40 | 90 | 004:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN RISER LLUVIAS | R22020600011 | New_Event | Bad Weather | Include | Include | Weather | 268 | 2022-02-06 | 24120 | keep | 0 | Feb | 2022 | 0.016428 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-02-06 01:17 | 2022-02-06 10:03 | 200 | 008:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | A22020600003 | New_Event | Bad Weather | Include | Include | Weather | 526 | 2022-02-06 | 105200 | keep | 0 | Feb | 2022 | 0.071651 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-06 01:23 | 2022-02-07 10:50 | 1 | 033:27 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B22020600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2007 | 2022-02-06 | 2007 | keep | 0 | Feb | 2022 | 0.001367 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-06 01:23 | 2022-02-06 01:24 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2859 | keep | 0 | Feb | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
SAN JUAN | 2022-02-06 01:26 | 2022-02-06 01:28 | 1073 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO AL CERRAR B.I. CONTRA 1620-1 Y 95% 1336-10 MAL TIEMPO | S22020600000 | Partial_restoration | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 2146 | keep | 0 | Feb | 2022 | 0.0014616 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 01:30 | 2022-02-06 01:38 | 1073 | 000:08 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE CERRO POR SCADA LLEVANDO 1620-1 Y 95% 1336-10 MAL TIEMPO | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 8 | 2022-02-06 | 8584 | keep | 0 | Feb | 2022 | 0.0058465 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
CANOVANAS | 2022-02-06 01:34 | 2022-02-06 03:28 | 15 | 001:54 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SUA2 AVERIADO SE CERRO N/O EN RISER AL LADO DE PISCINA HACIA SU30 | R22020600000 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 114 | 2022-02-06 | 1710 | keep | 0 | Feb | 2022 | 0.0011647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 02:16 | 2022-02-06 02:18 | 513 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CARGA POR 1118-10 MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 1026 | keep | 0 | Feb | 2022 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-02-06 02:16 | 2022-02-06 02:18 | 2782 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 20% DEL 1111-1 MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 5564 | keep | 0 | Feb | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-02-06 02:19 | 2022-02-06 15:29 | 50 | 013:10 | P | ESTRUCTURA AVERIADA | 3 X 50 EN CORTE DE LINEA SE REPARO POSTE PARTIDO EN LA PERILLA GOI BY-220206-04 | B22020600103 | New_Event | Defective Pole | Include | Include | Equipment | 790 | 2022-02-06 | 39500 | keep | 0 | Feb | 2022 | 0.026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-06 03:01 | 2022-02-06 06:15 | 150 | 003:14 | P | DESGANCHE | SE REMOVIO ARBOL SOBRE LINEAS Y SE CERRARON MACHETES | P22020600024 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-02-06 | 29100 | keep | 0 | Feb | 2022 | 0.01982 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 03:02 | 2022-02-06 05:55 | 600 | 002:53 | P | DESGANCHE | SE ABRE MACHETE PARA RETIRAR ARBOL SOBRE LINEA | B22020600362 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-02-06 | 103800 | keep | 0 | Feb | 2022 | 0.070698 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
MAYAGÃœEZ | 2022-02-06 03:46 | 2022-02-06 03:47 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1287 | keep | 0 | Feb | 2022 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
GUAYAMA | 2022-02-06 03:57 | 2022-02-06 09:05 | 10 | 005:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR POSTE DE TELEFONO IMPACTO XMR | P22020600034 | New_Event |  |  | Include | Wildlife | 308 | 2022-02-06 | 3080 | keep | 0 | Feb | 2022 | 0.0020978 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-06 03:59 | 2022-02-06 04:01 | 418 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 836 | keep | 0 | Feb | 2022 | 0.0005694 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2022-02-06 03:59 | 2022-02-06 04:01 | 100 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO NO RECERRO LLEVA 40 AMP DEL 1014-16 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 04:02 | 2022-02-06 04:06 | 418 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF MAL TIEMPO | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 4 | 2022-02-06 | 1672 | keep | 0 | Feb | 2022 | 0.0011388 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2022-02-06 04:02 | 2022-02-06 04:06 | 100 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO PARTE POR 1013-13 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 4 | 2022-02-06 | 400 | keep | 0 | Feb | 2022 | 0.00027244 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 04:02 | 2022-02-07 13:28 | 40 | 033:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020600121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2006 | 2022-02-06 | 80240 | keep | 0 | Feb | 2022 | 0.054651 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-06 04:12 | 2022-02-06 10:38 | 58 | 006:26 | P | ESTRUCTURA AVERIADA | ABRIO PUENTES HACIA AVERIA HAY QUE REMPLAZAR 2 POSTES | C22020600004 | New_Event | Defective Pole | Include | Include | Equipment | 386 | 2022-02-06 | 22388 | keep | 0 | Feb | 2022 | 0.015248 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
VEGA BAJA | 2022-02-06 04:28 | 2022-02-06 04:29 | 538 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO MAL TIEMPO | B22020600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 538 | keep | 0 | Feb | 2022 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
BAYAMON | 2022-02-06 04:38 | 2022-02-06 04:39 | 2147 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO MAL TIEMPO | B22020600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 2147 | keep | 0 | Feb | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2022-02-06 04:49 | 2022-02-06 08:41 | 220 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN SU-8A HACIA T-18 MAL TIEMPO | R22020600022 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2022-02-06 | 51040 | keep | 0 | Feb | 2022 | 0.034763 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
CAGUAS | 2022-02-06 05:13 | 2022-02-06 09:20 | 40 | 004:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22020600007 | New_Event |  |  | Include | Wildlife | 247 | 2022-02-06 | 9880 | keep | 0 | Feb | 2022 | 0.0067292 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-06 05:14 | 2022-02-06 05:15 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2022-02-06 05:26 | 2022-02-06 05:52 | 60 | 000:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER PORTAFUSIBLE | S22020600135 | New_Event | Cutout Failure | Include | Include | Equipment | 26 | 2022-02-06 | 1560 | keep | 0 | Feb | 2022 | 0.0010625 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-06 05:33 | 2022-02-06 16:51 | 30 | 011:18 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020600136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 678 | 2022-02-06 | 20340 | keep | 0 | Feb | 2022 | 0.013853 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-02-06 05:38 | 2022-02-06 09:51 | 109 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R22020600025 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2022-02-06 | 27577 | keep | 0 | Feb | 2022 | 0.018783 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
ARECIBO | 2022-02-06 05:41 | 2022-02-06 13:52 | 150 | 008:11 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22020600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2022-02-06 | 73650 | keep | 0 | Feb | 2022 | 0.050163 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-02-06 05:49 | 2022-02-06 05:52 | 380 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO 95% DE SU CARGA POR EL 1620-03 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 0.00025882 | Momentary | FALSE | FALSE | Not_TMED_Event | 380
SAN JUAN | 2022-02-06 05:49 | 2022-02-06 05:52 | 36 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CARGA POR 1620-3 Y 95% 1336-10 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-06 05:49 | 2022-02-06 05:52 | 1073 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO LLEVA 1620-01 Y 95% 1336-10 MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 3219 | keep | 0 | Feb | 2022 | 0.0021924 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-02-06 05:53 | 2022-02-06 14:48 | 3 | 008:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R22020600027 | New_Event | Cutout Failure | Include | Include | Equipment | 535 | 2022-02-06 | 1605 | keep | 0 | Feb | 2022 | 0.0010932 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-02-06 05:55 | 2022-02-06 07:41 | 40 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22020600144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-02-06 | 4240 | keep | 0 | Feb | 2022 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-06 06:00 | 2022-02-06 08:01 | 1227 | 002:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | A22020600014 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 121 | 2022-02-06 | 148467 | keep | 0 | Feb | 2022 | 0.10112 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2022-02-06 06:14 | 2022-02-06 11:40 | 600 | 005:26 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO GOI BY-220206-03 | B22020600163 | New_Event | Switch Failure | Include | Include | Equipment | 326 | 2022-02-06 | 195600 | keep | 0 | Feb | 2022 | 0.13322 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-02-06 06:33 | 2022-02-07 12:25 | 50 | 029:52 | P | NO SE REPORTO CAUSA | 1 X 12 EN TRANSFORMADOR Y 1 X 40 EN BOVEDA | S22020600149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1792 | 2022-02-06 | 89600 | keep | 0 | Feb | 2022 | 0.061026 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-06 06:36 | 2022-02-06 12:45 | 30 | 006:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22020600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-02-06 | 11070 | keep | 0 | Feb | 2022 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-06 06:41 | 2022-02-07 11:57 | 42 | 029:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REPARO TERMINACION | B22020600155 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1756 | 2022-02-06 | 73752 | keep | 0 | Feb | 2022 | 0.050232 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
ARECIBO | 2022-02-06 06:43 | 2022-02-06 10:43 | 50 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22020600020 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2022-02-06 | 12000 | keep | 0 | Feb | 2022 | 0.0081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-06 06:44 | 2022-02-06 12:56 | 50 | 006:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22020600010 | New_Event | Bad Weather | Include | Include | Weather | 372 | 2022-02-06 | 18600 | keep | 0 | Feb | 2022 | 0.012668 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-06 06:56 | 2022-02-06 10:52 | 60 | 003:56 | P | DESGANCHE | 2 X 50 Y 2 X 40 EN CORTES DE LINEA | C22020600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-02-06 | 14160 | keep | 0 | Feb | 2022 | 0.0096443 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-06 07:03 | 2022-02-06 08:42 | 20 | 001:39 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22020600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-02-06 | 1980 | keep | 0 | Feb | 2022 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-06 07:13 | 2022-02-06 14:34 | 65 | 007:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR SE REEMPLAZO 2 DISCO Y CAJA PRIMARIA | R22020600034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 441 | 2022-02-06 | 28665 | keep | 0 | Feb | 2022 | 0.019524 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-02-06 07:17 | 2022-02-06 07:18 | 1844 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LLEVA 30% DE 1346-03 Y 30% DE 1529-15 | S22020600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-06 | 1844 | keep | 0 | Feb | 2022 | 0.0012559 | 0.0012559 | Momentary | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2022-02-06 07:17 | 2022-02-06 07:18 | 726 | 000:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE DEL 1346-02 QUE LLEVA 30% DE LA CARGA DEL 1346-03 | S22020600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-06 | 726 | keep | 0 | Feb | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
BAYAMON | 2022-02-06 07:17 | 2022-02-06 07:18 | 540 | 000:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE DEL 1346-02 QUE LLEVA 30% DE LA CARGA DEL 1529-15 | S22020600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-06 | 540 | keep | 0 | Feb | 2022 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
MAYAGÃœEZ | 2022-02-06 07:18 | 2022-02-06 13:56 | 70 | 006:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22020600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2022-02-06 | 27860 | keep | 0 | Feb | 2022 | 0.018975 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-02-06 07:26 | 2022-02-06 08:37 | 200 | 001:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A22020600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-02-06 | 14200 | keep | 0 | Feb | 2022 | 0.0096716 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-06 07:31 | 2022-02-06 12:10 | 60 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B22020600174 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2022-02-06 | 16740 | keep | 0 | Feb | 2022 | 0.011402 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-06 07:36 | 2022-02-06 10:34 | 130 | 002:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO Y REEMPLAZO DISCO | R22020600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-02-06 | 23140 | keep | 0 | Feb | 2022 | 0.015761 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-02-06 07:39 | 2022-02-06 16:24 | 50 | 008:45 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020600180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 525 | 2022-02-06 | 26250 | keep | 0 | Feb | 2022 | 0.017879 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 07:43 | 2022-02-06 11:02 | 2735 | 003:19 | T | DESGANCHE | DISPARO 9501-03 LLEVANDO LA CARGA DEL 9501-02 SE SECCIONALIZO ALIMENTADOR 25% EN SERVICIO | B22020600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-02-06 | 544265 | keep | 0 | Feb | 2022 | 0.3707 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-02-06 07:43 | 2022-02-06 09:41 | 1070 | 001:58 | T | DESGANCHE | LLEVA LA CARGA DEL 9501-02 SE ABRIO AMARRE Y SE CERRO POR SCADA | B22020600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-02-06 | 126260 | keep | 0 | Feb | 2022 | 0.085995 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
SAN JUAN | 2022-02-06 07:53 | 2022-02-06 18:32 | 50 | 010:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 Y 1 X 65 EN CORTES DE LINEA SE REPARO BAJANTE DE LINEA A CAJA EN CORTE DE LINEA | S22020600292 | New_Event | Wire Down | Include | Include | Equipment | 639 | 2022-02-06 | 31950 | keep | 0 | Feb | 2022 | 0.021761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-06 08:01 | 2022-02-06 08:26 | 920 | 000:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | AL CERRAR MACHETES SE DISPARO EL INTERRUPTOR | A22020600014 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 25 | 2022-02-06 | 23000 | keep | 0 | Feb | 2022 | 0.015665 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 08:02 | 2022-02-06 08:03 | 1 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1 | keep | 0 | Feb | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-02-06 08:03 | 2022-02-06 09:43 | 20 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR LLUVIA Y VIENTO | A22020600035 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-02-06 | 2000 | keep | 0 | Feb | 2022 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-06 08:23 | 2022-02-06 08:24 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22020600041 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 3431 | keep | 0 | Feb | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-02-06 08:24 | 2022-02-06 12:04 | 35 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO | A22020600059 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 220 | 2022-02-06 | 7700 | keep | 0 | Feb | 2022 | 0.0052444 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-02-06 08:26 | 2022-02-06 08:29 | 1227 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO NUEVAMENTE LOS MACHETES Y SE CERRO EL INTERRUPTOR | A22020600043 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2022-02-06 | 3681 | keep | 0 | Feb | 2022 | 0.0025071 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-06 08:29 | 2022-02-06 10:11 | 920 | 001:42 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO BAJANTE PRIMARIO ZAFADO EN MACHETES Y AL CERRAR LOS MACHETES QUE SE HABIAN ABIERTO SE DISPARO EL INTERRUPTOR | A22020600043 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 102 | 2022-02-06 | 93840 | keep | 0 | Feb | 2022 | 0.063914 | 0.00062661 | Sustained | FALSE | FALSE | Not_TMED_Event | 920
BAYAMON | 2022-02-06 08:32 | 2022-02-06 18:37 | 50 | 010:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22020600225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 605 | 2022-02-06 | 30250 | keep | 0 | Feb | 2022 | 0.020603 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 08:47 | 2022-02-06 08:49 | 996 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22020600000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-02-06 | 1992 | keep | 0 | Feb | 2022 | 0.0013567 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2022-02-06 08:49 | 2022-02-06 08:51 | 1447 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA DE 1419-09 Y 1419-12 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 2894 | keep | 0 | Feb | 2022 | 0.0019711 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-02-06 08:49 | 2022-02-06 08:51 | 266 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1112-04 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 532 | keep | 0 | Feb | 2022 | 0.00036234 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-02-06 08:49 | 2022-02-06 08:51 | 73 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1112-04 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 146 | keep | 0 | Feb | 2022 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2022-02-06 09:06 | 2022-02-06 09:07 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1909-08 LLEVA LA CARGA DEL 1907-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-06 09:06 | 2022-02-06 09:07 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1907-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
HUMACAO | 2022-02-06 09:08 | 2022-02-06 13:56 | 122 | 004:48 | P | DESGANCHE | 3 X 50 EN C/L | C22020600053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-02-06 | 35136 | keep | 0 | Feb | 2022 | 0.023931 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
BARRANQUITAS | 2022-02-06 09:09 | 2022-02-06 20:00 | 23 | 010:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22020600055 | New_Event | Bad Weather | Include | Include | Weather | 651 | 2022-02-06 | 14973 | keep | 0 | Feb | 2022 | 0.010198 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2022-02-06 09:15 | 2022-02-06 14:11 | 65 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22020600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-02-06 | 19240 | keep | 0 | Feb | 2022 | 0.013104 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2022-02-06 09:19 | 2022-02-06 12:19 | 7 | 003:00 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22020600059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 180 | 2022-02-06 | 1260 | keep | 0 | Feb | 2022 | 0.00085818 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-02-06 09:20 | 2022-02-06 09:40 | 10 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONEXIONES SECUNDARIAS | A22020600036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-02-06 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-06 09:20 | 2022-02-06 10:56 | 22 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | A22020600060 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2022-02-06 | 2112 | keep | 0 | Feb | 2022 | 0.0014385 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2022-02-06 09:22 | 2022-02-06 09:23 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BARRANQUITAS | 2022-02-06 09:22 | 2022-02-06 16:15 | 100 | 006:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L CERRO PUENTE | C22020600060 | New_Event | Wire Down | Include | Include | Equipment | 413 | 2022-02-06 | 41300 | keep | 0 | Feb | 2022 | 0.028129 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-06 09:23 | 2022-02-06 10:44 | 760 | 001:21 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES PARA SECCIONALIZAR AISLADOR ROTO Y SE CERRO EL INTERRUPTOR | A22020600062 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 81 | 2022-02-06 | 61560 | keep | 0 | Feb | 2022 | 0.041928 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
PONCE | 2022-02-06 09:27 | 2022-02-06 09:28 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2113 | keep | 0 | Feb | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BAYAMON | 2022-02-06 09:28 | 2022-02-06 09:29 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1909-08 LLEVA LA CARGA DEL 1907-05 | S22020600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-06 09:28 | 2022-02-06 09:29 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1907-05 | S22020600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-02-06 09:29 | 2022-02-06 17:03 | 80 | 007:34 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | S22020600264 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 454 | 2022-02-06 | 36320 | keep | 0 | Feb | 2022 | 0.024737 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-06 09:31 | 2022-02-06 18:39 | 60 | 009:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 40 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA | B22020600312 | New_Event | Wire Down | Include | Include | Equipment | 548 | 2022-02-06 | 32880 | keep | 0 | Feb | 2022 | 0.022394 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-02-06 09:34 | 2022-02-06 11:22 | 11 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN XMR MAL TIEMPO | C22020600069 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2022-02-06 | 1188 | keep | 0 | Feb | 2022 | 0.00080914 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-02-06 09:36 | 2022-02-06 15:45 | 100 | 006:09 | P | DESGANCHE | 3 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-02-06 | 36900 | keep | 0 | Feb | 2022 | 0.025132 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 09:39 | 2022-02-06 09:41 | 996 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL REALIZANDO OPERACIONES ALIMENTADOR 1116-05 SE CERRO POR SCADA | S22020600000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2022-02-06 | 1992 | keep | 0 | Feb | 2022 | 0.0013567 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
CAGUAS | 2022-02-06 09:39 | 2022-02-06 13:55 | 40 | 004:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | C22020600072 | New_Event | Bad Weather | Include | Include | Weather | 256 | 2022-02-06 | 10240 | keep | 0 | Feb | 2022 | 0.0069744 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-06 09:45 | 2022-02-06 15:35 | 30 | 005:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER | S22020600292 | New_Event | Bad Weather | Include | Include | Weather | 350 | 2022-02-06 | 10500 | keep | 0 | Feb | 2022 | 0.0071515 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-06 09:45 | 2022-02-06 12:54 | 80 | 003:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22020600010 | New_Event | Bad Weather | Include | Include | Weather | 189 | 2022-02-06 | 15120 | keep | 0 | Feb | 2022 | 0.010298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-06 09:46 | 2022-02-06 11:15 | 129 | 001:29 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN RISER HACIA SU-3 CONTAMINACION EN SU-2 | R22020600072 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 89 | 2022-02-06 | 11481 | keep | 0 | Feb | 2022 | 0.0078197 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
MAYAGÃœEZ | 2022-02-06 09:46 | 2022-02-06 16:59 | 40 | 007:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22020600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2022-02-06 | 17320 | keep | 0 | Feb | 2022 | 0.011797 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-06 09:47 | 2022-02-06 09:48 | 1647 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1647 | keep | 0 | Feb | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
AGUADILLA | 2022-02-06 09:49 | 2022-02-06 11:08 | 10 | 001:19 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMA | M22020600012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-02-06 | 790 | keep | 0 | Feb | 2022 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-06 09:54 | 2022-02-06 10:31 | 6 | 000:37 | P | SECUNDARIA/DESGANCHE | DESGANCHO Y LEVANTO SECUNDARIA NO FUNDIO | C22020600076 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 37 | 2022-02-06 | 222 | keep | 0 | Feb | 2022 | 0.0001512 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-02-06 09:57 | 2022-02-06 21:17 | 20 | 011:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR 50 KVA | A22020600086 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 680 | 2022-02-06 | 13600 | keep | 0 | Feb | 2022 | 0.0092629 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 10:02 | 2022-02-06 11:55 | 74 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN SU-15 HACIA T-6 MAL TIEMPO | R22020600075 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-02-06 | 8362 | keep | 0 | Feb | 2022 | 0.0056953 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
ARECIBO | 2022-02-06 10:05 | 2022-02-06 10:06 | 4607 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A22020600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-06 | 4607 | keep | 0 | Feb | 2022 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
ARECIBO | 2022-02-06 10:06 | 2022-02-06 12:49 | 100 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100AMP | A22020600080 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 163 | 2022-02-06 | 16300 | keep | 0 | Feb | 2022 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 10:08 | 2022-02-06 10:11 | 996 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL REALIZANDO OPERACIONES ALIMENTADOR 1116-05 SE CERRO POR SCADA | S22020600000 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2022-02-06 | 2988 | keep | 0 | Feb | 2022 | 0.0020351 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
ARECIBO | 2022-02-06 10:11 | 2022-02-06 10:16 | 1227 | 000:05 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE VOLVIO A ABRIR LOS MACHETES QUE SE HABIAN CERRADO Y SE CERRO EL INTERRUPTOR | A22020600078 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 5 | 2022-02-06 | 6135 | keep | 0 | Feb | 2022 | 0.0041785 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-02-06 10:16 | 2022-02-06 11:32 | 920 | 001:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO DE RISER HACIA SU-2 EN RESIDENCIAL TRINA PADILLA PARA SECCIONALIZAR TERMINACIONES QUEMADAS EN SU-2 Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR | A22020600078 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 76 | 2022-02-06 | 69920 | keep | 0 | Feb | 2022 | 0.047622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-06 10:21 | 2022-02-06 11:05 | 64 | 000:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R22020600079 | New_Event | Bad Weather | Include | Include | Weather | 44 | 2022-02-06 | 2816 | keep | 0 | Feb | 2022 | 0.001918 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2022-02-06 10:27 | 2022-02-06 15:00 | 50 | 004:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22020600390 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2022-02-06 | 13650 | keep | 0 | Feb | 2022 | 0.009297 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 10:37 | 2022-02-07 10:33 | 20 | 023:56 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA SE RETIRO CARGA PRIVADA CON PROBLEMAS | S22020600322 | New_Event | Other Causes | Include | Include | Other | 1436 | 2022-02-06 | 28720 | keep | 0 | Feb | 2022 | 0.019561 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-06 10:38 | 2022-02-07 17:21 | 8 | 030:43 | P | ESTRUCTURA AVERIADA | POSTE PRIMARIO PARTIDO TRASPATIO CON TRANSFORMADOR SE SECCIONALIZO | C22020600004 | New_Event | Defective Pole | Include | Include | Equipment | 1843 | 2022-02-06 | 14744 | keep | 0 | Feb | 2022 | 0.010042 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-06 10:39 | 2022-02-07 11:03 | 12 | 024:24 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | B22020600702 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1464 | 2022-02-06 | 17568 | keep | 0 | Feb | 2022 | 0.011965 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-02-06 10:39 | 2022-02-06 10:40 | 50 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO | A22020600085 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 50 | keep | 0 | Feb | 2022 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 10:40 | 2022-02-06 23:25 | 50 | 012:45 | P | DESGANCHE | SE ABRIO CORTE DE LINEA RETIRAR PELIGRO PARA RETIRAR ARBOL SOBRE LINEA | B22020600405 | New_Event | Vegetation Contact | Include | Include | Vegetation | 765 | 2022-02-06 | 38250 | keep | 0 | Feb | 2022 | 0.026052 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 10:41 | 2022-02-06 10:42 | 996 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL REALIZANDO OPERACIONES ALIMENTADOR 1116-05 SE CERRO POR SCADA | S22020600000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-02-06 | 996 | keep | 0 | Feb | 2022 | 0.00067837 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
ARECIBO | 2022-02-06 10:44 | 2022-02-06 12:18 | 200 | 001:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22020600062 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 94 | 2022-02-06 | 18800 | keep | 0 | Feb | 2022 | 0.012805 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-02-06 10:45 | 2022-02-06 10:57 | 80 | 000:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22020600325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2022-02-06 | 960 | keep | 0 | Feb | 2022 | 0.00065385 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-06 10:46 | 2022-02-06 15:49 | 20 | 005:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020600015 | New_Event | Bad Weather | Include | Include | Weather | 303 | 2022-02-06 | 6060 | keep | 0 | Feb | 2022 | 0.0041274 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-06 10:50 | 2022-02-06 10:52 | 539 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 1078 | keep | 0 | Feb | 2022 | 0.00073422 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
BAYAMON | 2022-02-06 10:53 | 2022-02-06 11:02 | 1070 | 000:09 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA CERRAR AMARRE CON 9501-02 SE SECCIONALIZO 9501-02 | B22020600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 9 | 2022-02-06 | 9630 | keep | 0 | Feb | 2022 | 0.0065589 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
SAN JUAN | 2022-02-06 10:57 | 2022-02-06 10:58 | 4291 | 000:01 | T | DESGANCHE | RECIERRE | S22020600000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-06 | 4291 | keep | 0 | Feb | 2022 | 0.0029226 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 10:58 | 2022-02-06 22:16 | 80 | 011:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22020600325 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 678 | 2022-02-06 | 54240 | keep | 0 | Feb | 2022 | 0.036943 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-06 10:58 | 2022-02-06 14:51 | 45 | 003:53 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA Y 1 X 80 EN SU | S22020400353 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 233 | 2022-02-06 | 10485 | keep | 0 | Feb | 2022 | 0.0071413 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-06 10:59 | 2022-02-06 13:49 | 100 | 002:50 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P22020600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-02-06 | 17000 | keep | 0 | Feb | 2022 | 0.011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 11:02 | 2022-02-06 11:57 | 2051 | 000:55 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR 50% EN SERVICIO | B22020600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-02-06 | 112805 | keep | 0 | Feb | 2022 | 0.076831 | 0.0013969 | Sustained | FALSE | FALSE | Not_TMED_Event | 2051
VEGA BAJA | 2022-02-06 11:07 | 2022-02-07 14:03 | 25 | 026:56 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO | B22020600440 | New_Event | Defective Pole | Include | Include | Equipment | 1616 | 2022-02-06 | 40400 | keep | 0 | Feb | 2022 | 0.027516 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-06 11:13 | 2022-02-06 11:33 | 3 | 000:20 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO V/S CONTRA 1116-03 | S22020500000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 20 | 2022-02-06 | 60 | keep | 0 | Feb | 2022 | 4.0866e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-06 11:30 | 2022-02-06 12:50 | 105 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R22020600087 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2022-02-06 | 8400 | keep | 0 | Feb | 2022 | 0.0057212 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
VEGA BAJA | 2022-02-06 11:31 | 2022-02-07 11:33 | 125 | 024:02 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 40 Y 1 X 10 EN CORTES DE LINEA | B22020600331 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1442 | 2022-02-06 | 180250 | keep | 0 | Feb | 2022 | 0.12277 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-02-06 11:32 | 2022-02-06 16:22 | 100 | 004:50 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO RISER SE REPARO AVERIA DEL TERMINACION EN SU-2 A SU-1 | A22020600114 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 290 | 2022-02-06 | 29000 | keep | 0 | Feb | 2022 | 0.019752 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 11:33 | 2022-02-06 12:03 | 2 | 000:30 | P | DESCONECTIVO DEFECTUOSO | SE CERRO EN V/S SE TRANSFIRIO LA CARGA AL 1116-03 100% EN SERVICIO SE REMPLAZO VACUUM SWITCH AVERIADO | S22020500000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 30 | 2022-02-06 | 60 | keep | 0 | Feb | 2022 | 4.0866e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-06 11:33 | 2022-02-06 17:05 | 50 | 005:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | P22020600094 | New_Event | Bad Weather | Include | Include | Weather | 332 | 2022-02-06 | 16600 | keep | 0 | Feb | 2022 | 0.011306 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 11:37 | 2022-02-06 13:37 | 60 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | S22020600360 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2022-02-06 | 7200 | keep | 0 | Feb | 2022 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-06 11:40 | 2022-02-06 12:18 | 1800 | 000:38 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES QUEMADOS CON GOI BY-220206-03 Y SE TRANSFIRIO CARGA AL 9405-05 | B22020600163 | New_Event | Switch Failure | Include | Include | Equipment | 38 | 2022-02-06 | 68400 | keep | 0 | Feb | 2022 | 0.046587 | 0.001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 1800
SAN JUAN | 2022-02-06 11:44 | 2022-02-06 12:12 | 23 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22020600365 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2022-02-06 | 644 | keep | 0 | Feb | 2022 | 0.00043863 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CANOVANAS | 2022-02-06 11:50 | 2022-02-06 12:06 | 1 | 000:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R22020600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2022-02-06 | 16 | keep | 0 | Feb | 2022 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-06 11:57 | 2022-02-06 13:29 | 1367 | 001:32 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR 75% EN SERVICIO | B22020600183 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-02-06 | 125764 | keep | 0 | Feb | 2022 | 0.085657 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-06 12:01 | 2022-02-06 12:02 | 1604 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE | C22020600000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2022-02-06 | 1604 | keep | 0 | Feb | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-02-06 12:02 | 2022-02-06 19:02 | 225 | 007:00 | P | ESTRUCTURA AVERIADA | 3 X 100 EN C/L SECCIONALIZO POSTE PARTIDO | C22020600130 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 420 | 2022-02-06 | 94500 | keep | 0 | Feb | 2022 | 0.064364 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
BAYAMON | 2022-02-06 12:13 | 2022-02-06 17:40 | 1000 | 005:27 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES Y SE NORMALIZO CARGA MEDIANTE GOI BY-220206-03 | B22020600165 | New_Event | Switch Failure | Include | Include | Equipment | 327 | 2022-02-06 | 327000 | keep | 0 | Feb | 2022 | 0.22272 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
BARRANQUITAS | 2022-02-06 12:48 | 2022-02-07 18:58 | 16 | 030:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 100 KVA X 100KVA | C22020700031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1810 | 2022-02-06 | 28960 | keep | 0 | Feb | 2022 | 0.019725 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2022-02-06 13:00 | 2022-02-06 18:17 | 50 | 005:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR ROTO | P22020600101 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 317 | 2022-02-06 | 15850 | keep | 0 | Feb | 2022 | 0.010795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-06 13:02 | 2022-02-06 18:58 | 12 | 005:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR CONTAMINACION EN EL PORTAFUSIBLE | R22020600131 | New_Event | Cutout Failure | Include | Include | Equipment | 356 | 2022-02-06 | 4272 | keep | 0 | Feb | 2022 | 0.0029096 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-06 13:05 | 2022-02-06 13:40 | 8 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22020600019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-02-06 | 280 | keep | 0 | Feb | 2022 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-02-06 13:07 | 2022-02-06 17:32 | 40 | 004:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22020600143 | New_Event | Bad Weather | Include | Include | Weather | 265 | 2022-02-06 | 10600 | keep | 0 | Feb | 2022 | 0.0072196 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-06 13:08 | 2022-02-07 12:41 | 45 | 023:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020600583 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1413 | 2022-02-06 | 63585 | keep | 0 | Feb | 2022 | 0.043307 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-02-06 13:10 | 2022-02-06 13:11 | 1415 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1415 | keep | 0 | Feb | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
BAYAMON | 2022-02-06 13:11 | 2022-02-06 13:12 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1720-08 | B22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2402 | keep | 0 | Feb | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-02-06 13:11 | 2022-02-06 13:12 | 1 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1709-02 DISPARO Y SE CERRO POR CONTROL | B22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1 | keep | 0 | Feb | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-06 13:13 | 2022-02-07 08:20 | 20 | 019:07 | P | NO SE REPORTO CAUSA | 2 X 30 EN BANCO DE TRANSFORMADORES Y 1 X 50 EN CORTE DE LINEA | S22020600435 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1147 | 2022-02-06 | 22940 | keep | 0 | Feb | 2022 | 0.015624 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-02-06 13:15 | 2022-02-06 17:08 | 10 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | P22020600103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2022-02-06 | 2330 | keep | 0 | Feb | 2022 | 0.001587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-06 13:17 | 2022-02-07 14:59 | 30 | 025:42 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22020600591 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1542 | 2022-02-06 | 46260 | keep | 0 | Feb | 2022 | 0.031507 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-06 13:19 | 2022-02-06 13:37 | 1264 | 000:18 | T | ERROR HUMANO | MANAGER DE BAYAMON INDICO FEEDER INCORRECTO ALEGANDO CONDUCTOR VIVO EN EL SUELO | S22020600000 | New_Event | Human Error | Include | Include | Other | 18 | 2022-02-06 | 22752 | keep | 0 | Feb | 2022 | 0.015496 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
FAJARDO | 2022-02-06 13:21 | 2022-02-06 13:22 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22020600099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1830 | keep | 0 | Feb | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
ARECIBO | 2022-02-06 13:26 | 2022-02-06 17:54 | 20 | 004:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR ARBOL SECO IMPACTA LINEA AL CAERSE RETIRO RAMAS SOBRE LAS LINEAS | A22020600116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-02-06 | 5360 | keep | 0 | Feb | 2022 | 0.0036507 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-02-06 13:28 | 2022-02-06 15:57 | 20 | 002:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN XMR SE REPARO SECUNDAIA | P22020600105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 149 | 2022-02-06 | 2980 | keep | 0 | Feb | 2022 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-06 13:28 | 2022-02-06 16:37 | 15 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22020600604 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-02-06 | 2835 | keep | 0 | Feb | 2022 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-06 13:29 | 2022-02-07 17:45 | 20 | 028:16 | P | ESTRUCTURA AVERIADA | 2 X 30 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO Y TRANSFORMADOR | S22020600450 | New_Event | Defective Pole | Include | Include | Equipment | 1696 | 2022-02-06 | 33920 | keep | 0 | Feb | 2022 | 0.023103 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-06 13:29 | 2022-02-06 13:42 | 683 | 000:13 | P | DESGANCHE | ALIMENTADOR SECCIONALIZADO 75% EN SERVICIO | B22020600183 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 13 | 2022-02-06 | 8879 | keep | 0 | Feb | 2022 | 0.0060474 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-06 13:31 | 2022-02-06 17:43 | 150 | 004:12 | P | DESGANCHE | 2 X 200 EN C/L | C22020600156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-02-06 | 37800 | keep | 0 | Feb | 2022 | 0.025745 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-06 13:37 | 2022-02-06 13:58 | 620 | 000:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | S22020600000 | Additional_clients | Wire Down | Include | Include | Equipment | 21 | 2022-02-06 | 13020 | keep | 0 | Feb | 2022 | 0.0088679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 13:42 | 2022-02-06 13:51 | 2735 | 000:09 | T | DESGANCHE | DISPARO 9501-03 LLEVANDO LA CARGA DEL 9501-02 SE CERRO INTERRUPTOR 75% EN SERVICIO | B22020600183 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 9 | 2022-02-06 | 24615 | keep | 0 | Feb | 2022 | 0.016765 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 13:42 | 2022-02-06 13:51 | 1070 | 000:09 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVANDO 9501-02 AL CERRAR EL INTERRUPTOR ENTRO UN 75% DEL 9501-02 EN SERVICIO | B22020600183 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 9 | 2022-02-06 | 9630 | keep | 0 | Feb | 2022 | 0.0065589 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 13:46 | 2022-02-06 19:22 | 1280 | 005:36 | P | LINEA DE TRANSMISION 38KV | SE PASO PARTE DE LA CARGA 1346-02 AL 1346-03 POR OVERHEAD QUE CAYO SOBRE ALIMENTADOR 1346-02. BKR 1346-02 NO QUISO CERRAR. 30% DE 1346-02 ESTA POR 1529-15 | S22020600398 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 336 | 2022-02-06 | 430080 | keep | 0 | Feb | 2022 | 0.29293 | 0.0008718 | Sustained | FALSE | FALSE | Not_TMED_Event | 1280
BAYAMON | 2022-02-06 13:46 | 2022-02-06 15:02 | 1500 | 001:16 | P | LINEA DE TRANSMISION 38KV | SE PASO 60% DEL 30% QUE LLEVA EL 1346-02 AL 1907-04 CERRANDO N/O POR LINEA OVERHEAD QUE CAYO EN ALIMENTADOR | S22020600398 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 76 | 2022-02-06 | 114000 | keep | 0 | Feb | 2022 | 0.077645 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
CAGUAS | 2022-02-06 13:47 | 2022-02-06 13:48 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020600162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1342 | keep | 0 | Feb | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BAYAMON | 2022-02-06 13:51 | 2022-02-06 16:21 | 683 | 002:30 | P | DESGANCHE | ALIMENTADOR SECCIONALIZADO 90% EN SERVICIO | B22020600183 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-02-06 | 102450 | keep | 0 | Feb | 2022 | 0.069778 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-06 13:55 | 2022-02-06 13:56 | 1378 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22020600167 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 1378 | keep | 0 | Feb | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
SAN JUAN | 2022-02-06 13:56 | 2022-02-06 17:01 | 49 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN SU-6A AL T-14 SE SECCIONALIZO CABLE SOTERRADO AVERIADO POR PERSONAL DE AAA | R22020600102 | New_Event |  |  | Include | Wildlife | 185 | 2022-02-06 | 9065 | keep | 0 | Feb | 2022 | 0.0061741 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CAGUAS | 2022-02-06 13:56 | 2022-02-06 13:57 | 1378 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22020600167 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 1378 | keep | 0 | Feb | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
CAGUAS | 2022-02-06 13:57 | 2022-02-06 16:32 | 40 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | C22020600072 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 155 | 2022-02-06 | 6200 | keep | 0 | Feb | 2022 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-06 13:58 | 2022-02-06 20:03 | 60 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | S22020600360 | Partial_restoration | Wire Down | Include | Include | Equipment | 365 | 2022-02-06 | 21900 | keep | 0 | Feb | 2022 | 0.014916 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-06 14:06 | 2022-02-06 14:07 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1597 | keep | 0 | Feb | 2022 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
CAGUAS | 2022-02-06 14:08 | 2022-02-06 16:20 | 85 | 002:12 | P | DESGANCHE | 2 X 65 EN C/L | C22020600174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-02-06 | 11220 | keep | 0 | Feb | 2022 | 0.0076419 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 1717 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 326230 | keep | 0 | Feb | 2022 | 0.22219 | 0.0011694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 974 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 185060 | keep | 0 | Feb | 2022 | 0.12604 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 1905 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 361950 | keep | 0 | Feb | 2022 | 0.24652 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 1262 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 239780 | keep | 0 | Feb | 2022 | 0.16331 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 200 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 38000 | keep | 0 | Feb | 2022 | 0.025882 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 222 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600135 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 42180 | keep | 0 | Feb | 2022 | 0.028729 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
PONCE | 2022-02-06 14:08 | 2022-02-06 17:18 | 537 | 003:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P22020600135 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-02-06 | 102030 | keep | 0 | Feb | 2022 | 0.069492 | 0.00036575 | Sustained | FALSE | FALSE | Not_TMED_Event | 537
VEGA BAJA | 2022-02-06 14:10 | 2022-02-07 12:08 | 85 | 021:58 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B22202060064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1318 | 2022-02-06 | 112030 | keep | 0 | Feb | 2022 | 0.076303 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2022-02-06 14:13 | 2022-02-07 18:47 | 45 | 028:34 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO | A22020600121 | New_Event | Defective Pole | Include | Include | Equipment | 1714 | 2022-02-06 | 77130 | keep | 0 | Feb | 2022 | 0.052533 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-02-06 14:17 | 2022-02-06 16:38 | 50 | 002:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S22020600485 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2022-02-06 | 7050 | keep | 0 | Feb | 2022 | 0.0048017 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-06 14:19 | 2022-02-06 14:20 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 3744 | keep | 0 | Feb | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
UTUADO | 2022-02-06 14:24 | 2022-02-06 23:18 | 10 | 008:54 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR LLUVIA Y VIENTOS | A22020600123 | New_Event | Bad Weather | Include | Include | Weather | 534 | 2022-02-06 | 5340 | keep | 0 | Feb | 2022 | 0.003637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-06 14:27 | 2022-02-07 11:37 | 75 | 021:10 | P | DESGANCHE | 2 X 50 CORTE DE LINEA | B22020600655 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1270 | 2022-02-06 | 95250 | keep | 0 | Feb | 2022 | 0.064874 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-02-06 14:43 | 2022-02-06 14:44 | 595 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 595 | keep | 0 | Feb | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
CAGUAS | 2022-02-06 14:46 | 2022-02-06 17:20 | 32 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L RETIRO SECUNDARIA CRUZANDO CAJA | C22020600184 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2022-02-06 | 4928 | keep | 0 | Feb | 2022 | 0.0033564 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
UTUADO | 2022-02-06 14:46 | 2022-02-07 09:59 | 25 | 019:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | A22020600127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1153 | 2022-02-06 | 28825 | keep | 0 | Feb | 2022 | 0.019633 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-06 14:48 | 2022-02-06 18:40 | 20 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020600048 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2022-02-06 | 4640 | keep | 0 | Feb | 2022 | 0.0031603 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-06 14:50 | 2022-02-06 18:33 | 2190 | 003:43 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | M22020600051 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-02-06 | 488370 | keep | 0 | Feb | 2022 | 0.33263 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-02-06 14:52 | 2022-02-06 17:57 | 50 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020600052 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2022-02-06 | 9250 | keep | 0 | Feb | 2022 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-06 14:56 | 2022-02-08 21:27 | 25 | 054:31 | P | CABLE SOTERRADO AVERIADO | SE TIRO AEREO PROVISIONAL DEL PM-25 @ PM-26 EVENTO DEL DIA 6 AUNQUE DIERON UN EVENTO DEL DIA 8 | M22020800008 | New_Event | UG Cable Fault | Include | Include | Equipment | 3271 | 2022-02-06 | 81775 | keep | 0 | Feb | 2022 | 0.055697 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-06 14:59 | 2022-02-06 17:35 | 100 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020600054 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-02-06 | 15600 | keep | 0 | Feb | 2022 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-06 15:03 | 2022-02-07 10:40 | 5 | 019:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE RETEZO LINEA BAJITA | A22020600133 | New_Event | Wire Down | Include | Include | Equipment | 1177 | 2022-02-06 | 5885 | keep | 0 | Feb | 2022 | 0.0040082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-06 15:12 | 2022-02-06 17:31 | 30 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22020600524 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-02-06 | 4170 | keep | 0 | Feb | 2022 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-02-06 15:13 | 2022-02-07 12:48 | 35 | 021:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y DESCARGAS ELECTRICAS | A22020600131 | New_Event | Bad Weather | Include | Include | Weather | 1295 | 2022-02-06 | 45325 | keep | 0 | Feb | 2022 | 0.030871 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-02-06 15:15 | 2022-02-06 15:58 | 60 | 000:43 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYOS | R22020600107 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 43 | 2022-02-06 | 2580 | keep | 0 | Feb | 2022 | 0.0017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-06 15:20 | 2022-02-07 10:48 | 120 | 019:28 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE E LINEA | B22020600606 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1168 | 2022-02-06 | 140160 | keep | 0 | Feb | 2022 | 0.095462 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-02-06 15:27 | 2022-02-07 18:13 | 42 | 026:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE Y LEVANTO PRIMARIA | C22020600201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1606 | 2022-02-06 | 67452 | keep | 0 | Feb | 2022 | 0.045941 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BARRANQUITAS | 2022-02-06 15:31 | 2022-02-07 11:57 | 100 | 020:26 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C22020600205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1226 | 2022-02-06 | 122600 | keep | 0 | Feb | 2022 | 0.083502 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 15:35 | 2022-02-06 15:38 | 824 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 2472 | keep | 0 | Feb | 2022 | 0.0016837 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-02-06 15:35 | 2022-02-06 15:38 | 200 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-06 15:35 | 2022-02-06 15:38 | 2720 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 8160 | keep | 0 | Feb | 2022 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-02-06 15:36 | 2022-02-06 16:30 | 60 | 000:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO PARTIDO Y SE REALIZO DESGANCHE | S22020600539 | New_Event | Wire Down | Include | Include | Equipment | 54 | 2022-02-06 | 3240 | keep | 0 | Feb | 2022 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-06 15:38 | 2022-02-06 15:41 | 30 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER | S22020600292 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 90 | keep | 0 | Feb | 2022 | 6.1299e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-06 15:40 | 2022-02-07 13:14 | 100 | 021:34 | P | DESGANCHE | 2 X 100 Y 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22020600690 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1294 | 2022-02-06 | 129400 | keep | 0 | Feb | 2022 | 0.088134 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-06 15:41 | 2022-02-06 15:44 | 824 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 2472 | keep | 0 | Feb | 2022 | 0.0016837 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-02-06 15:41 | 2022-02-06 15:44 | 200 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-06 15:41 | 2022-02-06 15:44 | 2720 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 8160 | keep | 0 | Feb | 2022 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2022-02-06 15:44 | 2022-02-06 16:15 | 30 | 000:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER | S22020600292 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 31 | 2022-02-06 | 930 | keep | 0 | Feb | 2022 | 0.00063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-02-06 15:52 | 2022-02-07 14:10 | 10 | 022:18 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25KVA X 25KVA Y 2 X 10 EN XMR | C22020600220 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1338 | 2022-02-06 | 13380 | keep | 0 | Feb | 2022 | 0.0091131 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-06 15:53 | 2022-02-06 18:40 | 40 | 002:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L AVE CRUZO LINEAS | P22020600205 | New_Event |  |  | Include | Wildlife | 167 | 2022-02-06 | 6680 | keep | 0 | Feb | 2022 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-06 15:55 | 2022-02-06 20:15 | 70 | 004:20 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020600136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-02-06 | 18200 | keep | 0 | Feb | 2022 | 0.012396 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-02-06 16:09 | 2022-02-07 12:16 | 50 | 020:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A22020600139 | New_Event | Wire Down | Include | Include | Equipment | 1207 | 2022-02-06 | 60350 | keep | 0 | Feb | 2022 | 0.041104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-06 16:09 | 2022-02-07 14:19 | 120 | 022:10 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B22020600709 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1330 | 2022-02-06 | 159600 | keep | 0 | Feb | 2022 | 0.1087 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-02-06 16:12 | 2022-02-06 19:42 | 75 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L MAL TIEMPO | P22020600223 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2022-02-06 | 15750 | keep | 0 | Feb | 2022 | 0.010727 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-06 16:15 | 2022-02-06 16:20 | 824 | 000:05 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 5 | 2022-02-06 | 4120 | keep | 0 | Feb | 2022 | 0.0028061 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-02-06 16:15 | 2022-02-06 16:20 | 200 | 000:05 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 5 | 2022-02-06 | 1000 | keep | 0 | Feb | 2022 | 0.0006811 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-06 16:15 | 2022-02-06 16:20 | 2720 | 000:05 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | Additional_clients | Bad Weather | Include | Include | Weather | 5 | 2022-02-06 | 13600 | keep | 0 | Feb | 2022 | 0.0092629 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 16:20 | 2022-02-06 16:21 | 30 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER | S22020600292 | Partial_restoration | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 30 | keep | 0 | Feb | 2022 | 2.0433e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 16:21 | 2022-02-06 16:29 | 824 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | Partial_restoration | Bad Weather | Include | Include | Weather | 8 | 2022-02-06 | 6592 | keep | 0 | Feb | 2022 | 0.0044898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 16:21 | 2022-02-06 16:29 | 200 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | Partial_restoration | Bad Weather | Include | Include | Weather | 8 | 2022-02-06 | 1600 | keep | 0 | Feb | 2022 | 0.0010898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 16:21 | 2022-02-06 16:29 | 2720 | 000:08 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1119-04 LLEVANDO 95% 1115-05 Y 120 AMP 1119-02 | S22020600000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 8 | 2022-02-06 | 21760 | keep | 0 | Feb | 2022 | 0.014821 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2022-02-06 16:21 | 2022-02-06 17:37 | 273 | 001:16 | P | DESGANCHE | SE RETIRO BAMBUA SOBRE EL ALIMENTADOR 100% EN SERVICIO | B22020600183 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-02-06 | 20748 | keep | 0 | Feb | 2022 | 0.014131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-02-06 16:22 | 2022-02-06 20:00 | 30 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A22020600143 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2022-02-06 | 6540 | keep | 0 | Feb | 2022 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-06 16:26 | 2022-02-06 16:27 | 6244 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22020600567 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 6244 | keep | 0 | Feb | 2022 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
BAYAMON | 2022-02-06 16:29 | 2022-02-06 19:28 | 5 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN SU NO ID | S22020600571 | Partial_restoration | Bad Weather | Include | Include | Weather | 179 | 2022-02-06 | 895 | keep | 0 | Feb | 2022 | 0.00060958 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 16:29 | 2022-02-06 17:44 | 30 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER | S22020600292 | Partial_restoration | Bad Weather | Include | Include | Weather | 75 | 2022-02-06 | 2250 | keep | 0 | Feb | 2022 | 0.0015325 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 16:30 | 2022-02-06 16:31 | 225 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR MACHETES Y SECCIONALIZAR CONDUCTOR PRIMARIO LLEVA CARGA 1303-04 | S22020600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-06 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-02-06 16:30 | 2022-02-06 16:31 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR MACHETES Y SECCIONALIZAR CONDUCTOR PRIMARIO LLEVA CARGA 1303-04 | S22020600000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-02-06 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 16:31 | 2022-02-06 20:23 | 60 | 003:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO PARTIDO Y SE REALIZO DESGANCHE | S22020600539 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 232 | 2022-02-06 | 13920 | keep | 0 | Feb | 2022 | 0.0094808 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-06 16:34 | 2022-02-06 16:35 | 1746 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO Y SE CERRO POR CONTROL | B22020600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 1746 | keep | 0 | Feb | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2022-02-06 16:36 | 2022-02-06 16:37 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1401-08 LLEVANDO CARGA 1346-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-06 16:36 | 2022-02-06 16:37 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1401-08 LLEVANDO CARGA 1346-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-02-06 16:40 | 2022-02-06 16:42 | 700 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR 1620-05 LLEVANDO PARTE 1206-03 | S22020600583 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 0.00047677 | Momentary | FALSE | FALSE | Not_TMED_Event | 700
SAN JUAN | 2022-02-06 16:40 | 2022-02-06 16:42 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR 1620-05 LLEVANDO PARTE 1206-03 | S22020600583 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 3230 | keep | 0 | Feb | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
MAYAGÃœEZ | 2022-02-06 16:41 | 2022-02-06 16:42 | 2073 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22020600080 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 2073 | keep | 0 | Feb | 2022 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2022-02-06 16:42 | 2022-02-06 20:25 | 80 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020600084 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 223 | 2022-02-06 | 17840 | keep | 0 | Feb | 2022 | 0.012151 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-06 16:46 | 2022-02-06 16:47 | 290 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1526-03 LLEVANDO PARTE DE LA CARGA 1530-06 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 290 | keep | 0 | Feb | 2022 | 0.00019752 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2022-02-06 16:46 | 2022-02-06 16:47 | 200 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1526-03 LLEVANDO PARTE DE LA CARGA 1530-06 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-02-06 16:54 | 2022-02-06 16:57 | 1500 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04, 1336-09 Y PARTE 1204-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-06 | 4500 | keep | 0 | Feb | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-02-06 16:54 | 2022-02-06 16:57 | 2000 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04, 1336-09 Y PARTE 1204-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-06 | 6000 | keep | 0 | Feb | 2022 | 0.0040866 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-02-06 16:54 | 2022-02-06 16:57 | 5290 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04, 1336-09 Y PARTE 1204-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-06 | 15870 | keep | 0 | Feb | 2022 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-02-06 16:54 | 2022-02-06 16:57 | 207 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04, 1336-09 Y PARTE 1204-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-06 | 621 | keep | 0 | Feb | 2022 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-02-06 17:01 | 2022-02-06 21:01 | 22 | 004:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO CABRE SOTERRADO DEL T-14 AL T-15 | R22020600102 | Partial_restoration |  |  | Include | Wildlife | 240 | 2022-02-06 | 5280 | keep | 0 | Feb | 2022 | 0.0035962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-06 17:16 | 2022-02-06 22:04 | 40 | 004:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22020600115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-02-06 | 11520 | keep | 0 | Feb | 2022 | 0.0078462 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-06 17:16 | 2022-02-06 20:17 | 110 | 003:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L REMPLAZO AISLADOR Y FIJO LINEA | C22020600239 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 181 | 2022-02-06 | 19910 | keep | 0 | Feb | 2022 | 0.013561 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-02-06 17:21 | 2022-02-06 17:22 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020600241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 4634 | keep | 0 | Feb | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2022-02-06 17:21 | 2022-02-07 13:30 | 10 | 020:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR LA MISMA CAPACIDAD | M22020600100 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1209 | 2022-02-06 | 12090 | keep | 0 | Feb | 2022 | 0.0082344 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-06 17:22 | 2022-02-06 21:19 | 220 | 003:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SECCIONALIZO CONDUCTOR ROTO | C22020600242 | New_Event | Wire Down | Include | Include | Equipment | 237 | 2022-02-06 | 52140 | keep | 0 | Feb | 2022 | 0.035512 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
ARECIBO | 2022-02-06 17:31 | 2022-02-07 10:40 | 3 | 017:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A22020600148 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1029 | 2022-02-06 | 3087 | keep | 0 | Feb | 2022 | 0.0021025 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-02-06 17:41 | 2022-02-06 19:44 | 60 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020600105 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2022-02-06 | 7380 | keep | 0 | Feb | 2022 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-06 17:43 | 2022-02-06 17:44 | 770 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | S22020600655 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-06 | 770 | keep | 0 | Feb | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-02-06 17:44 | 2022-02-06 23:13 | 257 | 005:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO SE ENCONTRO PUENTE PRIMARIO ABIERTO SALIDA TRONCAL | S22020600668 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 329 | 2022-02-06 | 84553 | keep | 0 | Feb | 2022 | 0.057589 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
BAYAMON | 2022-02-06 17:55 | 2022-02-06 17:56 | 996 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1116-03 LLEVANDO CARGA 1116-05 1116 04 Y 1117-08 DISPARO FUE AL HACER PRUEBA DE MH 18 HACIA PARALELAS | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 996 | keep | 0 | Feb | 2022 | 0.00067837 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
BAYAMON | 2022-02-06 17:55 | 2022-02-06 17:56 | 169 | 000:01 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR 1116-03 LLEVANDO CARGA 1116-05 1116 04 Y 1117-08 DISPARO FUE AL HACER PRUEBA DE MH 18 HACIA PARALELAS | S22020600000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-06 | 169 | keep | 0 | Feb | 2022 | 0.00011511 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-02-06 17:55 | 2022-02-06 17:56 | 5 | 000:01 | T | ERROR HUMANO | DISPARO DE INTERRUPTOR 1116-03 LLEVANDO CARGA 1116-05 1116 04 Y 1117-08 DISPARO FUE AL HACER PRUEBA DE MH 18 HACIA PARALELAS | S22020600000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-06 | 5 | keep | 0 | Feb | 2022 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-06 17:55 | 2022-02-06 17:56 | 466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1116-03 LLEVANDO CARGA 1116-05 1116 04 Y 1117-08 DISPARO FUE AL HACER PRUEBA DE MH 18 HACIA PARALELAS | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 466 | keep | 0 | Feb | 2022 | 0.00031739 | 0.00031739 | Momentary | FALSE | FALSE | Not_TMED_Event | 466
CANOVANAS | 2022-02-06 17:55 | 2022-02-06 19:30 | 60 | 001:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R22020600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-02-06 | 5700 | keep | 0 | Feb | 2022 | 0.0038822 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-06 17:56 | 2022-02-06 20:02 | 30 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN PARALELA Y 1 X 80 EN RISER | S22020600415 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-02-06 | 3780 | keep | 0 | Feb | 2022 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-06 18:00 | 2022-02-07 09:40 | 8 | 015:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22020600151 | New_Event | Bad Weather | Include | Include | Weather | 940 | 2022-02-06 | 7520 | keep | 0 | Feb | 2022 | 0.0051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-06 18:29 | 2022-02-06 18:33 | 290 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLUVIA FUERTE | S22020600689 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2022-02-06 | 1160 | keep | 0 | Feb | 2022 | 0.00079007 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2022-02-06 18:30 | 2022-02-07 14:13 | 114 | 019:43 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | B22020600783 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1183 | 2022-02-06 | 134862 | keep | 0 | Feb | 2022 | 0.091854 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
BAYAMON | 2022-02-06 18:34 | 2022-02-06 19:36 | 290 | 001:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLUVIA FUERTE SE CERRO CUANDO PARO LA LLUVIA | S22020600689 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 62 | 2022-02-06 | 17980 | keep | 0 | Feb | 2022 | 0.012246 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2022-02-06 18:34 | 2022-02-06 23:43 | 215 | 005:09 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M22020600116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2022-02-06 | 66435 | keep | 0 | Feb | 2022 | 0.045249 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
AGUADILLA | 2022-02-06 18:34 | 2022-02-07 09:20 | 80 | 014:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 100 EN CORTES LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020600115 | New_Event | Bad Weather | Include | Include | Weather | 886 | 2022-02-06 | 70880 | keep | 0 | Feb | 2022 | 0.048276 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-06 18:48 | 2022-02-07 17:25 | 12 | 022:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | B22020600800 | New_Event | Wire Down | Include | Include | Equipment | 1357 | 2022-02-06 | 16284 | keep | 0 | Feb | 2022 | 0.011091 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-06 18:49 | 2022-02-06 21:37 | 40 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN AEREO PROVISIONAL MAL TIEMPO | R22020600135 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2022-02-06 | 6720 | keep | 0 | Feb | 2022 | 0.004577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-06 18:55 | 2022-02-06 22:44 | 100 | 003:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 80 EN CORTE DE LINEA POR FUERTE LLUVIA | M22020600127 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2022-02-06 | 22900 | keep | 0 | Feb | 2022 | 0.015597 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-06 19:01 | 2022-02-06 21:12 | 7 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN XMR MAL TIEMPO | C22020600263 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2022-02-06 | 917 | keep | 0 | Feb | 2022 | 0.00062456 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-02-06 19:02 | 2022-02-07 20:40 | 40 | 025:38 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO PUENTES | C22020600130 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1538 | 2022-02-06 | 61520 | keep | 0 | Feb | 2022 | 0.041901 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-06 19:06 | 2022-02-06 19:10 | 2178 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO NO CAUSA | C22020600266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-06 | 8712 | keep | 0 | Feb | 2022 | 0.0059337 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
SAN JUAN | 2022-02-06 19:16 | 2022-02-07 10:04 | 30 | 014:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22020600717 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 888 | 2022-02-06 | 26640 | keep | 0 | Feb | 2022 | 0.018144 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-06 19:17 | 2022-02-07 13:08 | 200 | 017:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22020600138 | New_Event | Wire Down | Include | Include | Equipment | 1071 | 2022-02-06 | 214200 | keep | 0 | Feb | 2022 | 0.14589 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-02-06 19:19 | 2022-02-06 19:21 | 87 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 20% DE LA CARGA POR EL 1658-14 CERRADO POR CONTROL | R22020600139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 174 | keep | 0 | Feb | 2022 | 0.00011851 | 5.9255e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-02-06 19:19 | 2022-02-06 19:21 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA EL 20% DEL 1657-02 CERRADO POR CONTROL | R22020600139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 2 | keep | 0 | Feb | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-02-06 19:19 | 2022-02-06 22:30 | 100 | 003:11 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR AVERIA DE ARBOL SOBRE LINEA | M22020600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-02-06 | 19100 | keep | 0 | Feb | 2022 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-06 19:44 | 2022-02-07 10:55 | 30 | 015:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020600151 | New_Event | Bad Weather | Include | Include | Weather | 911 | 2022-02-06 | 27330 | keep | 0 | Feb | 2022 | 0.018614 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-06 19:46 | 2022-02-07 12:28 | 250 | 016:42 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020600152 | New_Event | Bad Weather | Include | Include | Weather | 1002 | 2022-02-06 | 250500 | keep | 0 | Feb | 2022 | 0.17061 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
VEGA BAJA | 2022-02-06 19:46 | 2022-02-06 21:23 | 12 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22020600697 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2022-02-06 | 1164 | keep | 0 | Feb | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-06 19:56 | 2022-02-06 19:57 | 1017 | 000:01 | T | DESGANCHE | RECIERRE | C22020600341 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-06 | 1017 | keep | 0 | Feb | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2022-02-06 19:57 | 2022-02-07 00:22 | 1017 | 004:25 | T | DESGANCHE | SE ABRIO MACHETES EN CARR 171 KM 1.1 BO. SUD, CIDRA. | C22020600341 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 265 | 2022-02-06 | 269505 | keep | 0 | Feb | 2022 | 0.18356 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-02-06 19:58 | 2022-02-06 19:59 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 4381 | keep | 0 | Feb | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2022-02-06 19:59 | 2022-02-06 20:00 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020600364 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 2203 | keep | 0 | Feb | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-02-06 20:03 | 2022-02-07 12:52 | 120 | 016:49 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B22020600825 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1009 | 2022-02-06 | 121080 | keep | 0 | Feb | 2022 | 0.082467 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-02-06 20:10 | 2022-02-07 10:40 | 1 | 014:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | R22020600150 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 870 | 2022-02-06 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-06 20:12 | 2022-02-07 09:48 | 60 | 013:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020600749 | New_Event | Vegetation Contact | Include | Include | Vegetation | 816 | 2022-02-06 | 48960 | keep | 0 | Feb | 2022 | 0.033346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-06 20:12 | 2022-02-06 20:13 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 990 | keep | 0 | Feb | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2022-02-06 20:16 | 2022-02-06 21:43 | 100 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN SU2 MAL TIEMPO | S22020600752 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-02-06 | 8700 | keep | 0 | Feb | 2022 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-06 20:19 | 2022-02-07 14:56 | 25 | 018:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25KVA Y 75KVA X 50KVA | C22020600386 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1117 | 2022-02-06 | 27925 | keep | 0 | Feb | 2022 | 0.01902 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-02-06 20:21 | 2022-02-07 00:27 | 90 | 004:06 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN SU-22A, SECCIONALIZARON TRAMO PROBANDO MALO DEL SU-18 @ T-116 | R22020600156 | New_Event | UG Cable Fault | Include | Include | Equipment | 246 | 2022-02-06 | 22140 | keep | 0 | Feb | 2022 | 0.015079 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-02-06 20:25 | 2022-02-06 21:32 | 889 | 001:07 | T | NO SE REPORTO CAUSA | SE RELEVO CARGA PARA REMPLAZAR FUSIBLE FUNDIDO EN LA ALTA | C22020600341 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-02-06 | 59563 | keep | 0 | Feb | 2022 | 0.040568 | 0.00060549 | Sustained | FALSE | FALSE | Not_TMED_Event | 889
CAGUAS | 2022-02-06 20:25 | 2022-02-06 21:32 | 3463 | 001:07 | T | NO SE REPORTO CAUSA | SE RELEVO CARGA PARA REEMPLAZAR FUSIBLE FUNDIDO EN LA ALTA | C22020600394 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-02-06 | 232021 | keep | 0 | Feb | 2022 | 0.15803 | 0.0023586 | Sustained | FALSE | FALSE | Not_TMED_Event | 3463
CAGUAS | 2022-02-06 20:25 | 2022-02-06 23:33 | 700 | 003:08 | P | ESTRUCTURA AVERIADA | SECCIONALIZARON POSTE ROTO Y SE NORMALIZO PARTE DE LA CARGA TRANSFERIDA DEL 3602-01 X 3406-02. | C22020600394 | New_Event | Defective Pole | Include | Include | Equipment | 188 | 2022-02-06 | 131600 | keep | 0 | Feb | 2022 | 0.089632 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
GUAYAMA | 2022-02-06 20:26 | 2022-02-06 22:02 | 45 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P22020600292 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2022-02-06 | 4320 | keep | 0 | Feb | 2022 | 0.0029423 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-02-06 20:39 | 2022-02-07 12:38 | 35 | 015:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22020600847 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 959 | 2022-02-06 | 33565 | keep | 0 | Feb | 2022 | 0.022861 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-02-06 20:40 | 2022-02-06 20:41 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020600160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 1097 | keep | 0 | Feb | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
SAN JUAN | 2022-02-06 20:49 | 2022-02-06 20:50 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1401-08 LLEVANDO CARGA 1346-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-06 20:49 | 2022-02-06 20:50 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1401-08 LLEVANDO CARGA 1346-05 | S22020600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-06 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2022-02-06 21:02 | 2022-02-06 22:11 | 80 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22020600423 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-02-06 | 5520 | keep | 0 | Feb | 2022 | 0.0037596 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-06 21:06 | 2022-02-07 13:27 | 130 | 016:21 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B22020600855 | New_Event | Vegetation Contact | Include | Include | Vegetation | 981 | 2022-02-06 | 127530 | keep | 0 | Feb | 2022 | 0.08686 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-02-06 21:06 | 2022-02-07 15:51 | 40 | 018:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU | B22020600855 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1125 | 2022-02-06 | 45000 | keep | 0 | Feb | 2022 | 0.030649 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-06 21:06 | 2022-02-07 03:01 | 40 | 005:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22020600159 | New_Event | Bad Weather | Include | Include | Weather | 355 | 2022-02-06 | 14200 | keep | 0 | Feb | 2022 | 0.0096716 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-06 21:18 | 2022-02-07 09:31 | 10 | 012:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S22020600772 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 733 | 2022-02-06 | 7330 | keep | 0 | Feb | 2022 | 0.0049924 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-06 21:23 | 2022-02-07 10:33 | 30 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22020600436 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2022-02-06 | 23700 | keep | 0 | Feb | 2022 | 0.016142 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-06 21:32 | 2022-02-07 08:41 | 10 | 011:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020600170 | New_Event | Bad Weather | Include | Include | Weather | 669 | 2022-02-06 | 6690 | keep | 0 | Feb | 2022 | 0.0045565 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-06 21:33 | 2022-02-06 21:35 | 1287 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22020600172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-06 | 2574 | keep | 0 | Feb | 2022 | 0.0017531 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2022-02-06 21:36 | 2022-02-07 12:15 | 2 | 014:39 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020600174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 879 | 2022-02-06 | 1758 | keep | 0 | Feb | 2022 | 0.0011974 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-06 21:38 | 2022-02-06 21:40 | 996 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO LLEVA CARGA 1116-5 Y 1116-4 MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 1992 | keep | 0 | Feb | 2022 | 0.0013567 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
BAYAMON | 2022-02-06 21:38 | 2022-02-06 21:40 | 169 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SU CARGA POR 1116-3 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 338 | keep | 0 | Feb | 2022 | 0.00023021 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-02-06 21:38 | 2022-02-06 21:40 | 5 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SU CARGA POR 1116-3 | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-02-06 | 10 | keep | 0 | Feb | 2022 | 6.811e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-06 21:40 | 2022-02-06 22:38 | 12 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR NEUTRAL Y CONECTORES SECUNDARIOS | B22020500224 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-06 | 696 | keep | 0 | Feb | 2022 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-06 21:58 | 2022-02-06 22:01 | 50 | 000:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER A SU-7 MAL TIEMPO | S22020600782 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2022-02-06 | 150 | keep | 0 | Feb | 2022 | 0.00010216 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-02-06 22:01 | 2022-02-07 17:34 | 60 | 019:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE INSTALO CORTE DE LINEA EN EL PUENTE ABIERTO | A22060700162 | New_Event | Wire Down | Include | Include | Equipment | 1173 | 2022-02-06 | 70380 | keep | 0 | Feb | 2022 | 0.047935 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-06 22:12 | 2022-02-07 19:29 | 1 | 021:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTARON CONDUCTORES PRIMARIOS Y SE CERRO PUENTES | C22020600454 | New_Event | Wire Down | Include | Include | Equipment | 1277 | 2022-02-06 | 1277 | keep | 0 | Feb | 2022 | 0.00086976 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-02-06 22:30 | 2022-02-07 | 45 | 001:30 | P | DESGANCHE | SE REALIZO DESGANCHE DE ARBOL Y SE CERRO PUENTE | M22020600140 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-02-06 | 4050 | keep | 0 | Feb | 2022 | 0.0027584 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-06 23:05 | 2022-02-06 23:06 | 844 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO MAL TIEMPO | S22020600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-06 | 844 | keep | 0 | Feb | 2022 | 0.00057484 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
CAGUAS | 2022-02-06 23:12 | 2022-02-07 09:15 | 289 | 010:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22020600386 | New_Event | Cutout Failure | Include | Include | Equipment | 603 | 2022-02-06 | 174267 | keep | 0 | Feb | 2022 | 0.11869 | 0.00019684 | Sustained | FALSE | FALSE | Not_TMED_Event | 289
SAN JUAN | 2022-02-06 23:14 | 2022-02-07 00:27 | 770 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA REPARAR PUENTE PRIMARIO SALIDA TRONCAL | S22020600798 | Additional_clients | Wire Down | Include | Include | Equipment | 73 | 2022-02-06 | 56210 | keep | 0 | Feb | 2022 | 0.038284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-06 23:31 | 2022-02-07 02:40 | 1746 | 003:09 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE ABRIO DE SU-5 A SU-6 FTE. REPETIDORA WKAQ Y SE CERRO INTERRUPTOR 50% EN SERVICIO SE CONTINUARA EN LA MANANA TRAMO INUNDADO | B22020600877 | New_Event | Bad Weather | Include | Include | Weather | 189 | 2022-02-06 | 329994 | keep | 0 | Feb | 2022 | 0.22476 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
CAGUAS | 2022-02-06 23:33 | 2022-02-07 23:31 | 200 | 023:58 | P | ESTRUCTURA AVERIADA | REEMPLAZARON POSTE ROTO, SE LEVANTO LINEA Y CERRARON MACHETES | C22020700231 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1438 | 2022-02-06 | 287600 | keep | 0 | Feb | 2022 | 0.19588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-06 23:41 | 2022-02-07 11:43 | 548 | 012:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN LA SALIDA DEL CONVERTIDOR MAL TIEMPO | C22020600470 | New_Event | Bad Weather | Include | Include | Weather | 722 | 2022-02-06 | 395656 | keep | 0 | Feb | 2022 | 0.26948 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-02-06 23:49 | 2022-02-07 17:17 | 70 | 017:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22020600471 | New_Event | Bad Weather | Include | Include | Weather | 1048 | 2022-02-06 | 73360 | keep | 0 | Feb | 2022 | 0.049965 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-02-07 00:16 | 2022-02-07 00:17 | 922 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO SU CARGA POR 1401-8 LLUVIA FUERTE | S22020700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-07 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-07 00:16 | 2022-02-07 00:17 | 135 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO LLEVA 1346-5 LLUVIA FUERTE | S22020700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-07 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2022-02-07 00:22 | 2022-02-07 16:11 | 509 | 015:49 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA REEMPLAZO 2 X 30 EN CORTE DE LINEAS Y CERRARON MACHETES | C22020700267 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 949 | 2022-02-07 | 483041 | keep | 0 | Feb | 2022 | 0.329 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 00:24 | 2022-02-07 11:13 | 25 | 010:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU | S22020700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 649 | 2022-02-07 | 16225 | keep | 0 | Feb | 2022 | 0.011051 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-02-07 00:24 | 2022-02-07 10:18 | 17 | 009:54 | P | LINEA DE TRANSMISION 38KV | 1 X 80 EN CORTE DE LINEA TRAMO DE LINEA 300 SOBRE ALIMENTADOR | P22020700001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 594 | 2022-02-07 | 10098 | keep | 0 | Feb | 2022 | 0.0068777 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-02-07 00:29 | 2022-02-07 18:22 | 300 | 017:53 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ESTABLECIO GOI PARA REPARAR TERMINACIONES SOTERRADAS | S22020600030 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1073 | 2022-02-07 | 321900 | keep | 0 | Feb | 2022 | 0.21924 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-02-07 01:02 | 2022-02-07 09:40 | 150 | 008:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22020700001 | New_Event | Bad Weather | Include | Include | Weather | 518 | 2022-02-07 | 77700 | keep | 0 | Feb | 2022 | 0.052921 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-02-07 01:33 | 2022-02-07 11:23 | 80 | 009:50 | P | DESGANCHE | 1 X 50 Y 1 X 80 EN CORTES DE LINEA SE REALIZO DESGANCHE | M22020700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 590 | 2022-02-07 | 47200 | keep | 0 | Feb | 2022 | 0.032148 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-02-07 02:37 | 2022-02-07 13:23 | 36 | 010:46 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C22020700015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 646 | 2022-02-07 | 23256 | keep | 0 | Feb | 2022 | 0.01584 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-02-07 02:37 | 2022-02-07 11:17 | 25 | 008:40 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO Y SE LEVANTO CONDUCTOR PRIMARIO | C22020700171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 520 | 2022-02-07 | 13000 | keep | 0 | Feb | 2022 | 0.0088542 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-07 02:40 | 2022-02-08 16:47 | 873 | 038:07 | P | MAL TIEMPO/RAYOS/WET ASH | SE REALIZO MANTENIMIENTO A VARIOS SU POR CONTAMINACION A CAUSA DE INUNDACIONES SE CERRO SU-5 @ SU-6 | B22020600877 | Partial_restoration | Bad Weather | Include | Include | Weather | 2287 | 2022-02-07 | 1996551 | keep | 0 | Feb | 2022 | 1.3598 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-07 02:40 | 2022-02-07 02:41 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22020700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-07 | 1097 | keep | 0 | Feb | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
ARECIBO | 2022-02-07 03:21 | 2022-02-07 10:50 | 25 | 007:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22020700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2022-02-07 | 11225 | keep | 0 | Feb | 2022 | 0.0076453 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-02-07 03:30 | 2022-02-07 09:36 | 25 | 006:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22020700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 366 | 2022-02-07 | 9150 | keep | 0 | Feb | 2022 | 0.006232 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-02-07 04:19 | 2022-02-07 09:13 | 25 | 004:54 | P | DESGANCHE | 1 X 20 EN C/L SE REALIZO DESGANCHE | R22020700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-02-07 | 7350 | keep | 0 | Feb | 2022 | 0.0050061 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-07 05:05 | 2022-02-07 12:07 | 100 | 007:02 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2022-02-07 | 42200 | keep | 0 | Feb | 2022 | 0.028742 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-07 05:12 | 2022-02-07 05:17 | 1712 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | P22020700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-07 | 8560 | keep | 0 | Feb | 2022 | 0.0058302 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-02-07 05:12 | 2022-02-07 05:17 | 7 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | P22020700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-07 | 35 | keep | 0 | Feb | 2022 | 2.3838e-05 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-07 05:16 | 2022-02-07 15:31 | 12 | 010:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTAR CONDUCTOR PRIMARIO | B22020700022 | New_Event | Wire Down | Include | Include | Equipment | 615 | 2022-02-07 | 7380 | keep | 0 | Feb | 2022 | 0.0050265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-07 05:21 | 2022-02-07 11:27 | 40 | 006:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22020700007 | New_Event | Cutout Failure | Include | Include | Equipment | 366 | 2022-02-07 | 14640 | keep | 0 | Feb | 2022 | 0.0099712 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-07 05:38 | 2022-02-07 05:40 | 2190 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22020700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-07 | 4380 | keep | 0 | Feb | 2022 | 0.0029832 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
CAGUAS | 2022-02-07 06:03 | 2022-02-07 13:25 | 200 | 007:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C22020700026 | New_Event | Wire Down | Include | Include | Equipment | 442 | 2022-02-07 | 88400 | keep | 0 | Feb | 2022 | 0.060209 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-02-07 06:07 | 2022-02-07 06:08 | 4641 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE DE INTERRUPTOR | M22020700000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-02-07 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
BAYAMON | 2022-02-07 06:08 | 2022-02-07 09:14 | 100 | 003:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETES | S22020700015 | New_Event | Wire Down | Include | Include | Equipment | 186 | 2022-02-07 | 18600 | keep | 0 | Feb | 2022 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-07 06:08 | 2022-02-07 13:30 | 400 | 007:22 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN CORTE DE LINEA SE REPARO CABLE DE 15 KV EN MALAS CONDICIONES | M22020700011 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 442 | 2022-02-07 | 176800 | keep | 0 | Feb | 2022 | 0.12042 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-02-07 06:10 | 2022-02-07 10:51 | 30 | 004:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA Y 1 X 50 EN PROVISIONAL AEREO LLUVIA FUERTE | S22020700017 | New_Event | Bad Weather | Include | Include | Weather | 281 | 2022-02-07 | 8430 | keep | 0 | Feb | 2022 | 0.0057416 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-07 06:22 | 2022-02-07 11:28 | 50 | 005:06 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN SU-18 SE REPARO TERMINACION AVERIADA | R22020700022 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 306 | 2022-02-07 | 15300 | keep | 0 | Feb | 2022 | 0.010421 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-07 06:31 | 2022-02-07 15:29 | 50 | 008:58 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER 1 X 20 EN TRANSFORMADOR Y 2 X 50 EN CORTE DE LINEA | S22002070002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 538 | 2022-02-07 | 26900 | keep | 0 | Feb | 2022 | 0.018321 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-07 06:31 | 2022-02-07 10:40 | 50 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22020700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-02-07 | 12450 | keep | 0 | Feb | 2022 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-07 06:48 | 2022-02-07 09:37 | 71 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020700015 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2022-02-07 | 11999 | keep | 0 | Feb | 2022 | 0.0081725 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
SAN JUAN | 2022-02-07 06:52 | 2022-02-07 11:38 | 10 | 004:46 | P | NO SE REPORTO CAUSA | 2 X 25 DE RISER A TRANSCLOSURE | S22020700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2022-02-07 | 2860 | keep | 0 | Feb | 2022 | 0.0019479 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 07:07 | 2022-02-07 08:14 | 3114 | 001:07 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO INTERRUPTOR POR CONTROL 40% DE SU CARGA TRANSFERIDA POR EL 1718-03 | B22020700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-02-07 | 208638 | keep | 0 | Feb | 2022 | 0.1421 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
CANOVANAS | 2022-02-07 07:10 | 2022-02-07 10:15 | 25 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22020700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-02-07 | 4625 | keep | 0 | Feb | 2022 | 0.0031501 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-07 07:14 | 2022-02-07 10:51 | 10 | 003:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | S22020700031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 217 | 2022-02-07 | 2170 | keep | 0 | Feb | 2022 | 0.001478 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 07:14 | 2022-02-07 07:15 | 878 | 000:01 | T | DESGANCHE | RECERRO | B22020700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-07 | 878 | keep | 0 | Feb | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2022-02-07 07:15 | 2022-02-07 12:08 | 195 | 004:53 | P | DESGANCHE | 3 X 65 EN CIRTE DE LINEA | B22020700090 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-02-07 | 57135 | keep | 0 | Feb | 2022 | 0.038914 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
BARRANQUITAS | 2022-02-07 07:15 | 2022-02-07 14:51 | 7 | 007:36 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | C22020700053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 456 | 2022-02-07 | 3192 | keep | 0 | Feb | 2022 | 0.0021741 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-02-07 07:28 | 2022-02-07 10:34 | 2842 | 003:06 | T | DESGANCHE | DISPARO INTERRUPTOR SE SECCIONALIZO ARBOL SOBRE LINEA Y POSTE PARTIDO | C22020700062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-02-07 | 528612 | keep | 0 | Feb | 2022 | 0.36004 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
MAYAGÃœEZ | 2022-02-07 07:32 | 2022-02-07 08:51 | 60 | 001:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020700020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-02-07 | 4740 | keep | 0 | Feb | 2022 | 0.0032284 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-07 07:34 | 2022-02-07 10:06 | 10 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 100 EN SU 5 | S22020700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-02-07 | 1520 | keep | 0 | Feb | 2022 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 07:36 | 2022-02-07 20:13 | 3 | 012:37 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO BASE DE FUSIBLE SMU 20 EN SU 27 | S22020700043 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 757 | 2022-02-07 | 2271 | keep | 0 | Feb | 2022 | 0.0015468 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-02-07 07:38 | 2022-02-07 09:11 | 40 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22020700086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-02-07 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-07 07:45 | 2022-02-07 13:13 | 5 | 005:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 40 EN SUBESTACION CLIENTE | S22020700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 328 | 2022-02-07 | 1640 | keep | 0 | Feb | 2022 | 0.001117 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-02-07 07:56 | 2022-02-08 10:53 | 15 | 026:57 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR SE REEMPLAZO XMR AVERIADO 50KVA X 50KVA | R22020700113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1617 | 2022-02-07 | 24255 | keep | 0 | Feb | 2022 | 0.01652 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 08:08 | 2022-02-07 11:54 | 30 | 003:46 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | S22020700056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-02-07 | 6780 | keep | 0 | Feb | 2022 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-07 08:23 | 2022-02-07 18:44 | 25 | 010:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22020700134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 621 | 2022-02-07 | 15525 | keep | 0 | Feb | 2022 | 0.010574 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-07 08:24 | 2022-02-07 18:10 | 50 | 009:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22020700136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 586 | 2022-02-07 | 29300 | keep | 0 | Feb | 2022 | 0.019956 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-07 08:25 | 2022-02-07 10:08 | 25 | 001:43 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22020700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-02-07 | 2575 | keep | 0 | Feb | 2022 | 0.0017538 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-02-07 08:27 | 2022-02-07 10:56 | 30 | 002:29 | P | PARARRAYOS DEFECTUOSO | 3 X 100 EN SU 7 SE REMPLAZARON 2 PARARRAYOS | S22020700072 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 149 | 2022-02-07 | 4470 | keep | 0 | Feb | 2022 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-02-07 08:27 | 2022-02-07 12:17 | 20 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22020700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2022-02-07 | 4600 | keep | 0 | Feb | 2022 | 0.003133 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-07 08:28 | 2022-02-07 11:30 | 50 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22020700073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-02-07 | 9100 | keep | 0 | Feb | 2022 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-07 08:30 | 2022-02-07 12:07 | 5 | 003:37 | P | DESGANCHE | 2 X 30 EN RISER SE REALIZO DESGANCHE | R22020700047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-02-07 | 1085 | keep | 0 | Feb | 2022 | 0.00073899 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-02-07 08:31 | 2022-02-07 13:38 | 1 | 005:07 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | R22020700048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 307 | 2022-02-07 | 307 | keep | 0 | Feb | 2022 | 0.0002091 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-07 08:34 | 2022-02-07 11:28 | 7 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN XMR MAL TIEMPO | C22020700133 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2022-02-07 | 1218 | keep | 0 | Feb | 2022 | 0.00082957 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-02-07 08:41 | 2022-02-07 14:19 | 25 | 005:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2022-02-07 | 8450 | keep | 0 | Feb | 2022 | 0.0057553 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-02-07 08:44 | 2022-02-07 16:04 | 78 | 007:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22020700140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2022-02-07 | 34320 | keep | 0 | Feb | 2022 | 0.023375 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
PONCE | 2022-02-07 08:44 | 2022-02-07 08:45 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-07 | 732 | keep | 0 | Feb | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
BARRANQUITAS | 2022-02-07 08:51 | 2022-02-07 10:13 | 10 | 001:22 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN XMR DESGANCHE | C22020700146 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 82 | 2022-02-07 | 820 | keep | 0 | Feb | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 08:52 | 2022-02-07 16:09 | 30 | 007:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA | S22020700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 437 | 2022-02-07 | 13110 | keep | 0 | Feb | 2022 | 0.0089292 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-07 08:57 | 2022-02-07 13:59 | 70 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR EN AZOTEA VIEJO SAN JUAN | S22020700093 | New_Event | Wire Down | Include | Include | Equipment | 302 | 2022-02-07 | 21140 | keep | 0 | Feb | 2022 | 0.014398 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-02-07 09:01 | 2022-02-07 09:02 | 4035 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22020700027 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-07 | 4035 | keep | 0 | Feb | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-02-07 09:02 | 2022-02-07 12:38 | 48 | 003:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P22020700048 | 1st_after_momentary |  |  | Include | Wildlife | 216 | 2022-02-07 | 10368 | keep | 0 | Feb | 2022 | 0.0070616 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
ARECIBO | 2022-02-07 09:05 | 2022-02-07 10:20 | 15 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22020700022 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-02-07 | 1125 | keep | 0 | Feb | 2022 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 09:07 | 2022-02-07 09:48 | 12 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22020700166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2022-02-07 | 492 | keep | 0 | Feb | 2022 | 0.0003351 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-07 09:07 | 2022-02-07 10:49 | 30 | 001:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B22020700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-02-07 | 3060 | keep | 0 | Feb | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-07 09:09 | 2022-02-07 11:11 | 50 | 002:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020700038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-02-07 | 6100 | keep | 0 | Feb | 2022 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-07 09:10 | 2022-02-07 15:05 | 5 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22020700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2022-02-07 | 1775 | keep | 0 | Feb | 2022 | 0.0012089 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-07 09:13 | 2022-02-07 15:34 | 2190 | 006:21 | T | DESGANCHE | SE REALIZO DESGANCHE MASIVO EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22020700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2022-02-07 | 834390 | keep | 0 | Feb | 2022 | 0.5683 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-02-07 09:14 | 2022-02-07 11:26 | 2 | 002:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO ZAFADO EN TRANSFORMADOR | M22020700047 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2022-02-07 | 264 | keep | 0 | Feb | 2022 | 0.00017981 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-02-07 09:20 | 2022-02-07 09:22 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% 1111-01 | S22020700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-07 | 1000 | keep | 0 | Feb | 2022 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-02-07 09:20 | 2022-02-07 09:22 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% 1111-01 | S22020700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-07 | 5564 | keep | 0 | Feb | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-02-07 09:22 | 2022-02-07 17:39 | 15 | 008:17 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZARON TERMINACIONES EN SU 3 | S22020700102 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 497 | 2022-02-07 | 7455 | keep | 0 | Feb | 2022 | 0.0050776 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-07 09:37 | 2022-02-07 16:30 | 40 | 006:53 | P | NO SE REPORTO CAUSA | 2 X 100 EN SALIDA DE CONVERTIDOR | S22020700114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 413 | 2022-02-07 | 16520 | keep | 0 | Feb | 2022 | 0.011252 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-07 09:38 | 2022-02-07 11:35 | 8 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y DESCARGA ELECTRICAS | A22020700026 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2022-02-07 | 936 | keep | 0 | Feb | 2022 | 0.00063751 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-07 09:45 | 2022-02-07 14:38 | 12 | 004:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | B22020500046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 293 | 2022-02-07 | 3516 | keep | 0 | Feb | 2022 | 0.0023947 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-07 09:46 | 2022-02-07 18:17 | 80 | 008:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22020700196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 511 | 2022-02-07 | 40880 | keep | 0 | Feb | 2022 | 0.027843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-02-07 10:00 | 2022-02-07 10:30 | 20 | 000:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | A22020700031 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-02-07 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-07 10:06 | 2022-02-07 16:29 | 10 | 006:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 20 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE CAJA A TRANSFORMADOR | S22020700131 | New_Event | Wire Down | Include | Include | Equipment | 383 | 2022-02-07 | 3830 | keep | 0 | Feb | 2022 | 0.0026086 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 10:18 | 2022-02-07 17:38 | 10 | 007:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN CORTE DE LINEA SE DESPEGO PUENTE PRIMARIO SOBRE TENSOR | B22020700214 | New_Event | Wire Down | Include | Include | Equipment | 440 | 2022-02-07 | 4400 | keep | 0 | Feb | 2022 | 0.0029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-07 10:23 | 2022-02-07 13:40 | 10 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020700073 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2022-02-07 | 1970 | keep | 0 | Feb | 2022 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-07 10:34 | 2022-02-07 11:16 | 2273 | 000:42 | P | DESGANCHE | SE ABRIO PUENTES PARA SECCIONALIZAR ARBOL SOBRE DE LINEA Y POSTE PARTIDO CERRARON MACHETES 80% EN SERVICIO | C22020700162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2022-02-07 | 95466 | keep | 0 | Feb | 2022 | 0.065021 | 0.0015481 | Sustained | FALSE | FALSE | Not_TMED_Event | 2273
CANOVANAS | 2022-02-07 10:39 | 2022-02-07 12:31 | 15 | 001:52 | P | DESGANCHE | 1 X 25 EN C/L SE REALIZO DESGANCHE | R22020700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-02-07 | 1680 | keep | 0 | Feb | 2022 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 10:41 | 2022-02-07 18:01 | 20 | 007:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22020700142 | New_Event | Cutout Failure | Include | Include | Equipment | 440 | 2022-02-07 | 8800 | keep | 0 | Feb | 2022 | 0.0059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-07 10:44 | 2022-02-07 13:30 | 20 | 002:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B22020700238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-02-07 | 3320 | keep | 0 | Feb | 2022 | 0.0022612 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-07 10:45 | 2022-02-07 15:41 | 75 | 004:56 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B22020600808 | New_Event | Defective Pole | Include | Include | Equipment | 296 | 2022-02-07 | 22200 | keep | 0 | Feb | 2022 | 0.01512 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-02-07 10:48 | 2022-02-07 16:19 | 25 | 005:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-02-07 | 8275 | keep | 0 | Feb | 2022 | 0.0056361 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-07 10:50 | 2022-02-07 12:26 | 30 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 80 DE SU A BOVEDA | S22020700148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-02-07 | 2880 | keep | 0 | Feb | 2022 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-02-07 10:59 | 2022-02-07 11:57 | 20 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R22020700064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-07 | 1160 | keep | 0 | Feb | 2022 | 0.00079007 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-07 11:01 | 2022-02-08 20:38 | 12 | 033:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C22020700230 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2017 | 2022-02-07 | 24204 | keep | 0 | Feb | 2022 | 0.016485 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-07 11:02 | 2022-02-07 11:06 | 418 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR MAL TIEMPO | S22020700157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-07 | 1672 | keep | 0 | Feb | 2022 | 0.0011388 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2022-02-07 11:02 | 2022-02-07 11:06 | 50 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1013-13 LLEVANDO 40 AMP 1014-16 | S22020700157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-07 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-07 11:12 | 2022-02-07 11:13 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR | S22020700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-07 | 271 | keep | 0 | Feb | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CAGUAS | 2022-02-07 11:16 | 2022-02-07 20:56 | 450 | 009:40 | P | DESGANCHE | SE ABRIO PUENTE PARA SECCIONALIZAR POSTE PARTIDO POR ARBOL QUE CAYO SOBRE LAS LINEAS | C22020700162 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 580 | 2022-02-07 | 261000 | keep | 0 | Feb | 2022 | 0.17777 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 11:19 | 2022-02-07 16:03 | 2 | 004:44 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA SE DEJO FUERA TRANSFORMADOR DE AREAS COMUNES DE PARQUES NACIONALES | B22020700279 | New_Event | Service Transformer Failure | Include | Include | Equipment | 284 | 2022-02-07 | 568 | keep | 0 | Feb | 2022 | 0.00038686 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-07 11:20 | 2022-02-07 16:45 | 10 | 005:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSCLOSURE | S22020700169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2022-02-07 | 3250 | keep | 0 | Feb | 2022 | 0.0022136 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-07 11:20 | 2022-02-07 11:48 | 6 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN PEDESTAL | P22020700055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-02-07 | 168 | keep | 0 | Feb | 2022 | 0.00011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-02-07 11:21 | 2022-02-07 16:20 | 50 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22020700281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-02-07 | 14950 | keep | 0 | Feb | 2022 | 0.010182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-07 11:22 | 2022-02-07 11:41 | 50 | 000:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22020700167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-02-07 | 950 | keep | 0 | Feb | 2022 | 0.00064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-07 11:27 | 2022-02-07 14:12 | 12 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA LLUVIAS | B22020700286 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-02-07 | 1980 | keep | 0 | Feb | 2022 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-07 11:28 | 2022-02-07 11:29 | 3046 | 000:01 | T | DESGANCHE | RECIERRE | R22020700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-07 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-02-07 11:29 | 2022-02-07 12:21 | 10 | 000:52 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHO REMPLAZO CAJA QUEMADA Y LEVANTO CONDUCTOR | R22020700094 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-02-07 | 520 | keep | 0 | Feb | 2022 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-07 11:29 | 2022-02-07 12:21 | 15 | 000:52 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION | R22020700091 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 52 | 2022-02-07 | 780 | keep | 0 | Feb | 2022 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-07 11:30 | 2022-02-07 11:49 | 20 | 000:19 | P | NO SE REPORTO CAUSA | 2 X 40 EN SU 6 | S22020700169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-02-07 | 380 | keep | 0 | Feb | 2022 | 0.00025882 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-07 11:30 | 2022-02-07 15:24 | 25 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN SU Y SE LEVANTO NEUTRAL PRIMARIO | B22020700289 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2022-02-07 | 5850 | keep | 0 | Feb | 2022 | 0.0039844 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-02-07 11:40 | 2022-02-07 11:41 | 4154 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22020700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-07 | 4154 | keep | 0 | Feb | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
BAYAMON | 2022-02-07 11:45 | 2022-02-07 16:29 | 200 | 004:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA TRASPATIO EN CORTE DE LINEA | S22020700176 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2022-02-07 | 56800 | keep | 0 | Feb | 2022 | 0.038686 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-02-07 11:47 | 2022-02-07 12:37 | 40 | 000:50 | P | LINEA DE TRANSMISION 38KV | SE ABRIO C/L PARA REPARAR CABLE DE LINEA 300 QUE CAYO SOBRE FEEDER | P22020700057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-02-07 | 2000 | keep | 0 | Feb | 2022 | 0.0013622 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-07 11:49 | 2022-02-07 12:28 | 15 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE BAJARON TAP | R22020700051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-02-07 | 585 | keep | 0 | Feb | 2022 | 0.00039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 11:58 | 2022-02-07 16:12 | 50 | 004:14 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S22020700180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 254 | 2022-02-07 | 12700 | keep | 0 | Feb | 2022 | 0.0086499 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-07 12:00 | 2022-02-07 12:02 | 1681 | 000:02 | T | DESGANCHE | DISPARO INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06. CARGA DE 1303-04 POR 1303-05 | S22020700182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-02-07 | 3362 | keep | 0 | Feb | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-07 12:00 | 2022-02-07 12:02 | 1598 | 000:02 | T | DESGANCHE | DISPARO INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06. CARGA DE 1303-04 POR 1303-05 | S22020700182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-02-07 | 3196 | keep | 0 | Feb | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-02-07 12:03 | 2022-02-07 12:26 | 1681 | 000:23 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 SE CERRO POR SCADA ABRIENDO MACHETES EN CARR 176 CAMINO LOS GUANOS. 1346-06 100% Y 1303-01 90%. | S22020700182 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-02-07 | 38663 | keep | 0 | Feb | 2022 | 0.026333 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-07 12:03 | 2022-02-07 12:26 | 1598 | 000:23 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 SE CERRO POR SCADA ABRIENDO MACHETES EN CARR 176 CAMINO LOS GUANOS. 1346-06 100% Y 1303-01 90%. | S22020700182 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-02-07 | 36754 | keep | 0 | Feb | 2022 | 0.025033 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2022-02-07 12:16 | 2022-02-07 15:16 | 100 | 003:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-02-07 | 18000 | keep | 0 | Feb | 2022 | 0.01226 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-07 12:21 | 2022-02-07 12:24 | 3046 | 0:03 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | R22020700000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-02-07 | 9138 | keep | 0 | Feb | 2022 | 0.0062239 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-07 12:24 | 2022-02-07 17:12 | 10 | 004:48 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHO REMPLAZO CAJA QUEMADA Y LEVANTO CONDUCTOR | R22020700094 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-02-07 | 2880 | keep | 0 | Feb | 2022 | 0.0019616 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-07 12:24 | 2022-02-07 12:34 | 15 | 000:10 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION | R22020700091 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 10 | 2022-02-07 | 150 | keep | 0 | Feb | 2022 | 0.00010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-07 12:26 | 2022-02-07 14:32 | 200 | 002:06 | P | DESGANCHE | SE CERRO MACHETES EN CARRETERA 176 CAMINO LOS GUANOS SE REALIZO DESGANCHE | S22020700182 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-02-07 | 25200 | keep | 0 | Feb | 2022 | 0.017164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-07 12:28 | 2022-02-07 15:10 | 10 | 002:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN XMR SE REPARO SECUNDARIA | P22020700062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 162 | 2022-02-07 | 1620 | keep | 0 | Feb | 2022 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-07 12:30 | 2022-02-07 15:55 | 15 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EVENTO DEL DIA 6 NO HABIA CLIENTES ANTES SIN SERVICIO | P22020600313 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-02-07 | 3075 | keep | 0 | Feb | 2022 | 0.0020944 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-07 12:33 | 2022-02-07 16:38 | 10 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER MAL TIEMPO VIENTOS FUERTES | A22020700042 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2022-02-07 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-07 12:35 | 2022-02-07 15:02 | 50 | 002:27 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22020700063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-02-07 | 7350 | keep | 0 | Feb | 2022 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-07 12:54 | 2022-02-07 15:10 | 8 | 002:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22020700043 | New_Event | Bad Weather | Include | Include | Weather | 136 | 2022-02-07 | 1088 | keep | 0 | Feb | 2022 | 0.00074103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-02-07 12:56 | 2022-02-07 15:00 | 35 | 002:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020700109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-02-07 | 4340 | keep | 0 | Feb | 2022 | 0.002956 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-02-07 13:00 | 2022-02-07 13:20 | 1 | 000:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P22020700075 | New_Event | Bad Weather | Include | Include | Weather | 20 | 2022-02-07 | 20 | keep | 0 | Feb | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-07 13:07 | 2022-02-07 18:44 | 2 | 005:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020700049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2022-02-07 | 674 | keep | 0 | Feb | 2022 | 0.00045906 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-02-07 13:11 | 2022-02-07 16:45 | 40 | 003:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M22020700112 | New_Event | Wire Down | Include | Include | Equipment | 214 | 2022-02-07 | 8560 | keep | 0 | Feb | 2022 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-07 13:22 | 2022-02-07 16:17 | 40 | 002:55 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020700219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-02-07 | 7000 | keep | 0 | Feb | 2022 | 0.0047677 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-07 13:26 | 2022-02-07 19:59 | 30 | 006:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22020700222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2022-02-07 | 11790 | keep | 0 | Feb | 2022 | 0.0080301 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-07 13:59 | 2022-02-07 15:00 | 290 | 001:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA LEVANTAR CONDUCTOR PARTIDO EN AZOTEA VIEJO SAN JUAN | S22020700231 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2022-02-07 | 17690 | keep | 0 | Feb | 2022 | 0.012049 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
SAN JUAN | 2022-02-07 14:17 | 2022-02-07 14:45 | 10 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22020700175 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-02-07 | 280 | keep | 0 | Feb | 2022 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-07 14:21 | 2022-02-07 14:22 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020700088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-07 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
MAYAGÃœEZ | 2022-02-07 14:26 | 2022-02-07 14:27 | 4381 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22020700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-07 | 4381 | keep | 0 | Feb | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-02-07 14:27 | 2022-02-07 16:45 | 30 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020700135 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 138 | 2022-02-07 | 4140 | keep | 0 | Feb | 2022 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-07 14:28 | 2022-02-07 14:29 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M22020700000 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-07 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-02-07 14:29 | 2022-02-07 18:16 | 100 | 003:47 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22020700133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-02-07 | 22700 | keep | 0 | Feb | 2022 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-07 14:35 | 2022-02-07 14:36 | 6197 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR CAJA PRIMARIA AVERIADA | C22020700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-07 | 6197 | keep | 0 | Feb | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2022-02-07 14:36 | 2022-02-07 18:43 | 98 | 004:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA CAJA PRIMARIA AVERIADA | C22020700289 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 247 | 2022-02-07 | 24206 | keep | 0 | Feb | 2022 | 0.016487 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2022-02-07 14:47 | 2022-02-07 18:44 | 1 | 003:57 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN BANCO DE XMR DESGANCHO | R22020700099 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 237 | 2022-02-07 | 237 | keep | 0 | Feb | 2022 | 0.00016142 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-02-07 14:47 | 2022-02-07 17:05 | 70 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22020700059 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2022-02-07 | 9660 | keep | 0 | Feb | 2022 | 0.0065794 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-02-07 14:47 | 2022-02-07 16:37 | 1 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER MAL TIEMPO VIENTOS FUERTES | A22020700060 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2022-02-07 | 110 | keep | 0 | Feb | 2022 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-07 14:53 | 2022-02-08 22:42 | 1 | 031:49 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR Y SE REEMPLAZARON DOS MACHETES AVERIADOS QUE LE SIRVE SOLO A LA PLANTA FILTRACION AAA. AUNQUE SE ABRIO EL INTERRUPTOR A LAS 1719 DEL 2/08/2022 REALMENTE ESTABAN FUERA DESDE LAS 14:53 A LAS 2/07/2022. | B22020700428 | New_Event | Switch Failure | Include | Include | Equipment | 1909 | 2022-02-07 | 1909 | keep | 0 | Feb | 2022 | 0.0013002 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-07 14:57 | 2022-02-07 15:23 | 1 | 000:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22020700249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-02-07 | 26 | keep | 0 | Feb | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-07 15:00 | 2022-02-07 16:15 | 2 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22020700114 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-02-07 | 150 | keep | 0 | Feb | 2022 | 0.00010216 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-07 15:19 | 2022-02-07 18:23 | 200 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22020700441 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-02-07 | 36800 | keep | 0 | Feb | 2022 | 0.025064 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-07 15:21 | 2022-02-07 19:08 | 15 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22020700443 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-02-07 | 3405 | keep | 0 | Feb | 2022 | 0.0023191 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-07 15:22 | 2022-02-07 16:40 | 70 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020700151 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2022-02-07 | 5460 | keep | 0 | Feb | 2022 | 0.0037188 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-02-07 15:22 | 2022-02-07 18:40 | 80 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020700150 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2022-02-07 | 15840 | keep | 0 | Feb | 2022 | 0.010789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-02-07 15:22 | 2022-02-07 17:40 | 40 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A22020700064 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-02-07 | 5520 | keep | 0 | Feb | 2022 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-07 15:23 | 2022-02-07 15:26 | 1200 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE 1206-03 SE CERRO POR SCADA | S22020700265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-07 | 3600 | keep | 0 | Feb | 2022 | 0.0024519 | 0.00081731 | Momentary | FALSE | FALSE | Not_TMED_Event | 1200
SAN JUAN | 2022-02-07 15:23 | 2022-02-07 15:26 | 3718 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO PARTE DE 1206-03 SE CERRO POR SCADA | S22020700265 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-07 | 11154 | keep | 0 | Feb | 2022 | 0.0075969 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-07 15:26 | 2022-02-07 18:44 | 1 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22020700249 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-02-07 | 198 | keep | 0 | Feb | 2022 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-07 15:26 | 2022-02-07 18:05 | 8 | 002:39 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C22020700296 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 159 | 2022-02-07 | 1272 | keep | 0 | Feb | 2022 | 0.00086635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-02-07 15:31 | 2022-02-07 19:50 | 50 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | M22020700154 | New_Event | Wire Down | Include | Include | Equipment | 259 | 2022-02-07 | 12950 | keep | 0 | Feb | 2022 | 0.0088202 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-07 15:37 | 2022-02-07 17:17 | 40 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020700156 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-02-07 | 4000 | keep | 0 | Feb | 2022 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-07 15:40 | 2022-02-07 21:27 | 80 | 005:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE LEVANTO PRIMARIA | B22020600690 | New_Event | Wire Down | Include | Include | Equipment | 347 | 2022-02-07 | 27760 | keep | 0 | Feb | 2022 | 0.018907 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-02-07 15:41 | 2022-02-07 16:00 | 776 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA 38KV EN VEGA BAJA TC DEBIDO A DISPARO LINEA 2200 | B22020700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-07 | 14744 | keep | 0 | Feb | 2022 | 0.010042 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2022-02-07 15:41 | 2022-02-07 16:00 | 2216 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA 38KV EN VEGA BAJA TC DEBIDO A DISPARO LINEA 2200 | B22020700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-07 | 42104 | keep | 0 | Feb | 2022 | 0.028677 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2022-02-07 15:41 | 2022-02-07 16:23 | 4702 | 000:42 | T | LINEA DE TRANSMISION 38KV | OVERHEAD DE LINEA 2200 SOBRE ALIMENTADOR SE SECCIONALIZO Y SE CERRO POR CONTROL 30% EN SERVICIO | B22020700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-02-07 | 197484 | keep | 0 | Feb | 2022 | 0.13451 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2022-02-07 15:41 | 2022-02-07 15:42 | 2704 | 000:01 | T | LINEA DE TRANSMISION 38KV | OVER HEAD LINEA 2200 SE AVERIO | B22020700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-07 | 2704 | keep | 0 | Feb | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2022-02-07 15:42 | 2022-02-07 18:21 | 75 | 002:39 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B22020600808 | Partial_restoration | Defective Pole | Include | Include | Equipment | 159 | 2022-02-07 | 11925 | keep | 0 | Feb | 2022 | 0.0081221 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 15:43 | 2022-02-07 17:19 | 5 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 | B22020700455 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-02-07 | 480 | keep | 0 | Feb | 2022 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-07 15:48 | 2022-02-07 18:04 | 2 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 40 Y 2 X 25 EN CORTES DE LINEA NO CAUSA | R22020700103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-02-07 | 272 | keep | 0 | Feb | 2022 | 0.00018526 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-02-07 15:56 | 2022-02-07 18:00 | 10 | 002:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS | A22020700067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 124 | 2022-02-07 | 1240 | keep | 0 | Feb | 2022 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-07 16:03 | 2022-02-07 19:55 | 10 | 003:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO UNA CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22020700162 | New_Event | Cutout Failure | Include | Include | Equipment | 232 | 2022-02-07 | 2320 | keep | 0 | Feb | 2022 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-07 16:10 | 2022-02-07 16:11 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M22020700000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2022-02-07 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-02-07 16:11 | 2022-02-07 17:01 | 50 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEA CULEBRA CRUZO FASES | M22020700165 | 1st_after_momentary |  |  | Include | Wildlife | 50 | 2022-02-07 | 2500 | keep | 0 | Feb | 2022 | 0.0017027 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-07 16:16 | 2022-02-07 18:40 | 118 | 002:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C22020700303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-02-07 | 16992 | keep | 0 | Feb | 2022 | 0.011573 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
VEGA BAJA | 2022-02-07 16:23 | 2022-02-07 18:06 | 3290 | 001:43 | P | LINEA DE TRANSMISION 38KV | ALIMENTADOR SECCIONALIZADO POR OVERHEAD LINEA 2200 | B22020700000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2022-02-07 | 338870 | keep | 0 | Feb | 2022 | 0.2308 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-07 16:25 | 2022-02-07 16:32 | 15 | 000:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RECONECTAR SECUNDARIA | C22020700304 | New_Event | Secondary Wire Down | Include | Include | Equipment | 7 | 2022-02-07 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 16:39 | 2022-02-07 16:48 | 30 | 000:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22020700513 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-02-07 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-02-07 16:41 | 2022-02-07 17:49 | 3502 | 001:08 | T | DESGANCHE | DISPARO INTERRUPTOR SE SECCIONALIZO ABRIENDO CORTE DE LINEA PARA CONTINUAR PATRULLANDO | A22020700069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-02-07 | 238136 | keep | 0 | Feb | 2022 | 0.16219 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
BAYAMON | 2022-02-07 16:54 | 2022-02-07 19:11 | 1 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN MONTURA TRANSFORMADORES SE REPARO BAJANTE PRIMARIO DE CAJA A EQUIPO DE MEDICION | S22020700287 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2022-02-07 | 137 | keep | 0 | Feb | 2022 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-07 16:58 | 2022-02-07 18:18 | 42 | 001:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO PORTAFUSIBLE | R22020700107 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2022-02-07 | 3360 | keep | 0 | Feb | 2022 | 0.0022885 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CAGUAS | 2022-02-07 17:00 | 2022-02-07 18:09 | 40 | 001:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA REPARAR TENSOR SUBESTACION NO TIENE RTU | C22020700306 | New_Event |  |  | Include | Wildlife | 69 | 2022-02-07 | 2760 | keep | 0 | Feb | 2022 | 0.0018798 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-07 17:00 | 2022-02-07 20:00 | 4 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22020700035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-02-07 | 720 | keep | 0 | Feb | 2022 | 0.00049039 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-07 17:01 | 2022-02-07 17:02 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M22020700000 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-02-07 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 17:02 | 2022-02-07 20:41 | 30 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE TRANSFORMADOR | S22020700289 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-02-07 | 6570 | keep | 0 | Feb | 2022 | 0.0044748 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-07 17:02 | 2022-02-07 18:18 | 50 | 001:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEA CULEBRA CRUZO FASES | M22020700165 | 1st_after_momentary |  |  | Include | Wildlife | 76 | 2022-02-07 | 3800 | keep | 0 | Feb | 2022 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-07 17:05 | 2022-02-07 17:50 | 1 | 000:45 | P | OTRAS CAUSAS | 2 X 250 EN BOVEDA DE CLIENTE PROBLEMA DE CLIENTE | S22020700290 | New_Event | Other Causes | Include | Include | Other | 45 | 2022-02-07 | 45 | keep | 0 | Feb | 2022 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-07 17:21 | 2022-02-07 20:30 | 58 | 003:09 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE SE CERRO PUENTE SE REEMPLAZO POSTE PRIMARIO TRASPATIO CON TRANSFORMADOR | C22020600004 | New_Event | Defective Pole | Include | Include | Equipment | 189 | 2022-02-07 | 10962 | keep | 0 | Feb | 2022 | 0.0074662 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-02-07 17:35 | 2022-02-07 18:10 | 30 | 000:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22020700291 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2022-02-07 | 1050 | keep | 0 | Feb | 2022 | 0.00071515 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-02-07 17:39 | 2022-02-07 19:01 | 6 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R22020700110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-02-07 | 492 | keep | 0 | Feb | 2022 | 0.0003351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-02-07 17:40 | 2022-02-08 10:10 | 300 | 016:30 | P | ESTRUCTURA AVERIADA | 3 X 100 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO | A22020700078 | New_Event | Defective Pole | Include | Include | Equipment | 990 | 2022-02-07 | 297000 | keep | 0 | Feb | 2022 | 0.20229 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-02-07 17:49 | 2022-02-07 18:18 | 300 | 000:29 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER SE REPARARON CONECCIONES EN SU-2 | M22020700176 | New_Event | UG Cable Fault | Include | Include | Equipment | 29 | 2022-02-07 | 8700 | keep | 0 | Feb | 2022 | 0.0059255 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-02-07 17:49 | 2022-02-07 18:25 | 1100 | 000:36 | P | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS PRIMARIAS Y SE CERRO CORTE DE LINEA | A22020700069 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-02-07 | 39600 | keep | 0 | Feb | 2022 | 0.026971 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 17:52 | 2022-02-07 18:24 | 4 | 000:32 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSCLOSURE DE CLIENTE | S22020700292 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2022-02-07 | 128 | keep | 0 | Feb | 2022 | 8.718e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-02-07 18:06 | 2022-02-07 18:14 | 4702 | 000:08 | T | NO SE REPORTO CAUSA | CERRANDO MACHETES ALIMENTADOR DISPARO, SE CERRARON EN MUERTO LOS MACHETES Y LUEGO SE CERRO INTERRUPTOR POR CONTROL CON TODA SU CARGA | B22020700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-07 | 37616 | keep | 0 | Feb | 2022 | 0.02562 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2022-02-07 18:14 | 2022-02-07 20:49 | 30 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-2 | B22020700546 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-02-07 | 4650 | keep | 0 | Feb | 2022 | 0.0031671 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-07 18:18 | 2022-02-07 18:19 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M22020700000 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-02-07 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-07 18:19 | 2022-02-07 19:15 | 50 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEA CULEBRA CRUZO FASES | M22020700165 | 1st_after_momentary |  |  | Include | Wildlife | 56 | 2022-02-07 | 2800 | keep | 0 | Feb | 2022 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-07 18:21 | 2022-02-08 09:50 | 60 | 015:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22020700180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 929 | 2022-02-07 | 55740 | keep | 0 | Feb | 2022 | 0.037964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-07 18:24 | 2022-02-08 10:24 | 8 | 016:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO BARRAS DE PEDESTAL Y DIO MANTENIMIENTO A OTRO PEDESTAL | C22020700319 | New_Event | Secondary Wire Down | Include | Include | Equipment | 960 | 2022-02-07 | 7680 | keep | 0 | Feb | 2022 | 0.0052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-07 18:29 | 2022-02-07 19:14 | 7 | 000:45 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | C22020700261 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 45 | 2022-02-07 | 315 | keep | 0 | Feb | 2022 | 0.00021455 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-02-07 18:35 | 2022-02-08 17:03 | 4 | 022:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22020700183 | New_Event | Bad Weather | Include | Include | Weather | 1348 | 2022-02-07 | 5392 | keep | 0 | Feb | 2022 | 0.0036725 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-02-07 18:35 | 2022-02-08 08:07 | 20 | 013:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRO FUSIBLE DE TRANSFORMADOR MAQUINARIA IMPACTO POSTE Y CAUSO QUE SE ABRIERA EL FUSIBLE | A22020700097 | New_Event |  |  | Include | Wildlife | 812 | 2022-02-07 | 16240 | keep | 0 | Feb | 2022 | 0.011061 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-07 18:36 | 2022-02-07 19:09 | 20 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO LINEA A CAJA | S22020700300 | New_Event | Wire Down | Include | Include | Equipment | 33 | 2022-02-07 | 660 | keep | 0 | Feb | 2022 | 0.00044952 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-07 18:37 | 2022-02-07 19:13 | 1 | 000:36 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020700184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-02-07 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-07 18:38 | 2022-02-08 10:33 | 40 | 015:55 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B22020700576 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 955 | 2022-02-07 | 38200 | keep | 0 | Feb | 2022 | 0.026018 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-07 18:43 | 2022-02-07 20:35 | 98 | 001:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA | C22020700289 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 112 | 2022-02-07 | 10976 | keep | 0 | Feb | 2022 | 0.0074757 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-07 18:45 | 2022-02-07 21:19 | 15 | 002:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN XMR | P22020700107 | New_Event | Cutout Failure | Include | Include | Equipment | 154 | 2022-02-07 | 2310 | keep | 0 | Feb | 2022 | 0.0015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-07 18:56 | 2022-02-08 12:26 | 50 | 017:30 | P | DESGANCHE | 1 X 50 EN C/L | C22020700327 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1050 | 2022-02-07 | 52500 | keep | 0 | Feb | 2022 | 0.035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-07 19:09 | 2022-02-08 10:26 | 10 | 015:17 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020700615 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 917 | 2022-02-07 | 9170 | keep | 0 | Feb | 2022 | 0.0062456 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-07 19:11 | 2022-02-07 20:39 | 15 | 001:28 | P | OTRAS CAUSAS | 1 X 80 EN S/U POR CONTAMINACION EN GABINETE | P22020700110 | New_Event | Other Causes | Include | Include | Other | 88 | 2022-02-07 | 1320 | keep | 0 | Feb | 2022 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 19:16 | 2022-02-08 13:39 | 40 | 018:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO RISER Y 1 X 50 EN RISER | B22020700014 | New_Event | Cutout Failure | Include | Include | Equipment | 1103 | 2022-02-07 | 44120 | keep | 0 | Feb | 2022 | 0.03005 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-07 19:16 | 2022-02-08 10:17 | 10 | 015:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020700621 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 901 | 2022-02-07 | 9010 | keep | 0 | Feb | 2022 | 0.0061367 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-07 19:22 | 2022-02-07 19:23 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22020700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-07 | 3025 | keep | 0 | Feb | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
ARECIBO | 2022-02-07 19:29 | 2022-02-08 13:46 | 2 | 018:17 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA RAMA CAYO Y CRUZO FASES | A22020700096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1097 | 2022-02-07 | 2194 | keep | 0 | Feb | 2022 | 0.0014943 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-07 19:45 | 2022-02-07 20:42 | 1 | 000:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | B22020700639 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2022-02-07 | 57 | keep | 0 | Feb | 2022 | 3.8822e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-07 20:05 | 2022-02-08 11:35 | 70 | 015:30 | P | DESGANCHE | 1 X 50 Y 1 X 25 EN CORTES DE LINEA SE REALIZO DESGANCHE MASIVO SE CERRO PUENTE Y SE RETIRO PARARRAYOS AVERIADO | A22020700119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 930 | 2022-02-07 | 65100 | keep | 0 | Feb | 2022 | 0.044339 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-02-07 20:40 | 2022-02-07 21:36 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y TOMA | S22020700310 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-02-07 | 560 | keep | 0 | Feb | 2022 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 20:42 | 2022-02-07 20:47 | 1983 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CARGA TRANSFERIDA AL 1801-02 DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | B22020700658 | New_Event | Cutout Failure | Include | Include | Equipment | 5 | 2022-02-07 | 9915 | keep | 0 | Feb | 2022 | 0.0067531 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-02-07 20:42 | 2022-02-07 20:47 | 186 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA 1711-04 SE VERIFICO PERSONAL FUERA DE LA LINEA | B22020700658 | Additional_clients | Cutout Failure | Include | Include | Equipment | 5 | 2022-02-07 | 930 | keep | 0 | Feb | 2022 | 0.00063342 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 20:47 | 2022-02-07 21:59 | 1 | 001:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | B22020700639 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 72 | 2022-02-07 | 72 | keep | 0 | Feb | 2022 | 4.9039e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-07 20:54 | 2022-02-08 17:22 | 1 | 020:28 | P | NO SE REPORTO CAUSA | 2 X 100 EN SU-24 | S22020700318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1228 | 2022-02-07 | 1228 | keep | 0 | Feb | 2022 | 0.00083639 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-07 20:56 | 2022-02-08 16:03 | 20 | 019:07 | P | DESGANCHE | 2 X 30 EN C/L SE REALIZO DESGANCHE SE INSTALO POSTE Y SE INSTALO C/L | C22020700359 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1147 | 2022-02-07 | 22940 | keep | 0 | Feb | 2022 | 0.015624 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-07 20:59 | 2022-02-08 09:09 | 10 | 012:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22020700666 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 730 | 2022-02-07 | 7300 | keep | 0 | Feb | 2022 | 0.004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-07 21:45 | 2022-02-08 01:08 | 15 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA | B22020600680 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-02-07 | 3045 | keep | 0 | Feb | 2022 | 0.0020739 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-07 21:52 | 2022-02-08 00:09 | 50 | 002:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 3 CAJAS DE 100 AMP | B22020700683 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2022-02-07 | 6850 | keep | 0 | Feb | 2022 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-07 21:53 | 2022-02-08 09:35 | 40 | 011:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22020700321 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 702 | 2022-02-07 | 28080 | keep | 0 | Feb | 2022 | 0.019125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-07 22:04 | 2022-02-08 10:46 | 40 | 012:42 | P | DESGANCHE | 1 X 40 EN C/L | C22020700365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 762 | 2022-02-07 | 30480 | keep | 0 | Feb | 2022 | 0.02076 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-02-07 22:20 | 2022-02-08 00:15 | 31 | 001:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN CORTE DE LINEA | P22020700135 | New_Event | Wire Down | Include | Include | Equipment | 115 | 2022-02-07 | 3565 | keep | 0 | Feb | 2022 | 0.0024281 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2022-02-08 01:29 | 2022-02-08 02:48 | 50 | 001:19 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | B22020800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-02-08 | 3950 | keep | 0 | Feb | 2022 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-08 01:47 | 2022-02-08 11:25 | 30 | 009:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A22020800002 | New_Event | Bad Weather | Include | Include | Weather | 578 | 2022-02-08 | 17340 | keep | 0 | Feb | 2022 | 0.01181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-02-08 05:31 | 2022-02-08 10:00 | 40 | 004:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22020800003 | New_Event | Bad Weather | Include | Include | Weather | 269 | 2022-02-08 | 10760 | keep | 0 | Feb | 2022 | 0.0073286 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-08 06:20 | 2022-02-08 18:29 | 75 | 012:09 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU-1 | S22020800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 729 | 2022-02-08 | 54675 | keep | 0 | Feb | 2022 | 0.037239 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-02-08 06:29 | 2022-02-08 06:30 | 2486 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22020800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-02-08 | 2486 | keep | 0 | Feb | 2022 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
CAGUAS | 2022-02-08 06:30 | 2022-02-08 12:41 | 10 | 006:11 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN C/L AVERIA DEL SU - 3 @ SU - 2 CERRO EN RISER @ SU - 3 Y EN SU - 1 @ SU - 2 | C22020800006 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 371 | 2022-02-08 | 3710 | keep | 0 | Feb | 2022 | 0.0025269 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-08 06:58 | 2022-02-08 17:09 | 1 | 010:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C22020800007 | New_Event | Bad Weather | Include | Include | Weather | 611 | 2022-02-08 | 611 | keep | 0 | Feb | 2022 | 0.00041615 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-08 07:03 | 2022-02-08 07:04 | 34 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1512-05 | S22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 34 | keep | 0 | Feb | 2022 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-02-08 07:03 | 2022-02-08 07:04 | 19 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1512-04 | S22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 19 | keep | 0 | Feb | 2022 | 1.2941e-05 | 1.2941e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-02-08 07:18 | 2022-02-08 11:57 | 15 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22020800013 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2022-02-08 | 4185 | keep | 0 | Feb | 2022 | 0.0028504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-08 07:24 | 2022-02-08 14:43 | 20 | 007:19 | P | NO SE REPORTO CAUSA | 1X40 EN RISER DE ELLOS | S22020800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 439 | 2022-02-08 | 8780 | keep | 0 | Feb | 2022 | 0.00598 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-08 07:24 | 2022-02-08 07:25 | 2302 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C22020800009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-08 | 2302 | keep | 0 | Feb | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2022-02-08 07:25 | 2022-02-08 17:41 | 45 | 010:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 SMU 20 DE 175 AMP EN EL SU - 3 ELIMINO AISLADOR ROTO EN EL SU - 4 | C22020800038 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 616 | 2022-02-08 | 27720 | keep | 0 | Feb | 2022 | 0.01888 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2022-02-08 07:28 | 2022-02-08 09:09 | 50 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA POR CAJA PRIMARIAA DE CORTE DE LINEA DEFECTUOSA | P22020800001 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2022-02-08 | 5050 | keep | 0 | Feb | 2022 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-08 07:39 | 2022-02-08 11:36 | 10 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22020800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2022-02-08 | 2370 | keep | 0 | Feb | 2022 | 0.0016142 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-02-08 07:39 | 2022-02-08 10:28 | 15 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A22020800007 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2022-02-08 | 2535 | keep | 0 | Feb | 2022 | 0.0017266 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-08 07:42 | 2022-02-08 12:01 | 200 | 004:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 2 X 100 EN CORTE DE LINEA | B22020800023 | New_Event | Cutout Failure | Include | Include | Equipment | 259 | 2022-02-08 | 51800 | keep | 0 | Feb | 2022 | 0.035281 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-02-08 07:43 | 2022-02-08 07:44 | 2697 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22020800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-08 | 2697 | keep | 0 | Feb | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-02-08 07:44 | 2022-02-08 09:22 | 100 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A22020800008 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 98 | 2022-02-08 | 9800 | keep | 0 | Feb | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-08 07:53 | 2022-02-08 09:34 | 16 | 001:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | R22020800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-02-08 | 1616 | keep | 0 | Feb | 2022 | 0.0011007 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2022-02-08 08:03 | 2022-02-08 17:36 | 119 | 009:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN C/L | P22020800046 | New_Event | Cutout Failure | Include | Include | Equipment | 573 | 2022-02-08 | 68187 | keep | 0 | Feb | 2022 | 0.046442 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
SAN JUAN | 2022-02-08 08:08 | 2022-02-08 09:07 | 15 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22020800003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-02-08 | 885 | keep | 0 | Feb | 2022 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-08 08:11 | 2022-02-08 09:10 | 80 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA SAFADO | P22020800002 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2022-02-08 | 4720 | keep | 0 | Feb | 2022 | 0.0032148 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-08 08:24 | 2022-02-08 13:47 | 1 | 005:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 1 X 80 EN CORTE E LINEA | B22020800031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 323 | 2022-02-08 | 323 | keep | 0 | Feb | 2022 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-08 08:25 | 2022-02-08 08:27 | 1494 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22020800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-08 | 2988 | keep | 0 | Feb | 2022 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2022-02-08 08:26 | 2022-02-08 11:45 | 40 | 003:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22020800015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 199 | 2022-02-08 | 7960 | keep | 0 | Feb | 2022 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-02-08 08:55 | 2022-02-08 09:30 | 3 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO | A22020800019 | New_Event | Wire Down | Include | Include | Equipment | 35 | 2022-02-08 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-02-08 09:18 | 2022-02-08 11:49 | 1447 | 002:31 | S | ERROR HUMANO | SUBESTACION SE FUE A LOCKOUT PERSONAL DE CDS REALIZANDO PRUEBA DE MEGGER EN LOW TAP CHANGER Y SE TRANSFIRIO A LA 1111-00 POR BKR TIE | S22020800000 | New_Event | Human Error | Include | Include | Other | 151 | 2022-02-08 | 218497 | keep | 0 | Feb | 2022 | 0.14882 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-02-08 09:18 | 2022-02-08 11:49 | 266 | 002:31 | T | ERROR HUMANO | SUBESTACION SE FUE A LOCKOUT CARGA POR EL 1112-04 | S22020800000 | New_Event | Human Error | Include | Include | Other | 151 | 2022-02-08 | 40166 | keep | 0 | Feb | 2022 | 0.027357 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-02-08 09:18 | 2022-02-08 11:49 | 73 | 002:31 | T | ERROR HUMANO | SUBESTACION SE FUE A LOCKOUT CARGA POR EL 1112-04 | S22020800000 | New_Event | Human Error | Include | Include | Other | 151 | 2022-02-08 | 11023 | keep | 0 | Feb | 2022 | 0.0075077 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
PONCE | 2022-02-08 09:21 | 2022-02-08 10:21 | 200 | 001:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA SE REPARO PIN POLE TOP | P22020800006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-02-08 | 12000 | keep | 0 | Feb | 2022 | 0.0081731 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-08 09:23 | 2022-02-08 15:11 | 10 | 005:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR SE REPARO SECUNDARIA | S22020700323 | New_Event | Secondary Wire Down | Include | Include | Equipment | 348 | 2022-02-08 | 3480 | keep | 0 | Feb | 2022 | 0.0023702 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-08 09:34 | 2022-02-08 09:35 | 3699 | 000:01 | T | DESGANCHE | RECIERRE 2402-04 LLEVA CARGA DEL 2404-07 | R22020800017 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-08 | 3699 | keep | 0 | Feb | 2022 | 0.0025194 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-08 09:35 | 2022-02-08 10:15 | 16 | 000:40 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | R22020800004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-02-08 | 640 | keep | 0 | Feb | 2022 | 0.0004359 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-02-08 09:36 | 2022-02-08 09:37 | 1017 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 1017 | keep | 0 | Feb | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2022-02-08 09:37 | 2022-02-08 11:57 | 6 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22020800017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-02-08 | 840 | keep | 0 | Feb | 2022 | 0.00057212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-08 09:39 | 2022-02-08 19:57 | 80 | 010:18 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C22020800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2022-02-08 | 49440 | keep | 0 | Feb | 2022 | 0.033673 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-08 09:50 | 2022-02-08 18:15 | 15 | 008:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020800019 | New_Event | Bad Weather | Include | Include | Weather | 505 | 2022-02-08 | 7575 | keep | 0 | Feb | 2022 | 0.0051593 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-08 09:52 | 2022-02-08 11:10 | 15 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B22020700537 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2022-02-08 | 1170 | keep | 0 | Feb | 2022 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-08 09:53 | 2022-02-08 12:45 | 200 | 002:52 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B22020800066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2022-02-08 | 34400 | keep | 0 | Feb | 2022 | 0.02343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-02-08 09:57 | 2022-02-08 13:32 | 200 | 003:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-02-08 | 43000 | keep | 0 | Feb | 2022 | 0.029287 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-02-08 09:59 | 2022-02-08 11:27 | 100 | 001:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-02-08 | 8800 | keep | 0 | Feb | 2022 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-02-08 10:00 | 2022-02-08 11:50 | 1 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR PARA TRABAJOS DE INSTALACION DE NEUTRAL PRIMARIO | A22020800029 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-02-08 | 110 | keep | 0 | Feb | 2022 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-08 10:08 | 2022-02-08 10:09 | 1066 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 1066 | keep | 0 | Feb | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2022-02-08 10:10 | 2022-02-08 15:40 | 60 | 005:30 | P | ESTRUCTURA AVERIADA | PUENTES PRIMARIOS ABIERTOS PARA REMPLAZAR POSTE PRIMARIO PARTIDO | A22020800039 | Partial_restoration | Defective Pole | Include | Include | Equipment | 330 | 2022-02-08 | 19800 | keep | 0 | Feb | 2022 | 0.013486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-08 10:12 | 2022-02-08 14:21 | 1 | 004:09 | P | NO SE REPORTO CAUSA | 2 X 30 RISER | B22020800073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-02-08 | 249 | keep | 0 | Feb | 2022 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-08 10:17 | 2022-02-08 13:41 | 15 | 003:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1X30 EN TRANSFORMADOR SE REPARO TRONCAL SECUNDARIO AVERIADO Y VARIAS TOMAS DE SERVICIO | S22020800074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 204 | 2022-02-08 | 3060 | keep | 0 | Feb | 2022 | 0.0020842 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-08 10:23 | 2022-02-08 10:24 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-02-08 10:30 | 2022-02-08 15:57 | 135 | 005:27 | P | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE VOVLIO A CERRAR POR DESGANCHE PRIMARIO | S22020800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-02-08 | 44145 | keep | 0 | Feb | 2022 | 0.030067 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
VEGA BAJA | 2022-02-08 10:33 | 2022-02-08 10:34 | 2368 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22020800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-08 | 2368 | keep | 0 | Feb | 2022 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-02-08 10:33 | 2022-02-08 10:34 | 538 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22020800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-08 | 538 | keep | 0 | Feb | 2022 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-02-08 10:33 | 2022-02-08 10:34 | 1284 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22020800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-08 | 1284 | keep | 0 | Feb | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2022-02-08 10:34 | 2022-02-08 16:38 | 40 | 006:04 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B22020700576 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 364 | 2022-02-08 | 14560 | keep | 0 | Feb | 2022 | 0.0099167 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-08 10:34 | 2022-02-08 16:57 | 10 | 006:23 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REFIERE SECTOR PARA DESGANCHE | B22020800630 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-02-08 | 3830 | keep | 0 | Feb | 2022 | 0.0026086 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-08 10:35 | 2022-02-08 12:15 | 15 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PROVISIONAL AEREO PARA REPARAR LINEA AVERIADA | M22020800018 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2022-02-08 | 1500 | keep | 0 | Feb | 2022 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-02-08 10:41 | 2022-02-08 13:09 | 21 | 002:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA BAJANTE PRIMARIO Y DESGANCHE | R22020800024 | New_Event | Cutout Failure | Include | Include | Equipment | 148 | 2022-02-08 | 3108 | keep | 0 | Feb | 2022 | 0.0021168 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-02-08 10:50 | 2022-02-08 11:49 | 1 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22020700122 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-02-08 | 59 | keep | 0 | Feb | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-02-08 10:53 | 2022-02-08 18:00 | 1 | 007:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22020800032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 427 | 2022-02-08 | 427 | keep | 0 | Feb | 2022 | 0.00029083 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-08 10:58 | 2022-02-08 10:59 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22020800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
MAYAGÃœEZ | 2022-02-08 11:00 | 2022-02-08 15:28 | 30 | 004:28 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO | M22020800027 | New_Event | Defective Pole | Include | Include | Equipment | 268 | 2022-02-08 | 8040 | keep | 0 | Feb | 2022 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-08 11:01 | 2022-02-08 13:36 | 20 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22020800041 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2022-02-08 | 3100 | keep | 0 | Feb | 2022 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-02-08 11:08 | 2022-02-08 11:09 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 527 | keep | 0 | Feb | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2022-02-08 11:10 | 2022-02-08 14:09 | 50 | 002:59 | P | NO SE REPORTO CAUSA | 1X100 EN CORTE DE LINEA | S22020800108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2022-02-08 | 8950 | keep | 0 | Feb | 2022 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-08 11:11 | 2022-02-08 12:00 | 1 | 000:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-1 | S22020800114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-02-08 | 49 | keep | 0 | Feb | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-08 11:12 | 2022-02-08 15:32 | 80 | 004:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22020800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2022-02-08 | 20800 | keep | 0 | Feb | 2022 | 0.014167 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-08 11:16 | 2022-02-08 12:01 | 15 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R22020800023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-02-08 | 675 | keep | 0 | Feb | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-08 11:26 | 2022-02-08 13:43 | 100 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L CAMION IMPACTO POSTE | C22020800039 | New_Event |  |  | Include | Wildlife | 137 | 2022-02-08 | 13700 | keep | 0 | Feb | 2022 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-08 11:27 | 2022-02-08 11:28 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220208000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 527 | keep | 0 | Feb | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2022-02-08 11:30 | 2022-02-09 00:20 | 65 | 012:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L SE RETIRO MALLA ENREDADA EN LA LINEA | S22020800123 | New_Event |  |  | Include | Wildlife | 770 | 2022-02-08 | 50050 | keep | 0 | Feb | 2022 | 0.034089 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-02-08 11:41 | 2022-02-08 19:00 | 1 | 007:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S22020800128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 439 | 2022-02-08 | 439 | keep | 0 | Feb | 2022 | 0.000299 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-08 11:41 | 2022-02-08 14:31 | 85 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40 EN C/L MAL TIEMPO | C22020800041 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2022-02-08 | 14450 | keep | 0 | Feb | 2022 | 0.0098418 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2022-02-08 11:45 | 2022-02-08 15:18 | 8 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22020800054 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2022-02-08 | 1704 | keep | 0 | Feb | 2022 | 0.0011606 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-02-08 11:48 | 2022-02-08 15:19 | 25 | 003:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO CAJA PRIMARIA CON CORROSION | R22020800034 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2022-02-08 | 5275 | keep | 0 | Feb | 2022 | 0.0035928 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-02-08 11:48 | 2022-02-08 15:19 | 11 | 003:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR SE REPARO SECUNDARIA | R22020800026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 211 | 2022-02-08 | 2321 | keep | 0 | Feb | 2022 | 0.0015808 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-02-08 12:09 | 2022-02-08 16:07 | 7 | 003:58 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C22020800046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 238 | 2022-02-08 | 1666 | keep | 0 | Feb | 2022 | 0.0011347 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-02-08 12:10 | 2022-02-08 14:10 | 85 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L MAL TIEMPO | P22020800025 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2022-02-08 | 10200 | keep | 0 | Feb | 2022 | 0.0069472 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-02-08 12:14 | 2022-02-08 16:43 | 10 | 004:29 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO SECUNDARIA | S22020800115 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 269 | 2022-02-08 | 2690 | keep | 0 | Feb | 2022 | 0.0018321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-08 12:15 | 2022-02-08 13:34 | 11 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | R22020800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2022-02-08 | 869 | keep | 0 | Feb | 2022 | 0.00059187 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-02-08 12:17 | 2022-02-08 12:18 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 1085 | keep | 0 | Feb | 2022 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-02-08 12:22 | 2022-02-08 18:39 | 15 | 006:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA | B22020800127 | New_Event | Service Transformer Failure | Include | Include | Equipment | 377 | 2022-02-08 | 5655 | keep | 0 | Feb | 2022 | 0.0038516 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-08 12:23 | 2022-02-08 18:33 | 2 | 006:10 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2022-02-08 | 740 | keep | 0 | Feb | 2022 | 0.00050401 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-02-08 12:31 | 2022-02-08 14:12 | 1 | 001:41 | P | OTRAS CAUSAS | EQUIPO DE MEDICION DEFECTUOSO SE BYPASEO PT Y CT | B22020800022 | New_Event | Other Causes | Include | Include | Other | 101 | 2022-02-08 | 101 | keep | 0 | Feb | 2022 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-08 12:37 | 2022-02-08 13:00 | 3 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22020800065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-02-08 | 69 | keep | 0 | Feb | 2022 | 4.6996e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-02-08 12:41 | 2022-02-08 15:03 | 7 | 002:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO CAJA QUEMADA Y BAJANTE SECUNDARIO | C22020800051 | New_Event | Cutout Failure | Include | Include | Equipment | 142 | 2022-02-08 | 994 | keep | 0 | Feb | 2022 | 0.00067701 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-02-08 12:48 | 2022-02-08 12:53 | 1447 | 000:05 | S | ERROR HUMANO | PERSONAL DE CDS DISPARO SUBESTACION LLEVA 1419-09 Y 1419-12 | S22020800000 | New_Event | Human Error | Include | Include | Other | 5 | 2022-02-08 | 7235 | keep | 0 | Feb | 2022 | 0.0049277 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-02-08 12:48 | 2022-02-08 12:53 | 266 | 000:05 | T | ERROR HUMANO | PERSONAL DE CDS DISPARO SUBESTACION CARGA POR EL 1112-04 | S22020800000 | New_Event | Human Error | Include | Include | Other | 5 | 2022-02-08 | 1330 | keep | 0 | Feb | 2022 | 0.00090586 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-02-08 12:48 | 2022-02-08 12:53 | 73 | 000:05 | T | ERROR HUMANO | PERSONAL DE CDS DISPARO SUBESTACION CARGA POR EL 1112-04 | S22020800000 | New_Event | Human Error | Include | Include | Other | 5 | 2022-02-08 | 365 | keep | 0 | Feb | 2022 | 0.0002486 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
HUMACAO | 2022-02-08 12:57 | 2022-02-08 16:30 | 138 | 003:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN C/L MAL TIEMPO | C22020800053 | New_Event | Bad Weather | Include | Include | Weather | 213 | 2022-02-08 | 29394 | keep | 0 | Feb | 2022 | 0.02002 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
BAYAMON | 2022-02-08 12:58 | 2022-02-08 18:00 | 15 | 005:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL | B22020600342 | New_Event | Secondary Wire Down | Include | Include | Equipment | 302 | 2022-02-08 | 4530 | keep | 0 | Feb | 2022 | 0.0030854 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-08 13:05 | 2022-02-09 12:37 | 4 | 023:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | C22020800056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1412 | 2022-02-08 | 5648 | keep | 0 | Feb | 2022 | 0.0038468 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-08 13:09 | 2022-02-08 16:22 | 8 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22020800048 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2022-02-08 | 1544 | keep | 0 | Feb | 2022 | 0.0010516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-02-08 13:14 | 2022-02-08 18:06 | 11 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22020800037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2022-02-08 | 3212 | keep | 0 | Feb | 2022 | 0.0021877 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-02-08 13:17 | 2022-02-08 16:57 | 4 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO CAJA AVERIADA Y PARARRAYO | C22020800061 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2022-02-08 | 880 | keep | 0 | Feb | 2022 | 0.00059936 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-02-08 13:17 | 2022-02-08 15:15 | 1 | 001:58 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A22020800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2022-02-08 | 118 | keep | 0 | Feb | 2022 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-08 13:17 | 2022-02-08 15:15 | 2266 | 001:58 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A22020800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2022-02-08 | 267388 | keep | 0 | Feb | 2022 | 0.18212 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2022-02-08 13:17 | 2022-02-08 15:15 | 1399 | 001:58 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A22020800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2022-02-08 | 165082 | keep | 0 | Feb | 2022 | 0.11244 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2022-02-08 13:30 | 2022-02-08 22:02 | 49 | 008:32 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO MEDIANTE GOI BY-220208-02 | S22020800130 | New_Event | Defective Pole | Include | Include | Equipment | 512 | 2022-02-08 | 25088 | keep | 0 | Feb | 2022 | 0.017087 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
ARECIBO | 2022-02-08 13:37 | 2022-02-08 19:01 | 60 | 005:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-02-08 | 19440 | keep | 0 | Feb | 2022 | 0.01324 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-08 13:45 | 2022-02-08 14:39 | 1 | 000:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION SOTERRADA HACIA RISER | A22020800079 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 54 | 2022-02-08 | 54 | keep | 0 | Feb | 2022 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-08 14:00 | 2022-02-09 14:34 | 1 | 024:34 | P | NO SE REPORTO CAUSA | 3 X 40 EN SU-1A | S22020800164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1474 | 2022-02-08 | 1474 | keep | 0 | Feb | 2022 | 0.0010039 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-08 14:02 | 2022-02-08 16:12 | 60 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L SE RETIRO AVE | R22020800042 | New_Event |  |  | Include | Wildlife | 130 | 2022-02-08 | 7800 | keep | 0 | Feb | 2022 | 0.0053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-08 14:05 | 2022-02-08 21:18 | 3 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22020800063 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2022-02-08 | 1299 | keep | 0 | Feb | 2022 | 0.00088474 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-02-08 14:06 | 2022-02-08 15:20 | 40 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22020800152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-02-08 | 2960 | keep | 0 | Feb | 2022 | 0.002016 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-08 14:16 | 2022-02-08 14:39 | 10 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR T-15 | B22020800053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-02-08 | 230 | keep | 0 | Feb | 2022 | 0.00015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-08 14:18 | 2022-02-08 18:24 | 1 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S22020800166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-02-08 | 246 | keep | 0 | Feb | 2022 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-08 14:55 | 2022-02-08 19:04 | 12 | 004:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR Y SE REALIZO DESGANCHE SECUNDARIO | S22020800169 | New_Event | Secondary Wire Down | Include | Include | Equipment | 249 | 2022-02-08 | 2988 | keep | 0 | Feb | 2022 | 0.0020351 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-08 14:55 | 2022-02-08 17:28 | 10 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C22020800083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2022-02-08 | 1530 | keep | 0 | Feb | 2022 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-08 14:57 | 2022-02-08 18:35 | 1 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN EQUIPO DE MEDICION | P22020800032 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2022-02-08 | 218 | keep | 0 | Feb | 2022 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-08 15:10 | 2022-02-08 16:40 | 3 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22020800102 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2022-02-08 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-02-08 15:12 | 2022-02-08 16:51 | 10 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22020800011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2022-02-08 | 990 | keep | 0 | Feb | 2022 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-08 15:16 | 2022-02-08 16:30 | 1 | 001:14 | P | NO SE REPORTO CAUSA | 2X65 DE RISER @ GABINETE DEL CLIENTE | S20020800174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-02-08 | 74 | keep | 0 | Feb | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-08 15:28 | 2022-02-08 16:45 | 1 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN MONTURA TRIFASICA AAA NO CAUSA | P22020800035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-02-08 | 77 | keep | 0 | Feb | 2022 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-08 15:30 | 2022-02-08 17:00 | 12 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22020800065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-02-08 | 1080 | keep | 0 | Feb | 2022 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-02-08 15:40 | 2022-02-08 15:53 | 300 | 000:13 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTES LUEGO DE REMPLAZAR POSTE PRIMARIO PARTIDO | A22020800039 | Additional_clients | Defective Pole | Include | Include | Equipment | 13 | 2022-02-08 | 3900 | keep | 0 | Feb | 2022 | 0.0026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-08 15:41 | 2022-02-08 19:36 | 1 | 003:55 | P | NO SE REPORTO CAUSA | 2 X 25 EN MONTURA DE TRANSFORMADORES | B22020800165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-02-08 | 235 | keep | 0 | Feb | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-08 15:46 | 2022-02-09 00:18 | 5 | 008:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA Y BAJANTE SECUNDARIO | B22020800167 | New_Event | Cutout Failure | Include | Include | Equipment | 512 | 2022-02-08 | 2560 | keep | 0 | Feb | 2022 | 0.0017436 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-02-08 15:53 | 2022-02-08 15:58 | 2231 | 000:05 | T | ESTRUCTURA AVERIADA | DISPARO DEL INTERRUPTOR AL PERSONAL DE LUMA CERRAR CAJAS DE CORTE DE LINEA SE VERIFICO PERSONAL FUERA DE LAS LINEAS | A22020800108 | Additional_clients | Defective Pole | Include | Include | Equipment | 5 | 2022-02-08 | 11155 | keep | 0 | Feb | 2022 | 0.0075976 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-08 16:15 | 2022-02-09 11:29 | 15 | 019:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 50KVA | B22020800171 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1154 | 2022-02-08 | 17310 | keep | 0 | Feb | 2022 | 0.01179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-02-08 16:24 | 2022-02-08 17:57 | 12 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22020800173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-02-08 | 1116 | keep | 0 | Feb | 2022 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-02-08 16:26 | 2022-02-09 15:58 | 10 | 023:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA | B22020800174 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1412 | 2022-02-08 | 14120 | keep | 0 | Feb | 2022 | 0.0096171 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-08 16:30 | 2022-02-08 23:21 | 52 | 006:51 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO MEDIANTE GOI BY-220208-02 | S22020800130 | New_Event | Defective Pole | Include | Include | Equipment | 411 | 2022-02-08 | 21372 | keep | 0 | Feb | 2022 | 0.014556 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
ARECIBO | 2022-02-08 16:30 | 2022-02-08 17:07 | 15 | 000:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR FOREMAN REPORTO NO SE ENCONTRO CAUSA | A22020800110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-02-08 | 555 | keep | 0 | Feb | 2022 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-08 16:50 | 2022-02-08 20:05 | 75 | 003:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A22020800111 | New_Event |  |  | Include | Wildlife | 195 | 2022-02-08 | 14625 | keep | 0 | Feb | 2022 | 0.009961 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2022-02-08 16:53 | 2022-02-08 17:40 | 12 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22020800044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2022-02-08 | 564 | keep | 0 | Feb | 2022 | 0.00038414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-02-08 17:08 | 2022-02-08 20:45 | 75 | 003:37 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A22020800114 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 217 | 2022-02-08 | 16275 | keep | 0 | Feb | 2022 | 0.011085 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-02-08 17:14 | 2022-02-08 20:42 | 1 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22020800100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-02-08 | 208 | keep | 0 | Feb | 2022 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-08 17:15 | 2022-02-08 17:17 | 4028 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-08 | 8056 | keep | 0 | Feb | 2022 | 0.0054869 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
CAGUAS | 2022-02-08 17:23 | 2022-02-08 19:12 | 7 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22020800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-02-08 | 763 | keep | 0 | Feb | 2022 | 0.00051968 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-08 17:32 | 2022-02-08 18:13 | 15 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22020800130 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2022-02-08 | 615 | keep | 0 | Feb | 2022 | 0.00041887 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-02-08 17:32 | 2022-02-08 17:33 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-08 | 1310 | keep | 0 | Feb | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
PONCE | 2022-02-08 17:43 | 2022-02-08 18:32 | 15 | 000:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR PERITO TRABAJANDO EN RESIDENCIA CRUZO BASE DE CONTADOR | P22020800046 | New_Event |  |  | Include | Wildlife | 49 | 2022-02-08 | 735 | keep | 0 | Feb | 2022 | 0.00050061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-08 17:55 | 2022-02-09 08:27 | 4 | 014:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020800087 | New_Event | Bad Weather | Include | Include | Weather | 872 | 2022-02-08 | 3488 | keep | 0 | Feb | 2022 | 0.0023757 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-02-08 17:55 | 2022-02-08 20:50 | 10 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22020800117 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2022-02-08 | 1750 | keep | 0 | Feb | 2022 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-08 17:56 | 2022-02-08 22:07 | 10 | 004:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | B22020800186 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 251 | 2022-02-08 | 2510 | keep | 0 | Feb | 2022 | 0.0017095 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-02-08 18:07 | 2022-02-08 21:33 | 8 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22020800088 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2022-02-08 | 1648 | keep | 0 | Feb | 2022 | 0.0011224 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-08 18:26 | 2022-02-08 20:00 | 50 | 001:34 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B22020800189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-02-08 | 4700 | keep | 0 | Feb | 2022 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-08 18:33 | 2022-02-09 11:27 | 40 | 016:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR IGUANA | B22020800190 | New_Event |  |  | Include | Wildlife | 1014 | 2022-02-08 | 40560 | keep | 0 | Feb | 2022 | 0.027625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-02-08 18:35 | 2022-02-08 19:27 | 6 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR SE REEMPLAZO CAJA PRIMARIA CON CORROSION | R22020800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-02-08 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-08 18:49 | 2022-02-09 13:47 | 20 | 018:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 50KVA | B22020800191 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1138 | 2022-02-08 | 22760 | keep | 0 | Feb | 2022 | 0.015502 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-08 18:55 | 2022-02-08 19:33 | 8 | 000:38 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22020800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-02-08 | 304 | keep | 0 | Feb | 2022 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-08 18:57 | 2022-02-08 19:03 | 3941 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL SE VERIFICO PERSONAL FUERA | B22020800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-02-08 | 23646 | keep | 0 | Feb | 2022 | 0.016105 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
YAUCO | 2022-02-08 19:28 | 2022-02-08 22:05 | 115 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE BRISA | P22020800052 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2022-02-08 | 18055 | keep | 0 | Feb | 2022 | 0.012297 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
BAYAMON | 2022-02-08 20:22 | 2022-02-08 20:28 | 81 | 000:06 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA FIJAR MACHETE A POSTE | B22020800000 | New_Event | Switch Failure | Include | Include | Equipment | 6 | 2022-02-08 | 486 | keep | 0 | Feb | 2022 | 0.00033101 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2022-02-08 21:36 | 2022-02-08 22:44 | 100 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L Y SE CERRO PUENTE ANTES DEL C/L CON VOLTAJE SIN CARGA | B22020800216 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-02-08 | 6800 | keep | 0 | Feb | 2022 | 0.0046314 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-08 22:32 | 2022-02-08 23:14 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22020800176 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-02-08 | 420 | keep | 0 | Feb | 2022 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-08 22:56 | 2022-02-09 08:51 | 19 | 009:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 Y 1 X 15 EN XMR CRUCE POR AVE | B22020800225 | New_Event |  |  | Include | Wildlife | 595 | 2022-02-08 | 11305 | keep | 0 | Feb | 2022 | 0.0076998 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2022-02-08 22:58 | 2022-02-09 02:16 | 45 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R22020800048 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-02-08 | 8910 | keep | 0 | Feb | 2022 | 0.0060686 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-02-08 23:00 | 2022-02-08 23:01 | 1854 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | C22020800113 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-08 | 1854 | keep | 0 | Feb | 2022 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2022-02-08 23:02 | 2022-02-08 23:03 | 1854 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | C22020800114 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-08 | 1854 | keep | 0 | Feb | 2022 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2022-02-08 23:03 | 2022-02-08 23:04 | 1854 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | C22020800115 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-08 | 1854 | keep | 0 | Feb | 2022 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2022-02-08 23:10 | 2022-02-08 23:11 | 1854 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | C22020800116 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-08 | 1854 | keep | 0 | Feb | 2022 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2022-02-08 23:11 | 2022-02-09 01:05 | 1854 | 001:54 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO VSW EN MH-1 @ MH-2 PARA SECCIONALIZAR PISTOLA AVERIADA EN CAJAS SECAS DEL MH-1 HACIA CARGA DE LA ALCALDIA. | C22020800117 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 114 | 2022-02-08 | 211356 | keep | 0 | Feb | 2022 | 0.14395 | 0.0012628 | Sustained | FALSE | FALSE | Not_TMED_Event | 1854
BAYAMON | 2022-02-08 23:30 | 2022-02-09 01:10 | 2 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22020800195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-02-08 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-02-09 02:21 | 2022-02-09 02:22 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 LLEVANDO EL 1303-04 | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-02-09 02:21 | 2022-02-09 02:22 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 LLEVANDO EL 1303-04 | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
FAJARDO | 2022-02-09 02:37 | 2022-02-09 04:14 | 5 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN XMR CRUCE POR CULEBRA | R22020900002 | New_Event |  |  | Include | Wildlife | 97 | 2022-02-09 | 485 | keep | 0 | Feb | 2022 | 0.00033033 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-02-09 06:44 | 2022-02-09 10:58 | 25 | 004:14 | P | DESGANCHE | 1 X30 EN CORTE DE LINEA SE REPARO BAJANTE SECUNDARIO | C22020900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-02-09 | 6350 | keep | 0 | Feb | 2022 | 0.004325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-09 06:52 | 2022-02-09 13:46 | 9 | 006:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B22020800012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 414 | 2022-02-09 | 3726 | keep | 0 | Feb | 2022 | 0.0025378 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-02-09 07:02 | 2022-02-09 07:53 | 533 | 000:51 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | S22020900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-02-09 | 27183 | keep | 0 | Feb | 2022 | 0.018514 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
ARECIBO | 2022-02-09 07:07 | 2022-02-09 10:13 | 15 | 003:06 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR FUSIBLE CORROIDO | A22020900001 | New_Event | Other Causes | Include | Include | Other | 186 | 2022-02-09 | 2790 | keep | 0 | Feb | 2022 | 0.0019003 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-09 07:13 | 2022-02-09 08:59 | 1 | 001:46 | P | OTRAS CAUSAS | PROBLEMA INTERNO DEL CLIENTE | P22020900001 | New_Event | Other Causes | Include | Include | Other | 106 | 2022-02-09 | 106 | keep | 0 | Feb | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-09 07:15 | 2022-02-10 19:49 | 16 | 036:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE INSTALO PROVISIONAL @ T-116 | B22020900002 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2194 | 2022-02-09 | 35104 | keep | 0 | Feb | 2022 | 0.023909 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-02-09 07:17 | 2022-02-10 09:07 | 1 | 025:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B22020900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1550 | 2022-02-09 | 1550 | keep | 0 | Feb | 2022 | 0.0010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-02-09 07:38 | 2022-02-09 10:36 | 8 | 002:58 | P | NO SE REPORTO CAUSA | 1X10 EN TRANSFORMADOR | R22020900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2022-02-09 | 1424 | keep | 0 | Feb | 2022 | 0.00096988 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-02-09 07:49 | 2022-02-09 14:50 | 35 | 007:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA Y SE REEMPLAZO AISLADOR | C22020900010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 421 | 2022-02-09 | 14735 | keep | 0 | Feb | 2022 | 0.010036 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-02-09 07:53 | 2022-02-09 11:15 | 1 | 003:22 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE ABIERTO | S22020900000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-02-09 | 202 | keep | 0 | Feb | 2022 | 0.00013758 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-09 07:54 | 2022-02-09 07:55 | 2450 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C22020900012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-09 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-02-09 07:55 | 2022-02-09 12:11 | 45 | 004:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR 1 X 50 EN CORTE DE LINEA | C22020900015 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 256 | 2022-02-09 | 11520 | keep | 0 | Feb | 2022 | 0.0078462 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-02-09 07:59 | 2022-02-09 08:00 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 3000 | keep | 0 | Feb | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BARRANQUITAS | 2022-02-09 07:59 | 2022-02-09 14:45 | 25 | 006:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA CABLE ARREADO | C22020900013 | New_Event | Wire Down | Include | Include | Equipment | 406 | 2022-02-09 | 10150 | keep | 0 | Feb | 2022 | 0.0069131 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-02-09 08:20 | 2022-02-09 12:51 | 5 | 004:31 | P | ESTRUCTURA AVERIADA | SE REMPLAZO CRUCETA QUE TIENE UN TRANSFORMADOR | A22020900002 | New_Event | Defective Pole | Include | Include | Equipment | 271 | 2022-02-09 | 1355 | keep | 0 | Feb | 2022 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-09 08:27 | 2022-02-09 08:28 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 281 | keep | 0 | Feb | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-02-09 08:27 | 2022-02-09 08:28 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 1252 | keep | 0 | Feb | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-02-09 08:27 | 2022-02-09 08:28 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 595 | keep | 0 | Feb | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-02-09 08:27 | 2022-02-09 08:28 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 51 | keep | 0 | Feb | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-02-09 08:27 | 2022-02-09 08:28 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 721 | keep | 0 | Feb | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-02-09 08:27 | 2022-02-09 08:28 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | A22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 1382 | keep | 0 | Feb | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-02-09 08:27 | 2022-02-09 08:28 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | A22020900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-09 | 654 | keep | 0 | Feb | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2022-02-09 08:28 | 2022-02-09 11:44 | 4 | 003:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22020800087 | Partial_restoration | Bad Weather | Include | Include | Weather | 196 | 2022-02-09 | 784 | keep | 0 | Feb | 2022 | 0.00053398 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-09 08:41 | 2022-02-09 13:25 | 200 | 004:44 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | S22020900022 | New_Event | Switch Failure | Include | Include | Equipment | 284 | 2022-02-09 | 56800 | keep | 0 | Feb | 2022 | 0.038686 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-02-09 08:49 | 2022-02-09 11:45 | 3 | 002:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M22020900005 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2022-02-09 | 528 | keep | 0 | Feb | 2022 | 0.00035962 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-02-09 09:04 | 2022-02-09 17:22 | 1 | 008:18 | P | CABLE SOTERRADO AVERIADO | SE EMPALMO CABLE PRIMARIO SOTERRADO AVERIADO | R22020900009 | New_Event | UG Cable Fault | Include | Include | Equipment | 498 | 2022-02-09 | 498 | keep | 0 | Feb | 2022 | 0.00033919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-09 09:05 | 2022-02-09 09:49 | 8 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A22020800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-02-09 | 352 | keep | 0 | Feb | 2022 | 0.00023975 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-09 09:06 | 2022-02-11 09:15 | 12 | 048:09 | P | NO SE REPORTO CAUSA | 1 X 25 SUM-20 | S22020900027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2889 | 2022-02-09 | 34668 | keep | 0 | Feb | 2022 | 0.023612 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-02-09 09:10 | 2022-02-09 10:07 | 3 | 000:57 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO CON TRANSFORMADOR | A22020900006 | New_Event | Defective Pole | Include | Include | Equipment | 57 | 2022-02-09 | 171 | keep | 0 | Feb | 2022 | 0.00011647 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-02-09 09:18 | 2022-02-09 09:19 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR EL 8007-04 | A22020900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-09 09:18 | 2022-02-09 09:19 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22020900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
UTUADO | 2022-02-09 09:25 | 2022-02-09 13:35 | 30 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22020900010 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2022-02-09 | 7500 | keep | 0 | Feb | 2022 | 0.0051082 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-09 09:29 | 2022-02-09 10:47 | 860 | 001:18 | T | DESGANCHE | DISPARO INTERRUPTOR SE LE DIO PRUEBA PROBO MALO SE RETIRO RAMA SOBRE LAS LINEAS | P22020900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-02-09 | 67080 | keep | 0 | Feb | 2022 | 0.045688 | 0.00058574 | Sustained | FALSE | FALSE | Not_TMED_Event | 860
BAYAMON | 2022-02-09 09:46 | 2022-02-09 17:20 | 40 | 007:34 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | B22020900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 454 | 2022-02-09 | 18160 | keep | 0 | Feb | 2022 | 0.012369 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-09 10:03 | 2022-02-09 10:07 | 1578 | 000:04 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 30% POR EL 1336-08 | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-09 | 6312 | keep | 0 | Feb | 2022 | 0.0042991 | 0.0010748 | Momentary | FALSE | FALSE | Not_TMED_Event | 1578
SAN JUAN | 2022-02-09 10:03 | 2022-02-09 10:07 | 5290 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 30% DEL 1204-04 Y 1336-09 | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-09 | 21160 | keep | 0 | Feb | 2022 | 0.014412 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-02-09 10:03 | 2022-02-09 10:07 | 207 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1336-08 | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-09 | 828 | keep | 0 | Feb | 2022 | 0.00056395 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-02-09 10:03 | 2022-02-10 11:18 | 20 | 025:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A CAJA | S22020900122 | New_Event | Wire Down | Include | Include | Equipment | 1515 | 2022-02-09 | 30300 | keep | 0 | Feb | 2022 | 0.020637 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-09 10:03 | 2022-02-09 10:06 | 143 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-09 | 429 | keep | 0 | Feb | 2022 | 0.00029219 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-02-09 10:03 | 2022-02-09 10:06 | 1000 | 000:03 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 80% POR EL 1404-06 | S22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-09 | 3000 | keep | 0 | Feb | 2022 | 0.0020433 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2022-02-09 10:12 | 2022-02-09 12:25 | 60 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 80 EN C/L | B22020900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-02-09 | 7980 | keep | 0 | Feb | 2022 | 0.0054351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-02-09 10:17 | 2022-02-09 12:41 | 50 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA DE CORTE DE LINEA Y PARARRAYO | P22020900007 | New_Event | Cutout Failure | Include | Include | Equipment | 144 | 2022-02-09 | 7200 | keep | 0 | Feb | 2022 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-09 10:18 | 2022-02-09 16:00 | 6 | 005:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22020900048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 342 | 2022-02-09 | 2052 | keep | 0 | Feb | 2022 | 0.0013976 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-02-09 10:25 | 2022-02-09 11:50 | 1 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN CORTE DE LINEA DE ELLOS Y SE LE REMPLAZO EL PORTAFUSIBLE | R22020900011 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2022-02-09 | 85 | keep | 0 | Feb | 2022 | 5.7893e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-09 10:51 | 2022-02-09 14:50 | 95 | 003:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA EN EL PISO | P22020900019 | New_Event | Wire Down | Include | Include | Equipment | 239 | 2022-02-09 | 22705 | keep | 0 | Feb | 2022 | 0.015464 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CAGUAS | 2022-02-09 11:00 | 2022-02-09 13:14 | 35 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CL | C22020900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-02-09 | 4690 | keep | 0 | Feb | 2022 | 0.0031943 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-02-09 11:03 | 2022-02-09 11:04 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 1702 | keep | 0 | Feb | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2022-02-09 11:04 | 2022-02-09 12:28 | 15 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B22020900033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2022-02-09 | 1260 | keep | 0 | Feb | 2022 | 0.00085818 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-09 11:07 | 2022-02-09 12:10 | 20 | 001:03 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B22020900034 | New_Event | Defective Pole | Include | Include | Equipment | 63 | 2022-02-09 | 1260 | keep | 0 | Feb | 2022 | 0.00085818 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-02-09 11:12 | 2022-02-09 11:13 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22020900024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 3973 | keep | 0 | Feb | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
HUMACAO | 2022-02-09 11:19 | 2022-02-09 11:20 | 2141 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 2141 | keep | 0 | Feb | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
ARECIBO | 2022-02-09 11:20 | 2022-02-09 11:33 | 1 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22020900025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2022-02-09 | 13 | keep | 0 | Feb | 2022 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-09 11:21 | 2022-02-09 18:50 | 8 | 007:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS | C22020900046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 449 | 2022-02-09 | 3592 | keep | 0 | Feb | 2022 | 0.0024465 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-02-09 11:29 | 2022-02-09 14:54 | 196 | 003:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | P22020900027 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2022-02-09 | 40180 | keep | 0 | Feb | 2022 | 0.027366 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
ARECIBO | 2022-02-09 11:58 | 2022-02-09 14:05 | 6 | 002:07 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A22020900026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 127 | 2022-02-09 | 762 | keep | 0 | Feb | 2022 | 0.00051899 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-02-09 12:07 | 2022-02-09 13:08 | 50 | 001:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE | P22020900035 | New_Event |  |  | Include | Wildlife | 61 | 2022-02-09 | 3050 | keep | 0 | Feb | 2022 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-09 12:08 | 2022-02-09 14:37 | 11 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22020900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-02-09 | 1639 | keep | 0 | Feb | 2022 | 0.0011163 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-02-09 12:10 | 2022-02-09 12:12 | 2234 | 000:02 | T | ESTRUCTURA AVERIADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22020900044 | Additional_clients | Defective Pole | Include | Include | Equipment | 2 | 2022-02-09 | 4468 | keep | 0 | Feb | 2022 | 0.0030431 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-09 12:12 | 2022-02-09 19:55 | 20 | 007:43 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B22020900034 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 463 | 2022-02-09 | 9260 | keep | 0 | Feb | 2022 | 0.0063069 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-09 12:12 | 2022-02-09 17:31 | 40 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 50 EN CORTE DE LINEA | B22020900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-02-09 | 12760 | keep | 0 | Feb | 2022 | 0.0086908 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-09 12:33 | 2022-02-09 14:03 | 10 | 001:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | B22020800047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 90 | 2022-02-09 | 900 | keep | 0 | Feb | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-09 12:43 | 2022-02-09 17:50 | 25 | 005:07 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 30 EN CORTE DE LINEA | B22020900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 307 | 2022-02-09 | 7675 | keep | 0 | Feb | 2022 | 0.0052274 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-02-09 12:43 | 2022-02-09 16:00 | 8 | 003:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE LEVANTO LINEA SECUNDARIA | P22020900039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 197 | 2022-02-09 | 1576 | keep | 0 | Feb | 2022 | 0.0010734 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-09 12:47 | 2022-02-09 15:00 | 200 | 002:13 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | C22020900065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-02-09 | 26600 | keep | 0 | Feb | 2022 | 0.018117 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-02-09 12:57 | 2022-02-09 14:01 | 15 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR TOMA Y SECUNDARIA | C22020900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-02-09 | 960 | keep | 0 | Feb | 2022 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-09 13:04 | 2022-02-09 13:45 | 13 | 000:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REPARAR SECUNDARIA | C22020900069 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 41 | 2022-02-09 | 533 | keep | 0 | Feb | 2022 | 0.00036302 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-02-09 13:10 | 2022-02-09 16:37 | 13 | 003:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22020900070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 207 | 2022-02-09 | 2691 | keep | 0 | Feb | 2022 | 0.0018328 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-02-09 13:10 | 2022-02-09 17:00 | 30 | 003:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-02-09 | 6900 | keep | 0 | Feb | 2022 | 0.0046996 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-09 13:10 | 2022-02-09 15:10 | 8 | 002:00 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A22020900040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 120 | 2022-02-09 | 960 | keep | 0 | Feb | 2022 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-02-09 13:13 | 2022-02-09 16:48 | 25 | 003:35 | P | PARARRAYOS DEFECTUOSO | 1X50 EN CORTE DE LINEA Y SE ELIMINO PARARRAYOS DESTRUIDO | R22090900027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 215 | 2022-02-09 | 5375 | keep | 0 | Feb | 2022 | 0.0036609 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-09 13:15 | 2022-02-09 17:02 | 1879 | 003:47 | T | NO SE REPORTO CAUSA | DISPARO | C22020900074 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-02-09 | 426533 | keep | 0 | Feb | 2022 | 0.29051 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-09 13:40 | 2022-02-09 19:31 | 80 | 005:51 | P | DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE | R22020900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2022-02-09 | 28080 | keep | 0 | Feb | 2022 | 0.019125 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-09 14:01 | 2022-02-09 15:42 | 12 | 001:41 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA DESGANCHE | B22020900016 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 101 | 2022-02-09 | 1212 | keep | 0 | Feb | 2022 | 0.00082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-09 14:15 | 2022-02-09 14:16 | 650 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22020900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 650 | keep | 0 | Feb | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
ARECIBO | 2022-02-09 14:15 | 2022-02-09 20:40 | 5 | 006:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA POR 25 KVA | A22020900047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 385 | 2022-02-09 | 1925 | keep | 0 | Feb | 2022 | 0.0013111 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-09 14:40 | 2022-02-09 15:18 | 6 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22020900014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-02-09 | 228 | keep | 0 | Feb | 2022 | 0.00015529 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-09 14:48 | 2022-02-09 16:40 | 15 | 001:52 | P | ESTRUCTURA AVERIADA | REEMPLAZO DE POSTE CON TRANSFORMADOR. TRABAJOS SE REALIZARON COMO NO PROGRAMADO | S22020900075 | New_Event | Defective Pole | Include | Include | Equipment | 112 | 2022-02-09 | 1680 | keep | 0 | Feb | 2022 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-09 15:11 | 2022-02-09 15:12 | 2362 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22020900000 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-09 | 2362 | keep | 0 | Feb | 2022 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
BARRANQUITAS | 2022-02-09 15:12 | 2022-02-09 18:52 | 400 | 003:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTES DE LINEA CRUCE CON LAGARTO | C22020900134 | 1st_after_momentary |  |  | Include | Wildlife | 220 | 2022-02-09 | 88000 | keep | 0 | Feb | 2022 | 0.059936 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
GUAYAMA | 2022-02-09 15:21 | 2022-02-09 16:08 | 6 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO DE CONEXIONES EN LINEA SECUNDARIA | P22020900055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2022-02-09 | 282 | keep | 0 | Feb | 2022 | 0.00019207 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-09 15:24 | 2022-02-09 19:35 | 10 | 004:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA | B22020900078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 251 | 2022-02-09 | 2510 | keep | 0 | Feb | 2022 | 0.0017095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-09 15:35 | 2022-02-09 17:06 | 12 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22020900052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2022-02-09 | 1092 | keep | 0 | Feb | 2022 | 0.00074376 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-09 15:54 | 2022-02-09 22:10 | 60 | 006:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22020900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2022-02-09 | 22560 | keep | 0 | Feb | 2022 | 0.015366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-09 16:10 | 2022-02-09 18:21 | 36 | 002:11 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | R22020900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-02-09 | 4716 | keep | 0 | Feb | 2022 | 0.003212 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2022-02-09 16:24 | 2022-02-09 21:06 | 75 | 004:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22020900093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2022-02-09 | 21150 | keep | 0 | Feb | 2022 | 0.014405 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-09 16:25 | 2022-02-09 20:04 | 35 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22020900085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-02-09 | 7665 | keep | 0 | Feb | 2022 | 0.0052206 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-02-09 16:29 | 2022-02-09 21:24 | 80 | 004:55 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S22020900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2022-02-09 | 23600 | keep | 0 | Feb | 2022 | 0.016074 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-02-09 16:35 | 2022-02-09 17:43 | 4 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN CORTE DE LINEA CRUCE CON CONDUCTOR | C22020900132 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-02-09 | 272 | keep | 0 | Feb | 2022 | 0.00018526 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-09 16:46 | 2022-02-09 18:50 | 60 | 002:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B22020900099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-02-09 | 7440 | keep | 0 | Feb | 2022 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-02-09 16:59 | 2022-02-09 18:02 | 125 | 001:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22020900058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-02-09 | 7875 | keep | 0 | Feb | 2022 | 0.0053636 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-02-09 17:02 | 2022-02-09 17:52 | 1500 | 000:50 | P | NO SE REPORTO CAUSA | DISPARO SE TRANSFIRIO PARTE DE LA CARGA AL 3006-01 | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 50 | 2022-02-09 | 75000 | keep | 0 | Feb | 2022 | 0.051082 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-09 17:10 | 2022-02-09 21:18 | 250 | 004:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L SE REEMPLAZARON 3 CAJAS AVERIADAS | B22020900106 | New_Event | Cutout Failure | Include | Include | Equipment | 248 | 2022-02-09 | 62000 | keep | 0 | Feb | 2022 | 0.042228 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-02-09 17:29 | 2022-02-09 17:49 | 1 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-A3A | R22020900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-02-09 | 20 | keep | 0 | Feb | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-09 17:30 | 2022-02-09 18:26 | 1 | 000:56 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJA TRANSFORMADOR PARA REMPLAZO BUSHING SECUNDARIO | A22020900060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 56 | 2022-02-09 | 56 | keep | 0 | Feb | 2022 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-09 17:52 | 2022-02-09 18:09 | 1400 | 000:17 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-02-09 | 23800 | keep | 0 | Feb | 2022 | 0.01621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-09 18:09 | 2022-02-09 18:21 | 1250 | 000:12 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-02-09 | 15000 | keep | 0 | Feb | 2022 | 0.010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-09 18:18 | 2022-02-09 19:22 | 15 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22020900107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-02-09 | 960 | keep | 0 | Feb | 2022 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-09 18:21 | 2022-02-09 18:44 | 1200 | 000:23 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-02-09 | 27600 | keep | 0 | Feb | 2022 | 0.018798 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-09 18:36 | 2022-02-09 18:45 | 1 | 000:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER @ BOMBAS | R22020900063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-02-09 | 9 | keep | 0 | Feb | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-09 18:36 | 2022-02-09 19:25 | 1117 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 SE ENERGIZO A TRAVES DE LA LINEA 1600 | M22020900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2022-02-09 | 54733 | keep | 0 | Feb | 2022 | 0.037278 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-02-09 18:36 | 2022-02-09 19:25 | 1671 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 SE ENERGIZO A TRAVES DE LA LINEA 1600 | M22020900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2022-02-09 | 81879 | keep | 0 | Feb | 2022 | 0.055767 | 0.0011381 | Sustained | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2022-02-09 18:36 | 2022-02-09 19:25 | 527 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 SE ENERGIZO A TRAVES DE LA LINEA 1600 | M22020900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2022-02-09 | 25823 | keep | 0 | Feb | 2022 | 0.017588 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2022-02-09 18:36 | 2022-02-09 19:25 | 671 | 000:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 SE ENERGIZO A TRAVES DE LA LINEA 1600 | M22020900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2022-02-09 | 32879 | keep | 0 | Feb | 2022 | 0.022394 | 0.00045702 | Sustained | FALSE | FALSE | Not_TMED_Event | 671
CAGUAS | 2022-02-09 18:44 | 2022-02-09 18:52 | 1170 | 000:08 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-09 | 9360 | keep | 0 | Feb | 2022 | 0.0063751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-09 18:49 | 2022-02-09 18:50 | 1510 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22020900146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 1510 | keep | 0 | Feb | 2022 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2022-02-09 18:52 | 2022-02-09 19:07 | 1120 | 000:15 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-02-09 | 16800 | keep | 0 | Feb | 2022 | 0.011442 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-02-09 18:52 | 2022-02-09 19:30 | 100 | 000:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22020900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-02-09 | 3800 | keep | 0 | Feb | 2022 | 0.0025882 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-09 19:07 | 2022-02-10 00:15 | 25 | 005:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S22020900102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2022-02-09 | 7700 | keep | 0 | Feb | 2022 | 0.0052444 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-09 19:07 | 2022-02-09 19:11 | 990 | 000:04 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-09 | 3960 | keep | 0 | Feb | 2022 | 0.0026971 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-02-09 19:09 | 2022-02-10 09:25 | 25 | 014:16 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE DESCONECTO PARARRAYOS AVERIADO | A22020900064 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 856 | 2022-02-09 | 21400 | keep | 0 | Feb | 2022 | 0.014575 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-09 19:10 | 2022-02-10 09:35 | 10 | 014:25 | P | NO SE REPORTO CAUSA | 2X10 EN TRANSFORMADOR | C22020900150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 865 | 2022-02-09 | 8650 | keep | 0 | Feb | 2022 | 0.0058915 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-09 19:11 | 2022-02-09 23:35 | 70 | 004:24 | P | DESGANCHE | SE ABRIO CORTE DE LINEA POR CONDUCTOR VIVO EN EL SUELO (NO FUNDIO) | S22020900105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-02-09 | 18480 | keep | 0 | Feb | 2022 | 0.012587 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-02-09 19:11 | 2022-02-09 19:18 | 860 | 000:07 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-02-09 | 6020 | keep | 0 | Feb | 2022 | 0.0041002 | 0.00058574 | Sustained | FALSE | FALSE | Not_TMED_Event | 860
CAGUAS | 2022-02-09 19:18 | 2022-02-09 19:27 | 830 | 000:09 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES | C22020900074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-02-09 | 7470 | keep | 0 | Feb | 2022 | 0.0050878 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-09 19:24 | 2022-02-09 19:25 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22020900122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 990 | keep | 0 | Feb | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2022-02-09 19:29 | 2022-02-09 21:50 | 1 | 002:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A22020900065 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2022-02-09 | 141 | keep | 0 | Feb | 2022 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-09 19:32 | 2022-02-10 09:43 | 1 | 014:11 | P | NO SE REPORTO CAUSA | 2 X 25 EN C/L | B22020900118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 851 | 2022-02-09 | 851 | keep | 0 | Feb | 2022 | 0.00057961 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-09 19:54 | 2022-02-10 11:04 | 200 | 015:10 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22020900109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 910 | 2022-02-09 | 182000 | keep | 0 | Feb | 2022 | 0.12396 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-02-09 19:56 | 2022-02-09 21:06 | 30 | 001:10 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | R22020900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-02-09 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-09 20:00 | 2022-02-09 20:30 | 20 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22020900121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-02-09 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-09 20:50 | 2022-02-10 15:53 | 7 | 019:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 25 KVA | A22020900067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1143 | 2022-02-09 | 8001 | keep | 0 | Feb | 2022 | 0.0054494 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-09 20:57 | 2022-02-10 14:00 | 20 | 017:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L Y SE REEMPLAZO PORTA FUSIBLE | B22020900164 | New_Event | Cutout Failure | Include | Include | Equipment | 1023 | 2022-02-09 | 20460 | keep | 0 | Feb | 2022 | 0.013935 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-09 21:18 | 2022-02-10 01:28 | 652 | 004:10 | S | PROTECCION DEFECTUOSA | EN AVERIA DE CAJAS AVERIADAS DEL 9201-02 FUNDIO DOS FUSIBLES DE LA ALTA DEL XMR 9201-00. SE REEMPLAZO DOS FUSIBLES, SE NORMALIZO LA CARGA DEL 9201-01 Y SE TRANSFIRIO LA CARGA DEL 9201-02 POR EL 9201-03. BKR 9201-02 CON BATERIAS 48V DAÃ‘ADAS | B22020900142 | New_Event | Protection Miscoordination | Include | Include | Other | 250 | 2022-02-09 | 163000 | keep | 0 | Feb | 2022 | 0.11102 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-02-09 21:18 | 2022-02-10 01:36 | 2704 | 004:18 | S | PROTECCION DEFECTUOSA | EN AVERIA DE CAJAS AVERIADAS DEL 9201-02 FUNDIO DOS FUSIBLES DE LA ALTA DEL XMR 9201-00. SE REEMPLAZO DOS FUSIBLES, SE NORMALIZO LA CARGA DEL 9201-01 Y SE TRANSFIRIO LA CARGA DEL 9201-02 POR EL 9201-03. BKR 9201-02 CON BATERIAS 48V DAÃ‘ADAS | B22020900142 | New_Event | Protection Miscoordination | Include | Include | Other | 258 | 2022-02-09 | 697632 | keep | 0 | Feb | 2022 | 0.47515 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2022-02-09 21:21 | 2022-02-09 21:22 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22020900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-09 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
VEGA BAJA | 2022-02-09 21:44 | 2022-02-10 09:57 | 35 | 012:13 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22020900184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 733 | 2022-02-09 | 25655 | keep | 0 | Feb | 2022 | 0.017474 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-02-09 22:00 | 2022-02-09 22:35 | 10 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | M22020900037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-02-09 | 350 | keep | 0 | Feb | 2022 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-09 22:16 | 2022-02-10 04:25 | 80 | 006:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22020900124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-02-09 | 29520 | keep | 0 | Feb | 2022 | 0.020106 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-09 22:23 | 2022-02-09 22:46 | 1 | 000:23 | P | OTRAS CAUSAS | 3 X 30 EN RISER @ SUB. LECHONERA GABY, RISER ADYACENTE DE REVISTA HIPICA CON PROBLEMA INTERIOR CAUSO QUE FUNDIERA RISER DE LECHONERA | R22020900077 | New_Event | Other Causes | Include | Include | Other | 23 | 2022-02-09 | 23 | keep | 0 | Feb | 2022 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-09 23:35 | 2022-02-10 00:40 | 150 | 001:05 | P | DESGANCHE | SE REALIZO DESGANCHE, SE LEVANTO CONDUCTOR Y SE CERRO C/L (NO FUNDIO) | S22020900105 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-02-09 | 9750 | keep | 0 | Feb | 2022 | 0.0066407 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-10 02:13 | 2022-02-10 11:48 | 15 | 009:35 | P | NO SE REPORTO CAUSA | 1X30 EN CORTE DE LINEA | C22021000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 575 | 2022-02-10 | 8625 | keep | 0 | Feb | 2022 | 0.0058744 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-10 03:04 | 2022-02-10 05:05 | 1979 | 002:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION AVE CRUZO FASE EN LA SALIDA DEL TRANSFORMADOR | P22021000027 | New_Event |  |  | Include | Wildlife | 121 | 2022-02-10 | 239459 | keep | 0 | Feb | 2022 | 0.16309 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2022-02-10 03:04 | 2022-02-10 05:05 | 3114 | 002:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION AVE CRUZO FASE EN LA SALIDA DEL TRANSFORMADOR | P22021000058 | New_Event |  |  | Include | Wildlife | 121 | 2022-02-10 | 376794 | keep | 0 | Feb | 2022 | 0.25663 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-02-10 03:04 | 2022-02-10 05:05 | 5069 | 002:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION AVE CRUZO FASE EN LA SALIDA DEL TRANSFORMADOR | P22021000027 | New_Event |  |  | Include | Wildlife | 121 | 2022-02-10 | 613349 | keep | 0 | Feb | 2022 | 0.41775 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-02-10 03:04 | 2022-02-10 05:05 | 2696 | 002:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION AVE CRUZO FASE EN LA SALIDA DEL TRANSFORMADOR | P22021000027 | New_Event |  |  | Include | Wildlife | 121 | 2022-02-10 | 326216 | keep | 0 | Feb | 2022 | 0.22218 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-02-10 03:04 | 2022-02-10 06:48 | 5063 | 003:44 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION AVE CRUZO FASE EN LA SALIDA DEL TRANSFORMADOR | P22021000055 | New_Event |  |  | Include | Wildlife | 224 | 2022-02-10 | 1134112 | keep | 0 | Feb | 2022 | 0.77244 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
MAYAGÃœEZ | 2022-02-10 03:08 | 2022-02-10 10:24 | 75 | 007:16 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA DISTINTOS SE RETIRO RAMAS SOBRE LAS LINEAS | M22021000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2022-02-10 | 32700 | keep | 0 | Feb | 2022 | 0.022272 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-02-10 03:28 | 2022-02-10 05:53 | 60 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN PROVISIONAL AEREO | R22021000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-02-10 | 8700 | keep | 0 | Feb | 2022 | 0.0059255 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-10 03:50 | 2022-02-10 11:23 | 150 | 007:33 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | M22021000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 453 | 2022-02-10 | 67950 | keep | 0 | Feb | 2022 | 0.04628 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-02-10 04:16 | 2022-02-10 09:21 | 42 | 005:05 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22021000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2022-02-10 | 12810 | keep | 0 | Feb | 2022 | 0.0087248 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CANOVANAS | 2022-02-10 04:27 | 2022-02-10 09:08 | 52 | 004:41 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | R22021000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2022-02-10 | 14612 | keep | 0 | Feb | 2022 | 0.0099522 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
HUMACAO | 2022-02-10 04:58 | 2022-02-10 10:32 | 50 | 005:34 | P | DESGANCHE | 1X100 EN CORTE DE LINEA Y SE RETIRO UNA RAMA | C22021000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2022-02-10 | 16700 | keep | 0 | Feb | 2022 | 0.011374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-10 06:08 | 2022-02-10 08:27 | 15 | 002:19 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN XMR SE REPARO TERMINACION | R22021000013 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 139 | 2022-02-10 | 2085 | keep | 0 | Feb | 2022 | 0.0014201 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-10 06:26 | 2022-02-10 09:38 | 35 | 003:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA INFORMA FOREMAN REQUIERE DESGANCHE | M22021000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-02-10 | 6720 | keep | 0 | Feb | 2022 | 0.004577 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-02-10 06:40 | 2022-02-10 11:46 | 40 | 005:06 | P | DESGANCHE | 1X50 Y 1X30 EN DISTINTOS CORTES DE LINEA Y SE RETIRARON VARIAS RAMAS DEL 8KV | C22021000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-02-10 | 12240 | keep | 0 | Feb | 2022 | 0.0083366 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-02-10 06:43 | 2022-02-10 14:30 | 236 | 007:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R22021000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2022-02-10 | 110212 | keep | 0 | Feb | 2022 | 0.075065 | 0.00016074 | Sustained | FALSE | FALSE | Not_TMED_Event | 236
SAN JUAN | 2022-02-10 07:01 | 2022-02-10 12:41 | 5 | 005:40 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | R22021000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2022-02-10 | 1700 | keep | 0 | Feb | 2022 | 0.0011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-02-10 07:21 | 2022-02-10 10:26 | 50 | 003:05 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P22021000080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-02-10 | 9250 | keep | 0 | Feb | 2022 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-10 07:23 | 2022-02-10 16:08 | 5 | 008:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 15KVA POR 25KVA Y SE REPUSIERON 2X10 EN TRANSFORMADOR | C22021000014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 525 | 2022-02-10 | 2625 | keep | 0 | Feb | 2022 | 0.0017879 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-10 07:39 | 2022-02-10 07:40 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 4381 | keep | 0 | Feb | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
PONCE | 2022-02-10 07:45 | 2022-02-10 07:46 | 5063 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021000083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 5063 | keep | 0 | Feb | 2022 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
SAN JUAN | 2022-02-10 07:59 | 2022-02-10 09:58 | 2000 | 001:59 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 1619-02 LELVANDO PARTE DE LA CARGA DEL 1336-06 NO CERRO POR SCADA SE CERRO EN LA SUBESTACION | R22021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-02-10 | 238000 | keep | 0 | Feb | 2022 | 0.1621 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-02-10 08:13 | 2022-02-10 11:00 | 275 | 002:47 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B22021000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-02-10 | 45925 | keep | 0 | Feb | 2022 | 0.031279 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
BARRANQUITAS | 2022-02-10 08:14 | 2022-02-10 10:07 | 10 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1X10 EN TRANSFORMADOR POR MAL TIEMPO Y LLUVIAS EN EL AREA | C22021000018 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-02-10 | 1130 | keep | 0 | Feb | 2022 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-10 08:39 | 2022-02-10 14:35 | 9 | 005:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES EN BAJANTE SECUNDARIO DEL TRANSFORMADOR | C22021000024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 356 | 2022-02-10 | 3204 | keep | 0 | Feb | 2022 | 0.0021822 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-02-10 08:45 | 2022-02-10 09:30 | 5 | 000:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22021000004 | New_Event | Wire Down | Include | Include | Equipment | 45 | 2022-02-10 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-02-10 09:01 | 2022-02-10 09:02 | 1415 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021000036 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-02-10 | 1415 | keep | 0 | Feb | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
VEGA BAJA | 2022-02-10 09:07 | 2022-02-10 11:02 | 22 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22021000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-02-10 | 2530 | keep | 0 | Feb | 2022 | 0.0017232 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2022-02-10 09:25 | 2022-02-10 10:39 | 12 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22021000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-02-10 | 888 | keep | 0 | Feb | 2022 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-10 09:37 | 2022-02-10 18:28 | 40 | 008:51 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE PRIMARIO CON TRANSFORMADOR | R22021000076 | New_Event | Defective Pole | Include | Include | Equipment | 531 | 2022-02-10 | 21240 | keep | 0 | Feb | 2022 | 0.014466 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-02-10 09:37 | 2022-02-10 11:02 | 7 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE | P22021000091 | New_Event |  |  | Include | Wildlife | 85 | 2022-02-10 | 595 | keep | 0 | Feb | 2022 | 0.00040525 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-02-10 09:38 | 2022-02-10 12:36 | 10 | 002:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 50KVA | C22021000035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 178 | 2022-02-10 | 1780 | keep | 0 | Feb | 2022 | 0.0012123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-10 09:51 | 2022-02-10 13:36 | 1 | 003:45 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | C22021000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2022-02-10 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-10 09:52 | 2022-02-10 12:39 | 60 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22021000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2022-02-10 | 10020 | keep | 0 | Feb | 2022 | 0.0068246 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-10 10:10 | 2022-02-10 10:59 | 15 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22020900059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2022-02-10 | 735 | keep | 0 | Feb | 2022 | 0.00050061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-10 10:13 | 2022-02-10 13:28 | 6 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22021000028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-02-10 | 1170 | keep | 0 | Feb | 2022 | 0.00079688 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-02-10 10:15 | 2022-02-10 12:51 | 10 | 002:36 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHE CON WR-6010918 Y SE VOLVIO A CERRAR LUEGO DE CONCLUIDOS LOS TRABAJOS | C22021000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-02-10 | 1560 | keep | 0 | Feb | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-10 10:18 | 2022-02-10 14:14 | 30 | 003:56 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22020100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-02-10 | 7080 | keep | 0 | Feb | 2022 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-10 10:21 | 2022-02-10 14:12 | 8 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 10 XMR | B22021000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2022-02-10 | 1848 | keep | 0 | Feb | 2022 | 0.0012587 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-10 10:37 | 2022-02-10 10:38 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 3X50 EN CORTE DE LINEA Y 3X15 EN RISER | C22021000142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 1 | keep | 0 | Feb | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-10 10:42 | 2022-02-10 13:32 | 200 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22021000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-02-10 | 34000 | keep | 0 | Feb | 2022 | 0.023157 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-02-10 10:50 | 2022-02-10 21:40 | 18 | 010:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R22021000131 | New_Event | Service Transformer Failure | Include | Include | Equipment | 650 | 2022-02-10 | 11700 | keep | 0 | Feb | 2022 | 0.0079688 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-02-10 10:58 | 2022-02-10 10:59 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22021000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 1227 | keep | 0 | Feb | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CAGUAS | 2022-02-10 11:02 | 2022-02-10 15:18 | 15 | 004:16 | P | DESGANCHE | 1X30 EN CORTE DE LINEA Y SE DESGANCHO BAMBUAS | C22021000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-02-10 | 3840 | keep | 0 | Feb | 2022 | 0.0026154 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-10 11:06 | 2022-02-10 12:14 | 6 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 20 DE RISER @ T-39 | B22021000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-02-10 | 408 | keep | 0 | Feb | 2022 | 0.00027789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-10 11:29 | 2022-02-10 13:00 | 30 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22021000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-02-10 | 2730 | keep | 0 | Feb | 2022 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-10 11:32 | 2022-02-11 13:44 | 12 | 026:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | M22021000063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1572 | 2022-02-10 | 18864 | keep | 0 | Feb | 2022 | 0.012848 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-02-10 11:39 | 2022-02-10 11:40 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220210000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 4279 | keep | 0 | Feb | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
ARECIBO | 2022-02-10 11:40 | 2022-02-10 12:50 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22021000012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-02-10 | 700 | keep | 0 | Feb | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-02-10 11:54 | 2022-02-10 14:12 | 4 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA Y REPTIL | R22021000142 | New_Event |  |  | Include | Wildlife | 138 | 2022-02-10 | 552 | keep | 0 | Feb | 2022 | 0.00037596 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-10 11:58 | 2022-02-10 15:00 | 1 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | B22021000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-02-10 | 182 | keep | 0 | Feb | 2022 | 0.00012396 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-10 12:12 | 2022-02-10 19:20 | 60 | 007:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEA Y SE REALIZO DESGANCHE | M22021000065 | New_Event | Wire Down | Include | Include | Equipment | 428 | 2022-02-10 | 25680 | keep | 0 | Feb | 2022 | 0.017491 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-10 12:39 | 2022-02-10 13:17 | 13 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22021000019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-02-10 | 494 | keep | 0 | Feb | 2022 | 0.00033646 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2022-02-10 12:42 | 2022-02-10 12:43 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22021000058 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-10 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-02-10 12:43 | 2022-02-10 14:23 | 8 | 001:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X25 EN C/L Y SE RETIRO AVE DEL TENDIDO ELECTRICO | C22021000061 | 1st_after_momentary |  |  | Include | Wildlife | 100 | 2022-02-10 | 800 | keep | 0 | Feb | 2022 | 0.00054488 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-02-10 12:45 | 2022-02-10 14:25 | 50 | 001:40 | P | DESGANCHE | 1 X 65 EN CORTE LINEA CRUCE DE FASE PRIMARIA POR BAMBU | P22021000106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-02-10 | 5000 | keep | 0 | Feb | 2022 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-10 12:45 | 2022-02-10 13:45 | 6 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B22021000125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-02-10 | 360 | keep | 0 | Feb | 2022 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-02-10 12:51 | 2022-02-10 12:59 | 2635 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LUEGO DE CONFIRMAR PERSONAL FUERA DEL 8KV | C22021000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-10 | 21080 | keep | 0 | Feb | 2022 | 0.014357 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
VEGA BAJA | 2022-02-10 12:58 | 2022-02-10 15:09 | 20 | 002:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA POR UNO DE 50 KVA | B22021000049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 131 | 2022-02-10 | 2620 | keep | 0 | Feb | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-10 12:59 | 2022-02-10 13:42 | 10 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22020900191 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-02-10 | 430 | keep | 0 | Feb | 2022 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-10 12:59 | 2022-02-10 15:51 | 10 | 002:52 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHE CON WR-6010918 Y SE VOLVIO A CERRAR LUEGO DE CONCLUIDOS LOS TRABAJOS | C22021000034 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-02-10 | 1720 | keep | 0 | Feb | 2022 | 0.0011715 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-10 13:05 | 2022-02-10 15:58 | 15 | 002:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 25KVA | C22021000065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 173 | 2022-02-10 | 2595 | keep | 0 | Feb | 2022 | 0.0017674 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-10 13:30 | 2022-02-10 22:00 | 1 | 008:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR UNO DE 10KVA | A22021000045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 510 | 2022-02-10 | 510 | keep | 0 | Feb | 2022 | 0.00034736 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-02-10 13:30 | 2022-02-10 15:03 | 8 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22021000042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2022-02-10 | 744 | keep | 0 | Feb | 2022 | 0.00050674 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-02-10 13:32 | 2022-02-10 15:30 | 12 | 001:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22021000046 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 118 | 2022-02-10 | 1416 | keep | 0 | Feb | 2022 | 0.00096443 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-10 13:53 | 2022-02-10 16:02 | 60 | 002:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22021000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-02-10 | 7740 | keep | 0 | Feb | 2022 | 0.0052717 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-10 14:08 | 2022-02-10 14:10 | 3295 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | B22021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-10 | 6590 | keep | 0 | Feb | 2022 | 0.0044884 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
CAGUAS | 2022-02-10 14:23 | 2022-02-10 15:44 | 6 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS EN PEDESTAL | C22021000081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2022-02-10 | 486 | keep | 0 | Feb | 2022 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-10 14:33 | 2022-02-10 16:29 | 50 | 001:56 | P | DESGANCHE | 1X100 EN CORTE DE LINEA Y SE RETIRO ARBOL DEL TENDIDO ELECTRICO PRIMARIO | C22021000082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-02-10 | 5800 | keep | 0 | Feb | 2022 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-10 14:43 | 2022-02-10 19:09 | 4 | 004:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR SE REPARO SECUNDARIA Y BARRAS EN PEDESTAL | B22020900068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 266 | 2022-02-10 | 1064 | keep | 0 | Feb | 2022 | 0.00072469 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-02-10 14:45 | 2022-02-10 15:15 | 108 | 000:30 | T | DESGANCHE | ARBOL CAYO SOBRE LINEA PRIMARIA TUMBO 4 POSTES SJ-220210-01 | S22021000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-02-10 | 3240 | keep | 0 | Feb | 2022 | 0.0022067 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
VEGA BAJA | 2022-02-10 15:00 | 2022-02-10 15:01 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 6 | keep | 0 | Feb | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-10 15:15 | 2022-02-10 16:04 | 60 | 000:49 | P | DESGANCHE | ARBOL CAYO SOBRE LINEA PRIMARIA TUMBO 4 POSTES SJ-220210-01 | S22021000065 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-02-10 | 2940 | keep | 0 | Feb | 2022 | 0.0020024 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-10 15:20 | 2022-02-10 19:28 | 50 | 004:08 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGACHE | B22021000071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-02-10 | 12400 | keep | 0 | Feb | 2022 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-10 15:25 | 2022-02-10 15:26 | 3902 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021000085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 3902 | keep | 0 | Feb | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2022-02-10 15:26 | 2022-02-10 16:45 | 32 | 001:19 | P | NO SE REPORTO CAUSA | 1X30 EN CORTE DE LINEA | C22021000086 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-02-10 | 2528 | keep | 0 | Feb | 2022 | 0.0017218 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2022-02-10 15:29 | 2022-02-11 17:36 | 12 | 026:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA POR UNO DE 50KVA | S22021000073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1567 | 2022-02-10 | 18804 | keep | 0 | Feb | 2022 | 0.012807 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-10 15:30 | 2022-02-10 18:30 | 8 | 003:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR LINEA SECUNDARIA POR POSTE PARTIDO | M22021000070 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 180 | 2022-02-10 | 1440 | keep | 0 | Feb | 2022 | 0.00098078 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-02-10 15:48 | 2022-02-10 22:20 | 70 | 006:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021000078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-02-10 | 27440 | keep | 0 | Feb | 2022 | 0.018689 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-02-10 15:54 | 2022-02-10 17:45 | 60 | 001:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22021000079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-02-10 | 6660 | keep | 0 | Feb | 2022 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-02-10 15:56 | 2022-02-10 17:38 | 20 | 001:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22021000114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-02-10 | 2040 | keep | 0 | Feb | 2022 | 0.0013894 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-02-10 16:00 | 2022-02-10 23:47 | 472 | 007:47 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE COLOCA PUENTE PRIMARIO | M22021000083 | New_Event | Switch Failure | Include | Include | Equipment | 467 | 2022-02-10 | 220424 | keep | 0 | Feb | 2022 | 0.15013 | 0.00032148 | Sustained | FALSE | FALSE | Not_TMED_Event | 472
ARECIBO | 2022-02-10 16:03 | 2022-02-10 16:04 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22021000058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-10 | 2107 | keep | 0 | Feb | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
SAN JUAN | 2022-02-10 16:04 | 2022-02-10 23:59 | 40 | 007:55 | P | DESGANCHE | SE ABRIO PUENTES Y SE CERRO MACHETES PARA DARLE SERVICIO A MAS CLIENTES Y CONTINUAR MAÃ‘ANA CON EL GOI SJ-220910-01B. ARBOL CAYO SOBRE LINEA PRIMARIA TUMBO 4 POSTES SJ-220210-01 | S22021000065 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 475 | 2022-02-10 | 19000 | keep | 0 | Feb | 2022 | 0.012941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-10 16:09 | 2022-02-10 16:44 | 12 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO PEDESTAL Y BARRAS DE PEDESTAL | C22021000094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-02-10 | 420 | keep | 0 | Feb | 2022 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-02-10 16:11 | 2022-02-10 17:11 | 160 | 001:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22021000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-02-10 | 9600 | keep | 0 | Feb | 2022 | 0.0065385 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2022-02-10 16:46 | 2022-02-10 21:19 | 80 | 004:33 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22021000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2022-02-10 | 21840 | keep | 0 | Feb | 2022 | 0.014875 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-10 16:52 | 2022-02-11 19:28 | 8 | 026:36 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO CAJAS SECAS EN MH-2 Y MH-17 Y 1 X 100 EN SU-10 | S22021000079 | New_Event | Switch Failure | Include | Include | Equipment | 1596 | 2022-02-10 | 12768 | keep | 0 | Feb | 2022 | 0.0086962 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-02-10 16:53 | 2022-02-10 19:05 | 637 | 002:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO 2 AISLADORES Y SE TIRO PALOMA | R22021000177 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 132 | 2022-02-10 | 84084 | keep | 0 | Feb | 2022 | 0.057269 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
CAGUAS | 2022-02-10 16:58 | 2022-02-10 21:00 | 4 | 004:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO LINEA SECUNDARIA DERRIBADA POR CAMION | C22021000103 | New_Event |  |  | Include | Wildlife | 242 | 2022-02-10 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-02-10 16:58 | 2022-02-10 17:38 | 5 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22021000091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-02-10 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-02-10 17:19 | 2022-02-10 23:08 | 140 | 005:49 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE DESGANCHO ARBOL SOBRE LINEAS Y REPARO CONDUCTOR ROTO | C22021000110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2022-02-10 | 48860 | keep | 0 | Feb | 2022 | 0.033278 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
PONCE | 2022-02-10 17:19 | 2022-02-10 19:44 | 20 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P22021000121 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2022-02-10 | 2900 | keep | 0 | Feb | 2022 | 0.0019752 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-10 17:21 | 2022-02-11 12:30 | 9 | 019:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONEXIONES DE LA SECUNDARIA Y SE BAJO TAP DEL 4 AL 2 SE DEJO EN 125 VOLTIOS | C22021000111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1149 | 2022-02-10 | 10341 | keep | 0 | Feb | 2022 | 0.0070432 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-02-10 17:55 | 2022-02-10 22:26 | 100 | 004:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021000096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-02-10 | 27100 | keep | 0 | Feb | 2022 | 0.018458 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-10 17:56 | 2022-02-10 19:20 | 10 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R22021000177 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2022-02-10 | 840 | keep | 0 | Feb | 2022 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-10 18:30 | 2022-02-11 10:00 | 7 | 015:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | C22021000131 | New_Event |  |  | Include | Wildlife | 930 | 2022-02-10 | 6510 | keep | 0 | Feb | 2022 | 0.0044339 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-02-10 18:38 | 2022-02-10 19:26 | 160 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22021000216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-02-10 | 7680 | keep | 0 | Feb | 2022 | 0.0052308 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
PONCE | 2022-02-10 18:54 | 2022-02-10 20:39 | 100 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA EN CORTE DE LINEA | P22021000125 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2022-02-10 | 10500 | keep | 0 | Feb | 2022 | 0.0071515 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-02-10 19:07 | 2022-02-10 21:28 | 100 | 002:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22021000141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-02-10 | 14100 | keep | 0 | Feb | 2022 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-10 20:10 | 2022-02-11 09:32 | 12 | 013:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN CORTE DE LINEA SE REMPLAZO MACETILLA DE CAJA PRIMARIA AVERIADA | A22021000072 | New_Event | Cutout Failure | Include | Include | Equipment | 802 | 2022-02-10 | 9624 | keep | 0 | Feb | 2022 | 0.0065549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-10 20:15 | 2022-02-10 21:53 | 10 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22021000108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-02-10 | 980 | keep | 0 | Feb | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-10 21:02 | 2022-02-10 21:11 | 30 | 000:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CAJAS EN CORTE DE LINEA PARA REMPLAZAR HOT CLAMP QUEMADO | P22021000132 | New_Event | Wire Down | Include | Include | Equipment | 9 | 2022-02-10 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-10 22:02 | 2022-02-11 01:59 | 200 | 003:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22021000119 | New_Event |  |  | Include | Wildlife | 237 | 2022-02-10 | 47400 | keep | 0 | Feb | 2022 | 0.032284 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-02-10 23:13 | 2022-02-11 02:05 | 195 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN VIVO EN MACHETE | B22021000084 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2022-02-10 | 33540 | keep | 0 | Feb | 2022 | 0.022844 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
AGUADILLA | 2022-02-10 23:47 | 2022-02-11 00:12 | 1415 | 000:25 | T | DESCONECTIVO DEFECTUOSO | SE INSTALO PUENTE PROVISIONAL PARA ENERGIZAR LA LINEA HAY QUE REMPLAZAR MACHETE SE CREA WR6055989 PARA REMPLAZO DE MACHETES | M22021000125 | Additional_clients | Switch Failure | Include | Include | Equipment | 25 | 2022-02-10 | 35375 | keep | 0 | Feb | 2022 | 0.024094 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-10 23:59 | 2022-02-11 02:45 | 30 | 002:46 | P | DESGANCHE | SE REMPLAZO POSTE Y SE CERRO MACHETE 100% EN SERVICIO | S22021000065 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-02-10 | 4980 | keep | 0 | Feb | 2022 | 0.0033919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-11 00:22 | 2022-02-11 01:56 | 18 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22021100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-02-11 | 1692 | keep | 0 | Feb | 2022 | 0.0011524 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2022-02-11 00:43 | 2022-02-11 12:23 | 60 | 011:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2022-02-11 | 42000 | keep | 0 | Feb | 2022 | 0.028606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-11 01:06 | 2022-02-11 09:38 | 25 | 008:32 | P | NO SE REPORTO CAUSA | 1 X 60 EN CORTE DE LINEA | B22021100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 512 | 2022-02-11 | 12800 | keep | 0 | Feb | 2022 | 0.008718 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-02-11 02:10 | 2022-02-11 09:18 | 8 | 007:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR POR CULEBRA QUE CRUZO LINEAS | A22021100003 | New_Event |  |  | Include | Wildlife | 428 | 2022-02-11 | 3424 | keep | 0 | Feb | 2022 | 0.0023321 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-11 02:45 | 2022-02-11 03:54 | 108 | 001:09 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DE FOREMAN PARA REEMPALZAR MACHETE AVERIADO MEDIANTE GOI SJ-220211-01 | S22021100008 | New_Event | Switch Failure | Include | Include | Equipment | 69 | 2022-02-11 | 7452 | keep | 0 | Feb | 2022 | 0.0050755 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
CAGUAS | 2022-02-11 02:53 | 2022-02-11 02:54 | 2178 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECIERRA | C22021100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-11 | 2178 | keep | 0 | Feb | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2022-02-11 02:54 | 2022-02-11 10:45 | 144 | 007:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN CORTE DE LINEA CRUCE POR PALOMA | C22021100018 | 1st_after_momentary |  |  | Include | Wildlife | 471 | 2022-02-11 | 67824 | keep | 0 | Feb | 2022 | 0.046195 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2022-02-11 03:37 | 2022-02-11 06:28 | 5668 | 002:51 | T | PARARRAYOS DEFECTUOSO | REEMPLAZO PARARRAYO Y BAJANTE DE LINEA A CAJA QUEMADO | R22021100010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 171 | 2022-02-11 | 969228 | keep | 0 | Feb | 2022 | 0.66014 | 0.0038604 | Sustained | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2022-02-11 03:54 | 2022-02-11 18:09 | 30 | 014:15 | P | DESGANCHE | SE REMPLAZO POSTE Y SE CERRO MACHETE 100% EN SERVICIO. GOI SJ-220210-01 | S22021000065 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 855 | 2022-02-11 | 25650 | keep | 0 | Feb | 2022 | 0.01747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-11 04:44 | 2022-02-11 12:34 | 168 | 007:50 | P | DESGANCHE | 1 X 80 Y 1 X 50 EN CORTES DE LINEA SE RETIRO BAMBUA DE LA LINEA Y SE ELIMINO PARARRAYO | C22021100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 470 | 2022-02-11 | 78960 | keep | 0 | Feb | 2022 | 0.053779 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
BAYAMON | 2022-02-11 06:12 | 2022-02-11 06:13 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 5252 | keep | 0 | Feb | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2022-02-11 06:15 | 2022-02-11 18:10 | 6 | 011:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE LEVANTO SECUNDARIA | B22021100011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 715 | 2022-02-11 | 4290 | keep | 0 | Feb | 2022 | 0.0029219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-02-11 07:02 | 2022-02-11 07:03 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P22021100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 1712 | keep | 0 | Feb | 2022 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-02-11 07:02 | 2022-02-11 07:03 | 7 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P22021100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 7 | keep | 0 | Feb | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-02-11 07:13 | 2022-02-11 07:14 | 513 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1118-10 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 513 | keep | 0 | Feb | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-02-11 07:13 | 2022-02-11 07:14 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% 1111-1 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 2782 | keep | 0 | Feb | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
VEGA BAJA | 2022-02-11 07:25 | 2022-02-11 11:15 | 3 | 003:50 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | B22021100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2022-02-11 | 690 | keep | 0 | Feb | 2022 | 0.00046996 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-02-11 08:05 | 2022-02-11 09:20 | 51 | 001:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22021100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-02-11 | 3825 | keep | 0 | Feb | 2022 | 0.0026052 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
CAGUAS | 2022-02-11 08:15 | 2022-02-11 16:57 | 2 | 008:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 37.5KVA | C22021100012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 522 | 2022-02-11 | 1044 | keep | 0 | Feb | 2022 | 0.00071106 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-02-11 08:27 | 2022-02-11 09:22 | 6 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | R22021100047 | New_Event |  |  | Include | Wildlife | 55 | 2022-02-11 | 330 | keep | 0 | Feb | 2022 | 0.00022476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-02-11 08:42 | 2022-02-11 12:17 | 1 | 003:35 | P | OTRAS CAUSAS | 1 X 40 EN RISER PROA | R22021100050 | New_Event | Other Causes | Include | Include | Other | 215 | 2022-02-11 | 215 | keep | 0 | Feb | 2022 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-11 09:05 | 2022-02-11 14:09 | 25 | 005:04 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN CORTE DE LINEA Y SE REALIZO TERMINACION | R22021100053 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 304 | 2022-02-11 | 7600 | keep | 0 | Feb | 2022 | 0.0051763 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-02-11 09:08 | 2022-02-11 12:30 | 16 | 003:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22021000098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 202 | 2022-02-11 | 3232 | keep | 0 | Feb | 2022 | 0.0022013 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2022-02-11 09:10 | 2022-02-11 09:11 | 18 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P22021100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 18 | keep | 0 | Feb | 2022 | 1.226e-05 | 1.226e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-02-11 09:10 | 2022-02-11 09:13 | 494 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P22021100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-11 | 1482 | keep | 0 | Feb | 2022 | 0.0010094 | 0.00033646 | Momentary | FALSE | FALSE | Not_TMED_Event | 494
CAGUAS | 2022-02-11 09:21 | 2022-02-11 12:00 | 13 | 002:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C22021100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-02-11 | 2067 | keep | 0 | Feb | 2022 | 0.0014078 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-02-11 09:30 | 2022-02-11 10:40 | 20 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22021000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-02-11 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-11 09:39 | 2022-02-11 15:45 | 100 | 006:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZARON DISCOS | C22021100021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 366 | 2022-02-11 | 36600 | keep | 0 | Feb | 2022 | 0.024928 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-11 09:42 | 2022-02-11 10:55 | 12 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA AJUSTAR TERMINACIONES | C22021100023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2022-02-11 | 876 | keep | 0 | Feb | 2022 | 0.00059664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-11 09:43 | 2022-02-11 09:44 | 552 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 40% POR 1204-1 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 552 | keep | 0 | Feb | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
MAYAGÃœEZ | 2022-02-11 09:46 | 2022-02-11 13:15 | 100 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REPARO BAJANTE DE CORTE DE LINEA | M22021100017 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2022-02-11 | 20900 | keep | 0 | Feb | 2022 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-02-11 09:49 | 2022-02-11 12:59 | 1943 | 003:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA EN TRONCAL DEL ALIMENTADOR Y SE CERRO INTERRUPTOR | M22021100018 | New_Event | Wire Down | Include | Include | Equipment | 190 | 2022-02-11 | 369170 | keep | 0 | Feb | 2022 | 0.25144 | 0.0013234 | Sustained | FALSE | FALSE | Not_TMED_Event | 1943
CAGUAS | 2022-02-11 09:55 | 2022-02-11 12:09 | 4 | 002:14 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA RETIRAR BAMBUA Y LEVANTAR SECUNDARIA | C22021100030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 134 | 2022-02-11 | 536 | keep | 0 | Feb | 2022 | 0.00036507 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-02-11 09:56 | 2022-02-11 09:57 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS A ABANICO | C22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-11 | 2410 | keep | 0 | Feb | 2022 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2022-02-11 09:56 | 2022-02-11 09:57 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-11 | 2826 | keep | 0 | Feb | 2022 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
HUMACAO | 2022-02-11 10:04 | 2022-02-11 14:03 | 50 | 003:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 Y 1 X 8 EN CORTE DE LINEA Y TRANSFORMADOR SE REEMPLAZO DISCOS | C22021100036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 239 | 2022-02-11 | 11950 | keep | 0 | Feb | 2022 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-11 10:06 | 2022-02-11 16:20 | 9 | 006:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22021100023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 374 | 2022-02-11 | 3366 | keep | 0 | Feb | 2022 | 0.0022926 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-02-11 10:37 | 2022-02-11 11:18 | 25 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER RATON CRUZO FASE | S22021100029 | New_Event |  |  | Include | Wildlife | 41 | 2022-02-11 | 1025 | keep | 0 | Feb | 2022 | 0.00069812 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-02-11 10:37 | 2022-02-11 16:45 | 30 | 006:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A22021100019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 368 | 2022-02-11 | 11040 | keep | 0 | Feb | 2022 | 0.0075193 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-11 10:40 | 2022-02-11 10:42 | 676 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DE LAS PIEDRAS | C22021100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-02-11 | 1352 | keep | 0 | Feb | 2022 | 0.00092084 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-02-11 10:40 | 2022-02-11 10:42 | 2873 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DE LAS PIEDRAS | C22021100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-02-11 | 5746 | keep | 0 | Feb | 2022 | 0.0039136 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2022-02-11 10:40 | 2022-02-11 10:42 | 3902 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DE LAS PIEDRAS | C22021100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-02-11 | 7804 | keep | 0 | Feb | 2022 | 0.0053153 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
BAYAMON | 2022-02-11 10:45 | 2022-02-11 10:46 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | B22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 222 | keep | 0 | Feb | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-02-11 10:45 | 2022-02-11 10:46 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | B22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 4456 | keep | 0 | Feb | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
SAN JUAN | 2022-02-11 11:19 | 2022-02-11 11:20 | 513 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% POR 1118-10 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 513 | keep | 0 | Feb | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-02-11 11:19 | 2022-02-11 11:20 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% 1111-1 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 2782 | keep | 0 | Feb | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CAGUAS | 2022-02-11 11:24 | 2022-02-11 13:03 | 5 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA QUE CONTRATISTA TRABAJE EN LA SECUNDARIA | C22021000102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2022-02-11 | 495 | keep | 0 | Feb | 2022 | 0.00033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-11 11:32 | 2022-02-11 12:30 | 100 | 000:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M22021100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-02-11 | 5800 | keep | 0 | Feb | 2022 | 0.0039504 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-11 11:36 | 2022-02-11 13:26 | 167 | 001:50 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22021100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-02-11 | 18370 | keep | 0 | Feb | 2022 | 0.012512 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
HUMACAO | 2022-02-11 11:43 | 2022-02-11 14:45 | 150 | 003:02 | P | DESGANCHE | 1 X 65 Y 1 X 30 EN CORTE DE LINEA | C22021100096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-02-11 | 27300 | keep | 0 | Feb | 2022 | 0.018594 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-02-11 11:48 | 2022-02-11 14:34 | 35 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22021100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-02-11 | 5810 | keep | 0 | Feb | 2022 | 0.0039572 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-02-11 11:48 | 2022-02-11 14:41 | 89 | 002:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22021100102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-02-11 | 15397 | keep | 0 | Feb | 2022 | 0.010487 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
CAGUAS | 2022-02-11 11:54 | 2022-02-11 16:35 | 20 | 004:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22021100105 | New_Event | Wire Down | Include | Include | Equipment | 281 | 2022-02-11 | 5620 | keep | 0 | Feb | 2022 | 0.0038278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-11 12:14 | 2022-02-11 15:48 | 200 | 003:34 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22021100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-02-11 | 42800 | keep | 0 | Feb | 2022 | 0.029151 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-02-11 12:26 | 2022-02-11 16:05 | 60 | 003:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22021100041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 219 | 2022-02-11 | 13140 | keep | 0 | Feb | 2022 | 0.0089496 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-11 12:28 | 2022-02-11 16:08 | 60 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-16 Y 1 X 65 EN RISER | B22021100042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2022-02-11 | 13200 | keep | 0 | Feb | 2022 | 0.0089905 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-02-11 12:30 | 2022-02-11 13:25 | 6 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22021100032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-02-11 | 330 | keep | 0 | Feb | 2022 | 0.00022476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-11 12:32 | 2022-02-11 13:43 | 386 | 001:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22021100117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-02-11 | 27406 | keep | 0 | Feb | 2022 | 0.018666 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
BAYAMON | 2022-02-11 12:39 | 2022-02-11 14:58 | 8 | 002:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-34 AVERIADO | B22021100047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 139 | 2022-02-11 | 1112 | keep | 0 | Feb | 2022 | 0.00075738 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-11 12:44 | 2022-02-11 12:45 | 1843 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22021100120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-11 | 1843 | keep | 0 | Feb | 2022 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2022-02-11 12:45 | 2022-02-12 12:17 | 1 | 023:32 | P | DESGANCHE | 2 X 50 EN C/L | C22021100207 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1412 | 2022-02-11 | 1412 | keep | 0 | Feb | 2022 | 0.00096171 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-02-11 12:50 | 2022-02-11 18:36 | 18 | 005:46 | P | ESTRUCTURA AVERIADA | SE RETIRO POSTE PARTIDO Y SE RETEZARON LINEAS | C22021100123 | New_Event | Defective Pole | Include | Include | Equipment | 346 | 2022-02-11 | 6228 | keep | 0 | Feb | 2022 | 0.0042419 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-02-11 12:52 | 2022-02-11 12:53 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
BAYAMON | 2022-02-11 12:53 | 2022-02-11 18:55 | 50 | 006:02 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B22021100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-02-11 | 18100 | keep | 0 | Feb | 2022 | 0.012328 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-11 12:53 | 2022-02-11 18:20 | 60 | 005:27 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | S22021100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-02-11 | 19620 | keep | 0 | Feb | 2022 | 0.013363 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-11 13:01 | 2022-02-11 13:52 | 12 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE BARRAS SECUNDARIAS EN PEDESTAL | B22021100048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-02-11 | 612 | keep | 0 | Feb | 2022 | 0.00041683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-11 13:04 | 2022-02-11 16:59 | 150 | 003:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22021100129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-02-11 | 35250 | keep | 0 | Feb | 2022 | 0.024009 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-02-11 13:06 | 2022-02-11 14:04 | 6 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22021100035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-11 | 348 | keep | 0 | Feb | 2022 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-11 13:17 | 2022-02-11 15:54 | 90 | 002:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22021100134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-02-11 | 14130 | keep | 0 | Feb | 2022 | 0.0096239 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-02-11 13:25 | 2022-02-11 17:52 | 150 | 004:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22021100055 | New_Event | Bad Weather | Include | Include | Weather | 267 | 2022-02-11 | 40050 | keep | 0 | Feb | 2022 | 0.027278 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-11 13:32 | 2022-02-11 13:59 | 6 | 000:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MONTURA PARA CERRAR PUENTE DE LINEA A CAJA TRANSFORMADOR | S22021100088 | New_Event | Wire Down | Include | Include | Equipment | 27 | 2022-02-11 | 162 | keep | 0 | Feb | 2022 | 0.00011034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-11 13:34 | 2022-02-11 14:38 | 6 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS | C22021100145 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2022-02-11 | 384 | keep | 0 | Feb | 2022 | 0.00026154 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-02-11 13:42 | 2022-02-11 16:12 | 112 | 002:30 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C22021100149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-02-11 | 16800 | keep | 0 | Feb | 2022 | 0.011442 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
CAGUAS | 2022-02-11 13:45 | 2022-02-11 13:46 | 1116 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22021100151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 1116 | keep | 0 | Feb | 2022 | 0.0007601 | 0.0007601 | Momentary | FALSE | FALSE | Not_TMED_Event | 1116
CAGUAS | 2022-02-11 13:58 | 2022-02-11 15:50 | 300 | 001:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 1 X 40 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22021100164 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2022-02-11 | 33600 | keep | 0 | Feb | 2022 | 0.022885 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-02-11 14:14 | 2022-02-11 16:15 | 132 | 002:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22021100066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-02-11 | 15972 | keep | 0 | Feb | 2022 | 0.010878 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
ARECIBO | 2022-02-11 14:23 | 2022-02-11 16:05 | 20 | 001:42 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A22021100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-02-11 | 2040 | keep | 0 | Feb | 2022 | 0.0013894 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-02-11 14:30 | 2022-02-11 19:16 | 1783 | 004:46 | P | LINEA DE TRANSMISION 38KV | SE ABREN MACHETES DEBIDO A TRAMO LINEA 1700 SOBRE ALIMENTADOR | P22202110005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 286 | 2022-02-11 | 509938 | keep | 0 | Feb | 2022 | 0.34732 | 0.0012144 | Sustained | FALSE | FALSE | Not_TMED_Event | 1783
PONCE | 2022-02-11 14:36 | 2022-02-11 16:11 | 2039 | 001:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR LINEA PRIMARIA PARTIDA SE ABRIO MACHETES EN CARR 14 KM 14.0 BO JACAGUAS JUANA DIAZ Y SE COLOCO INTERRUPTOR EN SERVICIO. | P22021100050 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2022-02-11 | 193705 | keep | 0 | Feb | 2022 | 0.13193 | 0.0013888 | Sustained | FALSE | FALSE | Not_TMED_Event | 2039
BAYAMON | 2022-02-11 14:47 | 2022-02-11 17:35 | 10 | 002:48 | P | NO SE REPORTO CAUSA | 2 X 10 EN XMR | B22021100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-02-11 | 1680 | keep | 0 | Feb | 2022 | 0.0011442 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-11 14:48 | 2022-02-11 19:58 | 12 | 005:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO CAJA PRIMARIA | B22021100060 | New_Event | Cutout Failure | Include | Include | Equipment | 310 | 2022-02-11 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-11 14:50 | 2022-02-11 15:35 | 300 | 000:45 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | M22021100038 | New_Event | Defective Pole | Include | Include | Equipment | 45 | 2022-02-11 | 13500 | keep | 0 | Feb | 2022 | 0.0091948 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-02-11 15:11 | 2022-02-11 17:42 | 95 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22021100191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-02-11 | 14345 | keep | 0 | Feb | 2022 | 0.0097703 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
PONCE | 2022-02-11 15:13 | 2022-02-11 15:14 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22021100056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
SAN JUAN | 2022-02-11 15:17 | 2022-02-11 18:06 | 10 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22021100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-11 | 1690 | keep | 0 | Feb | 2022 | 0.0011511 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-11 15:18 | 2022-02-11 15:19 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22021100057 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
PONCE | 2022-02-11 15:22 | 2022-02-11 17:44 | 50 | 002:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22021100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-02-11 | 7100 | keep | 0 | Feb | 2022 | 0.0048358 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-11 15:31 | 2022-02-11 15:32 | 521 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 521 | keep | 0 | Feb | 2022 | 0.00035485 | 0.00035485 | Momentary | FALSE | FALSE | Not_TMED_Event | 521
MAYAGÃœEZ | 2022-02-11 15:40 | 2022-02-11 16:25 | 6 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA ROTA | M22021100076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-02-11 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-02-11 15:41 | 2022-02-11 15:42 | 2201 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A22021100034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-11 | 2201 | keep | 0 | Feb | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
BARRANQUITAS | 2022-02-11 15:41 | 2022-02-11 17:17 | 73 | 001:36 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22021100129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-02-11 | 7008 | keep | 0 | Feb | 2022 | 0.0047731 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
ARECIBO | 2022-02-11 15:42 | 2022-02-11 17:42 | 60 | 002:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A22021100035 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2022-02-11 | 7200 | keep | 0 | Feb | 2022 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-02-11 15:47 | 2022-02-11 15:48 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22021100062 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
UTUADO | 2022-02-11 15:59 | 2022-02-11 18:32 | 3 | 002:33 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | A22021100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-02-11 | 459 | keep | 0 | Feb | 2022 | 0.00031262 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-02-11 16:00 | 2022-02-11 17:00 | 1 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA CRUZADA CON TENSOR | M22021100065 | New_Event |  |  | Include | Wildlife | 60 | 2022-02-11 | 60 | keep | 0 | Feb | 2022 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-11 16:01 | 2022-02-11 16:02 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22021100070 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
HUMACAO | 2022-02-11 16:08 | 2022-02-11 22:56 | 46 | 006:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22021100200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2022-02-11 | 18768 | keep | 0 | Feb | 2022 | 0.012783 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
PONCE | 2022-02-11 16:11 | 2022-02-11 18:20 | 44 | 002:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRARON MACHETES | P22021100064 | Partial_restoration | Wire Down | Include | Include | Equipment | 129 | 2022-02-11 | 5676 | keep | 0 | Feb | 2022 | 0.0038659 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-11 16:12 | 2022-02-11 19:20 | 100 | 003:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22021100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-02-11 | 18800 | keep | 0 | Feb | 2022 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-11 16:12 | 2022-02-11 18:46 | 20 | 002:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A22021100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-02-11 | 3080 | keep | 0 | Feb | 2022 | 0.0020978 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-11 16:22 | 2022-02-11 19:16 | 50 | 002:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A22021100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-02-11 | 8700 | keep | 0 | Feb | 2022 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-11 16:38 | 2022-02-12 16:03 | 1 | 023:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA Y SE RETIRO IGUANA DE LA LINEA | S22021100058 | New_Event |  |  | Include | Wildlife | 1405 | 2022-02-11 | 1405 | keep | 0 | Feb | 2022 | 0.00095694 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-11 16:40 | 2022-02-11 17:31 | 27 | 000:51 | S | LINEA DE TRANSMISION 38KV | SE ABRIO MB PARA LLENAR DE SF6 DEL 0040 ESTABA VACIO Y EN LOCKOUT AUTORIZADO POR RANGEL VAZQUEZ | B22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-02-11 | 1377 | keep | 0 | Feb | 2022 | 0.00093787 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-02-11 16:40 | 2022-02-11 17:31 | 603 | 000:51 | S | LINEA DE TRANSMISION 38KV | SE ABRIO MB PARA LLENAR DE SF6 DEL 0040 ESTABA VACIO Y EN LOCKOUT AUTORIZADO POR RANGEL VAZQUEZ | B22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-02-11 | 30753 | keep | 0 | Feb | 2022 | 0.020946 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-02-11 16:40 | 2022-02-11 17:31 | 6 | 000:51 | S | LINEA DE TRANSMISION 38KV | SE ABRIO MB PARA LLENAR DE SF6 DEL 0040 ESTABA VACIO Y EN LOCKOUT AUTORIZADO POR RANGEL VAZQUEZ | B22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-02-11 | 306 | keep | 0 | Feb | 2022 | 0.00020842 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-02-11 16:40 | 2022-02-11 17:31 | 325 | 000:51 | S | LINEA DE TRANSMISION 38KV | SE ABRIO MB PARA LLENAR DE SF6 DEL 0040 ESTABA VACIO Y EN LOCKOUT AUTORIZADO POR RANGEL VAZQUEZ | B22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-02-11 | 16575 | keep | 0 | Feb | 2022 | 0.011289 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-02-11 16:40 | 2022-02-11 17:31 | 172 | 000:51 | S | LINEA DE TRANSMISION 38KV | SE ABRIO MB PARA LLENAR DE SF6 DEL 0040 ESTABA VACIO Y EN LOCKOUT AUTORIZADO POR RANGEL VAZQUEZ | B22021100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-02-11 | 8772 | keep | 0 | Feb | 2022 | 0.0059746 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2022-02-11 16:41 | 2022-02-11 20:38 | 12 | 003:57 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | A22021100040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 237 | 2022-02-11 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-11 16:43 | 2022-02-11 18:39 | 6 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XME Y SE REPARO NEUTRAL Y SECUNDARIA | B22021100027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2022-02-11 | 696 | keep | 0 | Feb | 2022 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-11 16:45 | 2022-02-11 17:15 | 15 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22021100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-02-11 | 450 | keep | 0 | Feb | 2022 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-11 16:48 | 2022-02-11 19:25 | 129 | 002:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO DISCO | C22021100205 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 157 | 2022-02-11 | 20253 | keep | 0 | Feb | 2022 | 0.013794 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
SAN JUAN | 2022-02-11 17:08 | 2022-02-11 23:25 | 150 | 006:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22021100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 377 | 2022-02-11 | 56550 | keep | 0 | Feb | 2022 | 0.038516 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-02-11 17:11 | 2022-02-11 18:45 | 60 | 001:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22021100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-02-11 | 5640 | keep | 0 | Feb | 2022 | 0.0038414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-11 17:23 | 2022-02-12 01:29 | 60 | 008:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22021100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 486 | 2022-02-11 | 29160 | keep | 0 | Feb | 2022 | 0.019861 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-11 17:40 | 2022-02-11 19:57 | 45 | 002:17 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22021100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-02-11 | 6165 | keep | 0 | Feb | 2022 | 0.004199 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-02-11 17:58 | 2022-02-11 22:16 | 1 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22021100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2022-02-11 | 258 | keep | 0 | Feb | 2022 | 0.00017572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-11 19:01 | 2022-02-11 21:50 | 1 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO Y SE REMPLAZO CAJA QUEMADA | A22021100047 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2022-02-11 | 169 | keep | 0 | Feb | 2022 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-11 19:08 | 2022-02-12 14:30 | 350 | 019:22 | P | HERRAJE ROTO O PODRIDO | 2 X 15 EN TRANSFORMADOR Y SE ABRIO MACHETES PARA REEMPLAZO DE CRUCETA PARTIDA | S22021100076 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1162 | 2022-02-11 | 406700 | keep | 0 | Feb | 2022 | 0.277 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
CAGUAS | 2022-02-11 19:09 | 2022-02-11 22:30 | 355 | 003:21 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA Y SE LEVANTO ALAMBRE PRIMARIO | C22021100212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-02-11 | 71355 | keep | 0 | Feb | 2022 | 0.0486 | 0.00024179 | Sustained | FALSE | FALSE | Not_TMED_Event | 355
AGUADILLA | 2022-02-11 19:10 | 2022-02-11 19:11 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22021100093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-02-11 19:11 | 2022-02-11 21:15 | 100 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22021100095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-02-11 | 12400 | keep | 0 | Feb | 2022 | 0.0084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-11 19:16 | 2022-02-11 22:00 | 15 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22021100094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2022-02-11 | 2460 | keep | 0 | Feb | 2022 | 0.0016755 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-02-11 19:27 | 2022-02-11 20:22 | 1 | 000:55 | P | NO SE REPORTO CAUSA | 1 X 25 EN BCO DE TRANSFORMADORES HACIA BOMBAS | R22021100103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2022-02-11 | 55 | keep | 0 | Feb | 2022 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-11 20:00 | 2022-02-11 21:09 | 12 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22021100095 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-02-11 | 828 | keep | 0 | Feb | 2022 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-11 20:50 | 2022-02-12 10:25 | 40 | 013:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22021100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2022-02-11 | 32600 | keep | 0 | Feb | 2022 | 0.022204 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-02-11 20:51 | 2022-02-12 12:47 | 10 | 015:56 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 25 KVA X 25 KVA | R22021100104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 956 | 2022-02-11 | 9560 | keep | 0 | Feb | 2022 | 0.0065113 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-11 21:28 | 2022-02-12 09:30 | 7 | 012:02 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22021100216 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 722 | 2022-02-11 | 5054 | keep | 0 | Feb | 2022 | 0.0034423 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-02-11 22:35 | 2022-02-11 22:36 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-11 22:35 | 2022-02-11 22:36 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S22021100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-11 | 135 | keep | 0 | Feb | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2022-02-11 22:39 | 2022-02-12 03:15 | 125 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22021100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-02-11 | 34500 | keep | 0 | Feb | 2022 | 0.023498 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2022-02-11 22:46 | 2022-02-12 10:39 | 25 | 011:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22021100083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 713 | 2022-02-11 | 17825 | keep | 0 | Feb | 2022 | 0.012141 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-02-11 22:50 | 2022-02-12 09:55 | 100 | 011:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P22021100085 | New_Event |  |  | Include | Wildlife | 665 | 2022-02-11 | 66500 | keep | 0 | Feb | 2022 | 0.045293 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-12 00:36 | 2022-02-12 00:37 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
HUMACAO | 2022-02-12 00:37 | 2022-02-12 02:16 | 2354 | 001:39 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECERRO 3 VECES SE DEJO FUERA SE SECCIONALIZO SU-PDR2 QUE ESTABA EN FUEGO CERRADO POR CONTROL VER CG-220213-01 | C22021300000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 99 | 2022-02-12 | 233046 | keep | 0 | Feb | 2022 | 0.15873 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
VEGA BAJA | 2022-02-12 00:37 | 2022-02-12 02:41 | 80 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22021200001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-02-12 | 9920 | keep | 0 | Feb | 2022 | 0.0067565 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-12 01:14 | 2022-02-12 17:09 | 300 | 015:55 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M22021200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 955 | 2022-02-12 | 286500 | keep | 0 | Feb | 2022 | 0.19513 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-02-12 01:20 | 2022-02-12 11:13 | 30 | 009:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN C/L MAL TIEMPO | C22021200001 | New_Event | Bad Weather | Include | Include | Weather | 593 | 2022-02-12 | 17790 | keep | 0 | Feb | 2022 | 0.012117 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-12 01:35 | 2022-02-12 07:46 | 50 | 006:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22021200001 | New_Event | Bad Weather | Include | Include | Weather | 371 | 2022-02-12 | 18550 | keep | 0 | Feb | 2022 | 0.012634 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-12 02:41 | 2022-02-12 02:56 | 308 | 000:15 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B22021200000 | New_Event | Cutout Failure | Include | Include | Equipment | 15 | 2022-02-12 | 4620 | keep | 0 | Feb | 2022 | 0.0031467 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-12 02:56 | 2022-02-12 04:54 | 50 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22021200014 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 118 | 2022-02-12 | 5900 | keep | 0 | Feb | 2022 | 0.0040185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-02-12 03:45 | 2022-02-12 03:46 | 2635 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22021200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-12 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-02-12 03:46 | 2022-02-12 13:18 | 100 | 009:32 | P | DESGANCHE | 1 X 100 EN C/L | C22021200015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 572 | 2022-02-12 | 57200 | keep | 0 | Feb | 2022 | 0.038959 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-12 03:55 | 2022-02-12 03:56 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1717-01 LLEVANDO LA CARGA TOTAL DEL 1717-05 Y 10% DEL 1806-02 | B22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 4533 | keep | 0 | Feb | 2022 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2022-02-12 03:55 | 2022-02-12 03:56 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1717-01 LLEVANDO LA CARGA TOTAL DEL 1717-05 Y 10% DEL 1806-02 | B22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 341 | keep | 0 | Feb | 2022 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2022-02-12 03:55 | 2022-02-12 03:56 | 462 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1717-01 LLEVANDO LA CARGA TOTAL DEL 1717-05 Y 10% DEL 1806-02 | B22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 462 | keep | 0 | Feb | 2022 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
FAJARDO | 2022-02-12 04:06 | 2022-02-12 04:07 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22021200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1830 | keep | 0 | Feb | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
CANOVANAS | 2022-02-12 04:07 | 2022-02-12 06:21 | 25 | 002:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L RETEZO LINEAS | R22021200001 | New_Event | Wire Down | Include | Include | Equipment | 134 | 2022-02-12 | 3350 | keep | 0 | Feb | 2022 | 0.0022817 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-12 04:37 | 2022-02-12 11:04 | 12 | 006:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO DE LINEA A CAJA Y 2 SECUNDARIA | B22021200019 | New_Event | Wire Down | Include | Include | Equipment | 387 | 2022-02-12 | 4644 | keep | 0 | Feb | 2022 | 0.003163 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-02-12 04:37 | 2022-02-12 10:49 | 80 | 006:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22021200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 372 | 2022-02-12 | 29760 | keep | 0 | Feb | 2022 | 0.020269 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-02-12 04:54 | 2022-02-12 04:58 | 308 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR SCADA EN COORDINACION CON JESUS TORRES EN TRABAJOS CAMBIO DE CAJA AVERIADA (NO TIENE QUE VER CON DISPARO) | B22021200020 | Additional_clients | Cutout Failure | Include | Include | Equipment | 4 | 2022-02-12 | 1232 | keep | 0 | Feb | 2022 | 0.00083911 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-12 04:58 | 2022-02-12 05:03 | 50 | 000:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22021200014 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 5 | 2022-02-12 | 250 | keep | 0 | Feb | 2022 | 0.00017027 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-12 05:03 | 2022-02-12 05:04 | 308 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NUEVAMENTE Y SE CERRO POR SCADA EN COORDINACION CON JESUS TORRES EN TRABAJOS CAMBIO DE CAJA AVERIADA (NO TIENE QUE VER CON DISPARO) | B22021200020 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-12 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-12 05:04 | 2022-02-12 06:05 | 50 | 001:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22021200014 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 61 | 2022-02-12 | 3050 | keep | 0 | Feb | 2022 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-12 05:12 | 2022-02-12 05:13 | 906 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22021200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 906 | keep | 0 | Feb | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2022-02-12 05:26 | 2022-02-12 11:29 | 44 | 006:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22021200007 | New_Event | Bad Weather | Include | Include | Weather | 363 | 2022-02-12 | 15972 | keep | 0 | Feb | 2022 | 0.010878 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2022-02-12 06:05 | 2022-02-12 06:06 | 308 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | B22021200000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-12 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-12 06:06 | 2022-02-12 06:25 | 50 | 000:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B22021200014 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 19 | 2022-02-12 | 950 | keep | 0 | Feb | 2022 | 0.00064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-12 06:20 | 2022-02-12 07:57 | 12 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S22021200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-02-12 | 1164 | keep | 0 | Feb | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-12 06:54 | 2022-02-12 14:50 | 50 | 007:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22021200032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2022-02-12 | 23800 | keep | 0 | Feb | 2022 | 0.01621 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-12 07:09 | 2022-02-12 07:13 | 36 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1620-3 | S22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-12 | 144 | keep | 0 | Feb | 2022 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-12 07:09 | 2022-02-12 07:13 | 1073 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO LLEVA CARGA 1620-1 SE PROBO QUEDO EN SERVICIO | S22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-12 | 4292 | keep | 0 | Feb | 2022 | 0.0029233 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
BAYAMON | 2022-02-12 07:14 | 2022-02-12 12:42 | 20 | 005:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22021200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 328 | 2022-02-12 | 6560 | keep | 0 | Feb | 2022 | 0.004468 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-12 07:16 | 2022-02-12 09:41 | 25 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA FOREMAN INDICO QUE NO SE DETERMINO CAUSA | A22021200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-02-12 | 3625 | keep | 0 | Feb | 2022 | 0.002469 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-02-12 07:48 | 2022-02-12 09:05 | 50 | 001:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADO ROTO | P22021200004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 77 | 2022-02-12 | 3850 | keep | 0 | Feb | 2022 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-12 08:06 | 2022-02-12 10:51 | 30 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22021200007 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-02-12 | 4950 | keep | 0 | Feb | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-12 08:10 | 2022-02-12 08:11 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 181 | keep | 0 | Feb | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
VEGA BAJA | 2022-02-12 08:21 | 2022-02-12 09:49 | 15 | 001:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-02-12 | 1320 | keep | 0 | Feb | 2022 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-12 08:26 | 2022-02-12 13:05 | 10 | 004:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RETEZAR LINEA SECUNDARIA Y REALIZAR DESGANCHE | B22021200042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 279 | 2022-02-12 | 2790 | keep | 0 | Feb | 2022 | 0.0019003 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-12 08:27 | 2022-02-12 21:53 | 35 | 013:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y SE RETIRO AVE | S22021200008 | New_Event |  |  | Include | Wildlife | 806 | 2022-02-12 | 28210 | keep | 0 | Feb | 2022 | 0.019214 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-02-12 08:27 | 2022-02-12 11:55 | 60 | 003:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN RISER SE ENCONTRO AVERIA NUEVA SU-34 A SU-34A SE CERRO N/O SU-34 A RISER | S22021200008 | New_Event |  |  | Include | Wildlife | 208 | 2022-02-12 | 12480 | keep | 0 | Feb | 2022 | 0.0085001 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-12 08:45 | 2022-02-12 12:18 | 43 | 003:33 | P | DESGANCHE | 1 X 65 EN C/L | R22021200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-02-12 | 9159 | keep | 0 | Feb | 2022 | 0.0062382 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2022-02-12 08:56 | 2022-02-12 15:38 | 40 | 006:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22021200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 402 | 2022-02-12 | 16080 | keep | 0 | Feb | 2022 | 0.010952 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-02-12 08:56 | 2022-02-12 10:54 | 1 | 001:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22021200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-02-12 | 118 | keep | 0 | Feb | 2022 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-12 09:09 | 2022-02-12 20:25 | 79 | 011:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DEJO ALAMBRE EN EL SUELO SECCIONALIZADO CON EVENTO C22021200274 PARA TRABAJAR MAÃ‘ANA | C22021200049 | New_Event | Wire Down | Include | Include | Equipment | 676 | 2022-02-12 | 53404 | keep | 0 | Feb | 2022 | 0.036373 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
ARECIBO | 2022-02-12 09:13 | 2022-02-12 11:01 | 75 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA JOURNEYMAN INFORMA QUE NO SE ENCONTRO CAUSA | A22021200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-02-12 | 8100 | keep | 0 | Feb | 2022 | 0.0055169 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-02-12 09:13 | 2022-02-13 10:16 | 100 | 025:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO DISCO | C22021200051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1503 | 2022-02-12 | 150300 | keep | 0 | Feb | 2022 | 0.10237 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-12 09:18 | 2022-02-12 11:03 | 20 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22021200049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-02-12 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-12 09:34 | 2022-02-12 15:37 | 200 | 006:03 | P | ESTRUCTURA AVERIADA | SJ-220212-50 REEMPLAZO DE POSTE PARTIDO SE REALIZARON OPERACIONES PARA SECCIONALIZAR EL POSTE Y SE TRANSFIRIO EL 88% DEL ALIMENTADOR AL 2402-02 | R22021100044 | New_Event | Defective Pole | Include | Include | Equipment | 363 | 2022-02-12 | 72600 | keep | 0 | Feb | 2022 | 0.049448 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-02-12 09:35 | 2022-02-12 19:28 | 1 | 009:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22021200072 | New_Event | Bad Weather | Include | Include | Weather | 593 | 2022-02-12 | 593 | keep | 0 | Feb | 2022 | 0.00040389 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-02-12 09:43 | 2022-02-12 11:15 | 50 | 001:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADO ROTO | P22021200004 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 92 | 2022-02-12 | 4600 | keep | 0 | Feb | 2022 | 0.003133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-02-12 09:50 | 2022-02-12 13:39 | 8 | 003:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22021200015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 229 | 2022-02-12 | 1832 | keep | 0 | Feb | 2022 | 0.0012478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-02-12 10:00 | 2022-02-12 13:09 | 1891 | 003:09 | S | LINEA DE TRANSMISION 38KV | CERRARON PUENTES EN LINEA 3700 | C22021200128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2022-02-12 | 357399 | keep | 0 | Feb | 2022 | 0.24342 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-02-12 10:00 | 2022-02-12 13:05 | 1250 | 003:05 | S | LINEA DE TRANSMISION 38KV | CERRARON PUENTES EN LINEA 3700 | C22021200128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-02-12 | 231250 | keep | 0 | Feb | 2022 | 0.1575 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-02-12 10:00 | 2022-02-12 13:09 | 2141 | 003:09 | S | LINEA DE TRANSMISION 38KV | CERRARON PUENTES EN LINEA 3700 | C22021200128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2022-02-12 | 404649 | keep | 0 | Feb | 2022 | 0.2756 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-02-12 10:00 | 2022-02-12 13:05 | 1827 | 003:05 | S | LINEA DE TRANSMISION 38KV | CERRARON PUENTES EN LINEA 3700 | C22021200128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-02-12 | 337995 | keep | 0 | Feb | 2022 | 0.23021 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2022-02-12 10:15 | 2022-02-12 13:00 | 3 | 002:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | M22021200010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2022-02-12 | 495 | keep | 0 | Feb | 2022 | 0.00033714 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-02-12 10:17 | 2022-02-12 14:20 | 6 | 004:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | B22021200051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 243 | 2022-02-12 | 1458 | keep | 0 | Feb | 2022 | 0.00099304 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-02-12 10:19 | 2022-02-12 14:26 | 4 | 004:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN TRANSFORMADOR | R22021100057 | New_Event | Cutout Failure | Include | Include | Equipment | 247 | 2022-02-12 | 988 | keep | 0 | Feb | 2022 | 0.00067292 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-02-12 10:48 | 2022-02-12 14:40 | 24 | 003:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22021200121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-02-12 | 5568 | keep | 0 | Feb | 2022 | 0.0037923 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2022-02-12 10:52 | 2022-02-12 12:38 | 25 | 001:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22021200016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 106 | 2022-02-12 | 2650 | keep | 0 | Feb | 2022 | 0.0018049 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-12 11:14 | 2022-02-12 11:15 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1590 | keep | 0 | Feb | 2022 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
AGUADILLA | 2022-02-12 11:14 | 2022-02-12 14:30 | 25 | 003:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | M22021200013 | New_Event | Wire Down | Include | Include | Equipment | 196 | 2022-02-12 | 4900 | keep | 0 | Feb | 2022 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-12 11:26 | 2022-02-12 12:24 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | B22021200062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-12 | 580 | keep | 0 | Feb | 2022 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-12 11:34 | 2022-02-12 15:06 | 30 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR CHANGO | C22021200143 | New_Event |  |  | Include | Wildlife | 212 | 2022-02-12 | 6360 | keep | 0 | Feb | 2022 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-12 11:50 | 2022-02-12 11:51 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 2825 | keep | 0 | Feb | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
UTUADO | 2022-02-12 11:50 | 2022-02-12 12:43 | 30 | 000:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A22021200019 | New_Event |  |  | Include | Wildlife | 53 | 2022-02-12 | 1590 | keep | 0 | Feb | 2022 | 0.0010829 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-12 12:22 | 2022-02-12 16:17 | 50 | 003:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE LEVANTO Y EMPALMO PRIMARIA | B22021200071 | New_Event | Wire Down | Include | Include | Equipment | 235 | 2022-02-12 | 11750 | keep | 0 | Feb | 2022 | 0.0080029 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-12 12:43 | 2022-02-12 13:29 | 6 | 000:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INFORMA JOURNEYMAN QUE REQUIERE DESGANCHE | M22021200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2022-02-12 | 276 | keep | 0 | Feb | 2022 | 0.00018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-12 12:59 | 2022-02-12 18:21 | 6 | 005:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | S22021200026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 322 | 2022-02-12 | 1932 | keep | 0 | Feb | 2022 | 0.0013159 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-02-12 13:00 | 2022-02-12 14:42 | 50 | 001:42 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22021200037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-02-12 | 5100 | keep | 0 | Feb | 2022 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-12 13:11 | 2022-02-12 15:28 | 50 | 002:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B22021200081 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2022-02-12 | 6850 | keep | 0 | Feb | 2022 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-12 13:16 | 2022-02-12 16:30 | 100 | 003:14 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M22021200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-02-12 | 19400 | keep | 0 | Feb | 2022 | 0.013213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-02-12 13:18 | 2022-02-12 13:42 | 50 | 000:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22021200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2022-02-12 | 1200 | keep | 0 | Feb | 2022 | 0.00081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-12 13:25 | 2022-02-12 17:01 | 130 | 003:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22021200025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-02-12 | 28080 | keep | 0 | Feb | 2022 | 0.019125 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-02-12 13:34 | 2022-02-12 18:00 | 60 | 004:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22021200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2022-02-12 | 15960 | keep | 0 | Feb | 2022 | 0.01087 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-12 13:46 | 2022-02-12 15:49 | 1 | 002:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO EN RISER | R22021200024 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2022-02-12 | 123 | keep | 0 | Feb | 2022 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-12 14:00 | 2022-02-12 19:05 | 9 | 005:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO PORTAFUSIBLES | B22021200086 | New_Event | Cutout Failure | Include | Include | Equipment | 305 | 2022-02-12 | 2745 | keep | 0 | Feb | 2022 | 0.0018696 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-02-12 14:08 | 2022-02-12 15:00 | 27 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA CORREGIR CONEXIONES DEL NEUTRAL SECUNDARIO | C22021200182 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-02-12 | 1404 | keep | 0 | Feb | 2022 | 0.00095626 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
ARECIBO | 2022-02-12 14:44 | 2022-02-12 20:10 | 80 | 005:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA INDICA JOURNEYMAN NO SE ENCONTRO CAUSA | A22021200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2022-02-12 | 26080 | keep | 0 | Feb | 2022 | 0.017763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-12 14:46 | 2022-02-13 16:13 | 20 | 025:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA | S22021200036 | New_Event | Wire Down | Include | Include | Equipment | 1527 | 2022-02-12 | 30540 | keep | 0 | Feb | 2022 | 0.020801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-12 14:58 | 2022-02-13 12:30 | 200 | 021:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22021200189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1292 | 2022-02-12 | 258400 | keep | 0 | Feb | 2022 | 0.176 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-02-12 15:01 | 2022-02-12 18:23 | 159 | 003:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA AISLADOR ROTO | C22021200191 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 202 | 2022-02-12 | 32118 | keep | 0 | Feb | 2022 | 0.021875 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
VEGA BAJA | 2022-02-12 15:25 | 2022-02-12 17:53 | 30 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L RAYOS | B22021200095 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2022-02-12 | 4440 | keep | 0 | Feb | 2022 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-12 15:28 | 2022-02-12 15:53 | 85 | 000:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22021200208 | New_Event |  |  | Include | Wildlife | 25 | 2022-02-12 | 2125 | keep | 0 | Feb | 2022 | 0.0014473 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
HUMACAO | 2022-02-12 15:28 | 2022-02-12 15:29 | 3701 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR EN SERVICIO | C22021200210 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-12 | 3701 | keep | 0 | Feb | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-02-12 15:29 | 2022-02-12 17:52 | 365 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C22021200214 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 143 | 2022-02-12 | 52195 | keep | 0 | Feb | 2022 | 0.03555 | 0.0002486 | Sustained | FALSE | FALSE | Not_TMED_Event | 365
CAGUAS | 2022-02-12 15:33 | 2022-02-12 17:00 | 88 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22021200213 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-02-12 | 7656 | keep | 0 | Feb | 2022 | 0.0052145 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
AGUADILLA | 2022-02-12 15:35 | 2022-02-12 17:40 | 20 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22021200036 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2022-02-12 | 2500 | keep | 0 | Feb | 2022 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-12 15:57 | 2022-02-12 15:58 | 533 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 QUE A SU VEZ LLEVA EL 30% DE LA CARGA DEL 1346-02 | S22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 533 | keep | 0 | Feb | 2022 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
BAYAMON | 2022-02-12 15:57 | 2022-02-12 15:58 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 QUE A SU VEZ LLEVA EL 30% DE LA CARGA DEL 1346-02 | S22021200058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1802 | keep | 0 | Feb | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-02-12 16:04 | 2022-02-13 08:20 | 9 | 016:16 | P | TRANSFORMADOR AVERIADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR TRANSFORMADOR 37.5 X 37.5 TRAS PATIO | S22021200044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 976 | 2022-02-12 | 8784 | keep | 0 | Feb | 2022 | 0.0059827 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-02-12 16:04 | 2022-02-12 18:06 | 500 | 002:02 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES QUEMADOS | R22021200038 | New_Event | Switch Failure | Include | Include | Equipment | 122 | 2022-02-12 | 61000 | keep | 0 | Feb | 2022 | 0.041547 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2022-02-12 16:07 | 2022-02-12 18:47 | 43 | 002:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22021200225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-02-12 | 6880 | keep | 0 | Feb | 2022 | 0.0046859 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2022-02-12 16:09 | 2022-02-13 20:34 | 15 | 028:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN XMR SE REPARO SECUNDARIA | S22021200049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1705 | 2022-02-12 | 25575 | keep | 0 | Feb | 2022 | 0.017419 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-12 16:09 | 2022-02-12 17:58 | 36 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22021200100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-02-12 | 3924 | keep | 0 | Feb | 2022 | 0.0026726 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2022-02-12 16:29 | 2022-02-12 19:33 | 78 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 65 EN CORTES DE LINEAS CRUCE POR CHANGO | C22021200234 | New_Event |  |  | Include | Wildlife | 184 | 2022-02-12 | 14352 | keep | 0 | Feb | 2022 | 0.0097751 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
MAYAGÃœEZ | 2022-02-12 16:29 | 2022-02-12 16:30 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1097 | keep | 0 | Feb | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
FAJARDO | 2022-02-12 16:31 | 2022-02-12 18:02 | 100 | 001:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22021200042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-02-12 | 9100 | keep | 0 | Feb | 2022 | 0.006198 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-12 16:32 | 2022-02-14 08:20 | 30 | 039:48 | P | DESCONECTIVO DEFECTUOSO | SE ABRE MACHETE PARA REMPLAZAR MACHETE QUEMADO | S22021200055 | New_Event | Switch Failure | Include | Include | Equipment | 2388 | 2022-02-12 | 71640 | keep | 0 | Feb | 2022 | 0.048794 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-12 16:35 | 2022-02-12 23:55 | 50 | 007:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2022-02-12 | 22000 | keep | 0 | Feb | 2022 | 0.014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-12 16:38 | 2022-02-12 20:08 | 50 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22021200104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-02-12 | 10500 | keep | 0 | Feb | 2022 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-12 17:00 | 2022-02-12 17:01 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22021200241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 4634 | keep | 0 | Feb | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-02-12 17:19 | 2022-02-13 11:56 | 60 | 018:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22021200245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1117 | 2022-02-12 | 67020 | keep | 0 | Feb | 2022 | 0.045647 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-02-12 17:19 | 2022-02-12 19:06 | 7 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P22021200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-02-12 | 749 | keep | 0 | Feb | 2022 | 0.00051014 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-02-12 17:28 | 2022-02-12 18:23 | 793 | 000:55 | P | DESGANCHE | DISPARO DE INTERRUPTOR. SE RETIRO RAMA SOBRE LAS LINEAS Y SE CERRO POR SCADA. | S22021200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-02-12 | 43615 | keep | 0 | Feb | 2022 | 0.029706 | 0.00054011 | Sustained | FALSE | FALSE | Not_TMED_Event | 793
AGUADILLA | 2022-02-12 17:33 | 2022-02-12 19:10 | 100 | 001:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22021200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-02-12 | 9700 | keep | 0 | Feb | 2022 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-12 17:57 | 2022-02-12 19:59 | 70 | 002:02 | P | DESGANCHE | 1 X 40 CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R22021200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-02-12 | 8540 | keep | 0 | Feb | 2022 | 0.0058166 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-02-12 18:00 | 2022-02-12 20:52 | 45 | 002:52 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22021200255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-02-12 | 7740 | keep | 0 | Feb | 2022 | 0.0052717 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2022-02-12 18:08 | 2022-02-12 18:40 | 8 | 000:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA CERRAR PUENTE DE CAJA AL TRANSFORMADOR | C22021200256 | New_Event | Wire Down | Include | Include | Equipment | 32 | 2022-02-12 | 256 | keep | 0 | Feb | 2022 | 0.00017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-12 18:13 | 2022-02-12 21:21 | 35 | 003:08 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA Y SE REPARO TERMINACION EN PROVISIONAL AEREO | S22021200089 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 188 | 2022-02-12 | 6580 | keep | 0 | Feb | 2022 | 0.0044816 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-02-12 18:34 | 2022-02-12 20:08 | 5 | 001:34 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA PARA RETIRAR ARBOL DE LA SECUNDARIA SE DEJO TRAMO DE SECUNDARIA AVERIADA ABIETO PARA TRABAJAR MAÃ‘ANA 2 CLIENTES FUERA | C22021200273 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 94 | 2022-02-12 | 470 | keep | 0 | Feb | 2022 | 0.00032011 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-02-12 18:45 | 2022-02-12 18:46 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 2216 | keep | 0 | Feb | 2022 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
SAN JUAN | 2022-02-12 18:48 | 2022-02-14 17:33 | 17 | 046:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR FASE | S22021200102 | New_Event | Wire Down | Include | Include | Equipment | 2805 | 2022-02-12 | 47685 | keep | 0 | Feb | 2022 | 0.032478 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2022-02-12 19:05 | 2022-02-12 21:20 | 10 | 002:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZARON TERMINACIONES | R22021200064 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 135 | 2022-02-12 | 1350 | keep | 0 | Feb | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-12 19:38 | 2022-02-12 19:39 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1859 | keep | 0 | Feb | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
HUMACAO | 2022-02-12 19:45 | 2022-02-12 21:39 | 2354 | 001:54 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO 3 VECES SE DEJO FUERA SE PATRULLO NO SE ENCONTRO NADA, SOLO MAL TIEMPO EN EL AREA CERRADO POR CONTROL | C22021200269 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2022-02-12 | 268356 | keep | 0 | Feb | 2022 | 0.18278 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2022-02-12 19:52 | 2022-02-13 09:08 | 30 | 013:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | C22021200268 | New_Event | Bad Weather | Include | Include | Weather | 796 | 2022-02-12 | 23880 | keep | 0 | Feb | 2022 | 0.016265 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-02-12 19:53 | 2022-02-12 21:50 | 80 | 001:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | A22021200042 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2022-02-12 | 9360 | keep | 0 | Feb | 2022 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-02-12 20:05 | 2022-02-12 20:06 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22021200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 2697 | keep | 0 | Feb | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
HUMACAO | 2022-02-12 20:08 | 2022-02-13 16:15 | 60 | 020:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22021200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1207 | 2022-02-12 | 72420 | keep | 0 | Feb | 2022 | 0.049325 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-12 20:10 | 2022-02-12 20:11 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22021200273 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1342 | keep | 0 | Feb | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
AGUADILLA | 2022-02-12 20:19 | 2022-02-13 00:29 | 10 | 004:10 | P | DESGANCHE | 1 X 40 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22021200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-02-12 | 2500 | keep | 0 | Feb | 2022 | 0.0017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-12 20:25 | 2022-02-13 12:55 | 400 | 016:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | C22021200274 | New_Event | Wire Down | Include | Include | Equipment | 990 | 2022-02-12 | 396000 | keep | 0 | Feb | 2022 | 0.26971 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2022-02-12 21:02 | 2022-02-13 15:11 | 100 | 018:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22021200276 | New_Event |  |  | Include | Wildlife | 1089 | 2022-02-12 | 108900 | keep | 0 | Feb | 2022 | 0.074171 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-02-12 21:20 | 2022-02-13 10:45 | 20 | 013:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22021200281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 805 | 2022-02-12 | 16100 | keep | 0 | Feb | 2022 | 0.010966 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-02-12 21:48 | 2022-02-12 21:49 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CANOVANAS | 2022-02-12 21:59 | 2022-02-12 22:52 | 35 | 000:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA | R22021200070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-02-12 | 1855 | keep | 0 | Feb | 2022 | 0.0012634 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-02-12 22:14 | 2022-02-13 09:05 | 78 | 010:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBU DE LINEA | P22021200057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 651 | 2022-02-12 | 50778 | keep | 0 | Feb | 2022 | 0.034585 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
ARECIBO | 2022-02-12 22:55 | 2022-02-13 07:27 | 100 | 008:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE CRUZO LINEA | A22021200047 | New_Event |  |  | Include | Wildlife | 512 | 2022-02-12 | 51200 | keep | 0 | Feb | 2022 | 0.034872 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-12 22:59 | 2022-02-13 10:12 | 90 | 011:13 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C22021200293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2022-02-12 | 60570 | keep | 0 | Feb | 2022 | 0.041254 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-02-12 23:08 | 2022-02-13 09:36 | 10 | 010:28 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22021200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 628 | 2022-02-12 | 6280 | keep | 0 | Feb | 2022 | 0.0042773 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-12 23:16 | 2022-02-13 09:29 | 12 | 010:13 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN C/L REEMPLAZO PISTOLA Y BUSHING EN EL T - 5 | R22021200076 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 613 | 2022-02-12 | 7356 | keep | 0 | Feb | 2022 | 0.0050101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-02-12 23:17 | 2022-02-12 23:18 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 2354 | keep | 0 | Feb | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
VEGA BAJA | 2022-02-12 23:19 | 2022-02-13 02:22 | 35 | 003:03 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO ARBOL SOBRE LINEA | B22021200120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-02-12 | 6405 | keep | 0 | Feb | 2022 | 0.0043624 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-02-12 23:20 | 2022-02-13 12:05 | 15 | 012:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22021200057 | New_Event | Cutout Failure | Include | Include | Equipment | 765 | 2022-02-12 | 11475 | keep | 0 | Feb | 2022 | 0.0078156 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-12 23:25 | 2022-02-12 23:26 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-12 | 1097 | keep | 0 | Feb | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
FAJARDO | 2022-02-12 23:31 | 2022-02-13 17:10 | 31 | 017:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REEMPLAZO CAJA PRIMARIA AVERIADA | R22021200073 | New_Event | Cutout Failure | Include | Include | Equipment | 1059 | 2022-02-12 | 32829 | keep | 0 | Feb | 2022 | 0.02236 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2022-02-12 23:31 | 2022-02-13 17:22 | 13 | 017:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO T-16 DE 50 KVA X 100 KVA | R22021200077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1071 | 2022-02-12 | 13923 | keep | 0 | Feb | 2022 | 0.0094829 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-02-13 00:21 | 2022-02-13 01:54 | 100 | 001:33 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-02-13 | 9300 | keep | 0 | Feb | 2022 | 0.0063342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-13 01:48 | 2022-02-13 05:04 | 25 | 003:16 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA | S22021300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-02-13 | 4900 | keep | 0 | Feb | 2022 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-02-13 01:57 | 2022-02-13 01:58 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22021300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
VEGA BAJA | 2022-02-13 02:13 | 2022-02-13 09:58 | 20 | 007:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2022-02-13 | 9300 | keep | 0 | Feb | 2022 | 0.0063342 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-13 03:08 | 2022-02-13 10:31 | 250 | 007:23 | P | SOBRECARGA | 2 X 65, 3 X 80 Y 3 X 100 EN CORTES DE LINEA CORDINO LOS FUSIBLES | R22021300024 | New_Event | Trip Due To Overload | Include | Include | Other | 443 | 2022-02-13 | 110750 | keep | 0 | Feb | 2022 | 0.075431 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-02-13 03:51 | 2022-02-13 03:52 | 1070 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 1070 | keep | 0 | Feb | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
SAN JUAN | 2022-02-13 06:25 | 2022-02-14 08:11 | 22 | 025:46 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR | R22021300048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1546 | 2022-02-13 | 34012 | keep | 0 | Feb | 2022 | 0.023165 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2022-02-13 06:29 | 2022-02-13 06:30 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1346-4 | S22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 726 | keep | 0 | Feb | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-02-13 06:29 | 2022-02-13 06:30 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-3 | S22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 3932 | keep | 0 | Feb | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 137 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 548 | keep | 0 | Feb | 2022 | 0.00037324 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 457 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 1828 | keep | 0 | Feb | 2022 | 0.001245 | 0.00031126 | Momentary | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 1225 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 4900 | keep | 0 | Feb | 2022 | 0.0033374 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 1452 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 5808 | keep | 0 | Feb | 2022 | 0.0039558 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 616 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 2464 | keep | 0 | Feb | 2022 | 0.0016782 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 3432 | 000:04 | P | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 13728 | keep | 0 | Feb | 2022 | 0.0093501 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-02-13 07:19 | 2022-02-13 07:23 | 552 | 000:04 | P | LINEA DE TRANSMISION 38KV | DISPARO L-3100 | S22021300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-02-13 | 2208 | keep | 0 | Feb | 2022 | 0.0015039 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
UTUADO | 2022-02-13 07:20 | 2022-02-13 11:31 | 10 | 004:11 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO BAMBUA SOBRE CONVERTIDOR | A22021300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-02-13 | 2510 | keep | 0 | Feb | 2022 | 0.0017095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-02-13 07:23 | 2022-02-13 17:34 | 63 | 010:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | R22021300014 | New_Event |  |  | Include | Wildlife | 611 | 2022-02-13 | 38493 | keep | 0 | Feb | 2022 | 0.026217 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
GUAYAMA | 2022-02-13 07:32 | 2022-02-13 10:06 | 89 | 002:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA | P22020130001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-02-13 | 13706 | keep | 0 | Feb | 2022 | 0.0093351 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2022-02-13 07:57 | 2022-02-13 10:01 | 15 | 002:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR 200 PIES DE SECUNDARIA | B22021200117 | New_Event | Secondary Wire Down | Include | Include | Equipment | 124 | 2022-02-13 | 1860 | keep | 0 | Feb | 2022 | 0.0012668 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-13 08:20 | 2022-02-13 10:48 | 30 | 002:28 | P | TRANSFORMADOR AVERIADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR TRANSFORMADOR 37.5 X 37.5 TRAS PATIO | S22021200044 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 148 | 2022-02-13 | 4440 | keep | 0 | Feb | 2022 | 0.0030241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-13 08:29 | 2022-02-13 12:27 | 111 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN TRONCAL | C22021300034 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2022-02-13 | 26418 | keep | 0 | Feb | 2022 | 0.017993 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
GUAYAMA | 2022-02-13 08:35 | 2022-02-13 12:33 | 39 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO PUENTE SAFADO EN CORTE DE LINEA | P22021300003 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2022-02-13 | 9282 | keep | 0 | Feb | 2022 | 0.0063219 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-02-13 08:50 | 2022-02-13 11:49 | 30 | 002:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-02-13 | 5370 | keep | 0 | Feb | 2022 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-13 08:57 | 2022-02-13 10:01 | 50 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22021300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-02-13 | 3200 | keep | 0 | Feb | 2022 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-13 08:59 | 2022-02-13 10:52 | 10 | 001:53 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 20 EN TRANSFORMADOR SE REPARO PEDESTAL SECUNDARIO | B22021300006 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 113 | 2022-02-13 | 1130 | keep | 0 | Feb | 2022 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-13 09:08 | 2022-02-13 10:43 | 40 | 001:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R22021300024 | New_Event |  |  | Include | Wildlife | 95 | 2022-02-13 | 3800 | keep | 0 | Feb | 2022 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-13 09:19 | 2022-02-13 11:04 | 160 | 001:45 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA | C22021300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-02-13 | 16800 | keep | 0 | Feb | 2022 | 0.011442 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
ARECIBO | 2022-02-13 09:30 | 2022-02-13 11:28 | 100 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22021300006 | New_Event |  |  | Include | Wildlife | 118 | 2022-02-13 | 11800 | keep | 0 | Feb | 2022 | 0.0080369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-02-13 09:37 | 2022-02-13 13:20 | 100 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CONVERTIDOR POR LLUVIA Y VIENTO | A22021300010 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-02-13 | 22300 | keep | 0 | Feb | 2022 | 0.015188 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-13 09:39 | 2022-02-14 10:19 | 40 | 024:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA | M22021300037 | New_Event | Bad Weather | Include | Include | Weather | 1480 | 2022-02-13 | 59200 | keep | 0 | Feb | 2022 | 0.040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-13 09:47 | 2022-02-13 13:43 | 50 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22021300012 | New_Event |  |  | Include | Wildlife | 236 | 2022-02-13 | 11800 | keep | 0 | Feb | 2022 | 0.0080369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-13 09:49 | 2022-02-13 13:35 | 164 | 003:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22021300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-02-13 | 37064 | keep | 0 | Feb | 2022 | 0.025244 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
AGUADILLA | 2022-02-13 09:51 | 2022-02-13 10:29 | 1415 | 000:38 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION SUP. FELIX CASIANO PARA REMPLAZO DE MACHETE PRIMARIO CON PUENTE PORTATIL | M22021300013 | New_Event | Switch Failure | Include | Include | Equipment | 38 | 2022-02-13 | 53770 | keep | 0 | Feb | 2022 | 0.036623 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
BAYAMON | 2022-02-13 10:17 | 2022-02-13 17:15 | 15 | 006:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR 75KVA Y SE REPUSO 1X20 EN TRANSFORMADOR | B22031300000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 418 | 2022-02-13 | 6270 | keep | 0 | Feb | 2022 | 0.0042705 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-13 10:20 | 2022-02-13 10:21 | 1860 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | S22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 1860 | keep | 0 | Feb | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
ARECIBO | 2022-02-13 10:30 | 2022-02-13 15:35 | 15 | 005:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO CONECTORES DE BAJANTE PRIMARIO | A22021300034 | New_Event | Wire Down | Include | Include | Equipment | 305 | 2022-02-13 | 4575 | keep | 0 | Feb | 2022 | 0.003116 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-13 10:58 | 2022-02-13 12:52 | 10 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REEMPLAZARON CONECTORES | C22021300060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2022-02-13 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-13 11:04 | 2022-02-13 12:16 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | B22021300007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2022-02-13 | 720 | keep | 0 | Feb | 2022 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-02-13 11:14 | 2022-02-13 15:00 | 50 | 003:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A22021300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-02-13 | 11300 | keep | 0 | Feb | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-13 12:18 | 2022-02-13 23:31 | 60 | 011:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22021300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 673 | 2022-02-13 | 40380 | keep | 0 | Feb | 2022 | 0.027503 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-13 12:22 | 2022-02-14 20:58 | 40 | 032:36 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C22021300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1956 | 2022-02-13 | 78240 | keep | 0 | Feb | 2022 | 0.053289 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-13 12:27 | 2022-02-13 14:05 | 111 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PB-B PARA CERRAR PUENTE ABIERTO EN TRONCAL | C22021300034 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-02-13 | 10878 | keep | 0 | Feb | 2022 | 0.007409 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
FAJARDO | 2022-02-13 12:51 | 2022-02-13 18:52 | 70 | 006:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN BANCO DE TRANSFORMADORES MAL TIEMPO | R22021300036 | New_Event | Bad Weather | Include | Include | Weather | 361 | 2022-02-13 | 25270 | keep | 0 | Feb | 2022 | 0.017211 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-02-13 13:02 | 2022-02-13 14:06 | 14 | 001:04 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO TRANSFORMADOR PARA REPARAR TERMINACION EN AEREO PROVISIONAL | R22021300034 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 64 | 2022-02-13 | 896 | keep | 0 | Feb | 2022 | 0.00061026 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-02-13 13:16 | 2022-02-13 15:28 | 6 | 002:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C22021300086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 132 | 2022-02-13 | 792 | keep | 0 | Feb | 2022 | 0.00053943 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-02-13 13:24 | 2022-02-13 13:35 | 20 | 000:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES Y LLUVIAS | A22021300028 | New_Event | Bad Weather | Include | Include | Weather | 11 | 2022-02-13 | 220 | keep | 0 | Feb | 2022 | 0.00014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-13 13:34 | 2022-02-13 13:35 | 225 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1303-05 QUE LLEVA CARGA DEL 1303-04 PARA REALIZAR OPERACIONES POR CONDUCTOR EN EL SUELO Y SE CERRO POR SCADA | S22021300045 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-13 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-02-13 13:34 | 2022-02-13 13:35 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR SCADA PARA REALIZAR OPERACIONES POR CONDUCTOR EN EL SUELO LLEVANDO LA CARGA DEL 1303-04 | S22021300045 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-13 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-02-13 13:36 | 2022-02-13 16:03 | 225 | 002:27 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES CONTRA EL 1303-05 | S22021300045 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 147 | 2022-02-13 | 33075 | keep | 0 | Feb | 2022 | 0.022527 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-02-13 13:36 | 2022-02-13 13:45 | 870 | 000:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | REALIZANDO OERACIONES DISPARO Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1303-04 | S22021300045 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 9 | 2022-02-13 | 7830 | keep | 0 | Feb | 2022 | 0.005333 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-02-13 13:39 | 2022-02-13 13:40 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-13 13:39 | 2022-02-13 13:40 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
SAN JUAN | 2022-02-13 13:45 | 2022-02-13 16:01 | 506 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE NORMALIZARON LAS OPERACIONES | S22021300045 | Partial_restoration | Wire Down | Include | Include | Equipment | 136 | 2022-02-13 | 68816 | keep | 0 | Feb | 2022 | 0.04687 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-13 14:11 | 2022-02-14 12:19 | 5 | 022:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25 KVA | S22021300105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1328 | 2022-02-13 | 6640 | keep | 0 | Feb | 2022 | 0.0045225 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-02-13 14:19 | 2022-02-13 16:50 | 50 | 002:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22021300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-02-13 | 7550 | keep | 0 | Feb | 2022 | 0.0051423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-13 14:21 | 2022-02-13 17:34 | 33 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C22021300093 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2022-02-13 | 6369 | keep | 0 | Feb | 2022 | 0.0043379 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
UTUADO | 2022-02-13 14:26 | 2022-02-13 16:59 | 25 | 002:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22021300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-02-13 | 3825 | keep | 0 | Feb | 2022 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-13 14:42 | 2022-02-13 14:44 | 1860 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POR SCADA | S22021300000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-13 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-02-13 14:44 | 2022-02-13 20:57 | 620 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN SALIDA DEL ALIMENTADOR | S22021300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 373 | 2022-02-13 | 231260 | keep | 0 | Feb | 2022 | 0.15751 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
CAGUAS | 2022-02-13 14:47 | 2022-02-13 19:36 | 130 | 004:49 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTE DE LINEA | C22021300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-02-13 | 37570 | keep | 0 | Feb | 2022 | 0.025589 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
GUAYAMA | 2022-02-13 14:48 | 2022-02-13 15:50 | 6 | 001:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE DE BAJANTE SECUNDARIO POR AVE | P22021300014 | New_Event |  |  | Include | Wildlife | 62 | 2022-02-13 | 372 | keep | 0 | Feb | 2022 | 0.00025337 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-02-13 14:50 | 2022-02-13 16:33 | 7 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR 3 BARRAS EN PEDESTAL Y BAJANTES SECUNDARIOS EN TRANSFORMADOR | P22021300013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2022-02-13 | 721 | keep | 0 | Feb | 2022 | 0.00049107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-02-13 14:51 | 2022-02-13 20:15 | 20 | 005:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22021300030 | New_Event | Wire Down | Include | Include | Equipment | 324 | 2022-02-13 | 6480 | keep | 0 | Feb | 2022 | 0.0044135 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-13 14:55 | 2022-02-13 16:52 | 70 | 001:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22021300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-02-13 | 8190 | keep | 0 | Feb | 2022 | 0.0055782 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-02-13 15:19 | 2022-02-13 15:21 | 2450 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE CERRO POR CONTROL | C22021300099 | New_Event |  |  | Include | Wildlife | 2 | 2022-02-13 | 4900 | keep | 0 | Feb | 2022 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-02-13 15:21 | 2022-02-13 16:37 | 80 | 001:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C22021300107 | 1st_after_momentary |  |  | Include | Wildlife | 76 | 2022-02-13 | 6080 | keep | 0 | Feb | 2022 | 0.0041411 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-13 15:34 | 2022-02-14 16:09 | 10 | 024:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS EN PEDESTAL | B22021300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1475 | 2022-02-13 | 14750 | keep | 0 | Feb | 2022 | 0.010046 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-13 15:44 | 2022-02-13 15:45 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 3941 | keep | 0 | Feb | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-02-13 16:09 | 2022-02-13 23:44 | 75 | 007:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22021300155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 455 | 2022-02-13 | 34125 | keep | 0 | Feb | 2022 | 0.023242 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-13 16:15 | 2022-02-13 16:16 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 EL 50% DE SU CARGA TRANSFERIDO AL 1909-07 Y LLEVA LA CARGA TOTAL DEL 1709-05 | B22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 767 | keep | 0 | Feb | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-02-13 16:15 | 2022-02-13 16:16 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 EL 50% DE SU CARGA TRANSFERIDO AL 1909-07 Y LLEVA LA CARGA TOTAL DEL 1709-05 | B22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 2364 | keep | 0 | Feb | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
ARECIBO | 2022-02-13 16:30 | 2022-02-13 17:05 | 20 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE QUEMADO | A22021300037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-02-13 | 700 | keep | 0 | Feb | 2022 | 0.00047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-02-13 16:37 | 2022-02-13 16:38 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22021300099 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-02-13 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-13 16:38 | 2022-02-13 18:18 | 80 | 001:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C22021300107 | 1st_after_momentary |  |  | Include | Wildlife | 100 | 2022-02-13 | 8000 | keep | 0 | Feb | 2022 | 0.0054488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-02-13 16:38 | 2022-02-13 16:39 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-13 16:38 | 2022-02-13 16:39 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO 17% DE LA CARGA DEL 9202-03 | B22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 500 | keep | 0 | Feb | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-02-13 16:41 | 2022-02-13 20:52 | 50 | 004:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22021300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-02-13 | 12550 | keep | 0 | Feb | 2022 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-13 16:48 | 2022-02-13 16:54 | 1844 | 000:06 | T | DESCONECTIVO DEFECTUOSO | PERSONAL REALIZANDO OPERACIONES DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1346-03 | S22021300000 | New_Event | Switch Failure | Include | Include | Equipment | 6 | 2022-02-13 | 11064 | keep | 0 | Feb | 2022 | 0.0075356 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2022-02-13 16:48 | 2022-02-13 16:54 | 2422 | 000:06 | T | DESCONECTIVO DEFECTUOSO | PERSONAL REALIZANDO PRUEBAS DISPARO INTERRUPTOR SE CERRO POR SCADA | S22021300000 | New_Event | Switch Failure | Include | Include | Equipment | 6 | 2022-02-13 | 14532 | keep | 0 | Feb | 2022 | 0.0098977 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
SAN JUAN | 2022-02-13 16:51 | 2022-02-14 01:51 | 1 | 009:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21202130016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 540 | 2022-02-13 | 540 | keep | 0 | Feb | 2022 | 0.00036779 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-13 17:34 | 2022-02-13 19:00 | 1 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | A22021300040 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2022-02-13 | 86 | keep | 0 | Feb | 2022 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-13 17:45 | 2022-02-13 17:46 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 320 | keep | 0 | Feb | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-02-13 17:47 | 2022-02-13 20:37 | 1 | 002:50 | T | NO SE REPORTO CAUSA | SE INSPECCIONO LA SUBESTACION NO SE ENCONTRO CONDICION Y SE CERRO POR SCADA | S22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-02-13 | 170 | keep | 0 | Feb | 2022 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-13 17:47 | 2022-02-14 00:52 | 1844 | 007:05 | T | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO LA CARGA AL 1907-04 CON SWITCH FORM SJ-220213-02 | S22021300000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 425 | 2022-02-13 | 783700 | keep | 0 | Feb | 2022 | 0.53377 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-13 17:47 | 2022-02-13 23:38 | 2422 | 005:51 | T | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO LA CARGA AL 1908-03 CON SWITCH FORM SJ-220213-02 SE REPARO CONDICION DE MACHETE QUEMADO EN SWITCHING UNIT Y SE NORMALIZARON LAS CARGAS | S22021300000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 351 | 2022-02-13 | 850122 | keep | 0 | Feb | 2022 | 0.57901 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-13 18:16 | 2022-02-14 09:59 | 140 | 015:43 | P | DESGANCHE | 1 X 200 EN C/L Y 1 X 15 EN XMR | C22021300109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 943 | 2022-02-13 | 132020 | keep | 0 | Feb | 2022 | 0.089918 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
VEGA BAJA | 2022-02-13 18:37 | 2022-02-14 16:48 | 8 | 022:11 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B22021300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1331 | 2022-02-13 | 10648 | keep | 0 | Feb | 2022 | 0.0072523 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-13 18:48 | 2022-02-13 20:32 | 35 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE RETEZO CONDUCTOR | S22021300003 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2022-02-13 | 3640 | keep | 0 | Feb | 2022 | 0.0024792 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2022-02-13 19:13 | 2022-02-14 09:00 | 6 | 013:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22021300045 | New_Event | Bad Weather | Include | Include | Weather | 827 | 2022-02-13 | 4962 | keep | 0 | Feb | 2022 | 0.0033796 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-02-13 19:13 | 2022-02-14 09:41 | 66 | 014:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22021300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 868 | 2022-02-13 | 57288 | keep | 0 | Feb | 2022 | 0.039019 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
MAYAGÃœEZ | 2022-02-13 19:40 | 2022-02-14 02:49 | 100 | 007:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2022-02-13 | 42900 | keep | 0 | Feb | 2022 | 0.029219 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-13 19:45 | 2022-02-14 14:45 | 12 | 019:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 25KVA Y SE REPUSO 1X15 EN EL TRANSFORMADOR NUEVO | B22021300027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1140 | 2022-02-13 | 13680 | keep | 0 | Feb | 2022 | 0.0093174 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-02-13 20:39 | 2022-02-14 11:06 | 40 | 014:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L RETEZO LINEAS | C22021300122 | New_Event | Wire Down | Include | Include | Equipment | 867 | 2022-02-13 | 34680 | keep | 0 | Feb | 2022 | 0.02362 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-13 20:57 | 2022-02-13 22:00 | 1860 | 001:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22021300344 | Additional_clients | Wire Down | Include | Include | Equipment | 63 | 2022-02-13 | 117180 | keep | 0 | Feb | 2022 | 0.079811 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-13 20:58 | 2022-02-14 00:40 | 30 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22021300343 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-02-13 | 6660 | keep | 0 | Feb | 2022 | 0.0045361 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-13 21:06 | 2022-02-13 21:07 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
CAGUAS | 2022-02-13 21:10 | 2022-02-14 09:54 | 40 | 012:44 | P | NO SE REPORTO CAUSA | CERRO CAJA NO FUNDIO | C22021300130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 764 | 2022-02-13 | 30560 | keep | 0 | Feb | 2022 | 0.020814 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-13 21:31 | 2022-02-14 17:41 | 20 | 020:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 37.5KVA | B22021300031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1210 | 2022-02-13 | 24200 | keep | 0 | Feb | 2022 | 0.016483 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-13 22:28 | 2022-02-14 01:48 | 112 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22021300118 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2022-02-13 | 22400 | keep | 0 | Feb | 2022 | 0.015257 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2022-02-13 22:43 | 2022-02-14 10:45 | 12 | 012:02 | P | TRANSFORMADOR AVERIADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR TRANSFORMADOR 25 KVA TRAS PATIO Y CRUCETA PARTIDA | S22021300389 | New_Event | Service Transformer Failure | Include | Include | Equipment | 722 | 2022-02-13 | 8664 | keep | 0 | Feb | 2022 | 0.005901 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-13 22:53 | 2022-02-13 22:54 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 2404-06 | R22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 4085 | keep | 0 | Feb | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-02-13 22:53 | 2022-02-13 22:54 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 2402-03 | R22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-13 | 7621 | keep | 0 | Feb | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CAGUAS | 2022-02-13 23:26 | 2022-02-14 12:52 | 44 | 013:26 | P | DESGANCHE | 1 X 50 EN C/L | C22021300140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 806 | 2022-02-13 | 35464 | keep | 0 | Feb | 2022 | 0.024154 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2022-02-13 23:38 | 2022-02-14 17:46 | 17 | 018:08 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO PUENTE A TERMINACION | S22021300108 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1088 | 2022-02-13 | 18496 | keep | 0 | Feb | 2022 | 0.012598 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2022-02-14 00:40 | 2022-02-14 11:06 | 300 | 010:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M22021400001 | New_Event | Wire Down | Include | Include | Equipment | 626 | 2022-02-14 | 187800 | keep | 0 | Feb | 2022 | 0.12791 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-02-14 01:49 | 2022-02-14 09:19 | 80 | 007:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22021400001 | New_Event |  |  | Include | Wildlife | 450 | 2022-02-14 | 36000 | keep | 0 | Feb | 2022 | 0.024519 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-14 02:57 | 2022-02-14 02:58 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2022-02-14 03:12 | 2022-02-14 08:24 | 20 | 005:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22021400001 | New_Event | Bad Weather | Include | Include | Weather | 312 | 2022-02-14 | 6240 | keep | 0 | Feb | 2022 | 0.00425 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-14 03:13 | 2022-02-14 10:03 | 41 | 006:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22021400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 410 | 2022-02-14 | 16810 | keep | 0 | Feb | 2022 | 0.011449 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2022-02-14 03:25 | 2022-02-14 11:52 | 82 | 008:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C22021400007 | New_Event |  |  | Include | Wildlife | 507 | 2022-02-14 | 41574 | keep | 0 | Feb | 2022 | 0.028316 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
SAN JUAN | 2022-02-14 03:43 | 2022-02-14 03:58 | 50 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | S22021400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-02-14 | 750 | keep | 0 | Feb | 2022 | 0.00051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-14 04:49 | 2022-02-14 04:50 | 2600 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL 40% DE LA CARGA TRANSFERIDA AL 1718-03 | B22021400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-14 | 2600 | keep | 0 | Feb | 2022 | 0.0017708 | 0.0017708 | Momentary | FALSE | FALSE | Not_TMED_Event | 2600
BAYAMON | 2022-02-14 04:50 | 2022-02-14 07:57 | 30 | 003:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA TRASPATIO | B22021400007 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2022-02-14 | 5610 | keep | 0 | Feb | 2022 | 0.0038209 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-14 04:50 | 2022-02-14 11:20 | 300 | 006:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO DE LINEA A MACHETES | B22021400041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 390 | 2022-02-14 | 117000 | keep | 0 | Feb | 2022 | 0.079688 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-02-14 06:25 | 2022-02-14 19:28 | 50 | 013:03 | P | DESGANCHE | 1 X 50 EN C/L | C22021400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 783 | 2022-02-14 | 39150 | keep | 0 | Feb | 2022 | 0.026665 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-14 06:30 | 2022-02-14 06:31 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO 17% DE LA CARGA DEL 9202-03 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-14 06:30 | 2022-02-14 06:31 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO 17% DE LA CARGA DEL 9202-03 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 500 | keep | 0 | Feb | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2022-02-14 06:41 | 2022-02-14 10:20 | 15 | 003:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEA | M22021400020 | New_Event |  |  | Include | Wildlife | 219 | 2022-02-14 | 3285 | keep | 0 | Feb | 2022 | 0.0022374 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-14 06:51 | 2022-02-14 11:40 | 33 | 004:49 | P | DESGANCHE | 1 X 50 EN C/L | C22021400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-02-14 | 9537 | keep | 0 | Feb | 2022 | 0.0064956 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
FAJARDO | 2022-02-14 07:37 | 2022-02-14 10:41 | 8 | 003:04 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R22021400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-02-14 | 1472 | keep | 0 | Feb | 2022 | 0.0010026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-14 07:49 | 2022-02-14 07:50 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 2858 | keep | 0 | Feb | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
ARECIBO | 2022-02-14 07:57 | 2022-02-14 10:07 | 6 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22021400008 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2022-02-14 | 780 | keep | 0 | Feb | 2022 | 0.00053125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-02-14 08:07 | 2022-02-14 08:08 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR 9207-08 LLEVANDO 9207-09 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 1859 | keep | 0 | Feb | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-02-14 08:07 | 2022-02-14 08:08 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR 9207-08 LLEVANDO 9207-09 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 7 | keep | 0 | Feb | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-14 08:17 | 2022-02-14 08:19 | 823 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DEL 1119-04 CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 95% DEL 1115-5 Y 120 AMP. DEL 1119-2 | S22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-14 | 1646 | keep | 0 | Feb | 2022 | 0.0011211 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
BAYAMON | 2022-02-14 08:17 | 2022-02-14 08:19 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DEL 1119-04 CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 95% DEL 1115-5 Y 120 AMP. DEL 1119-2 | S22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-14 | 1000 | keep | 0 | Feb | 2022 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-02-14 08:17 | 2022-02-14 08:19 | 2720 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 95% DEL 1115-5 Y 120 AMP. DEL 1119-2 | S22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-14 | 5440 | keep | 0 | Feb | 2022 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
YAUCO | 2022-02-14 08:17 | 2022-02-14 09:20 | 1 | 001:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE SAFADO EN RISER | P22021400004 | New_Event | Wire Down | Include | Include | Equipment | 63 | 2022-02-14 | 63 | keep | 0 | Feb | 2022 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-14 08:22 | 2022-02-14 10:49 | 100 | 002:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22021400009 | New_Event |  |  | Include | Wildlife | 147 | 2022-02-14 | 14700 | keep | 0 | Feb | 2022 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-14 08:28 | 2022-02-14 09:25 | 20 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA EN TRANSFORMADOR Y SE REPARO SECUNDARIA | M22021300045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-02-14 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-02-14 08:32 | 2022-02-14 10:03 | 8 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | M22021400040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2022-02-14 | 728 | keep | 0 | Feb | 2022 | 0.00049584 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-02-14 08:45 | 2022-02-14 08:51 | 3332 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22021400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-02-14 | 19992 | keep | 0 | Feb | 2022 | 0.013616 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
CAGUAS | 2022-02-14 08:55 | 2022-02-14 15:06 | 1 | 006:11 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | C22021400045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2022-02-14 | 371 | keep | 0 | Feb | 2022 | 0.00025269 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-02-14 09:05 | 2022-02-14 18:40 | 15 | 009:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A22021400016 | New_Event | Wire Down | Include | Include | Equipment | 575 | 2022-02-14 | 8625 | keep | 0 | Feb | 2022 | 0.0058744 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-02-14 09:06 | 2022-02-14 10:30 | 25 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PERSONAL DE TELEFONICA IMPACTO POSTE | M22021400038 | New_Event |  |  | Include | Wildlife | 84 | 2022-02-14 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-14 09:12 | 2022-02-14 13:37 | 30 | 004:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22021400039 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2022-02-14 | 7950 | keep | 0 | Feb | 2022 | 0.0054147 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-14 09:24 | 2022-02-14 09:25 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 1342 | keep | 0 | Feb | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BAYAMON | 2022-02-14 09:35 | 2022-02-14 16:25 | 50 | 006:50 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO DE CEMENTO COMPLETAMENTE DETERIORADO/AGRIETADO POR POSTE DE METAL | B22021400102 | New_Event | Defective Pole | Include | Include | Equipment | 410 | 2022-02-14 | 20500 | keep | 0 | Feb | 2022 | 0.013962 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 1526 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 1526 | keep | 0 | Feb | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 308 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 1397 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 1397 | keep | 0 | Feb | 2022 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 2926 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 2926 | keep | 0 | Feb | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2022-02-14 09:38 | 2022-02-14 09:39 | 1834 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 1834 | keep | 0 | Feb | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-02-14 09:38 | 2022-02-14 09:39 | 2324 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 2324 | keep | 0 | Feb | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 1570 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 1570 | keep | 0 | Feb | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 27 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 27 | keep | 0 | Feb | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 603 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 603 | keep | 0 | Feb | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 6 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 6 | keep | 0 | Feb | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 325 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 325 | keep | 0 | Feb | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2022-02-14 09:38 | 2022-02-14 09:39 | 172 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 172 | keep | 0 | Feb | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2022-02-14 09:38 | 2022-02-14 09:39 | 2861 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 2861 | keep | 0 | Feb | 2022 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2022-02-14 09:38 | 2022-02-14 09:39 | 2096 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 2096 | keep | 0 | Feb | 2022 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2022-02-14 09:38 | 2022-02-14 09:39 | 493 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DORADO TC | B22021400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-02-14 | 493 | keep | 0 | Feb | 2022 | 0.00033578 | 0.00033578 | Momentary | FALSE | FALSE | Not_TMED_Event | 493
UTUADO | 2022-02-14 09:46 | 2022-02-14 12:13 | 1 | 002:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A22021400022 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2022-02-14 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-14 09:53 | 2022-02-14 18:12 | 80 | 008:19 | P | DESGANCHE | 1X65 EN CORTE DE LINEA EN LA CALLE D Y 1X50 EN CORTE DE LINEA EN LA CALLE C | B22021400117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 499 | 2022-02-14 | 39920 | keep | 0 | Feb | 2022 | 0.027189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-14 10:04 | 2022-02-15 08:27 | 25 | 022:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN XMR | S22021400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1343 | 2022-02-14 | 33575 | keep | 0 | Feb | 2022 | 0.022868 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-14 10:10 | 2022-02-14 10:27 | 65 | 000:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN XMR CONDUCTOR CRUZADO | C22021400068 | New_Event | Wire Down | Include | Include | Equipment | 17 | 2022-02-14 | 1105 | keep | 0 | Feb | 2022 | 0.00075261 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-02-14 10:14 | 2022-02-14 10:28 | 1 | 000:14 | P | DESGANCHE | 1 X 20 EN RISER | R22021400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-02-14 | 14 | keep | 0 | Feb | 2022 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-14 10:34 | 2022-02-14 12:27 | 75 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22021400028 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-02-14 | 8475 | keep | 0 | Feb | 2022 | 0.0057723 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-02-14 10:38 | 2022-02-14 11:37 | 2354 | 000:59 | T | DESCONECTIVO DEFECTUOSO | ROMPE ARCO AVERIADO EN EL SU - 1 | C22021400000 | New_Event | Switch Failure | Include | Include | Equipment | 59 | 2022-02-14 | 138886 | keep | 0 | Feb | 2022 | 0.094595 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2022-02-14 10:45 | 2022-02-14 16:00 | 457 | 005:15 | P | TRANSFORMADOR AVERIADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR TRANSFORMADOR 25 KVA TRAS PATIO Y CRUCETA PARTIDA | S22021300389 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 315 | 2022-02-14 | 143955 | keep | 0 | Feb | 2022 | 0.098047 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-14 10:53 | 2022-02-14 14:16 | 6 | 003:23 | P | DESGANCHE | 1 X 100 EN C/L | C22021400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-02-14 | 1218 | keep | 0 | Feb | 2022 | 0.00082957 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-14 11:00 | 2022-02-15 17:02 | 12 | 030:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75KVA POR 75KVA | S22021400044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1802 | 2022-02-14 | 21624 | keep | 0 | Feb | 2022 | 0.014728 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-14 11:10 | 2022-02-14 11:11 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 4188 | keep | 0 | Feb | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-02-14 11:10 | 2022-02-14 11:11 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2402-02 | R22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 2675 | keep | 0 | Feb | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
VEGA BAJA | 2022-02-14 11:12 | 2022-02-14 13:13 | 1 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22021400156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-02-14 | 121 | keep | 0 | Feb | 2022 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-14 11:30 | 2022-02-14 13:31 | 7 | 002:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES | M22021400054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 121 | 2022-02-14 | 847 | keep | 0 | Feb | 2022 | 0.00057689 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-02-14 11:36 | 2022-02-14 13:28 | 5 | 001:52 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 2 X 8 EN TRANSFORMADOR SE REMPLAZO POSTE PARTIDO | M22021400055 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 112 | 2022-02-14 | 560 | keep | 0 | Feb | 2022 | 0.00038141 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-02-14 11:51 | 2022-02-14 11:52 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 215 | keep | 0 | Feb | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2022-02-14 12:02 | 2022-02-14 12:04 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO CARGA POR EL 1401-08 | S22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-14 | 1844 | keep | 0 | Feb | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-14 12:02 | 2022-02-14 12:04 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1346-5 | S22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-14 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2022-02-14 12:09 | 2022-02-14 12:10 | 222 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | B22021400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-14 | 222 | keep | 0 | Feb | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-02-14 12:09 | 2022-02-14 12:10 | 4456 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | B22021400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-14 | 4456 | keep | 0 | Feb | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-02-14 12:10 | 2022-02-14 21:22 | 25 | 009:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X50 EN CORTE DE LINEA Y SE REPARO PUENTE PRIMARIO QUE HABIA CHOCADO CON LA OTRA FASE | B22021400065 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 552 | 2022-02-14 | 13800 | keep | 0 | Feb | 2022 | 0.0093991 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-02-14 12:20 | 2022-02-14 13:08 | 26 | 000:48 | P | SECUNDARIA/ESTRUCTURA AVERIADA | POSTE SECUNDARIO PARTIDO SE RELOCALIZO LINEA SECUNDARIA | P22021400023 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 48 | 2022-02-14 | 1248 | keep | 0 | Feb | 2022 | 0.00085001 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
PONCE | 2022-02-14 12:25 | 2022-02-14 13:33 | 150 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEA CRUZADA POR LA BRISA | P22021400030 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-02-14 | 10200 | keep | 0 | Feb | 2022 | 0.0069472 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-14 12:33 | 2022-02-14 12:34 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 1362 | keep | 0 | Feb | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
GUAYAMA | 2022-02-14 12:36 | 2022-02-14 13:50 | 125 | 001:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 80 EN CORTE DE LINEA | P22021400026 | New_Event | Cutout Failure | Include | Include | Equipment | 74 | 2022-02-14 | 9250 | keep | 0 | Feb | 2022 | 0.0063001 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-02-14 12:39 | 2022-02-14 12:40 | 266 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 1717-04 LLEVANDO 20% 1716-02 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 266 | keep | 0 | Feb | 2022 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
BAYAMON | 2022-02-14 12:44 | 2022-02-14 18:47 | 1 | 006:03 | P | DESGANCHE | 1X140 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2022-02-14 | 363 | keep | 0 | Feb | 2022 | 0.00024724 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-14 12:58 | 2022-02-14 13:00 | 651 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-02 20% DE SU CARGA POR 1717-04 | B22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-14 | 1302 | keep | 0 | Feb | 2022 | 0.00088679 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
PONCE | 2022-02-14 13:02 | 2022-02-14 15:28 | 50 | 002:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22021400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2022-02-14 | 7300 | keep | 0 | Feb | 2022 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-14 13:05 | 2022-02-14 16:25 | 15 | 003:20 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | R22021400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-02-14 | 3000 | keep | 0 | Feb | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-14 13:08 | 2022-02-14 19:04 | 120 | 005:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L Y 1X65 EN C/L POR IGUANA EN EL 13KV | B22021400178 | New_Event |  |  | Include | Wildlife | 356 | 2022-02-14 | 42720 | keep | 0 | Feb | 2022 | 0.029096 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-02-14 13:14 | 2022-02-14 15:36 | 12 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22021300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-02-14 | 1704 | keep | 0 | Feb | 2022 | 0.0011606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-14 13:22 | 2022-02-14 17:40 | 200 | 004:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA FUERTES VIENTOS | M22021400064 | New_Event | Bad Weather | Include | Include | Weather | 258 | 2022-02-14 | 51600 | keep | 0 | Feb | 2022 | 0.035145 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-02-14 13:28 | 2022-02-14 14:20 | 2560 | 000:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR ALAMBRE PARTIDO | M22021400065 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2022-02-14 | 133120 | keep | 0 | Feb | 2022 | 0.090667 | 0.0017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 2560
BARRANQUITAS | 2022-02-14 13:32 | 2022-02-15 10:48 | 9 | 021:16 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 37.5KVA X 37.5KVA | C22021400111 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1276 | 2022-02-14 | 11484 | keep | 0 | Feb | 2022 | 0.0078217 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2022-02-14 13:37 | 2022-02-14 15:40 | 70 | 002:03 | P | FUEGO | SE ABRIO CORTE DE LINEA PARA APAGAR FUEGO EN POSTE NO HAY INFORMACION QUE LO PROVOCO | A22021400037 | New_Event | Fire | Include | Include | Public | 123 | 2022-02-14 | 8610 | keep | 0 | Feb | 2022 | 0.0058642 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-02-14 13:37 | 2022-02-14 15:22 | 50 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTE VIENTO | A22021400038 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-02-14 | 5250 | keep | 0 | Feb | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-14 14:02 | 2022-02-14 14:48 | 4 | 000:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN XMR CRUCE X AVE | C22021400113 | New_Event |  |  | Include | Wildlife | 46 | 2022-02-14 | 184 | keep | 0 | Feb | 2022 | 0.00012532 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-02-14 14:08 | 2022-02-14 14:09 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22021400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 2107 | keep | 0 | Feb | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
MAYAGÃœEZ | 2022-02-14 14:16 | 2022-02-14 16:02 | 70 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22021400084 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2022-02-14 | 7420 | keep | 0 | Feb | 2022 | 0.0050537 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-02-14 14:20 | 2022-02-14 15:24 | 728 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTES Y SE CERRO MACHETES PARA SECCIONALIZAR ALAMBRE PARTIDO | M22021400078 | Partial_restoration | Wire Down | Include | Include | Equipment | 64 | 2022-02-14 | 46592 | keep | 0 | Feb | 2022 | 0.031734 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-14 14:45 | 2022-02-15 04:55 | 15 | 014:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22021400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 850 | 2022-02-14 | 12750 | keep | 0 | Feb | 2022 | 0.008684 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-14 14:45 | 2022-02-14 16:00 | 12 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA Y SE REPARO SECUNDARIA | S22021200059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-02-14 | 900 | keep | 0 | Feb | 2022 | 0.00061299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-02-14 14:53 | 2022-02-14 18:47 | 8 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE DIERON CONECTORES Y SE REMPLAZO BAJANTE SECUNDARIO EN TRANSFORMADOR | B22021400193 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2022-02-14 | 1872 | keep | 0 | Feb | 2022 | 0.001275 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-02-14 15:00 | 2022-02-14 16:00 | 3 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22021400078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-02-14 | 180 | keep | 0 | Feb | 2022 | 0.0001226 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-02-14 15:05 | 2022-02-14 15:35 | 7 | 000:30 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REPARAR BARRA SECUNDARIA QUEMADA | M22021400085 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 30 | 2022-02-14 | 210 | keep | 0 | Feb | 2022 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-02-14 15:24 | 2022-02-14 18:55 | 5 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO PUENTES | M22021400090 | Partial_restoration | Wire Down | Include | Include | Equipment | 211 | 2022-02-14 | 1055 | keep | 0 | Feb | 2022 | 0.00071856 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-14 15:27 | 2022-02-14 15:38 | 1 | 000:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22021400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-02-14 | 11 | keep | 0 | Feb | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-14 15:30 | 2022-02-15 13:46 | 51 | 022:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25 KVA X 37.5 KVA | S22021400081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1336 | 2022-02-14 | 68136 | keep | 0 | Feb | 2022 | 0.046407 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
FAJARDO | 2022-02-14 15:52 | 2022-02-14 17:53 | 20 | 002:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRIMARIA | R22021400024 | New_Event | Cutout Failure | Include | Include | Equipment | 121 | 2022-02-14 | 2420 | keep | 0 | Feb | 2022 | 0.0016483 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-02-14 15:53 | 2022-02-15 09:58 | 60 | 018:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22021400122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1085 | 2022-02-14 | 65100 | keep | 0 | Feb | 2022 | 0.044339 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-02-14 16:05 | 2022-02-14 16:30 | 14 | 000:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 2.4 KV AVERIADO | P22021400047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 25 | 2022-02-14 | 350 | keep | 0 | Feb | 2022 | 0.00023838 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-02-14 16:08 | 2022-02-14 20:31 | 12 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA EN LA ENTRADA HACIA EL TRANSFORMADOR | B22021400200 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-02-14 | 3156 | keep | 0 | Feb | 2022 | 0.0021495 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-02-14 16:08 | 2022-02-15 07:53 | 30 | 015:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PERSONAS NO EMPLEADOS TUMBARON RAMA Y CRUZARON LINEAS | B22021400199 | New_Event |  |  | Include | Wildlife | 945 | 2022-02-14 | 28350 | keep | 0 | Feb | 2022 | 0.019309 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-14 16:26 | 2022-02-15 13:48 | 50 | 021:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO, NO FUNDIO FUSIBLE. | C22021400127 | New_Event | Wire Down | Include | Include | Equipment | 1282 | 2022-02-14 | 64100 | keep | 0 | Feb | 2022 | 0.043658 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-14 16:57 | 2022-02-14 22:43 | 60 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 65 EN CORTE DE LINEA | S22021400092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2022-02-14 | 20760 | keep | 0 | Feb | 2022 | 0.01414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-02-14 17:20 | 2022-02-14 17:21 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22021400053 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-14 | 464 | keep | 0 | Feb | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-02-14 17:21 | 2022-02-14 19:23 | 60 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUE DE FASE PRIMARIA POR AVE | P22021400053 | 1st_after_momentary |  |  | Include | Wildlife | 122 | 2022-02-14 | 7320 | keep | 0 | Feb | 2022 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-14 17:36 | 2022-02-14 17:45 | 1 | 000:09 | P | NO SE REPORTO CAUSA | 1X40 DE RISER @ BANCO DE TRANSFORMADORES DE ELLOS | B22021400216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-02-14 | 9 | keep | 0 | Feb | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-14 17:42 | 2022-02-14 17:43 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-02-14 17:50 | 2022-02-14 19:35 | 125 | 001:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22021400119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-02-14 | 13125 | keep | 0 | Feb | 2022 | 0.0089394 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-02-14 17:53 | 2022-02-14 20:28 | 20 | 002:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M22021400122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-02-14 | 3100 | keep | 0 | Feb | 2022 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-14 18:01 | 2022-02-14 18:50 | 12 | 000:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES ROTO | A22021400062 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2022-02-14 | 588 | keep | 0 | Feb | 2022 | 0.00040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-14 18:06 | 2022-02-14 23:14 | 10 | 005:08 | P | DESGANCHE | 1 X 50 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22021300127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-02-14 | 3080 | keep | 0 | Feb | 2022 | 0.0020978 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-14 18:23 | 2022-02-15 10:26 | 15 | 016:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021400220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 963 | 2022-02-14 | 14445 | keep | 0 | Feb | 2022 | 0.0098384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-02-14 18:36 | 2022-02-14 20:32 | 30 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22021400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-02-14 | 3480 | keep | 0 | Feb | 2022 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-14 18:37 | 2022-02-14 20:41 | 12 | 002:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 15KVA POR 37.5KVA Y SE REPUSO 1X15 EN TRANSFORMADOR | B22021400224 | New_Event | Service Transformer Failure | Include | Include | Equipment | 124 | 2022-02-14 | 1488 | keep | 0 | Feb | 2022 | 0.0010135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-14 19:14 | 2022-02-16 14:08 | 7 | 042:54 | P | CABLE SOTERRADO AVERIADO | 1 X 100 DE RISER @ SU-3 Y 1 X 20 EN PM T-14 SE REPARO CABLE SOTERRADO | S22021400099 | New_Event | UG Cable Fault | Include | Include | Equipment | 2574 | 2022-02-14 | 18018 | keep | 0 | Feb | 2022 | 0.012272 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-14 19:18 | 2022-02-14 19:19 | 10 | 000:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 25KVA | B22021400171 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-02-14 | 10 | keep | 0 | Feb | 2022 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-14 19:28 | 2022-02-15 17:20 | 1 | 021:52 | P | DESGANCHE | 1 X 20 EN RISER SE REALIZO DESGANCHE SIN SERVICIO DESDE EL DIA 14 | M22021500067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1312 | 2022-02-14 | 1312 | keep | 0 | Feb | 2022 | 0.0008936 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-14 19:31 | 2022-02-14 19:32 | 10 | 000:01 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B22021400165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 10 | keep | 0 | Feb | 2022 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-14 19:51 | 2022-02-14 21:14 | 2 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE | S22021300280 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-02-14 | 166 | keep | 0 | Feb | 2022 | 0.00011306 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-02-14 20:00 | 2022-02-14 20:01 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-14 | 1097 | keep | 0 | Feb | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
GUAYAMA | 2022-02-14 20:21 | 2022-02-14 23:20 | 8 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN XMR AVE CRUZO LINEAS | P22021400064 | New_Event |  |  | Include | Wildlife | 179 | 2022-02-14 | 1432 | keep | 0 | Feb | 2022 | 0.00097533 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-14 21:05 | 2022-02-15 15:05 | 4 | 018:00 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO CAJA SECA DE 4 VIAS Y PISTOLA EN MH-15 | S22021400110 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1080 | 2022-02-14 | 4320 | keep | 0 | Feb | 2022 | 0.0029423 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-14 21:32 | 2022-02-15 18:32 | 20 | 021:00 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y TRANSFORMADOR DE 50 KVA | B22021400238 | New_Event | Defective Pole | Include | Include | Equipment | 1260 | 2022-02-14 | 25200 | keep | 0 | Feb | 2022 | 0.017164 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-14 21:52 | 2022-02-15 00:25 | 200 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | B22021400244 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-02-14 | 30600 | keep | 0 | Feb | 2022 | 0.020842 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-02-14 23:41 | 2022-02-15 01:15 | 31 | 001:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO AISLADOR Y SE REPARO BAJANTE | R22021400033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 94 | 2022-02-14 | 2914 | keep | 0 | Feb | 2022 | 0.0019847 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2022-02-15 00:26 | 2022-02-15 00:27 | 424 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 424 | keep | 0 | Feb | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
MAYAGÃœEZ | 2022-02-15 00:26 | 2022-02-15 05:47 | 199 | 005:21 | T | ESTRUCTURA AVERIADA | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA DE POSTE PRIMARIO PARTIDO | M22021500001 | New_Event | Defective Pole | Include | Include | Equipment | 321 | 2022-02-15 | 63879 | keep | 0 | Feb | 2022 | 0.043508 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2022-02-15 00:33 | 2022-02-15 00:35 | 837 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR 1401-07 DISPARO Y SE CERRO POR CONTROL ESTE LLEVA LA CARGA DEL 1401-06 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-15 | 1674 | keep | 0 | Feb | 2022 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-02-15 00:33 | 2022-02-15 00:35 | 908 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1401-06 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-15 | 1816 | keep | 0 | Feb | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2022-02-15 00:40 | 2022-02-15 01:57 | 1105 | 001:17 | T | DESGANCHE | SE REALIZO DESGANCHE A VARETA | S22021500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-02-15 | 85085 | keep | 0 | Feb | 2022 | 0.057951 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2022-02-15 00:51 | 2022-02-15 00:53 | 1447 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1419-09 Y 1419-12 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-15 | 2894 | keep | 0 | Feb | 2022 | 0.0019711 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-02-15 00:51 | 2022-02-15 00:52 | 266 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1112-04 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 266 | keep | 0 | Feb | 2022 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-02-15 00:51 | 2022-02-15 00:52 | 73 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1112-04 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 73 | keep | 0 | Feb | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2022-02-15 00:51 | 2022-02-15 00:52 | 3114 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL 40% DE SU CARGA TRANSFERIDA | B22021500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-15 | 3114 | keep | 0 | Feb | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2022-02-15 00:53 | 2022-02-15 01:02 | 3114 | 000:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL 40% DE SU CARGA TRANSFERIDA | B22021500000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 9 | 2022-02-15 | 28026 | keep | 0 | Feb | 2022 | 0.019088 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2022-02-15 01:02 | 2022-02-15 03:59 | 1038 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN TRONCAL 40% DE SU CARGA TRANSFERIDA | B22021500000 | Partial_restoration | Wire Down | Include | Include | Equipment | 177 | 2022-02-15 | 183726 | keep | 0 | Feb | 2022 | 0.12513 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-15 01:10 | 2022-02-15 01:11 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 1859 | keep | 0 | Feb | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
SAN JUAN | 2022-02-15 01:15 | 2022-02-15 01:18 | 922 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1401-08 QUE LLEVA LA CARGA DEL 1346-05 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-15 | 2766 | keep | 0 | Feb | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-15 01:15 | 2022-02-15 01:18 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-15 | 405 | keep | 0 | Feb | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-02-15 03:04 | 2022-02-15 03:05 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-02-15 03:53 | 2022-02-15 05:01 | 7 | 001:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R22021500002 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2022-02-15 | 476 | keep | 0 | Feb | 2022 | 0.0003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-02-15 04:14 | 2022-02-15 04:17 | 40 | 000:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22021500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-15 | 120 | keep | 0 | Feb | 2022 | 8.1731e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-15 04:29 | 2022-02-15 14:31 | 60 | 010:02 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR | S22021500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 602 | 2022-02-15 | 36120 | keep | 0 | Feb | 2022 | 0.024601 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-15 05:01 | 2022-02-15 05:09 | 4188 | 000:08 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR LLEVA 2404-08 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | R22021500000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 8 | 2022-02-15 | 33504 | keep | 0 | Feb | 2022 | 0.022819 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-15 05:01 | 2022-02-15 05:09 | 2675 | 000:08 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR CARGA POR EL 2402-02 CERRADO POR CONTROL | R22021500000 | New_Event | Cutout Failure | Include | Include | Equipment | 8 | 2022-02-15 | 21400 | keep | 0 | Feb | 2022 | 0.014575 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2022-02-15 05:09 | 2022-02-15 05:26 | 7 | 000:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R22021500002 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 17 | 2022-02-15 | 119 | keep | 0 | Feb | 2022 | 8.105e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-15 05:13 | 2022-02-15 05:14 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22021500016 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-02-15 05:16 | 2022-02-15 08:06 | 65 | 002:50 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 100A EN SU - 3A NO CAUSA | R22021500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-02-15 | 11050 | keep | 0 | Feb | 2022 | 0.0075261 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-02-15 05:41 | 2022-02-15 05:42 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22021500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 2179 | keep | 0 | Feb | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2022-02-15 05:47 | 2022-02-15 06:50 | 50 | 001:03 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTES PRIMARIO PARA SECCIONALIZAR POSTE PRIMARIO AVERIADO | M22021500001 | New_Event | Defective Pole | Include | Include | Equipment | 63 | 2022-02-15 | 3150 | keep | 0 | Feb | 2022 | 0.0021455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-15 06:00 | 2022-02-15 07:49 | 243 | 001:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A22021500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-02-15 | 26487 | keep | 0 | Feb | 2022 | 0.01804 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
CANOVANAS | 2022-02-15 06:15 | 2022-02-15 11:59 | 1 | 005:44 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | R22021500048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 344 | 2022-02-15 | 344 | keep | 0 | Feb | 2022 | 0.0002343 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-15 06:39 | 2022-02-15 08:35 | 40 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 1 X 80 EN CORTE DE LINEA | P22021500005 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2022-02-15 | 4640 | keep | 0 | Feb | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-15 06:50 | 2022-02-15 13:38 | 25 | 006:48 | P | ESTRUCTURA AVERIADA | SE REPARO CONDICION DE POSTE CON PERILLA PARTIDA | M22021500012 | Partial_restoration | Defective Pole | Include | Include | Equipment | 408 | 2022-02-15 | 10200 | keep | 0 | Feb | 2022 | 0.0069472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-15 07:10 | 2022-02-15 14:35 | 50 | 007:25 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22021500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 445 | 2022-02-15 | 22250 | keep | 0 | Feb | 2022 | 0.015154 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-15 07:22 | 2022-02-15 10:51 | 110 | 003:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22021500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2022-02-15 | 22990 | keep | 0 | Feb | 2022 | 0.015658 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
VEGA BAJA | 2022-02-15 07:46 | 2022-02-15 10:27 | 30 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22021500043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-02-15 | 4830 | keep | 0 | Feb | 2022 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-15 08:06 | 2022-02-15 16:14 | 10 | 008:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22021500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 488 | 2022-02-15 | 4880 | keep | 0 | Feb | 2022 | 0.0033237 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-15 08:11 | 2022-02-15 10:28 | 12 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22021500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-02-15 | 1644 | keep | 0 | Feb | 2022 | 0.0011197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-15 08:13 | 2022-02-15 10:44 | 10 | 002:31 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR CON DERRAME DE ACEITE DE 50 KVA X 50 KVA | R22021500024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 151 | 2022-02-15 | 1510 | keep | 0 | Feb | 2022 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-15 08:35 | 2022-02-15 11:44 | 7 | 003:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR REPARO SECUNDARIA | R22021500027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 189 | 2022-02-15 | 1323 | keep | 0 | Feb | 2022 | 0.00090109 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-02-15 08:46 | 2022-02-15 08:49 | 75 | 000:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22021400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-15 | 225 | keep | 0 | Feb | 2022 | 0.00015325 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-15 09:03 | 2022-02-15 14:50 | 30 | 005:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22021500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 347 | 2022-02-15 | 10410 | keep | 0 | Feb | 2022 | 0.0070902 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-15 09:06 | 2022-02-15 12:18 | 1 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22021500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2022-02-15 | 192 | keep | 0 | Feb | 2022 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-15 09:15 | 2022-02-15 10:15 | 90 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22021500028 | New_Event |  |  | Include | Wildlife | 60 | 2022-02-15 | 5400 | keep | 0 | Feb | 2022 | 0.0036779 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-02-15 09:45 | 2022-02-15 11:33 | 10 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | A22021200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2022-02-15 | 1080 | keep | 0 | Feb | 2022 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-02-15 09:52 | 2022-02-15 10:06 | 25 | 000:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22021500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-02-15 | 350 | keep | 0 | Feb | 2022 | 0.00023838 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-15 09:55 | 2022-02-17 11:06 | 2 | 049:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA VERIFICADA EN BITACORA Y OMS ES DEL DIA 15 COMO SITUACION PELIGROSA | M22021500020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2951 | 2022-02-15 | 5902 | keep | 0 | Feb | 2022 | 0.0040198 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-02-15 10:01 | 2022-02-15 11:45 | 50 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22021500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-02-15 | 5200 | keep | 0 | Feb | 2022 | 0.0035417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-15 10:04 | 2022-02-15 10:05 | 671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 671 | keep | 0 | Feb | 2022 | 0.00045702 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
ARECIBO | 2022-02-15 10:38 | 2022-02-15 14:19 | 40 | 003:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-02-15 | 8840 | keep | 0 | Feb | 2022 | 0.0060209 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-15 10:43 | 2022-02-15 13:55 | 20 | 003:12 | P | DESGANCHE | 1 X 20 EN XMR Y SE REPARO SECUNDARIA | S22021500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-02-15 | 3840 | keep | 0 | Feb | 2022 | 0.0026154 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-02-15 11:10 | 2022-02-15 14:24 | 20 | 003:14 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO PISTOLA QUEMADA EN T-2 | P22021500012 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 194 | 2022-02-15 | 3880 | keep | 0 | Feb | 2022 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-15 11:23 | 2022-02-15 11:24 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22021500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 176 | keep | 0 | Feb | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
CANOVANAS | 2022-02-15 11:26 | 2022-02-15 14:33 | 15 | 003:07 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | R22021500038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-02-15 | 2805 | keep | 0 | Feb | 2022 | 0.0019105 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-15 11:27 | 2022-02-15 13:15 | 50 | 001:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22021500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-02-15 | 5400 | keep | 0 | Feb | 2022 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-15 11:30 | 2022-02-15 15:06 | 6 | 003:36 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO ROTO Y LINEA SECUNDARIA | M22021500030 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 216 | 2022-02-15 | 1296 | keep | 0 | Feb | 2022 | 0.0008827 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-15 11:32 | 2022-02-15 11:33 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 4431 | keep | 0 | Feb | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
ARECIBO | 2022-02-15 11:33 | 2022-02-15 17:50 | 6 | 006:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | A22021500030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 377 | 2022-02-15 | 2262 | keep | 0 | Feb | 2022 | 0.0015406 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-15 11:35 | 2022-02-15 14:52 | 15 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | M22021500033 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2022-02-15 | 2955 | keep | 0 | Feb | 2022 | 0.0020126 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-15 11:38 | 2022-02-15 17:40 | 1378 | 006:02 | T | DESGANCHE | SE REALIZO DESGANCHE DE ARBOLES EN VARIOS PUNTOS, CARR 189 FTE CANTA GALLO Y EN MARGINAL CARR 30 ANTIGUA PLANTA DE TRATAMIENTO | C22021500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-02-15 | 498836 | keep | 0 | Feb | 2022 | 0.33975 | 0.00093855 | Sustained | FALSE | FALSE | Not_TMED_Event | 1378
BAYAMON | 2022-02-15 11:43 | 2022-02-15 17:56 | 25 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA Y LINEA SECUNDARIA | B22021500066 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2022-02-15 | 9325 | keep | 0 | Feb | 2022 | 0.0063512 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-02-15 11:45 | 2022-02-15 13:47 | 20 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA REPARO BAJANTE PRIMARIA ABIERTO HACIA XMR | C22021500065 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-02-15 | 2440 | keep | 0 | Feb | 2022 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-15 12:05 | 2022-02-15 15:06 | 40 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22021500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-02-15 | 7240 | keep | 0 | Feb | 2022 | 0.0049311 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-15 12:13 | 2022-02-15 12:14 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22021500071 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-15 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-02-15 12:14 | 2022-02-15 13:40 | 90 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22021500072 | 1st_after_momentary |  |  | Include | Wildlife | 86 | 2022-02-15 | 7740 | keep | 0 | Feb | 2022 | 0.0052717 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-02-15 12:20 | 2022-02-15 12:21 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22021500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 2825 | keep | 0 | Feb | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
PONCE | 2022-02-15 12:34 | 2022-02-15 15:15 | 3 | 002:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22021500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-02-15 | 483 | keep | 0 | Feb | 2022 | 0.00032897 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-02-15 12:46 | 2022-02-15 16:41 | 10 | 003:55 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S22021500050 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 235 | 2022-02-15 | 2350 | keep | 0 | Feb | 2022 | 0.0016006 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-15 12:49 | 2022-02-15 16:14 | 8 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRAMO SECUNDARIO TRASPATIO | S22021500051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-02-15 | 1640 | keep | 0 | Feb | 2022 | 0.001117 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-02-15 12:59 | 2022-02-15 19:19 | 5 | 006:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A22021500033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 380 | 2022-02-15 | 1900 | keep | 0 | Feb | 2022 | 0.0012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-02-15 13:08 | 2022-02-15 13:09 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22021500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2022-02-15 13:22 | 2022-02-15 19:19 | 20 | 005:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO PRIMARIO | B22021500077 | New_Event | Wire Down | Include | Include | Equipment | 357 | 2022-02-15 | 7140 | keep | 0 | Feb | 2022 | 0.004863 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-15 13:27 | 2022-02-15 13:30 | 588 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1801-03 LLEVANDO 1711-04 Y PARTE 1711-01 | B22021500079 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-02-15 | 1764 | keep | 0 | Feb | 2022 | 0.0012015 | 0.00040048 | Momentary | FALSE | FALSE | Not_TMED_Event | 588
BAYAMON | 2022-02-15 13:27 | 2022-02-15 13:30 | 1983 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1801-03 LLEVANDO 1711-04 Y PARTE 1711-01 | B22021500079 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-02-15 | 5949 | keep | 0 | Feb | 2022 | 0.0040518 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-02-15 13:27 | 2022-02-15 13:30 | 1746 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1801-03 LLEVANDO 1711-04 Y PARTE 1711-01 | B22021500079 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-02-15 | 5238 | keep | 0 | Feb | 2022 | 0.0035676 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-02-15 13:30 | 2022-02-15 19:53 | 5 | 006:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN SU 2 SE LLEVO LINEA PRIMARIA A AISLADOR | B22021500092 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 383 | 2022-02-15 | 1915 | keep | 0 | Feb | 2022 | 0.0013043 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-15 13:34 | 2022-02-15 13:35 | 929 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1421-04 Y 1421-03 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 929 | keep | 0 | Feb | 2022 | 0.00063274 | 0.00063274 | Momentary | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2022-02-15 13:34 | 2022-02-15 13:35 | 533 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1414-04 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 533 | keep | 0 | Feb | 2022 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2022-02-15 13:34 | 2022-02-15 13:35 | 451 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1414-04 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 451 | keep | 0 | Feb | 2022 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2022-02-15 13:35 | 2022-02-15 14:13 | 10 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22021500069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-02-15 | 380 | keep | 0 | Feb | 2022 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-15 13:38 | 2022-02-15 14:36 | 199 | 000:58 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA CERRAR PUENTES Y NORMALIZAR LA CARGA DEL ALIMENTADOR LUEGO QUE SE REPARO CONDICION DE POSTE CON PERILLA PARTIDA | M22021500049 | New_Event | Defective Pole | Include | Include | Equipment | 58 | 2022-02-15 | 11542 | keep | 0 | Feb | 2022 | 0.0078612 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
UTUADO | 2022-02-15 13:40 | 2022-02-15 16:00 | 10 | 002:20 | P | ESTRUCTURA AVERIADA | SE RETIRO CARGA PARA ABRIR PUENTES Y REMPLAZAR POSTE PRIMARIO | A22021500036 | New_Event | Defective Pole | Include | Include | Equipment | 140 | 2022-02-15 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-15 14:10 | 2022-02-15 17:22 | 55 | 003:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22021500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-02-15 | 10560 | keep | 0 | Feb | 2022 | 0.0071924 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-02-15 14:17 | 2022-02-15 18:36 | 12 | 004:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN PROVISIONAL AEREO Y SE REMPLAZO CAJA PRIMARIA | S22021500063 | New_Event | Cutout Failure | Include | Include | Equipment | 259 | 2022-02-15 | 3108 | keep | 0 | Feb | 2022 | 0.0021168 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-15 14:19 | 2022-02-15 15:05 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR Y LEVANTAR SECUNDARIA | B22021500084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-02-15 | 460 | keep | 0 | Feb | 2022 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-15 14:33 | 2022-02-15 16:06 | 30 | 001:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-02-15 | 2790 | keep | 0 | Feb | 2022 | 0.0019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-15 14:33 | 2022-02-15 18:45 | 30 | 004:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22021500054 | New_Event |  |  | Include | Wildlife | 252 | 2022-02-15 | 7560 | keep | 0 | Feb | 2022 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-15 14:36 | 2022-02-15 17:07 | 110 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22021500096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-02-15 | 16610 | keep | 0 | Feb | 2022 | 0.011313 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BARRANQUITAS | 2022-02-15 14:56 | 2022-02-15 17:01 | 9 | 002:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN XMR REEMPLAZO CAJA XMR QUEMADA | C22021500098 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2022-02-15 | 1125 | keep | 0 | Feb | 2022 | 0.00076623 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-02-15 14:57 | 2022-02-15 16:16 | 12 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS SECUNDARIAS EN TRANSFORMADOR | S22021500065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2022-02-15 | 948 | keep | 0 | Feb | 2022 | 0.00064568 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-15 14:57 | 2022-02-15 16:50 | 3 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | P22021500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2022-02-15 | 339 | keep | 0 | Feb | 2022 | 0.00023089 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-02-15 15:07 | 2022-02-15 17:54 | 12 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 20 EN TRANSFORMADOR SE REMPLAZARON 2 CAJAS PRIMARIAS Y SE REPARO BAJANTE SECUNDARIO | S20215000073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2022-02-15 | 2004 | keep | 0 | Feb | 2022 | 0.0013649 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-02-15 15:15 | 2022-02-15 17:50 | 45 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22021500094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-02-15 | 6975 | keep | 0 | Feb | 2022 | 0.0047506 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-02-15 15:15 | 2022-02-16 04:43 | 50 | 013:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-6 | B22021500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 808 | 2022-02-15 | 40400 | keep | 0 | Feb | 2022 | 0.027516 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-15 15:18 | 2022-02-15 18:01 | 30 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M22021500057 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2022-02-15 | 4890 | keep | 0 | Feb | 2022 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-15 15:20 | 2022-02-15 18:35 | 15 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R2202150034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-02-15 | 2925 | keep | 0 | Feb | 2022 | 0.0019922 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-02-15 15:27 | 2022-02-15 17:17 | 15 | 001:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-02-15 | 1650 | keep | 0 | Feb | 2022 | 0.0011238 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-02-15 15:30 | 2022-02-16 11:04 | 33 | 019:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75 X 75KVA | R22021500046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1174 | 2022-02-15 | 38742 | keep | 0 | Feb | 2022 | 0.026387 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
UTUADO | 2022-02-15 15:37 | 2022-02-16 14:47 | 4 | 023:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1390 | 2022-02-15 | 5560 | keep | 0 | Feb | 2022 | 0.0037869 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-02-15 15:49 | 2022-02-15 16:09 | 15 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22021500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-02-15 | 300 | keep | 0 | Feb | 2022 | 0.00020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-15 16:20 | 2022-02-15 16:22 | 2617 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTORSE CERRO POR SCADA | B22021500100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-15 | 5234 | keep | 0 | Feb | 2022 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2022-02-15 16:39 | 2022-02-15 18:52 | 6 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO Y LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S22021500079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2022-02-15 | 798 | keep | 0 | Feb | 2022 | 0.00054351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-15 16:42 | 2022-02-15 21:05 | 20 | 004:23 | P | NO SE REPORTO CAUSA | 2X40 DEL SU-17 @ RISER | S22021500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-02-15 | 5260 | keep | 0 | Feb | 2022 | 0.0035826 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-15 16:54 | 2022-02-16 10:01 | 56 | 017:07 | P | DESGANCHE | 1 X 50 EN C/L | C22021500115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1027 | 2022-02-15 | 57512 | keep | 0 | Feb | 2022 | 0.039171 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-02-15 17:04 | 2022-02-15 17:28 | 1 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B22021500111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-02-15 | 24 | keep | 0 | Feb | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-15 17:20 | 2022-02-15 21:39 | 30 | 004:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22021500115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-02-15 | 7770 | keep | 0 | Feb | 2022 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-15 17:49 | 2022-02-15 18:25 | 1 | 000:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN RISER Y 1 X 15 EN BANCO DE XMR CRUCE POR AVE | C22021500128 | New_Event |  |  | Include | Wildlife | 36 | 2022-02-15 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-02-15 17:58 | 2022-02-16 10:24 | 7 | 016:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR REPARO SECUNDARIA | C22021500129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 986 | 2022-02-15 | 6902 | keep | 0 | Feb | 2022 | 0.0047009 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-02-15 18:02 | 2022-02-15 20:16 | 15 | 002:14 | P | DESGANCHE | 1 X 25 EN C/L | R22021500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-02-15 | 2010 | keep | 0 | Feb | 2022 | 0.001369 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-02-15 18:04 | 2022-02-15 19:57 | 400 | 001:53 | P | DESGANCHE | SE ABRIO MACHETES PARA RETIRAR NEUTRAL PRIMARIO CRUZADO CON ARBOLES | C22021500131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-02-15 | 45200 | keep | 0 | Feb | 2022 | 0.030786 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2022-02-15 18:12 | 2022-02-15 18:13 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22021500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 2126 | keep | 0 | Feb | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2022-02-15 18:45 | 2022-02-16 19:00 | 50 | 024:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE NORMALIZO | S22021500088 | New_Event | Wire Down | Include | Include | Equipment | 1455 | 2022-02-15 | 72750 | keep | 0 | Feb | 2022 | 0.04955 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-15 18:51 | 2022-02-15 22:21 | 8 | 003:30 | P | DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE | S22021500089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-02-15 | 1680 | keep | 0 | Feb | 2022 | 0.0011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-15 18:56 | 2022-02-15 20:58 | 1 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 20 EN BANCO DE TRANSFORMADORES Y SE CERRO PUENTE PRIMARIO | S22021500090 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-02-15 | 122 | keep | 0 | Feb | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-15 19:01 | 2022-02-15 19:50 | 15 | 000:49 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN C/L SE ELIMINO PARARRAYO | R22021500061 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 49 | 2022-02-15 | 735 | keep | 0 | Feb | 2022 | 0.00050061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-15 19:01 | 2022-02-15 21:00 | 15 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22021500049 | New_Event | Wire Down | Include | Include | Equipment | 119 | 2022-02-15 | 1785 | keep | 0 | Feb | 2022 | 0.0012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-02-15 19:03 | 2022-02-15 21:39 | 10 | 002:36 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22021500127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-02-15 | 1560 | keep | 0 | Feb | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-15 19:14 | 2022-02-15 19:17 | 922 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 LLEVA TRANSFERIDA LA CARGA DEL 1346-05 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-15 | 2766 | keep | 0 | Feb | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-15 19:14 | 2022-02-15 19:17 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA CARGA DEL 1346-05 | S22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-15 | 405 | keep | 0 | Feb | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2022-02-15 19:21 | 2022-02-15 23:01 | 50 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 C/L SE REMPLAZO CAJA PRIMARIA | B22021500129 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2022-02-15 | 11000 | keep | 0 | Feb | 2022 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-15 20:25 | 2022-02-16 00:24 | 7 | 003:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22021500098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 239 | 2022-02-15 | 1673 | keep | 0 | Feb | 2022 | 0.0011395 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-02-15 20:29 | 2022-02-15 21:57 | 1 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22021500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-02-15 | 88 | keep | 0 | Feb | 2022 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-02-15 20:34 | 2022-02-16 07:15 | 10 | 010:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE BRISA | P22021500042 | New_Event | Bad Weather | Include | Include | Weather | 641 | 2022-02-15 | 6410 | keep | 0 | Feb | 2022 | 0.0043658 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-15 21:54 | 2022-02-16 13:07 | 15 | 015:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES AVERIADO | A22021500055 | New_Event | Cutout Failure | Include | Include | Equipment | 913 | 2022-02-15 | 13695 | keep | 0 | Feb | 2022 | 0.0093276 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-15 22:22 | 2022-02-15 22:23 | 1647 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-15 | 1647 | keep | 0 | Feb | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
PONCE | 2022-02-15 22:55 | 2022-02-16 10:29 | 8 | 011:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO SAFADO EN CAJA PRIMARIA DE TRANSFORMADOR | P22021500045 | New_Event | Wire Down | Include | Include | Equipment | 694 | 2022-02-15 | 5552 | keep | 0 | Feb | 2022 | 0.0037814 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-15 22:58 | 2022-02-16 01:17 | 80 | 002:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLES | S22021500102 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2022-02-15 | 11120 | keep | 0 | Feb | 2022 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-15 23:00 | 2022-02-16 11:44 | 120 | 012:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22021500077 | New_Event | Cutout Failure | Include | Include | Equipment | 764 | 2022-02-15 | 91680 | keep | 0 | Feb | 2022 | 0.062443 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-02-16 00:28 | 2022-02-16 11:57 | 20 | 011:29 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C22021500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 689 | 2022-02-16 | 13780 | keep | 0 | Feb | 2022 | 0.0093855 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-16 03:14 | 2022-02-16 12:05 | 30 | 008:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22021600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 531 | 2022-02-16 | 15930 | keep | 0 | Feb | 2022 | 0.01085 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-16 03:30 | 2022-02-16 03:32 | 3046 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-16 | 6092 | keep | 0 | Feb | 2022 | 0.0041492 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-02-16 03:32 | 2022-02-16 06:22 | 100 | 002:50 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN RISER SE REEMPLAZO TERMINACION QUEMADA | R22021600001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 170 | 2022-02-16 | 17000 | keep | 0 | Feb | 2022 | 0.011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-16 03:47 | 2022-02-16 03:48 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-16 03:55 | 2022-02-16 05:52 | 36 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22021600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2022-02-16 | 4212 | keep | 0 | Feb | 2022 | 0.0028688 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-02-16 05:13 | 2022-02-16 05:14 | 4369 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 600 | C22021600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-16 | 4369 | keep | 0 | Feb | 2022 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2022-02-16 05:13 | 2022-02-16 05:14 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 600 | C22021600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-16 | 676 | keep | 0 | Feb | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2022-02-16 05:13 | 2022-02-16 05:14 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 600 | C22021600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-16 | 1606 | keep | 0 | Feb | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2022-02-16 05:13 | 2022-02-16 05:14 | 725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 600 | C22021600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-16 | 725 | keep | 0 | Feb | 2022 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
SAN JUAN | 2022-02-16 05:15 | 2022-02-16 05:16 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22021600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
AGUADILLA | 2022-02-16 05:42 | 2022-02-16 10:14 | 80 | 004:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | M22021600004 | New_Event | Bad Weather | Include | Include | Weather | 272 | 2022-02-16 | 21760 | keep | 0 | Feb | 2022 | 0.014821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-16 06:11 | 2022-02-16 06:12 | 3432 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE 80% DE LA CARGA A TRAVES DE LA PORTATIL 22 | S22021600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-16 | 3432 | keep | 0 | Feb | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-02-16 06:12 | 2022-02-16 10:12 | 60 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 20 EN XMR SE REEMPLAZO CAJA PRIMARIA | S22021600032 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 240 | 2022-02-16 | 14400 | keep | 0 | Feb | 2022 | 0.0098078 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-16 06:12 | 2022-02-16 09:40 | 20 | 003:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA TENSORES CRUZARON LINEAS PRIMARIAS | A22021600002 | New_Event | Wire Down | Include | Include | Equipment | 208 | 2022-02-16 | 4160 | keep | 0 | Feb | 2022 | 0.0028334 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-02-16 06:23 | 2022-02-16 11:15 | 5 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22021600001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2022-02-16 | 1460 | keep | 0 | Feb | 2022 | 0.0009944 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-02-16 06:23 | 2022-02-16 13:47 | 20 | 007:24 | P | DESGANCHE | 1 X 40 EN C/L | C22021600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2022-02-16 | 8880 | keep | 0 | Feb | 2022 | 0.0060481 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-16 06:28 | 2022-02-16 08:15 | 200 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L NO CAUSA | C22021600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-02-16 | 21400 | keep | 0 | Feb | 2022 | 0.014575 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-02-16 06:47 | 2022-02-16 06:48 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22021600005 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-16 | 2450 | keep | 0 | Feb | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-02-16 06:48 | 2022-02-16 09:54 | 80 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22021600006 | 1st_after_momentary |  |  | Include | Wildlife | 186 | 2022-02-16 | 14880 | keep | 0 | Feb | 2022 | 0.010135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-02-16 07:21 | 2022-02-16 11:18 | 66 | 003:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22021600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-02-16 | 15642 | keep | 0 | Feb | 2022 | 0.010654 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
SAN JUAN | 2022-02-16 07:24 | 2022-02-16 15:48 | 2 | 008:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22021600022 | New_Event | Wire Down | Include | Include | Equipment | 504 | 2022-02-16 | 1008 | keep | 0 | Feb | 2022 | 0.00068654 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-16 07:28 | 2022-02-16 11:10 | 1 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B22021600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-02-16 | 222 | keep | 0 | Feb | 2022 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-16 07:45 | 2022-02-16 07:46 | 3131 | 000:01 | T | DESGANCHE | RECIERRE | C22021600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-16 | 3131 | keep | 0 | Feb | 2022 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
CAGUAS | 2022-02-16 07:46 | 2022-02-16 14:29 | 80 | 006:43 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22021600012 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 403 | 2022-02-16 | 32240 | keep | 0 | Feb | 2022 | 0.021959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-02-16 07:56 | 2022-02-16 10:34 | 89 | 002:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22021600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-02-16 | 14062 | keep | 0 | Feb | 2022 | 0.0095776 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
UTUADO | 2022-02-16 08:02 | 2022-02-16 11:43 | 30 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA PERSONAL NO IDENTIFICO CAUSA | A22021600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-02-16 | 6630 | keep | 0 | Feb | 2022 | 0.0045157 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-16 08:08 | 2022-02-16 18:09 | 3 | 010:01 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHE | B22021600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 601 | 2022-02-16 | 1803 | keep | 0 | Feb | 2022 | 0.001228 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-02-16 08:12 | 2022-02-16 12:43 | 59 | 004:31 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUCETA Y 3 CAJAS PRIMARIAS Y 3 PARARRAYOS | S22021600028 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 271 | 2022-02-16 | 15989 | keep | 0 | Feb | 2022 | 0.01089 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
VEGA BAJA | 2022-02-16 08:15 | 2022-02-16 11:30 | 1 | 003:15 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22021600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-02-16 | 195 | keep | 0 | Feb | 2022 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-16 08:16 | 2022-02-16 09:59 | 100 | 001:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22021600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-02-16 | 10300 | keep | 0 | Feb | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-16 08:19 | 2022-02-16 12:22 | 75 | 004:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22021600029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2022-02-16 | 18225 | keep | 0 | Feb | 2022 | 0.012413 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-16 08:36 | 2022-02-16 15:49 | 67 | 007:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA POR 37.5 KVA Y SE REPUSO 1 X 10 EN NUEVO TRANSFORMADOR | B22021600011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 433 | 2022-02-16 | 29011 | keep | 0 | Feb | 2022 | 0.019759 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BARRANQUITAS | 2022-02-16 08:37 | 2022-02-16 13:40 | 5 | 005:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22021600011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 303 | 2022-02-16 | 1515 | keep | 0 | Feb | 2022 | 0.0010319 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-02-16 08:47 | 2022-02-16 11:37 | 3881 | 002:50 | P | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO FASE DE LINEA 5300 SOBRE LA DISTRIBUCION Y SE CERRO INTELLIRUPTER 2603-8E | C22021600020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 170 | 2022-02-16 | 659770 | keep | 0 | Feb | 2022 | 0.44937 | 0.0026433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3881
SAN JUAN | 2022-02-16 08:49 | 2022-02-16 10:59 | 100 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22021600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-02-16 | 13000 | keep | 0 | Feb | 2022 | 0.0088542 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-16 08:58 | 2022-02-16 08:59 | 658 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 658 | keep | 0 | Feb | 2022 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
SAN JUAN | 2022-02-16 08:59 | 2022-02-16 10:58 | 300 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 140 EN CORTES DE LINEA CRUCE CON AVE | R22021600019 | New_Event |  |  | Include | Wildlife | 119 | 2022-02-16 | 35700 | keep | 0 | Feb | 2022 | 0.024315 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-02-16 09:31 | 2022-02-16 12:29 | 100 | 002:58 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN C/L'S NO CAUSA | C22021600057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2022-02-16 | 17800 | keep | 0 | Feb | 2022 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-16 09:32 | 2022-02-16 09:40 | 4 | 000:08 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO PEDESTAL | R22021600029 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 8 | 2022-02-16 | 32 | keep | 0 | Feb | 2022 | 2.1795e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-02-16 10:14 | 2022-02-16 11:03 | 4133 | 000:49 | T | NO SE REPORTO CAUSA | DISARO DE INTERRUPTOR SE CERRO POR SCADA | S22021600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-02-16 | 202517 | keep | 0 | Feb | 2022 | 0.13793 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2022-02-16 10:58 | 2022-02-16 10:59 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 315 | keep | 0 | Feb | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
ARECIBO | 2022-02-16 11:06 | 2022-02-16 12:00 | 10 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO CONEXIONES SALIDA XMR | B22021600026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-02-16 | 540 | keep | 0 | Feb | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-16 11:26 | 2022-02-16 12:59 | 1157 | 001:33 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTES Y CAJA PRIMARIA QUEMADA CAUSA QUE ALIMENTADOR DISPARE | P22021600027 | New_Event | Wire Down | Include | Include | Equipment | 93 | 2022-02-16 | 107601 | keep | 0 | Feb | 2022 | 0.073287 | 0.00078803 | Sustained | FALSE | FALSE | Not_TMED_Event | 1157
BAYAMON | 2022-02-16 11:27 | 2022-02-16 11:28 | 2076 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1718-03 LLEVANDO 40% DEL 1710-05 | B22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 2076 | keep | 0 | Feb | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-02-16 11:27 | 2022-02-16 11:28 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1718-03 LLEVANDO 40% DEL 1710-05 | B22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 2605 | keep | 0 | Feb | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2022-02-16 11:32 | 2022-02-16 11:33 | 1474 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22021600049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 1474 | keep | 0 | Feb | 2022 | 0.0010039 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
MAYAGÃœEZ | 2022-02-16 11:50 | 2022-02-16 16:06 | 60 | 004:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y VIENTO | M22021600059 | New_Event | Bad Weather | Include | Include | Weather | 256 | 2022-02-16 | 15360 | keep | 0 | Feb | 2022 | 0.010462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-02-16 11:52 | 2022-02-16 11:55 | 2926 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22021600029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-16 | 8778 | keep | 0 | Feb | 2022 | 0.0059787 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
YAUCO | 2022-02-16 11:55 | 2022-02-16 16:00 | 40 | 004:05 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P22021600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-02-16 | 9800 | keep | 0 | Feb | 2022 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-16 11:58 | 2022-02-16 11:59 | 1510 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 1510 | keep | 0 | Feb | 2022 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
PONCE | 2022-02-16 12:02 | 2022-02-16 13:43 | 75 | 001:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | P22021600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-02-16 | 7575 | keep | 0 | Feb | 2022 | 0.0051593 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-02-16 12:22 | 2022-02-16 18:44 | 40 | 006:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA NO FUNDIO FUSIBLE | C22021600087 | New_Event | Cutout Failure | Include | Include | Equipment | 382 | 2022-02-16 | 15280 | keep | 0 | Feb | 2022 | 0.010407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-16 12:24 | 2022-02-16 15:27 | 20 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22021600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-02-16 | 3660 | keep | 0 | Feb | 2022 | 0.0024928 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-16 12:25 | 2022-02-16 15:34 | 15 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R22021600050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-02-16 | 2835 | keep | 0 | Feb | 2022 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-16 12:29 | 2022-02-16 16:14 | 100 | 003:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | M22021600068 | New_Event | Bad Weather | Include | Include | Weather | 225 | 2022-02-16 | 22500 | keep | 0 | Feb | 2022 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-02-16 12:33 | 2022-02-16 12:34 | 4154 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22021600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 4154 | keep | 0 | Feb | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-02-16 12:34 | 2022-02-16 15:01 | 100 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 200 EN C/L | R22021600056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-02-16 | 14700 | keep | 0 | Feb | 2022 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-16 12:36 | 2022-02-16 20:38 | 50 | 008:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE CORRIGIO CONDICION DE TIERRA DE POSTE ZAFADA CRUZANDO CON FASE | M22021600070 | New_Event |  |  | Include | Wildlife | 482 | 2022-02-16 | 24100 | keep | 0 | Feb | 2022 | 0.016414 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-16 12:42 | 2022-02-16 15:26 | 50 | 002:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B22021600039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-02-16 | 8200 | keep | 0 | Feb | 2022 | 0.005585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-16 12:45 | 2022-02-16 15:56 | 40 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C22021600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-02-16 | 7640 | keep | 0 | Feb | 2022 | 0.0052036 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-16 12:49 | 2022-02-16 15:13 | 100 | 002:24 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA NO CAUSA | C22021600091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-02-16 | 14400 | keep | 0 | Feb | 2022 | 0.0098078 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-16 13:15 | 2022-02-16 13:17 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1401-08 | S22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-16 | 1844 | keep | 0 | Feb | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-02-16 13:15 | 2022-02-16 13:17 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1346-05 | S22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-16 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
ARECIBO | 2022-02-16 13:23 | 2022-02-16 16:08 | 100 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22021600030 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2022-02-16 | 16500 | keep | 0 | Feb | 2022 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-02-16 13:24 | 2022-02-16 14:24 | 15 | 001:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 75KVA X 75KVA | R22021600059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2022-02-16 | 900 | keep | 0 | Feb | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-16 13:32 | 2022-02-16 13:33 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2022-02-16 13:37 | 2022-02-16 20:56 | 4 | 007:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA Y SE CERRO TRANSFORMADOR | A22021600032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 439 | 2022-02-16 | 1756 | keep | 0 | Feb | 2022 | 0.001196 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-02-16 13:41 | 2022-02-16 17:31 | 36 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE REALIZO DESGANCHE | S22021600096 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2022-02-16 | 8280 | keep | 0 | Feb | 2022 | 0.0056395 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2022-02-16 13:43 | 2022-02-16 15:59 | 30 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA INFORMA UT2 QUE NO IDENTIFICO CAUSA | A22021600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-02-16 | 4080 | keep | 0 | Feb | 2022 | 0.0027789 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-16 13:45 | 2022-02-16 13:46 | 3463 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021600100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 3463 | keep | 0 | Feb | 2022 | 0.0023586 | 0.0023586 | Momentary | FALSE | FALSE | Not_TMED_Event | 3463
CAGUAS | 2022-02-16 13:46 | 2022-02-16 17:17 | 50 | 003:31 | P | NO SE REPORTO CAUSA | SE ENCONTRO CAJA ABIERTA, NO FUNDIO FUSIBLE. NO SE REPORTO CAUSA | C22021600106 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-02-16 | 10550 | keep | 0 | Feb | 2022 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-16 13:46 | 2022-02-16 20:31 | 440 | 006:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | VEHICULO PRIVADO QUE CAYO POR UN BARRANCO SE SECCONALIZO ALIMENTADOR PARA PODER SACARLO CON UNA PH | B22021600040 | New_Event |  |  | Include | Wildlife | 405 | 2022-02-16 | 178200 | keep | 0 | Feb | 2022 | 0.12137 | 0.00029968 | Sustained | FALSE | FALSE | Not_TMED_Event | 440
UTUADO | 2022-02-16 14:02 | 2022-02-16 16:33 | 40 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A22021600035 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2022-02-16 | 6040 | keep | 0 | Feb | 2022 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-16 14:03 | 2022-02-16 17:14 | 3 | 003:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | M22021600090 | New_Event | Bad Weather | Include | Include | Weather | 191 | 2022-02-16 | 573 | keep | 0 | Feb | 2022 | 0.00039027 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-02-16 14:34 | 2022-02-16 15:26 | 45 | 000:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | P22021600049 | New_Event |  |  | Include | Wildlife | 52 | 2022-02-16 | 2340 | keep | 0 | Feb | 2022 | 0.0015938 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-02-16 14:36 | 2022-02-16 16:40 | 14 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO EN CAJA DE CORTE DE LINEA | P22021600050 | New_Event | Wire Down | Include | Include | Equipment | 124 | 2022-02-16 | 1736 | keep | 0 | Feb | 2022 | 0.0011824 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-02-16 14:42 | 2022-02-16 16:27 | 11 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR LAS TRES BARRAS DE PEDESTAL | C22021600109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2022-02-16 | 1155 | keep | 0 | Feb | 2022 | 0.00078667 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2022-02-16 14:48 | 2022-02-16 16:56 | 40 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P22021600051 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2022-02-16 | 5120 | keep | 0 | Feb | 2022 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-16 15:07 | 2022-02-17 14:41 | 8 | 023:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRAMO SECUNDARIO | B22021600061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1414 | 2022-02-16 | 11312 | keep | 0 | Feb | 2022 | 0.0077046 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-02-16 15:22 | 2022-02-16 18:45 | 30 | 003:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22021600044 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2022-02-16 | 6090 | keep | 0 | Feb | 2022 | 0.0041479 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-16 15:28 | 2022-02-16 17:05 | 1 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | S22021600111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-02-16 | 97 | keep | 0 | Feb | 2022 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-16 15:35 | 2022-02-16 18:05 | 120 | 002:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 2 X 50 EN CORTES DE LINEAS DISTINTOS CAMION CRUZO LINEAS | A22021600045 | New_Event |  |  | Include | Wildlife | 150 | 2022-02-16 | 18000 | keep | 0 | Feb | 2022 | 0.01226 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-02-16 15:37 | 2022-02-16 15:38 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220216000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2022-02-16 15:41 | 2022-02-16 17:54 | 100 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22021600046 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2022-02-16 | 13300 | keep | 0 | Feb | 2022 | 0.0090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-02-16 16:05 | 2022-02-16 16:06 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P220216000XX | New_Event |  |  | Include | Wildlife | 1 | 2022-02-16 | 464 | keep | 0 | Feb | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
MAYAGÃœEZ | 2022-02-16 16:05 | 2022-02-16 18:51 | 40 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M22021600111 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2022-02-16 | 6640 | keep | 0 | Feb | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-02-16 16:06 | 2022-02-16 17:13 | 35 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22021600061 | 1st_after_momentary |  |  | Include | Wildlife | 67 | 2022-02-16 | 2345 | keep | 0 | Feb | 2022 | 0.0015972 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-02-16 16:08 | 2022-02-16 17:29 | 30 | 001:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M22021600113 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2022-02-16 | 2430 | keep | 0 | Feb | 2022 | 0.0016551 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-16 16:09 | 2022-02-16 17:09 | 6 | 001:00 | P | DESGANCHE | SE REPARO TRAMO SECUNDARIO | B22021600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-02-16 | 360 | keep | 0 | Feb | 2022 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-02-16 16:13 | 2022-02-16 18:35 | 35 | 002:22 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN RISER SE REPARO PISTOLA | S22021600118 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 142 | 2022-02-16 | 4970 | keep | 0 | Feb | 2022 | 0.003385 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-02-16 16:19 | 2022-02-16 16:20 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021600064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
MAYAGÃœEZ | 2022-02-16 16:20 | 2022-02-16 18:39 | 1 | 002:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA SECUNDARIA AVERIADA | M22021600119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 139 | 2022-02-16 | 139 | keep | 0 | Feb | 2022 | 9.4672e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-16 16:24 | 2022-02-16 19:32 | 1444 | 003:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR LINEA PRIMARIA ROTA EN EL ALIMENTADOR 6014-02 QUE ESTA LLEVANDO LA CARGA DEL 6014-01 Y SE CERRO EL INTERRUPTOR | M22021600126 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2022-02-16 | 271472 | keep | 0 | Feb | 2022 | 0.1849 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-02-16 16:24 | 2022-02-16 19:32 | 3630 | 003:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR LINEA PRIMARIA ROTA Y SE CERRO EL INTERRUPTOR | M22021600126 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2022-02-16 | 682440 | keep | 0 | Feb | 2022 | 0.46481 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2022-02-16 16:25 | 2022-02-16 18:49 | 12 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS EN PEDESTAL | B22021600013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2022-02-16 | 1728 | keep | 0 | Feb | 2022 | 0.0011769 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-02-16 16:44 | 2022-02-16 18:44 | 40 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22021600069 | New_Event |  |  | Include | Wildlife | 120 | 2022-02-16 | 4800 | keep | 0 | Feb | 2022 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-02-16 16:44 | 2022-02-16 17:41 | 50 | 000:57 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P22021600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-02-16 | 2850 | keep | 0 | Feb | 2022 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-16 16:45 | 2022-02-16 20:02 | 50 | 003:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA Y REALIZO DESGANCHE | C22021600123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-02-16 | 9850 | keep | 0 | Feb | 2022 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-16 16:50 | 2022-02-16 16:51 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021600151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 4381 | keep | 0 | Feb | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
PONCE | 2022-02-16 17:04 | 2022-02-17 06:40 | 5 | 013:36 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR CRUCE DE FASES SECUNDARIAS POR RAMA | P22021600074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 816 | 2022-02-16 | 4080 | keep | 0 | Feb | 2022 | 0.0027789 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-02-16 17:05 | 2022-02-16 18:28 | 65 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22021600127 | New_Event |  |  | Include | Wildlife | 83 | 2022-02-16 | 5395 | keep | 0 | Feb | 2022 | 0.0036745 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-02-16 17:20 | 2022-02-16 18:18 | 15 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | R22021600087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-02-16 | 870 | keep | 0 | Feb | 2022 | 0.00059255 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-02-16 17:20 | 2022-02-16 18:40 | 63 | 001:20 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22021600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-02-16 | 5040 | keep | 0 | Feb | 2022 | 0.0034327 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2022-02-16 17:22 | 2022-02-16 21:43 | 12 | 004:21 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA Y SE ELIMINO PARARRAYOS DEFECTUOSO | B22021600077 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 261 | 2022-02-16 | 3132 | keep | 0 | Feb | 2022 | 0.0021332 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-16 17:45 | 2022-02-17 10:10 | 75 | 016:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR LA NOTA LA HICIERON MAL SAN GERMAN ES DE MAYAGÃœEZ | P22021600082 | New_Event | Wire Down | Include | Include | Equipment | 985 | 2022-02-16 | 73875 | keep | 0 | Feb | 2022 | 0.050316 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-02-16 18:10 | 2022-02-16 19:20 | 100 | 001:10 | P | LINEA DE TRANSMISION | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA 50200 | A22021600056 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 70 | 2022-02-16 | 7000 | keep | 0 | Feb | 2022 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-16 18:15 | 2022-02-16 19:52 | 8 | 001:37 | P | DESGANCHE | 1X15 EN TRANSFORMADOR | B22021600079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-02-16 | 776 | keep | 0 | Feb | 2022 | 0.00052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-02-16 18:34 | 2022-02-16 18:35 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
HUMACAO | 2022-02-16 18:42 | 2022-02-16 21:52 | 50 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C22021600140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2022-02-16 | 9500 | keep | 0 | Feb | 2022 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-16 18:44 | 2022-02-16 18:46 | 481 | 000:02 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA | R22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-16 | 962 | keep | 0 | Feb | 2022 | 0.00065521 | 0.00032761 | Momentary | FALSE | FALSE | Not_TMED_Event | 481
BAYAMON | 2022-02-16 18:51 | 2022-02-16 18:52 | 50 | 000:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22021600132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-16 | 50 | keep | 0 | Feb | 2022 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-16 18:55 | 2022-02-16 19:48 | 6 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA SECUNDARIA AVERIADA | M22021600098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-02-16 | 318 | keep | 0 | Feb | 2022 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-02-16 19:23 | 2022-02-17 16:57 | 15 | 021:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 25KVA | C22021600147 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1294 | 2022-02-16 | 19410 | keep | 0 | Feb | 2022 | 0.01322 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-16 19:32 | 2022-02-17 02:40 | 1784 | 007:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO MACHETES | M22021600230 | Partial_restoration | Wire Down | Include | Include | Equipment | 428 | 2022-02-16 | 763552 | keep | 0 | Feb | 2022 | 0.52005 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-02-16 20:13 | 2022-02-16 22:06 | 80 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA CAJA PRIMARIA AVERIADA | A22021600062 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-02-16 | 9040 | keep | 0 | Feb | 2022 | 0.0061571 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-16 20:19 | 2022-02-16 20:20 | 1291 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1346-02 SOLO 70% DE SU CARGA A TRAVES DEL 1346-02. A SU VEZ LLEVA 60% DEL 1346-03 | S22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 1291 | keep | 0 | Feb | 2022 | 0.00087929 | 0.00087929 | Momentary | FALSE | FALSE | Not_TMED_Event | 1291
SAN JUAN | 2022-02-16 20:19 | 2022-02-16 20:20 | 1453 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1346-02 SOLO 70% DE SU CARGA A TRAVES DEL 1346-02. A SU VEZ LLEVA 60% DEL 1346-03 | S22021600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-16 | 1453 | keep | 0 | Feb | 2022 | 0.00098963 | 0.00098963 | Momentary | FALSE | FALSE | Not_TMED_Event | 1453
MAYAGÃœEZ | 2022-02-16 20:27 | 2022-02-16 22:25 | 15 | 001:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22021600237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-02-16 | 1770 | keep | 0 | Feb | 2022 | 0.0012055 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-02-16 20:38 | 2022-02-16 21:38 | 100 | 001:00 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | R22021600094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-02-16 | 6000 | keep | 0 | Feb | 2022 | 0.0040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-16 20:59 | 2022-02-16 22:32 | 1 | 001:33 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN BANCO DE XMR DESGANCHO | R22021600017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 93 | 2022-02-16 | 93 | keep | 0 | Feb | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-16 22:54 | 2022-02-17 01:30 | 300 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-5 | S22021600164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2022-02-16 | 46800 | keep | 0 | Feb | 2022 | 0.031875 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-02-17 00:04 | 2022-02-17 00:05 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-02-17 00:35 | 2022-02-17 02:30 | 36 | 001:55 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA | B22021700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-02-17 | 4140 | keep | 0 | Feb | 2022 | 0.0028197 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2022-02-17 00:55 | 2022-02-17 03:30 | 65 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L LEVANTO CONDUCTOR | R22021700001 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2022-02-17 | 10075 | keep | 0 | Feb | 2022 | 0.006862 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-02-17 01:00 | 2022-02-17 05:49 | 50 | 004:49 | P | DESGANCHE | 1 X 65 N C/L DESGANCHE | P22021600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-02-17 | 14450 | keep | 0 | Feb | 2022 | 0.0098418 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-17 01:06 | 2022-02-17 01:07 | 5668 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22021700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 5668 | keep | 0 | Feb | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
UTUADO | 2022-02-17 04:04 | 2022-02-17 10:01 | 60 | 005:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A22021700001 | New_Event | Cutout Failure | Include | Include | Equipment | 357 | 2022-02-17 | 21420 | keep | 0 | Feb | 2022 | 0.014589 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-17 04:16 | 2022-02-17 15:26 | 6 | 011:10 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S22021700036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 670 | 2022-02-17 | 4020 | keep | 0 | Feb | 2022 | 0.002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-17 05:03 | 2022-02-17 13:47 | 30 | 008:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22021700003 | New_Event | Cutout Failure | Include | Include | Equipment | 524 | 2022-02-17 | 15720 | keep | 0 | Feb | 2022 | 0.010707 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-17 05:26 | 2022-02-17 09:44 | 30 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22021700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2022-02-17 | 7740 | keep | 0 | Feb | 2022 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-17 06:00 | 2022-02-17 16:44 | 30 | 010:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA POR 50KVA | B22021700005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 644 | 2022-02-17 | 19320 | keep | 0 | Feb | 2022 | 0.013159 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-17 06:00 | 2022-02-17 10:30 | 30 | 004:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO EN TRONCAL | B22021700005 | New_Event | Wire Down | Include | Include | Equipment | 270 | 2022-02-17 | 8100 | keep | 0 | Feb | 2022 | 0.0055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-17 06:18 | 2022-02-17 13:17 | 40 | 006:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22021700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 419 | 2022-02-17 | 16760 | keep | 0 | Feb | 2022 | 0.011415 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-17 06:43 | 2022-02-17 08:41 | 40 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO @ T-39 | R22021700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-02-17 | 4720 | keep | 0 | Feb | 2022 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-02-17 06:44 | 2022-02-17 13:00 | 34 | 006:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 37.5KVA | C22021700002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 376 | 2022-02-17 | 12784 | keep | 0 | Feb | 2022 | 0.0087071 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-02-17 06:56 | 2022-02-17 11:26 | 60 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22021700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2022-02-17 | 16200 | keep | 0 | Feb | 2022 | 0.011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-17 07:16 | 2022-02-17 16:28 | 170 | 009:12 | P | DESGANCHE | 2 X 50 EN CORTES DE LINEA | C22021700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 552 | 2022-02-17 | 93840 | keep | 0 | Feb | 2022 | 0.063914 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
SAN JUAN | 2022-02-17 07:19 | 2022-02-17 11:35 | 13 | 004:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22021700018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 256 | 2022-02-17 | 3328 | keep | 0 | Feb | 2022 | 0.0022667 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-02-17 07:51 | 2022-02-17 09:47 | 106 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C22021700006 | New_Event |  |  | Include | Wildlife | 116 | 2022-02-17 | 12296 | keep | 0 | Feb | 2022 | 0.0083747 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
BARRANQUITAS | 2022-02-17 08:16 | 2022-02-17 15:57 | 103 | 007:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22021700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 461 | 2022-02-17 | 47483 | keep | 0 | Feb | 2022 | 0.03234 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
BARRANQUITAS | 2022-02-17 08:20 | 2022-02-17 08:22 | 2410 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18400 | C22021700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-17 | 4820 | keep | 0 | Feb | 2022 | 0.0032829 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2022-02-17 08:20 | 2022-02-17 08:22 | 2826 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18400 | C22021700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-17 | 5652 | keep | 0 | Feb | 2022 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
AGUADILLA | 2022-02-17 08:21 | 2022-02-17 08:22 | 4882 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22021700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-17 | 4882 | keep | 0 | Feb | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-02-17 08:22 | 2022-02-17 12:23 | 20 | 004:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22021700011 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-02-17 | 4820 | keep | 0 | Feb | 2022 | 0.0032829 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-17 08:33 | 2022-02-17 10:38 | 50 | 002:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-02-17 | 6250 | keep | 0 | Feb | 2022 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-17 08:38 | 2022-02-17 12:15 | 100 | 003:37 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETE EN LA SALIDA DEL INTERRUPTOR NO CERRABAN BIEN SE OPERO SE CERRO | M22021700010 | New_Event | Switch Failure | Include | Include | Equipment | 217 | 2022-02-17 | 21700 | keep | 0 | Feb | 2022 | 0.01478 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-17 08:45 | 2022-02-17 10:20 | 80 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22021700028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-02-17 | 7600 | keep | 0 | Feb | 2022 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-17 08:59 | 2022-02-17 12:06 | 35 | 003:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | S22021700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-02-17 | 6545 | keep | 0 | Feb | 2022 | 0.0044578 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-02-17 09:01 | 2022-02-17 14:30 | 11 | 005:29 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR 50KVA X 50KVA | R22021700005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 329 | 2022-02-17 | 3619 | keep | 0 | Feb | 2022 | 0.0024649 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-02-17 09:02 | 2022-02-17 15:17 | 40 | 006:15 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE DE ARBOL SOBRE LINEA | R22021700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2022-02-17 | 15000 | keep | 0 | Feb | 2022 | 0.010216 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-17 09:12 | 2022-02-17 13:59 | 18 | 004:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA POR 37.5KVA | B22021700022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 287 | 2022-02-17 | 5166 | keep | 0 | Feb | 2022 | 0.0035185 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-02-17 09:25 | 2022-02-17 13:20 | 1 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN MONTURA DE TRANSFORMADORES CRUCE DE FASE POR AVE | P22021700010 | New_Event |  |  | Include | Wildlife | 235 | 2022-02-17 | 235 | keep | 0 | Feb | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-17 09:37 | 2022-02-17 11:22 | 40 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22021700021 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-02-17 | 4200 | keep | 0 | Feb | 2022 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-17 10:10 | 2022-02-17 17:17 | 200 | 007:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA NOTA MAL HECHA LA ATIENDE MAYAGÃœEZ | P22021600082 | Additional_clients | Wire Down | Include | Include | Equipment | 427 | 2022-02-17 | 85400 | keep | 0 | Feb | 2022 | 0.058166 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-17 10:17 | 2022-02-17 15:19 | 1 | 005:02 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L | S22021700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2022-02-17 | 302 | keep | 0 | Feb | 2022 | 0.00020569 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-17 10:26 | 2022-02-17 12:54 | 10 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | CAMION SE LLEVO SECUNDARIA. SE ABRIO XMR Y SE LEVANTO SECUNDARIA | B22021700030 | New_Event |  |  | Include | Wildlife | 148 | 2022-02-17 | 1480 | keep | 0 | Feb | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-17 10:27 | 2022-02-17 12:34 | 1 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | S22021700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-02-17 | 127 | keep | 0 | Feb | 2022 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-17 10:30 | 2022-02-17 11:25 | 70 | 000:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO MEDIANTE GOI BY-220217-01 | B22021700005 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2022-02-17 | 3850 | keep | 0 | Feb | 2022 | 0.0026222 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-02-17 10:33 | 2022-02-17 12:18 | 603 | 001:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO PIN POLE TOP PARTIDO | C22021700025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2022-02-17 | 63315 | keep | 0 | Feb | 2022 | 0.043124 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
CAGUAS | 2022-02-17 10:48 | 2022-02-17 10:49 | 329 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 329 | keep | 0 | Feb | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-02-17 10:48 | 2022-02-17 10:49 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 1879 | keep | 0 | Feb | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2022-02-17 10:48 | 2022-02-17 10:49 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 2608 | keep | 0 | Feb | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
UTUADO | 2022-02-17 10:56 | 2022-02-17 12:27 | 3 | 001:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22021700020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-02-17 | 273 | keep | 0 | Feb | 2022 | 0.00018594 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-02-17 11:09 | 2022-02-17 14:46 | 100 | 003:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22021700047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-02-17 | 21700 | keep | 0 | Feb | 2022 | 0.01478 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-17 11:14 | 2022-02-17 15:50 | 35 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22021700048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-02-17 | 9660 | keep | 0 | Feb | 2022 | 0.0065794 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-02-17 11:14 | 2022-02-17 19:07 | 30 | 007:53 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE DE 35 PIES METAL GALBANIZADO. SE REMPLAZO 400 PIES DE TRENZADOS 1-0 ALUMINIO TRENZADO. SE INSTALARON 150 PIES ALAMBRES 1-0 ALUMINIO PARA NEUTRAL PRIMARIO. | C22021100048 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 473 | 2022-02-17 | 14190 | keep | 0 | Feb | 2022 | 0.0096647 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-17 11:20 | 2022-02-17 12:45 | 10 | 001:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25 KVA A 4.16 KV AVERIADO | P22021700023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2022-02-17 | 850 | keep | 0 | Feb | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-17 11:36 | 2022-02-17 12:34 | 86 | 000:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA QUEMADA | B22021700040 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2022-02-17 | 4988 | keep | 0 | Feb | 2022 | 0.0033973 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
MAYAGÃœEZ | 2022-02-17 11:53 | 2022-02-17 20:30 | 20 | 008:37 | P | HERRAJE ROTO O PODRIDO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M22021700034 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 517 | 2022-02-17 | 10340 | keep | 0 | Feb | 2022 | 0.0070425 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-17 12:00 | 2022-02-17 15:15 | 12 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS EN PEDESTAL | B22021700044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-02-17 | 2340 | keep | 0 | Feb | 2022 | 0.0015938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-17 12:06 | 2022-02-17 12:07 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22021700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
BARRANQUITAS | 2022-02-17 12:11 | 2022-02-17 15:36 | 6 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | C22021700061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-02-17 | 1230 | keep | 0 | Feb | 2022 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-17 12:15 | 2022-02-17 12:30 | 199 | 000:15 | T | ERROR HUMANO | DISPARO INTERRUPTOR POR PERSONAL REMPLAZANDO FUSIBLE | M22021700037 | New_Event | Human Error | Include | Include | Other | 15 | 2022-02-17 | 2985 | keep | 0 | Feb | 2022 | 0.0020331 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
PONCE | 2022-02-17 12:16 | 2022-02-17 13:43 | 1 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS EN TRANSFORMADOR PARA FIJAR BAJANTE DE LINEA PRIMARIA A MONTURA DE TRANSFORMADORES | P22021700028 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2022-02-17 | 87 | keep | 0 | Feb | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-17 12:16 | 2022-02-17 12:17 | 424 | 000:01 | T | ERROR HUMANO | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 6008-04 | M22021700000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-17 | 424 | keep | 0 | Feb | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
MAYAGÃœEZ | 2022-02-17 12:16 | 2022-02-17 12:17 | 2530 | 000:01 | T | ERROR HUMANO | DISPARO INTERRUPTOR PERSONAL REMPLAZANDO FUSIBLE | M22021700000 | New_Event | Human Error | Include | Include | Other | 1 | 2022-02-17 | 2530 | keep | 0 | Feb | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
CAGUAS | 2022-02-17 12:22 | 2022-02-17 13:20 | 4 | 000:58 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE RETIRO POSTE PARTIDO VACANTE | C22021700065 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 58 | 2022-02-17 | 232 | keep | 0 | Feb | 2022 | 0.00015801 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-17 12:30 | 2022-02-17 15:41 | 100 | 003:11 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETE EN LA SALIDA DEL INTERRUPTOR ESTABAN MAL CERRADOS SE OPERO SE CERRO | M22021700010 | New_Event | Switch Failure | Include | Include | Equipment | 191 | 2022-02-17 | 19100 | keep | 0 | Feb | 2022 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-17 12:34 | 2022-02-17 12:35 | 5809 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1716-03 LLEVANDO LA CARGA DEL 1710-01 | B22021700000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-17 | 5809 | keep | 0 | Feb | 2022 | 0.0039565 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-17 12:34 | 2022-02-17 12:35 | 1812 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1716-03 LLEVANDO LA CARGA DEL 1710-01 | B22021700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-17 | 1812 | keep | 0 | Feb | 2022 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-02-17 12:35 | 2022-02-17 13:50 | 86 | 001:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA QUEMADA | B22021700040 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 75 | 2022-02-17 | 6450 | keep | 0 | Feb | 2022 | 0.0043931 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
SAN JUAN | 2022-02-17 13:02 | 2022-02-17 17:35 | 13 | 004:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO T-24 PARA REEMPLAZAR PISTOLA AVERIADA POR EXCAVACION DE A.A.A | R22021700014 | New_Event |  |  | Include | Wildlife | 273 | 2022-02-17 | 3549 | keep | 0 | Feb | 2022 | 0.0024172 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-02-17 13:16 | 2022-02-17 16:58 | 15 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22021700067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-02-17 | 3330 | keep | 0 | Feb | 2022 | 0.002268 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-02-17 13:27 | 2022-02-17 14:27 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR CONECTORES EN SECUNDARIA | R22021700016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-02-17 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-17 13:35 | 2022-02-17 20:07 | 10 | 006:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P22021700036 | New_Event | Wire Down | Include | Include | Equipment | 392 | 2022-02-17 | 3920 | keep | 0 | Feb | 2022 | 0.0026699 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-17 13:46 | 2022-02-17 16:48 | 100 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22021700055 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2022-02-17 | 18200 | keep | 0 | Feb | 2022 | 0.012396 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-17 13:58 | 2022-02-17 13:59 | 513 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 20% DE LA CARGA POR EL 20% 1118-10 | S22021700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-17 | 513 | keep | 0 | Feb | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-02-17 13:58 | 2022-02-17 13:59 | 2782 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S22021700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-17 | 2782 | keep | 0 | Feb | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-02-17 13:59 | 2022-02-17 16:37 | 15 | 002:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA | S22021700079 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 158 | 2022-02-17 | 2370 | keep | 0 | Feb | 2022 | 0.0016142 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-17 14:02 | 2022-02-17 14:03 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220217000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
CAGUAS | 2022-02-17 14:29 | 2022-02-17 14:30 | 125 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 125 | keep | 0 | Feb | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-02-17 14:30 | 2022-02-17 16:39 | 20 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22021700096 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-02-17 | 2580 | keep | 0 | Feb | 2022 | 0.0017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-02-17 14:36 | 2022-02-17 14:37 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021700042 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 969 | keep | 0 | Feb | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
VEGA BAJA | 2022-02-17 14:45 | 2022-02-17 14:46 | 16 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR POR RIGIDO Y SE LLEVO DISCO PRIMARIO A SU LUGAR | B22021700051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-02-17 | 16 | keep | 0 | Feb | 2022 | 1.0898e-05 | 1.0898e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-02-17 14:49 | 2022-02-17 20:21 | 40 | 005:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C22021700088 | New_Event | Wire Down | Include | Include | Equipment | 332 | 2022-02-17 | 13280 | keep | 0 | Feb | 2022 | 0.0090449 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-17 15:10 | 2022-02-17 19:09 | 10 | 003:59 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | S22021700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-02-17 | 2390 | keep | 0 | Feb | 2022 | 0.0016278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-17 15:16 | 2022-02-17 17:29 | 1863 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2022-02-17 | 247779 | keep | 0 | Feb | 2022 | 0.16876 | 0.0012689 | Sustained | FALSE | FALSE | Not_TMED_Event | 1863
PONCE | 2022-02-17 15:16 | 2022-02-17 17:29 | 708 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2022-02-17 | 94164 | keep | 0 | Feb | 2022 | 0.064135 | 0.00048222 | Sustained | FALSE | FALSE | Not_TMED_Event | 708
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 502 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 55722 | keep | 0 | Feb | 2022 | 0.037952 | 0.00034191 | Sustained | FALSE | FALSE | Not_TMED_Event | 502
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 2747 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 304917 | keep | 0 | Feb | 2022 | 0.20768 | 0.001871 | Sustained | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 1587 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 176157 | keep | 0 | Feb | 2022 | 0.11998 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 2671 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 296481 | keep | 0 | Feb | 2022 | 0.20193 | 0.0018192 | Sustained | FALSE | FALSE | Not_TMED_Event | 2671
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 508 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 56388 | keep | 0 | Feb | 2022 | 0.038406 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 64 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 7104 | keep | 0 | Feb | 2022 | 0.0048385 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 207 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 22977 | keep | 0 | Feb | 2022 | 0.01565 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
YAUCO | 2022-02-17 15:16 | 2022-02-17 17:07 | 286 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22021700053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2022-02-17 | 31746 | keep | 0 | Feb | 2022 | 0.021622 | 0.00019479 | Sustained | FALSE | FALSE | Not_TMED_Event | 286
ARECIBO | 2022-02-17 15:20 | 2022-02-17 17:46 | 900 | 002:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA PODER REPARAR LINEA PRIMARIA ZAFADA DE VARIOS AISLADORES | A22021700032 | New_Event | Wire Down | Include | Include | Equipment | 146 | 2022-02-17 | 131400 | keep | 0 | Feb | 2022 | 0.089496 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
MAYAGÃœEZ | 2022-02-17 15:30 | 2022-02-17 16:45 | 5 | 001:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | M22021700067 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 75 | 2022-02-17 | 375 | keep | 0 | Feb | 2022 | 0.00025541 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-17 15:39 | 2022-02-17 19:02 | 15 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22021700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-02-17 | 3045 | keep | 0 | Feb | 2022 | 0.0020739 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-02-17 15:40 | 2022-02-17 15:41 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 551 | keep | 0 | Feb | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2022-02-17 15:47 | 2022-02-17 16:43 | 190 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22021700088 | New_Event |  |  | Include | Wildlife | 56 | 2022-02-17 | 10640 | keep | 0 | Feb | 2022 | 0.0072469 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2022-02-17 15:53 | 2022-02-17 17:27 | 150 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE ABIERTO A CAJA | S22021700065 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2022-02-17 | 14100 | keep | 0 | Feb | 2022 | 0.0096034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-02-17 15:53 | 2022-02-17 18:53 | 100 | 003:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P22021700080 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2022-02-17 | 18000 | keep | 0 | Feb | 2022 | 0.01226 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-17 16:05 | 2022-02-17 17:12 | 8 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE DIERON CONECTORES SECUNDARIOS Y SE ELIMINO TENSOR | B22021700106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2022-02-17 | 536 | keep | 0 | Feb | 2022 | 0.00036507 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-17 16:12 | 2022-02-17 17:26 | 1 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | S22021700092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-02-17 | 74 | keep | 0 | Feb | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-17 16:49 | 2022-02-17 17:10 | 50 | 000:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 65 EN DISTINTOS CORTES DE LINEA AVE CRUZO FASE | P22021700113 | New_Event |  |  | Include | Wildlife | 21 | 2022-02-17 | 1050 | keep | 0 | Feb | 2022 | 0.00071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-17 17:06 | 2022-02-17 17:07 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021700075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BARRANQUITAS | 2022-02-17 17:24 | 2022-02-18 11:30 | 40 | 018:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22021700111 | New_Event | Wire Down | Include | Include | Equipment | 1086 | 2022-02-17 | 43440 | keep | 0 | Feb | 2022 | 0.029587 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-17 17:42 | 2022-02-17 19:15 | 10 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REEMPLAZO | C22021700114 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2022-02-17 | 930 | keep | 0 | Feb | 2022 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-17 17:46 | 2022-02-18 12:44 | 75 | 018:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22021700047 | New_Event | Cutout Failure | Include | Include | Equipment | 1138 | 2022-02-17 | 85350 | keep | 0 | Feb | 2022 | 0.058131 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-02-17 17:53 | 2022-02-18 18:38 | 48 | 024:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN LA SALIDA DE LA CAJA | B22021700077 | New_Event | Wire Down | Include | Include | Equipment | 1485 | 2022-02-17 | 71280 | keep | 0 | Feb | 2022 | 0.048548 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2022-02-17 17:58 | 2022-02-17 19:24 | 25 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA | S22021700112 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2022-02-17 | 2150 | keep | 0 | Feb | 2022 | 0.0014644 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-02-17 17:58 | 2022-02-17 21:40 | 15 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | S22021700111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-02-17 | 3330 | keep | 0 | Feb | 2022 | 0.002268 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-17 18:00 | 2022-02-17 21:50 | 40 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22021700049 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2022-02-17 | 9200 | keep | 0 | Feb | 2022 | 0.0062661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-17 18:10 | 2022-02-17 18:34 | 8 | 000:24 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA AJUSTAR BUSHING DE TRANSFORMADOR | A22021700052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 24 | 2022-02-17 | 192 | keep | 0 | Feb | 2022 | 0.00013077 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-17 18:13 | 2022-02-17 21:59 | 50 | 003:46 | P | NO SE REPORTO CAUSA | 2 X 65 C/L | B22021700117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-02-17 | 11300 | keep | 0 | Feb | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-17 18:45 | 2022-02-17 19:01 | 10 | 000:16 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA DESCONECTAR TOMA DE SERVICIO SOTERRADA NO IDENTIFICADA AVERIADA | B22021700080 | New_Event | Other Causes | Include | Include | Other | 16 | 2022-02-17 | 160 | keep | 0 | Feb | 2022 | 0.00010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-17 18:51 | 2022-02-18 07:51 | 2 | 013:00 | P | NO SE REPORTO CAUSA | FUSIBLE DE 8A NX EN TRANSFORMADOR NO SE REPORTA CAUSA | P22021700144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 780 | 2022-02-17 | 1560 | keep | 0 | Feb | 2022 | 0.0010625 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-02-17 19:47 | 2022-02-18 09:55 | 10 | 014:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B22021700084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 848 | 2022-02-17 | 8480 | keep | 0 | Feb | 2022 | 0.0057757 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-17 20:03 | 2022-02-17 22:20 | 15 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M22021700081 | New_Event |  |  | Include | Wildlife | 137 | 2022-02-17 | 2055 | keep | 0 | Feb | 2022 | 0.0013997 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-17 20:27 | 2022-02-17 20:28 | 128 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 128 | keep | 0 | Feb | 2022 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2022-02-17 20:27 | 2022-02-17 20:28 | 273 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 273 | keep | 0 | Feb | 2022 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2022-02-17 20:27 | 2022-02-17 20:28 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021700133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 1772 | keep | 0 | Feb | 2022 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
MAYAGÃœEZ | 2022-02-17 20:36 | 2022-02-17 20:37 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-02-17 21:00 | 2022-02-17 21:01 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
FAJARDO | 2022-02-17 21:23 | 2022-02-17 21:24 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22021700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-17 | 1830 | keep | 0 | Feb | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-17 21:37 | 2022-02-17 21:38 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220217000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-17 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
PONCE | 2022-02-17 22:42 | 2022-02-18 06:56 | 25 | 008:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22021700159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 494 | 2022-02-17 | 12350 | keep | 0 | Feb | 2022 | 0.0084115 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-02-17 22:45 | 2022-02-17 23:50 | 15 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A22021700061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-02-17 | 975 | keep | 0 | Feb | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-17 22:57 | 2022-02-17 22:58 | 2379 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR PUENTES PRIMARIOS ABIERTOS | A22021700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-17 | 2379 | keep | 0 | Feb | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
ARECIBO | 2022-02-17 22:58 | 2022-02-18 12:04 | 15 | 013:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22021700062 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 786 | 2022-02-17 | 11790 | keep | 0 | Feb | 2022 | 0.0080301 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-02-17 23:29 | 2022-02-18 08:59 | 100 | 009:30 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO EN EL SU-PDR1 HACIA PB1 SE CERRO PB3 BYPASS A PB1 | C22021700140 | New_Event | Switch Failure | Include | Include | Equipment | 570 | 2022-02-17 | 57000 | keep | 0 | Feb | 2022 | 0.038822 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-18 00:27 | 2022-02-18 09:32 | 200 | 009:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C22021800004 | New_Event | Bad Weather | Include | Include | Weather | 545 | 2022-02-18 | 109000 | keep | 0 | Feb | 2022 | 0.074239 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-02-18 00:59 | 2022-02-18 10:41 | 100 | 009:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA AVERIADA | C22021800006 | New_Event | Cutout Failure | Include | Include | Equipment | 582 | 2022-02-18 | 58200 | keep | 0 | Feb | 2022 | 0.03964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-18 02:14 | 2022-02-18 03:15 | 837 | 001:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO 1401-07 SEGUN SJ-220218-01 Y SE CERRO POR SCADA 30% EN SERVICIO LLEVA EL 1401-06 Y ENTRO 100% | S2202000015 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2022-02-18 | 51057 | keep | 0 | Feb | 2022 | 0.034775 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-02-18 02:14 | 2022-02-18 03:15 | 908 | 001:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO 1401-07 SEGUN SJ-220218-01 Y SE CERRO POR SCADA 30% EN SERVICIO LLEVA EL 1401-06 Y ENTRO 100% | S2202000015 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2022-02-18 | 55388 | keep | 0 | Feb | 2022 | 0.037725 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2022-02-18 02:17 | 2022-02-18 02:18 | 1860 | 000:01 | T | HERRAJE ROTO O PODRIDO | DISPARO Y SE CERRO POR SCADA | S22021800004 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1 | 2022-02-18 | 1860 | keep | 0 | Feb | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-02-18 02:18 | 2022-02-18 07:18 | 47 | 005:00 | P | HERRAJE ROTO O PODRIDO | SE ABRE MACHETE PARA REMPLAZAR CRUCETA Y CERRAR PUENTE | S22021800026 | 1st_after_momentary | Broken / Rusty Hardware | Include | Include | Equipment | 300 | 2022-02-18 | 14100 | keep | 0 | Feb | 2022 | 0.0096034 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CAGUAS | 2022-02-18 02:50 | 2022-02-18 14:24 | 5 | 011:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO Y NEUTRAL PARTIDO | C22021800165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 694 | 2022-02-18 | 3470 | keep | 0 | Feb | 2022 | 0.0023634 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-18 03:15 | 2022-02-18 03:50 | 637 | 000:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SEGUN SJ-220218-01 SE REPARO AISLADOR Y SE ABRIO POR SEGURIDAD 1401-07 (CRUCETA EN MALAS CONDICIONES DE MACHETES A CERRAR) | S2202000015 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 35 | 2022-02-18 | 22295 | keep | 0 | Feb | 2022 | 0.015185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-18 03:50 | 2022-02-18 03:52 | 837 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO 1401-07 POR SEGURIDAD PARA CERRAR MACHETES POR CRUCETA EN MALAS CONDICIONES Y SE CERRO POR SCADA 1401-07 QUE LLEVA 1401-06 LUEGO DE REPARADA CONDICION DE AISLADOR | S2202000015 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 2 | 2022-02-18 | 1674 | keep | 0 | Feb | 2022 | 0.0011402 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-18 03:50 | 2022-02-18 03:52 | 908 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO 1401-07 POR SEGURIDAD PARA CERRAR MACHETES POR CRUCETA EN MALAS CONDICIONES Y SE CERRO POR SCADA 1401-07 QUE LLEVA 1401-06 LUEGO DE REPARADA CONDICION DE AISLADOR | S2202000015 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2022-02-18 | 1816 | keep | 0 | Feb | 2022 | 0.0012369 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-18 03:52 | 2022-02-18 04:27 | 637 | 000:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | LUEGO DE REPARADA OTRA CONDICION DE AISLADOR AL CERRAR MACHETES DEL 1401-07 QUE LLEVA 1401-06 DISPARO 1401-07 SE ABRIERON Y SE CERRO 1401-07 POR SCADA | S2202000015 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 35 | 2022-02-18 | 22295 | keep | 0 | Feb | 2022 | 0.015185 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
BARRANQUITAS | 2022-02-18 04:10 | 2022-02-18 04:11 | 2410 | 000:01 | T | DESGANCHE | RECERRO | C22021800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-18 | 2410 | keep | 0 | Feb | 2022 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2022-02-18 04:11 | 2022-02-18 11:39 | 200 | 007:28 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22021800015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 448 | 2022-02-18 | 89600 | keep | 0 | Feb | 2022 | 0.061026 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-02-18 04:25 | 2022-02-18 10:57 | 10 | 006:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22021800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2022-02-18 | 3920 | keep | 0 | Feb | 2022 | 0.0026699 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-18 04:27 | 2022-02-18 04:28 | 837 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | LUEGO DE REPARADA OTRA CONDICION DE AISLADOR AL CERRAR MACHETES DEL 1401-07 QUE LLEVA 1401-06 DISPARO 1401-07 SE ABRIERON Y SE CERRO 1401-07 POR SCADA | S2202000015 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-18 | 837 | keep | 0 | Feb | 2022 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-02-18 04:27 | 2022-02-18 04:28 | 908 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | LUEGO DE REPARADA OTRA CONDICION DE AISLADOR AL CERRAR MACHETES DEL 1401-07 QUE LLEVA 1401-06 DISPARO 1401-07 SE ABRIERON Y SE CERRO 1401-07 POR SCADA | S2202000015 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-18 | 908 | keep | 0 | Feb | 2022 | 0.00061843 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-18 04:28 | 2022-02-18 05:05 | 637 | 000:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y PARARRAYOS Y SE CERO MACHETES EN 100% EN SERVICIO 1401-07 | S2202000015 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 37 | 2022-02-18 | 23569 | keep | 0 | Feb | 2022 | 0.016053 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
CANOVANAS | 2022-02-18 04:45 | 2022-02-18 06:48 | 15 | 002:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO CAJA PRIMARIA | R22021800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-02-18 | 1845 | keep | 0 | Feb | 2022 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-02-18 05:21 | 2022-02-18 08:59 | 1 | 003:38 | P | DESGANCHE | 1 X 30 EN C/L | C22021800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2022-02-18 | 218 | keep | 0 | Feb | 2022 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-18 06:14 | 2022-02-18 14:24 | 35 | 008:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 75KVA X 75KVA | C22021800013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 490 | 2022-02-18 | 17150 | keep | 0 | Feb | 2022 | 0.011681 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-02-18 06:43 | 2022-02-18 06:44 | 4431 | 000:01 | T | DESGANCHE | RECERRO | B22021800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-18 | 4431 | keep | 0 | Feb | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-02-18 06:44 | 2022-02-18 11:06 | 100 | 004:22 | P | DESGANCHE | 2 X 80 EN C/L, 1 X 50 EN C/L Y 1 X 30 EN C/L SE REALIZO DESGANCHE | B22021800003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-02-18 | 26200 | keep | 0 | Feb | 2022 | 0.017845 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-18 07:04 | 2022-02-18 07:05 | 3432 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 20% DE LA CARGA POR EL 1303-02 | S22021800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-18 | 3432 | keep | 0 | Feb | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-02-18 07:05 | 2022-02-18 07:18 | 357 | 000:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PARA CERRAR PUENTE ABIERTO EN EL TRONCAL SJ-220218-02 | S22021800031 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 13 | 2022-02-18 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0.00024315 | Sustained | FALSE | FALSE | Not_TMED_Event | 357
PONCE | 2022-02-18 07:05 | 2022-02-18 07:06 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 1979 | keep | 0 | Feb | 2022 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
SAN JUAN | 2022-02-18 07:18 | 2022-02-18 07:19 | 3432 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | S22021800000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-02-18 | 3432 | keep | 0 | Feb | 2022 | 0.0023375 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-18 07:18 | 2022-02-18 07:20 | 1860 | 000:02 | T | HERRAJE ROTO O PODRIDO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22021800000 | Additional_clients | Broken / Rusty Hardware | Include | Include | Equipment | 2 | 2022-02-18 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-18 07:18 | 2022-02-18 18:51 | 55 | 011:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR Y REPARAR CONDUCTOR ROTO VIVO EN EL SUELO, NO FUNDIO FUSIBLE | B22021800004 | New_Event | Wire Down | Include | Include | Equipment | 693 | 2022-02-18 | 38115 | keep | 0 | Feb | 2022 | 0.02596 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-02-18 07:19 | 2022-02-18 13:24 | 357 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PARA CERRAR PUENTE ABIERTO EN EL TRONCAL SJ-220218-02 | S22021800031 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 365 | 2022-02-18 | 130305 | keep | 0 | Feb | 2022 | 0.08875 | 0.00024315 | Sustained | FALSE | FALSE | Not_TMED_Event | 357
BAYAMON | 2022-02-18 07:20 | 2022-02-18 14:00 | 47 | 006:40 | P | HERRAJE ROTO O PODRIDO | SE ABRE MACHETE PARA REMPLAZAR CRUCETA Y CERRAR PUENTE | S22021800026 | 1st_after_momentary | Broken / Rusty Hardware | Include | Include | Equipment | 400 | 2022-02-18 | 18800 | keep | 0 | Feb | 2022 | 0.012805 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CAGUAS | 2022-02-18 07:34 | 2022-02-18 07:35 | 329 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C22021800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-18 | 329 | keep | 0 | Feb | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-02-18 07:34 | 2022-02-18 07:35 | 329 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C22021800018 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-18 | 329 | keep | 0 | Feb | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
ARECIBO | 2022-02-18 07:44 | 2022-02-18 13:04 | 10 | 005:20 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22021800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2022-02-18 | 3200 | keep | 0 | Feb | 2022 | 0.0021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-18 08:16 | 2022-02-18 08:17 | 1835 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22021800027 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-18 | 1835 | keep | 0 | Feb | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-02-18 08:17 | 2022-02-18 14:27 | 30 | 006:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C22021800143 | 1st_after_momentary |  |  | Include | Wildlife | 370 | 2022-02-18 | 11100 | keep | 0 | Feb | 2022 | 0.0075602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-18 08:25 | 2022-02-18 08:26 | 134 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-09 SE CERRO POR SCADA LLEVA 1115-03 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 134 | keep | 0 | Feb | 2022 | 9.1267e-05 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2022-02-18 08:25 | 2022-02-18 08:26 | 34 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-09 SE CERRO POR SCADA CARGA LLEVANDO 1115-04 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 34 | keep | 0 | Feb | 2022 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-02-18 08:25 | 2022-02-18 08:26 | 316 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-09 SE CERRO POR SCADA LLEVA 1115-03 Y 30% DEL 1115-04 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 316 | keep | 0 | Feb | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
BAYAMON | 2022-02-18 08:26 | 2022-02-18 11:54 | 35 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22021800057 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-02-18 | 7280 | keep | 0 | Feb | 2022 | 0.0049584 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-02-18 08:27 | 2022-02-18 09:43 | 15 | 001:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | R22021800004 | New_Event |  |  | Include | Wildlife | 76 | 2022-02-18 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-02-18 08:28 | 2022-02-18 12:31 | 20 | 004:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-02-18 | 4860 | keep | 0 | Feb | 2022 | 0.0033101 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-18 08:30 | 2022-02-18 15:28 | 90 | 006:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA REMPLAZARON AISLADOR ROTO | B22021800010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 418 | 2022-02-18 | 37620 | keep | 0 | Feb | 2022 | 0.025623 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-02-18 08:49 | 2022-02-18 11:40 | 30 | 002:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22021800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-02-18 | 5130 | keep | 0 | Feb | 2022 | 0.003494 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-02-18 08:56 | 2022-02-18 10:01 | 12 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS EN PEDESTAL | R22021800005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-02-18 | 780 | keep | 0 | Feb | 2022 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-18 08:59 | 2022-02-18 09:00 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1907-03 EN RELEVO DE CARGA POR DISPARO UNIDAD 2 AES LLEVANDO LA CARGA DEL 1909-09 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 222 | keep | 0 | Feb | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-02-18 08:59 | 2022-02-18 09:00 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1907-03 EN RELEVO DE CARGA POR DISPARO UNIDAD 2 AES LLEVANDO LA CARGA DEL 1909-09 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 4456 | keep | 0 | Feb | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-02-18 09:03 | 2022-02-18 10:52 | 10 | 001:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22021700086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 109 | 2022-02-18 | 1090 | keep | 0 | Feb | 2022 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-18 09:19 | 2022-02-18 11:55 | 100 | 002:36 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO EN EL SU-PDR1 HACIA PB1 SE CERRO PB3 BYPASS A PB1 | C22021700140 | Partial_restoration | Switch Failure | Include | Include | Equipment | 156 | 2022-02-18 | 15600 | keep | 0 | Feb | 2022 | 0.010625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-18 09:19 | 2022-02-18 14:52 | 1 | 005:33 | P | DESGANCHE | 1 X 30 EN C/L | C22021800009 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-02-18 | 333 | keep | 0 | Feb | 2022 | 0.0002268 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-18 09:20 | 2022-02-18 10:11 | 3 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C22021800074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-02-18 | 153 | keep | 0 | Feb | 2022 | 0.00010421 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-02-18 09:23 | 2022-02-18 13:39 | 50 | 004:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22021800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2022-02-18 | 12800 | keep | 0 | Feb | 2022 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-18 09:25 | 2022-02-18 13:45 | 175 | 004:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22021800011 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2022-02-18 | 45500 | keep | 0 | Feb | 2022 | 0.03099 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
HUMACAO | 2022-02-18 09:43 | 2022-02-18 13:32 | 6 | 003:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA AVERIADA | C22021800109 | New_Event | Cutout Failure | Include | Include | Equipment | 229 | 2022-02-18 | 1374 | keep | 0 | Feb | 2022 | 0.00093583 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-02-18 09:53 | 2022-02-18 09:54 | 2493 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22021800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 2493 | keep | 0 | Feb | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-02-18 09:53 | 2022-02-18 13:18 | 300 | 003:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M22021800019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 205 | 2022-02-18 | 61500 | keep | 0 | Feb | 2022 | 0.041887 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2022-02-18 09:54 | 2022-02-18 10:22 | 1 | 000:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE INSTALO HOT CLAMP EN BAJANTE PRIMARIO A CAJA DE MONTURA TRIFASICA DE BOMBA AAA | P22021800025 | New_Event | Wire Down | Include | Include | Equipment | 28 | 2022-02-18 | 28 | keep | 0 | Feb | 2022 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-18 10:06 | 2022-02-18 12:40 | 60 | 002:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22021800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-02-18 | 9240 | keep | 0 | Feb | 2022 | 0.0062933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-02-18 10:09 | 2022-02-18 15:09 | 5 | 005:00 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO PODRIDO | M22021800022 | New_Event | Defective Pole | Include | Include | Equipment | 300 | 2022-02-18 | 1500 | keep | 0 | Feb | 2022 | 0.0010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-18 10:28 | 2022-02-18 10:32 | 1984 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR 1529-12 SE CERRO POR SCADA LLEVA LA CARGA DEL 1911-07 | S22021800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 7936 | keep | 0 | Feb | 2022 | 0.0054052 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-02-18 10:28 | 2022-02-18 10:32 | 577 | 000:04 | T | NO SE REPORTO CAUSA | 1529-12 DISPARO Y SE CERRO POR SCADA LLEVA 1911-07 | S22021800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 2308 | keep | 0 | Feb | 2022 | 0.001572 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
HUMACAO | 2022-02-18 10:30 | 2022-02-18 13:02 | 14 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22018000134 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2022-02-18 | 2128 | keep | 0 | Feb | 2022 | 0.0014494 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-02-18 10:45 | 2022-02-18 13:44 | 160 | 002:59 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L Y 1 X 50 EN C/L SE REEMPLAZO PARARRAYO | B22021800027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 179 | 2022-02-18 | 28640 | keep | 0 | Feb | 2022 | 0.019507 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
PONCE | 2022-02-18 10:48 | 2022-02-18 11:27 | 1 | 000:39 | P | OTRAS CAUSAS | PROBLEMA INTERNO EN BOMBA AAA | P22021800040 | New_Event | Other Causes | Include | Include | Other | 39 | 2022-02-18 | 39 | keep | 0 | Feb | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-02-18 11:06 | 2022-02-18 18:17 | 15 | 007:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M22021800029 | New_Event | Cutout Failure | Include | Include | Equipment | 431 | 2022-02-18 | 6465 | keep | 0 | Feb | 2022 | 0.0044033 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-18 11:07 | 2022-02-18 15:38 | 11 | 004:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE A CAJA PRIMARIA XMR | B22021800036 | New_Event | Wire Down | Include | Include | Equipment | 271 | 2022-02-18 | 2981 | keep | 0 | Feb | 2022 | 0.0020303 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-02-18 11:11 | 2022-02-18 12:10 | 10 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B22021800038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-02-18 | 590 | keep | 0 | Feb | 2022 | 0.00040185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-18 11:12 | 2022-02-18 13:21 | 10 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22021800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-02-18 | 1290 | keep | 0 | Feb | 2022 | 0.00087861 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-18 11:31 | 2022-02-18 12:40 | 1 | 001:09 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN SU-7 CONTAMINACION | B22021800044 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 69 | 2022-02-18 | 69 | keep | 0 | Feb | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-18 11:38 | 2022-02-18 13:21 | 19 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR NEUTRAL DEL SUELO | C22021800148 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-02-18 | 1957 | keep | 0 | Feb | 2022 | 0.0013329 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-02-18 12:17 | 2022-02-18 12:18 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | M22021800036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 4304 | keep | 0 | Feb | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
HUMACAO | 2022-02-18 12:32 | 2022-02-18 15:17 | 35 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 25 Y 1 X 40 EN C/L NO CAUSA | C22021800159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-02-18 | 5775 | keep | 0 | Feb | 2022 | 0.0039333 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2022-02-18 12:40 | 2022-02-18 14:13 | 40 | 001:33 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C22021800162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-02-18 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-18 12:48 | 2022-02-18 14:50 | 20 | 002:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-02-18 | 2440 | keep | 0 | Feb | 2022 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-02-18 13:05 | 2022-02-18 16:05 | 10 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22021800015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-02-18 | 1800 | keep | 0 | Feb | 2022 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-02-18 13:15 | 2022-02-18 16:02 | 8 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22021800048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2022-02-18 | 1336 | keep | 0 | Feb | 2022 | 0.00090994 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-02-18 13:19 | 2022-02-18 18:13 | 100 | 004:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-02-18 | 29400 | keep | 0 | Feb | 2022 | 0.020024 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-02-18 13:26 | 2022-02-18 14:54 | 10 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | R22021800032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2022-02-18 | 880 | keep | 0 | Feb | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-18 13:26 | 2022-02-18 15:02 | 25 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA AUTOMOVIL IMPACTO POSTE PRIMARIO Y CRUZO FASES | P22021800053 | New_Event |  |  | Include | Wildlife | 96 | 2022-02-18 | 2400 | keep | 0 | Feb | 2022 | 0.0016346 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-18 13:48 | 2022-02-18 13:49 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22021800056 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
SAN JUAN | 2022-02-18 13:51 | 2022-02-18 16:11 | 20 | 002:20 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | R22021800044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-02-18 | 2800 | keep | 0 | Feb | 2022 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-18 13:52 | 2022-02-18 15:46 | 35 | 001:54 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | C22021800171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-02-18 | 3990 | keep | 0 | Feb | 2022 | 0.0027176 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-02-18 14:00 | 2022-02-18 16:40 | 124 | 002:40 | P | HERRAJE ROTO O PODRIDO | SE ABRE MACHETE PARA REMPLAZAR CRUCETA Y CERRAR PUENTE | S22021800026 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 160 | 2022-02-18 | 19840 | keep | 0 | Feb | 2022 | 0.013513 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
AGUADILLA | 2022-02-18 14:07 | 2022-02-18 14:08 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7003-02 | M22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 470 | keep | 0 | Feb | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
AGUADILLA | 2022-02-18 14:07 | 2022-02-18 14:08 | 1345 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 7003-01 | M22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 1345 | keep | 0 | Feb | 2022 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
BAYAMON | 2022-02-18 14:07 | 2022-02-18 14:11 | 2234 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | B22021800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 8936 | keep | 0 | Feb | 2022 | 0.0060863 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-02-18 14:33 | 2022-02-19 12:00 | 64 | 021:27 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22021800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1287 | 2022-02-18 | 82368 | keep | 0 | Feb | 2022 | 0.0561 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
UTUADO | 2022-02-18 14:39 | 2022-02-18 16:50 | 40 | 002:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-02-18 | 5240 | keep | 0 | Feb | 2022 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-18 14:44 | 2022-02-18 16:44 | 100 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 100 EN C/L MAL TIEMPO | C22021800174 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2022-02-18 | 12000 | keep | 0 | Feb | 2022 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-18 14:48 | 2022-02-18 14:49 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | LINEA 3700 FUERA DE SERVICIO | P220218000XX | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-18 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
GUAYAMA | 2022-02-18 14:51 | 2022-02-18 16:22 | 50 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETESO LINEA PRIMARIA | P22021800061 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2022-02-18 | 4550 | keep | 0 | Feb | 2022 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-18 15:04 | 2022-02-18 16:17 | 30 | 001:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | R22021800049 | New_Event | Cutout Failure | Include | Include | Equipment | 73 | 2022-02-18 | 2190 | keep | 0 | Feb | 2022 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-18 15:11 | 2022-02-18 18:19 | 100 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22021800066 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2022-02-18 | 18800 | keep | 0 | Feb | 2022 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-18 15:12 | 2022-02-18 17:40 | 160 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 100 EN CORTES DE LINEAS MAL TIEMPO | B22021800074 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2022-02-18 | 23680 | keep | 0 | Feb | 2022 | 0.016128 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
FAJARDO | 2022-02-18 15:21 | 2022-02-18 17:09 | 10 | 001:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | R22021800051 | New_Event | Cutout Failure | Include | Include | Equipment | 108 | 2022-02-18 | 1080 | keep | 0 | Feb | 2022 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-18 15:25 | 2022-02-18 17:21 | 50 | 001:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22021800188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-02-18 | 5800 | keep | 0 | Feb | 2022 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-18 15:28 | 2022-02-18 17:43 | 10 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | R22021800037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2022-02-18 | 1350 | keep | 0 | Feb | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-18 15:34 | 2022-02-18 20:27 | 327 | 004:53 | S | PARARRAYOS DEFECTUOSO | LOCKOUT EN LA SUBESTACION SE ELIMINO PARRARAYO DE BAJA FASE B | C22021800000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 293 | 2022-02-18 | 95811 | keep | 0 | Feb | 2022 | 0.065256 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-02-18 15:34 | 2022-02-18 18:12 | 5630 | 002:38 | S | PARARRAYOS DEFECTUOSO | LOCKOUT EN LA SUBESTACION SE ELIMINO PARRARAYO DE BAJA FASE B SE TRANSFIRIO 60% DE LA CARGA AL 3205-07 | C22021800000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 158 | 2022-02-18 | 889540 | keep | 0 | Feb | 2022 | 0.60586 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-02-18 15:34 | 2022-02-18 20:27 | 2126 | 004:53 | S | PARARRAYOS DEFECTUOSO | LOCKOUT EN LA SUBESTACION SE ELIMINO PARRARAYO DE BAJA FASE B | C22021800000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 293 | 2022-02-18 | 622918 | keep | 0 | Feb | 2022 | 0.42427 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-02-18 15:34 | 2022-02-18 20:27 | 551 | 004:53 | S | PARARRAYOS DEFECTUOSO | LOCKOUT EN LA SUBESTACION SE ELIMINO PARRARAYO DE BAJA FASE B | C22021800000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 293 | 2022-02-18 | 161443 | keep | 0 | Feb | 2022 | 0.10996 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
MAYAGÃœEZ | 2022-02-18 15:45 | 2022-02-18 18:53 | 70 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA VIENTOS FUERTES | M22021800073 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2022-02-18 | 13160 | keep | 0 | Feb | 2022 | 0.0089632 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-02-18 15:45 | 2022-02-18 16:33 | 6 | 000:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22021800042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-02-18 | 288 | keep | 0 | Feb | 2022 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-18 15:55 | 2022-02-18 22:46 | 50 | 006:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22021800086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 411 | 2022-02-18 | 20550 | keep | 0 | Feb | 2022 | 0.013997 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-18 15:56 | 2022-02-18 15:57 | 3046 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | R22021800054 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-02-18 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-02-18 15:57 | 2022-02-18 21:07 | 12 | 005:10 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN SU 3A SE REPARO TERMINACION | R22021800053 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 310 | 2022-02-18 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-18 16:08 | 2022-02-18 16:10 | 1310 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-18 | 2620 | keep | 0 | Feb | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
MAYAGÃœEZ | 2022-02-18 16:16 | 2022-02-18 18:50 | 45 | 002:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M22021800086 | New_Event | Cutout Failure | Include | Include | Equipment | 154 | 2022-02-18 | 6930 | keep | 0 | Feb | 2022 | 0.00472 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-02-18 16:17 | 2022-02-18 19:10 | 12 | 002:53 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE SALIDA BKR Y SE NORMALIZO 1512-5 | S22021800203 | New_Event | Switch Failure | Include | Include | Equipment | 173 | 2022-02-18 | 2076 | keep | 0 | Feb | 2022 | 0.001414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-18 16:17 | 2022-02-18 19:10 | 7 | 002:53 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE SALIDA BKR 4 | S22021800203 | New_Event | Switch Failure | Include | Include | Equipment | 173 | 2022-02-18 | 1211 | keep | 0 | Feb | 2022 | 0.00082481 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-18 16:17 | 2022-02-18 19:10 | 12 | 002:53 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE SALIDA 1512-4 SU CARGA POR 1512-5 | S22021800203 | New_Event | Switch Failure | Include | Include | Equipment | 173 | 2022-02-18 | 2076 | keep | 0 | Feb | 2022 | 0.001414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-18 16:23 | 2022-02-19 06:51 | 12 | 014:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L. SE REEMPLAZO CRUCETA Y SE LEVANTO CONDUCTOR | B22021800093 | New_Event | Wire Down | Include | Include | Equipment | 868 | 2022-02-18 | 10416 | keep | 0 | Feb | 2022 | 0.0070943 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-18 16:24 | 2022-02-18 17:25 | 3432 | 001:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO PORTATIL 22 PERSONA AJENA A LUMA TUMBO ARBOL Y CRUZO 3 FASES Y SE VERIFICO CARR.844 KM.4.2 CARRAIZO Y SE CERRO SECUNDARIO QUEDO EN SERVICIO LLEVA 80% DE SU CARGA | S22021800000 | New_Event |  |  | Include | Wildlife | 61 | 2022-02-18 | 209352 | keep | 0 | Feb | 2022 | 0.14259 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-02-18 16:24 | 2022-02-18 17:25 | 552 | 001:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO PORTATIL 22 PERSONA AJENA A LUMA TUMBO ARBOL Y CRUZO 3 FASES Y SE VERIFICO CARR.844 KM.4.2 CARAIZO Y SE CERRO SECUNDARIO QUEDO EN SERVICIO 40% DE SU CARGA POR 1204-1 | S22021800000 | New_Event |  |  | Include | Wildlife | 61 | 2022-02-18 | 33672 | keep | 0 | Feb | 2022 | 0.022934 | 0.00037596 | Sustained | FALSE | FALSE | Not_TMED_Event | 552
PONCE | 2022-02-18 16:31 | 2022-02-18 18:42 | 20 | 002:11 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P22021800074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2022-02-18 | 2620 | keep | 0 | Feb | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-18 16:49 | 2022-02-18 16:50 | 2524 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22021800057 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-18 | 2524 | keep | 0 | Feb | 2022 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-02-18 16:50 | 2022-02-18 18:52 | 60 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 Y 1 X 20 EN CORTE DE LINEAS SE RETIRO AVE CRUZANDO LINEAS Y SE REMPLAZARON 2 CAJAS PRIMARIAS | R22021800060 | 1st_after_momentary |  |  | Include | Wildlife | 122 | 2022-02-18 | 7320 | keep | 0 | Feb | 2022 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-18 16:50 | 2022-02-18 16:54 | 2900 | 000:04 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | C22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 11600 | keep | 0 | Feb | 2022 | 0.0079007 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
VEGA BAJA | 2022-02-18 16:52 | 2022-02-18 18:33 | 60 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | B22021800099 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2022-02-18 | 6060 | keep | 0 | Feb | 2022 | 0.0041274 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-02-18 17:10 | 2022-02-18 20:32 | 15 | 003:22 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABREN CAJAS EN TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO PARTIDO | P22021800075 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 202 | 2022-02-18 | 3030 | keep | 0 | Feb | 2022 | 0.0020637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-02-18 17:30 | 2022-02-18 19:37 | 40 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22021800102 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2022-02-18 | 5080 | keep | 0 | Feb | 2022 | 0.00346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-18 17:34 | 2022-02-19 12:59 | 63 | 019:25 | P | CABLE SOTERRADO AVERIADO | CABLE SOTERRADO AVERIADO DE SU-3 @ T-10 AVERIA VIEJA DE T-14 @ T-13 | B22021800111 | New_Event | UG Cable Fault | Include | Include | Equipment | 1165 | 2022-02-18 | 73395 | keep | 0 | Feb | 2022 | 0.049989 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2022-02-18 17:49 | 2022-02-18 17:50 | 552 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 CON R/R OFF LLEVA 30% DEL 1346-02 SE PROBO QUEDO EN SERVICIO | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 552 | keep | 0 | Feb | 2022 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
BAYAMON | 2022-02-18 17:49 | 2022-02-18 17:50 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | 1529-15 DISPARO CON R/R OFF LLEVA 30% DEL 1346-2 SE PROBO QUEDO EN SERVICIO | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 1802 | keep | 0 | Feb | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
HUMACAO | 2022-02-18 18:12 | 2022-02-18 20:27 | 2252 | 002:15 | P | PARARRAYOS DEFECTUOSO | SE CERRO INTERRUPTOR POR SCADA Y SE NORMALIZO SU CARGA 100% EN SERVICIO | C22021800000 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 135 | 2022-02-18 | 304020 | keep | 0 | Feb | 2022 | 0.20707 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-18 18:52 | 2022-02-18 18:55 | 2524 | 000:03 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22021800111 | Additional_clients |  |  | Include | Wildlife | 3 | 2022-02-18 | 7572 | keep | 0 | Feb | 2022 | 0.0051573 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-18 18:55 | 2022-02-18 19:07 | 12 | 000:12 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA PARTIDA | S22021800314 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 12 | 2022-02-18 | 144 | keep | 0 | Feb | 2022 | 9.8078e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-18 18:55 | 2022-02-18 19:53 | 60 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 Y 1 X 20 EN CORTE DE LINEAS SE RETIRO AVE CRUZANDO LINEAS Y SE REMPLAZARON 2 CAJAS PRIMARIAS | R22021800060 | 1st_after_momentary |  |  | Include | Wildlife | 58 | 2022-02-18 | 3480 | keep | 0 | Feb | 2022 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-18 19:02 | 2022-02-19 06:51 | 15 | 011:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | C22021800314 | New_Event | Bad Weather | Include | Include | Weather | 709 | 2022-02-18 | 10635 | keep | 0 | Feb | 2022 | 0.0072435 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-18 19:04 | 2022-02-18 19:08 | 500 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DEL 1424-08 AL CERRAR VS-15 @ VS-16 EN V/L D2022-00101 LLEVA 1336-08 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 2000 | keep | 0 | Feb | 2022 | 0.0013622 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-02-18 19:04 | 2022-02-18 19:08 | 1000 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO 1424-08 AL CERRAR VS-15 @ VS-16 EN V/L D2022-00101 LLEVANDO 80% DEL 1348-06 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 4000 | keep | 0 | Feb | 2022 | 0.0027244 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-02-18 19:04 | 2022-02-18 19:08 | 278 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO 1424-08 AL CERRAR VS-15 @ VS-16 EN V/L D2022-00101 LLEVANDO CARGA DEL 1348-07 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 1112 | keep | 0 | Feb | 2022 | 0.00075738 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-02-18 19:04 | 2022-02-18 19:08 | 9 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO 1424-08 AL CERRAR VS-15 @ VS-16 EN V/L D2022-00101 LLEVA 1348-7, 80% DEL 1348-6 Y PARTE DEL 1336-8 | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-02-18 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-02-18 19:14 | 2022-02-19 10:24 | 675 | 015:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CRUCE POR CULEBRA | C22021800320 | New_Event |  |  | Include | Wildlife | 910 | 2022-02-18 | 614250 | keep | 0 | Feb | 2022 | 0.41836 | 0.00045974 | Sustained | FALSE | FALSE | Not_TMED_Event | 675
MAYAGÃœEZ | 2022-02-18 19:19 | 2022-02-18 22:04 | 100 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | M22021800109 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2022-02-18 | 16500 | keep | 0 | Feb | 2022 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-18 19:30 | 2022-02-18 22:55 | 60 | 003:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22021800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-02-18 | 12300 | keep | 0 | Feb | 2022 | 0.0083775 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-18 19:31 | 2022-02-19 12:52 | 25 | 017:21 | P | DESGANCHE | SE REALIZO DESGANCHE | S22021800320 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1041 | 2022-02-18 | 26025 | keep | 0 | Feb | 2022 | 0.017726 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-18 19:56 | 2022-02-18 19:57 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22021800110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 4381 | keep | 0 | Feb | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
HUMACAO | 2022-02-18 20:27 | 2022-02-18 22:15 | 1011 | 001:48 | P | NO SE REPORTO CAUSA | CERRO EL IR 2603-7B NO CAUSA | C22021800366 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-02-18 | 109188 | keep | 0 | Feb | 2022 | 0.074367 | 0.00068859 | Sustained | FALSE | FALSE | Not_TMED_Event | 1011
CAGUAS | 2022-02-18 21:11 | 2022-02-18 21:12 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 4634 | keep | 0 | Feb | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
ARECIBO | 2022-02-18 21:11 | 2022-02-19 08:12 | 6 | 011:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A22021800060 | New_Event | Bad Weather | Include | Include | Weather | 661 | 2022-02-18 | 3966 | keep | 0 | Feb | 2022 | 0.0027012 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-18 21:14 | 2022-02-18 21:17 | 315 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | S22021800322 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-18 | 945 | keep | 0 | Feb | 2022 | 0.00064364 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2022-02-18 21:25 | 2022-02-18 21:27 | 1370 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO | S22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-18 | 2740 | keep | 0 | Feb | 2022 | 0.0018662 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
MAYAGÃœEZ | 2022-02-18 21:32 | 2022-02-19 02:10 | 100 | 004:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22021800111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-02-18 | 27800 | keep | 0 | Feb | 2022 | 0.018934 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-18 22:04 | 2022-02-18 22:20 | 3147 | 000:16 | T | ERROR HUMANO | DISPARO DEL INTERRUPTOR PERSONAL REMPLAZANDO CAJA PRIMARIA CAUSO EL DISPARO SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M22021800131 | New_Event | Human Error | Include | Include | Other | 16 | 2022-02-18 | 50352 | keep | 0 | Feb | 2022 | 0.034295 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
HUMACAO | 2022-02-18 22:12 | 2022-02-19 05:20 | 60 | 007:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 SMU DE 40 AMP MAL TIEMPO | C22021800381 | New_Event | Bad Weather | Include | Include | Weather | 428 | 2022-02-18 | 25680 | keep | 0 | Feb | 2022 | 0.017491 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-18 22:41 | 2022-02-19 00:09 | 50 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE CRUZO LINEAS | B22021800132 | New_Event |  |  | Include | Wildlife | 88 | 2022-02-18 | 4400 | keep | 0 | Feb | 2022 | 0.0029968 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-18 22:41 | 2022-02-18 22:42 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 1746 | keep | 0 | Feb | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
FAJARDO | 2022-02-18 22:50 | 2022-02-19 10:04 | 30 | 011:14 | P | DESGANCHE | 1 X 25 Y 1 X 15 EN TRANSFORMADORES DESGANCHO | R22021800139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 674 | 2022-02-18 | 20220 | keep | 0 | Feb | 2022 | 0.013772 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-18 23:46 | 2022-02-18 23:47 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22021800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-18 | 2147 | keep | 0 | Feb | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
CANOVANAS | 2022-02-19 00:13 | 2022-02-19 01:05 | 45 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | R22021900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-02-19 | 2340 | keep | 0 | Feb | 2022 | 0.0015938 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-02-19 00:55 | 2022-02-19 20:11 | 125 | 019:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L SE REPARO CONDUCTOR PARTIDO EN EL SUELO | R22021900077 | New_Event | Wire Down | Include | Include | Equipment | 1156 | 2022-02-19 | 144500 | keep | 0 | Feb | 2022 | 0.098418 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-02-19 02:18 | 2022-02-19 07:20 | 150 | 005:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22021900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-02-19 | 45300 | keep | 0 | Feb | 2022 | 0.030854 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-02-19 03:06 | 2022-02-19 03:55 | 8 | 000:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 5 EN TRANSFORMADOR ROEDOR CRUZO LINEAS | M22021900001 | New_Event |  |  | Include | Wildlife | 49 | 2022-02-19 | 392 | keep | 0 | Feb | 2022 | 0.00026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-19 03:08 | 2022-02-19 05:05 | 35 | 001:57 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | S22021900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-02-19 | 4095 | keep | 0 | Feb | 2022 | 0.0027891 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-02-19 04:05 | 2022-02-19 13:05 | 351 | 009:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTE DE LINEA CRUCE POR HILO | C22021900001 | New_Event |  |  | Include | Wildlife | 540 | 2022-02-19 | 189540 | keep | 0 | Feb | 2022 | 0.12909 | 0.00023906 | Sustained | FALSE | FALSE | Not_TMED_Event | 351
CANOVANAS | 2022-02-19 05:02 | 2022-02-19 05:03 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22021900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 1894 | keep | 0 | Feb | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
HUMACAO | 2022-02-19 05:20 | 2022-02-19 05:21 | 327 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CARGAS X 2603-06 | C22021900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-19 | 327 | keep | 0 | Feb | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-02-19 05:21 | 2022-02-19 08:07 | 60 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 SMU DE 40 AMP MAL TIEMPO | C22021800381 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 166 | 2022-02-19 | 9960 | keep | 0 | Feb | 2022 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-19 05:31 | 2022-02-19 07:01 | 2907 | 001:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA LEVANTAR ALAMBRES DEL SUELO 50% SE TRANSFIRIO AL 3406-01 | C22021900004 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2022-02-19 | 261630 | keep | 0 | Feb | 2022 | 0.1782 | 0.0019799 | Sustained | FALSE | FALSE | Not_TMED_Event | 2907
ARECIBO | 2022-02-19 05:55 | 2022-02-19 10:55 | 40 | 005:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22021900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-02-19 | 12000 | keep | 0 | Feb | 2022 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-19 06:11 | 2022-02-19 17:17 | 30 | 011:06 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22021900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 666 | 2022-02-19 | 19980 | keep | 0 | Feb | 2022 | 0.013608 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-19 07:01 | 2022-02-19 12:53 | 12 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L. SE REEMPLAZO CRUCETA Y SE LEVANTO CONDUCTOR | B22021800093 | Partial_restoration | Wire Down | Include | Include | Equipment | 352 | 2022-02-19 | 4224 | keep | 0 | Feb | 2022 | 0.0028769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-19 07:01 | 2022-02-19 07:07 | 1454 | 000:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR LLEVANDO UN 20% SUMANDO ASI UN 70% EN SERVICIO | C22021900004 | Partial_restoration | Wire Down | Include | Include | Equipment | 6 | 2022-02-19 | 8724 | keep | 0 | Feb | 2022 | 0.0059419 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-19 07:02 | 2022-02-19 09:13 | 15 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | C22021800314 | Partial_restoration | Bad Weather | Include | Include | Weather | 131 | 2022-02-19 | 1965 | keep | 0 | Feb | 2022 | 0.0013384 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-19 07:07 | 2022-02-19 10:12 | 872 | 003:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MACHETES 100% EN SERVICIO | C22021900004 | Partial_restoration | Wire Down | Include | Include | Equipment | 185 | 2022-02-19 | 161320 | keep | 0 | Feb | 2022 | 0.10987 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-02-19 07:07 | 2022-02-19 09:10 | 30 | 002:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A22021900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-02-19 | 3690 | keep | 0 | Feb | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-19 07:23 | 2022-02-19 15:20 | 125 | 007:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | C22021900036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 477 | 2022-02-19 | 59625 | keep | 0 | Feb | 2022 | 0.04061 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-02-19 07:56 | 2022-02-19 10:53 | 20 | 002:57 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22021900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-02-19 | 3540 | keep | 0 | Feb | 2022 | 0.0024111 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-19 08:02 | 2022-02-19 09:30 | 1 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22021900030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-02-19 | 88 | keep | 0 | Feb | 2022 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-19 08:06 | 2022-02-19 08:08 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22021900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-19 | 1740 | keep | 0 | Feb | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-02-19 08:06 | 2022-02-19 08:07 | 3114 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1710-05 LLEVANDO SOLO 60% DE SU CARGA | B22021900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 3114 | keep | 0 | Feb | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2022-02-19 08:06 | 2022-02-19 12:25 | 40 | 004:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22021900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-02-19 | 10360 | keep | 0 | Feb | 2022 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-19 08:07 | 2022-02-19 08:08 | 327 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22021900000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2022-02-19 | 327 | keep | 0 | Feb | 2022 | 0.00022272 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-19 08:08 | 2022-02-19 10:58 | 60 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 SMU DE 40 AMP. MAL TIEMPO | C22021800381 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 170 | 2022-02-19 | 10200 | keep | 0 | Feb | 2022 | 0.0069472 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-19 08:17 | 2022-02-19 09:45 | 10 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22021800097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2022-02-19 | 880 | keep | 0 | Feb | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-19 08:34 | 2022-02-19 12:12 | 1 | 003:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22021900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 218 | 2022-02-19 | 218 | keep | 0 | Feb | 2022 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-02-19 08:36 | 2022-02-19 09:54 | 2 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | C22021900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2022-02-19 | 156 | keep | 0 | Feb | 2022 | 0.00010625 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-02-19 08:48 | 2022-02-19 08:49 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22021900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 1894 | keep | 0 | Feb | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
SAN JUAN | 2022-02-19 09:00 | 2022-02-19 11:32 | 57 | 002:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | R22021900047 | New_Event | Bad Weather | Include | Include | Weather | 152 | 2022-02-19 | 8664 | keep | 0 | Feb | 2022 | 0.005901 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
CANOVANAS | 2022-02-19 09:16 | 2022-02-19 12:25 | 1 | 003:09 | P | HERRAJE ROTO O PODRIDO | 3 X 25 EN BANCO DE TRANSFORMADOR SE REEMPLAZO CRUCETA QUEMADA | R22021900049 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 189 | 2022-02-19 | 189 | keep | 0 | Feb | 2022 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-02-19 09:18 | 2022-02-19 16:30 | 15 | 007:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22021900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 432 | 2022-02-19 | 6480 | keep | 0 | Feb | 2022 | 0.0044135 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-02-19 09:22 | 2022-02-19 14:58 | 12 | 005:36 | P | OTRAS CAUSAS | 1 X 20 EN RISER FUSIBLE PODRIDO | A22021900011 | New_Event | Other Causes | Include | Include | Other | 336 | 2022-02-19 | 4032 | keep | 0 | Feb | 2022 | 0.0027462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-19 09:36 | 2022-02-19 09:44 | 4009 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO LA CAUSA | P220219000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-19 | 32072 | keep | 0 | Feb | 2022 | 0.021844 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
VEGA BAJA | 2022-02-19 09:41 | 2022-02-19 11:47 | 100 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22021900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-02-19 | 12600 | keep | 0 | Feb | 2022 | 0.0085818 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-19 09:56 | 2022-02-19 13:54 | 40 | 003:58 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA | B22021900044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-02-19 | 9520 | keep | 0 | Feb | 2022 | 0.006484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-19 10:02 | 2022-02-19 11:32 | 23 | 001:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA SECCIONALIZAR SECUNDARIA CON DESGANCHE | C22021900071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 90 | 2022-02-19 | 2070 | keep | 0 | Feb | 2022 | 0.0014099 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-02-19 10:06 | 2022-02-19 11:29 | 10 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22021800087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-02-19 | 830 | keep | 0 | Feb | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-19 10:39 | 2022-02-19 10:40 | 427 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22021900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 427 | keep | 0 | Feb | 2022 | 0.00029083 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2022-02-19 10:45 | 2022-02-19 13:16 | 17 | 002:31 | T | CABLE SOTERRADO AVERIADO | DISPARO SE ENCONTRO AVERIA DE BKR. A SU-20 PIN HOLE AVERIADO | S22021900150 | New_Event | UG Cable Fault | Include | Include | Equipment | 151 | 2022-02-19 | 2567 | keep | 0 | Feb | 2022 | 0.0017484 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-02-19 11:12 | 2022-02-19 12:57 | 1105 | 001:45 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF PERSONAL DE LA TECNICA TUVO QUE PATRULLAR LINEA PARA LOCALIZAR EL PERSONAL DE INGENIERIA QUE HABIA SOLICITADO EL RECIERRE EN OFF PARA PODER HACER PRUEBAS A INTERRUPTOR | A22021900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-02-19 | 116025 | keep | 0 | Feb | 2022 | 0.079024 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2022-02-19 11:25 | 2022-02-19 16:44 | 30 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22021900073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-02-19 | 9570 | keep | 0 | Feb | 2022 | 0.0065181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-19 11:26 | 2022-02-19 11:54 | 27 | 000:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 SMU DE 20 EN SU-2 MAL TIEMPO | C22021900075 | New_Event | Bad Weather | Include | Include | Weather | 28 | 2022-02-19 | 756 | keep | 0 | Feb | 2022 | 0.00051491 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2022-02-19 11:33 | 2022-02-19 13:24 | 80 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 15 EN CORTE DE LINEA Y TRANSFORMADOR CRUCE CON AVE | R22021900056 | New_Event |  |  | Include | Wildlife | 111 | 2022-02-19 | 8880 | keep | 0 | Feb | 2022 | 0.0060481 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-02-19 11:45 | 2022-02-19 13:55 | 10 | 002:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA A 4.16KV POR UNO DE 25KVA A 2.4KV | P22021900069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 130 | 2022-02-19 | 1300 | keep | 0 | Feb | 2022 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-19 11:46 | 2022-02-20 14:11 | 34 | 026:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 37.5KVA | C22021900078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1585 | 2022-02-19 | 53890 | keep | 0 | Feb | 2022 | 0.036704 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
ARECIBO | 2022-02-19 12:00 | 2022-02-19 21:35 | 12 | 009:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | A22021900032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 575 | 2022-02-19 | 6900 | keep | 0 | Feb | 2022 | 0.0046996 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-19 12:08 | 2022-02-19 17:56 | 30 | 005:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C22021900080 | New_Event | Cutout Failure | Include | Include | Equipment | 348 | 2022-02-19 | 10440 | keep | 0 | Feb | 2022 | 0.0071106 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-19 12:08 | 2022-02-19 14:30 | 2 | 002:22 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P22021900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-02-19 | 284 | keep | 0 | Feb | 2022 | 0.00019343 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-02-19 12:13 | 2022-02-19 15:37 | 6 | 003:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 15KVA POR UNO DE 37.5KVA | R22021900064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 204 | 2022-02-19 | 1224 | keep | 0 | Feb | 2022 | 0.00083366 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-19 12:25 | 2022-02-19 13:29 | 84 | 001:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C22021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-02-19 | 5376 | keep | 0 | Feb | 2022 | 0.0036616 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
YAUCO | 2022-02-19 12:30 | 2022-02-19 13:10 | 20 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22021900077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-02-19 | 800 | keep | 0 | Feb | 2022 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-02-19 12:35 | 2022-02-19 15:54 | 67 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22021900087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-02-19 | 13333 | keep | 0 | Feb | 2022 | 0.009081 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
AGUADILLA | 2022-02-19 12:40 | 2022-02-19 17:00 | 20 | 004:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA ZAFADA DE AISLADOR | M22021900040 | New_Event | Wire Down | Include | Include | Equipment | 260 | 2022-02-19 | 5200 | keep | 0 | Feb | 2022 | 0.0035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-19 12:46 | 2022-02-19 14:07 | 830 | 001:21 | P | DESGANCHE | SE RETIRO BAMBUA 60% DE SU CARGA POR 1206-4 | S22021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-02-19 | 67230 | keep | 0 | Feb | 2022 | 0.04579 | 0.00056531 | Sustained | FALSE | FALSE | Not_TMED_Event | 830
SAN JUAN | 2022-02-19 12:46 | 2022-02-19 14:07 | 1978 | 001:21 | P | DESGANCHE | SE RETIRO BAMBUA 40% DE SU CARGA POR 1206-4 | S22021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-02-19 | 160218 | keep | 0 | Feb | 2022 | 0.10912 | 0.0013472 | Sustained | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2022-02-19 12:46 | 2022-02-19 14:07 | 1799 | 001:21 | T | DESGANCHE | DISPARO SE RETIRO BAMBUA SOBRE LINEA Y SE CERRO INTERRUPTOR LLEVA 20% 1303-2, 40% 1204-4 Y 60% 1204-3 | S22021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-02-19 | 145719 | keep | 0 | Feb | 2022 | 0.099249 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-02-19 12:46 | 2022-02-19 14:07 | 487 | 001:21 | P | DESGANCHE | SE RETIRO BAMBUA SU CARGA POR 1206-4 | S22021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-02-19 | 39447 | keep | 0 | Feb | 2022 | 0.026867 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
BAYAMON | 2022-02-19 12:59 | 2022-02-19 13:30 | 75 | 000:31 | P | CABLE SOTERRADO AVERIADO | SE ABRE DE T-14A @ T14 PARA SECCIONALIZAR AVERIA DE CABLE SOTERRADO Y PODER TRABAJAR CON GOI BY220219-01 | B22011900057 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 31 | 2022-02-19 | 2325 | keep | 0 | Feb | 2022 | 0.0015835 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-19 13:04 | 2022-02-19 17:09 | 40 | 004:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C22021900093 | New_Event |  |  | Include | Wildlife | 245 | 2022-02-19 | 9800 | keep | 0 | Feb | 2022 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-19 13:07 | 2022-02-19 15:21 | 150 | 002:14 | P | NO SE REPORTO CAUSA | 2 X 200 EN CORTE DE LINEA | B22021900070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-02-19 | 20100 | keep | 0 | Feb | 2022 | 0.01369 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-02-19 13:16 | 2022-02-19 15:43 | 10 | 002:27 | P | CABLE SOTERRADO AVERIADO | DISPARO SE ENCONTRO AVERIA DE BKR. A SU-20 PIN HOLE AVERIA SE PASA CARGA AL 1111-1 | S22021900150 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 147 | 2022-02-19 | 1470 | keep | 0 | Feb | 2022 | 0.0010012 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-19 13:17 | 2022-02-19 15:07 | 1 | 001:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE CORTE DE LINEA | A22021900078 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2022-02-19 | 110 | keep | 0 | Feb | 2022 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-19 13:30 | 2022-02-19 16:57 | 63 | 003:27 | P | CABLE SOTERRADO AVERIADO | SE CERRO DE T-14A @ T-14 PARA QUE PERSONAL PUDIERA IR A ALMORZAR Y NO PENALIZAR CLIENTES | B22021900057 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 207 | 2022-02-19 | 13041 | keep | 0 | Feb | 2022 | 0.0088822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-19 13:50 | 2022-02-19 14:18 | 92 | 000:28 | P | DESGANCHE | SE ABRIO MACHETE PARA RETIRAR BAMBUA SOBRE LINEA | S22021900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-02-19 | 2576 | keep | 0 | Feb | 2022 | 0.0017545 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
GUAYAMA | 2022-02-19 14:14 | 2022-02-19 16:21 | 2100 | 002:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220219000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 127 | 2022-02-19 | 266700 | keep | 0 | Feb | 2022 | 0.18165 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-19 14:14 | 2022-02-19 16:21 | 922 | 002:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220219000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 127 | 2022-02-19 | 117094 | keep | 0 | Feb | 2022 | 0.079752 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-19 14:14 | 2022-02-19 16:21 | 1676 | 002:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220219000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 127 | 2022-02-19 | 212852 | keep | 0 | Feb | 2022 | 0.14497 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-19 14:14 | 2022-02-19 16:21 | 2844 | 002:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P220219000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 127 | 2022-02-19 | 361188 | keep | 0 | Feb | 2022 | 0.246 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
CAGUAS | 2022-02-19 14:18 | 2022-02-19 19:00 | 15 | 004:42 | P | DESGANCHE | 2 X 50 EN C/L | C22021900107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-02-19 | 4230 | keep | 0 | Feb | 2022 | 0.002881 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-19 14:23 | 2022-02-19 14:24 | 100 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1801-05 LLEVANDO PARTE 1801-01 | B22021900070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 100 | keep | 0 | Feb | 2022 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-19 14:23 | 2022-02-19 14:24 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVANDO PARTE 1801-01 | B22021900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 112 | keep | 0 | Feb | 2022 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
SAN JUAN | 2022-02-19 14:56 | 2022-02-19 17:04 | 30 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L AVE CRUZO LINEAS | R22021900073 | New_Event |  |  | Include | Wildlife | 128 | 2022-02-19 | 3840 | keep | 0 | Feb | 2022 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-19 15:09 | 2022-02-19 17:23 | 12 | 002:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR 150 PIES DE ALAMBRE SECUNDARIO | B22021900097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 134 | 2022-02-19 | 1608 | keep | 0 | Feb | 2022 | 0.0010952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-02-19 15:14 | 2022-02-19 15:15 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22021900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 5630 | keep | 0 | Feb | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
MAYAGÃœEZ | 2022-02-19 15:29 | 2022-02-19 18:50 | 85 | 003:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22021900047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-02-19 | 17085 | keep | 0 | Feb | 2022 | 0.011637 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2022-02-19 15:42 | 2022-02-19 17:58 | 10 | 002:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | B22021900098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 136 | 2022-02-19 | 1360 | keep | 0 | Feb | 2022 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-19 15:46 | 2022-02-19 18:35 | 12 | 002:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL | S22021900188 | New_Event | Secondary Wire Down | Include | Include | Equipment | 169 | 2022-02-19 | 2028 | keep | 0 | Feb | 2022 | 0.0013813 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-19 15:56 | 2022-02-19 19:45 | 250 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22021900050 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2022-02-19 | 57250 | keep | 0 | Feb | 2022 | 0.038993 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2022-02-19 16:23 | 2022-02-19 17:53 | 50 | 001:30 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C22021900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-02-19 | 4500 | keep | 0 | Feb | 2022 | 0.0030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-19 16:40 | 2022-02-19 19:17 | 10 | 002:37 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTES PARA REMPLAZO DE POSTE PARTIDO NO HABIA CLIENTES ANTES FUERA NO SE ABRE PUENTES FUERA MAS CLIENTES | M22021900057 | New_Event | Defective Pole | Include | Include | Equipment | 157 | 2022-02-19 | 1570 | keep | 0 | Feb | 2022 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-19 16:57 | 2022-02-19 23:10 | 75 | 006:13 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO AVERIADO TRAMO DE CABLE SOTERRADO Y SE NORMALIZO | B22011900057 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 373 | 2022-02-19 | 27975 | keep | 0 | Feb | 2022 | 0.019054 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-19 17:11 | 2022-02-19 17:12 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22021900102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 2113 | keep | 0 | Feb | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
GUAYAMA | 2022-02-19 17:14 | 2022-02-19 17:40 | 8 | 000:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22021900104 | New_Event |  |  | Include | Wildlife | 26 | 2022-02-19 | 208 | keep | 0 | Feb | 2022 | 0.00014167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-02-19 17:51 | 2022-02-19 22:23 | 30 | 004:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22021900033 | New_Event | Bad Weather | Include | Include | Weather | 272 | 2022-02-19 | 8160 | keep | 0 | Feb | 2022 | 0.0055577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-19 18:04 | 2022-02-19 22:05 | 10 | 004:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22021900073 | New_Event | Bad Weather | Include | Include | Weather | 241 | 2022-02-19 | 2410 | keep | 0 | Feb | 2022 | 0.0016414 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-19 18:52 | 2022-02-19 21:25 | 150 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA INFORMA UL2 TRAINED NO IDENTIFICO CAUSA | M22021900077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-02-19 | 22950 | keep | 0 | Feb | 2022 | 0.015631 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-19 19:39 | 2022-02-19 19:40 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVANDO CARGA 1911-06 | S22021900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-19 | 58 | keep | 0 | Feb | 2022 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
ARECIBO | 2022-02-19 20:01 | 2022-02-19 22:12 | 40 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22021900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-02-19 | 5240 | keep | 0 | Feb | 2022 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-19 21:34 | 2022-02-20 03:12 | 55 | 005:38 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22021900204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2022-02-19 | 18590 | keep | 0 | Feb | 2022 | 0.012662 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2022-02-19 22:00 | 2022-02-19 22:59 | 8 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P22021900112 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2022-02-19 | 472 | keep | 0 | Feb | 2022 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-02-19 22:15 | 2022-02-20 09:46 | 34 | 011:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE CON AVE | C22021900128 | New_Event |  |  | Include | Wildlife | 691 | 2022-02-19 | 23494 | keep | 0 | Feb | 2022 | 0.016002 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
AGUADILLA | 2022-02-19 22:18 | 2022-02-20 08:53 | 30 | 010:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEAS REQUIERE DESGANCHE | M22021900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 635 | 2022-02-19 | 19050 | keep | 0 | Feb | 2022 | 0.012975 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-19 23:02 | 2022-02-20 03:59 | 325 | 004:57 | T | OTRAS CAUSAS | SE ABRIO PUENTES HACIA 1 SOLO CLIENTE MEDIANTE BY-220219-02 Y SE CERRO POR SCADA SE LE CREO EVENTO B22022000003 PARA VERIFICAR PROA | B22021800111 | New_Event | Other Causes | Include | Include | Other | 297 | 2022-02-19 | 96525 | keep | 0 | Feb | 2022 | 0.065743 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
HUMACAO | 2022-02-19 23:32 | 2022-02-20 13:04 | 99 | 013:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22022000129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 812 | 2022-02-19 | 80388 | keep | 0 | Feb | 2022 | 0.054752 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
MAYAGÃœEZ | 2022-02-19 23:53 | 2022-02-20 12:50 | 4387 | 012:57 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DOS DISCOS QUEMADOS SE RETIRO ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR MANUAL ELECTRICO | M22021900091 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 777 | 2022-02-19 | 3408699 | keep | 0 | Feb | 2022 | 2.3216 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
SAN JUAN | 2022-02-20 00:53 | 2022-02-20 03:11 | 80 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S22022000003 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-02-20 | 11040 | keep | 0 | Feb | 2022 | 0.0075193 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-20 01:36 | 2022-02-20 01:37 | 177 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA 40% POR 1013-13 | S22022000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 177 | keep | 0 | Feb | 2022 | 0.00012055 | 0.00012055 | Momentary | FALSE | FALSE | Not_TMED_Event | 177
ARECIBO | 2022-02-20 02:04 | 2022-02-20 05:20 | 60 | 003:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22022000004 | New_Event | Wire Down | Include | Include | Equipment | 196 | 2022-02-20 | 11760 | keep | 0 | Feb | 2022 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-20 02:52 | 2022-02-20 02:53 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 50% DE SU CARGA POR EL 1909-07 Y LLEVA LA CARGA DEL 1709-05 | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 767 | keep | 0 | Feb | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-02-20 02:52 | 2022-02-20 02:53 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1709-03 LLEVANDO LA CARGA DEL 1709-05 | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 2364 | keep | 0 | Feb | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
SAN JUAN | 2022-02-20 03:08 | 2022-02-20 09:10 | 35 | 006:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO Y RETIRO CULEBRA DE LA LINEA | R22022000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-02-20 | 12670 | keep | 0 | Feb | 2022 | 0.0086295 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-02-20 03:14 | 2022-02-20 12:58 | 500 | 009:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | S22022022225 | New_Event | Wire Down | Include | Include | Equipment | 584 | 2022-02-20 | 292000 | keep | 0 | Feb | 2022 | 0.19888 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2022-02-20 03:14 | 2022-02-20 07:57 | 50 | 004:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22022000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2022-02-20 | 14150 | keep | 0 | Feb | 2022 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-20 03:54 | 2022-02-20 03:55 | 1681 | 000:01 | T | DESGANCHE | DISPARO 1303-04 Y SE CERRO POR SCADA LLEVA 1303-01 | S22022000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-20 | 1681 | keep | 0 | Feb | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-20 03:54 | 2022-02-20 03:55 | 1598 | 000:01 | T | DESGANCHE | DISPARO 1303-04 Y SE CERRO POR SCADA LLEVA 1346-06 | S22022000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-20 | 1598 | keep | 0 | Feb | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-02-20 04:05 | 2022-02-20 04:06 | 1681 | 000:01 | T | DESGANCHE | DISPARO 1303-04 Y SE CERRO POR SCADA LLEVA 1303-01 | S22022000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-20 | 1681 | keep | 0 | Feb | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-20 04:05 | 2022-02-20 04:06 | 1598 | 000:01 | T | DESGANCHE | DISPARO 1303-04 Y SE CERRO POR SCADA LLEVA 1346-06 | S22022000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-20 | 1598 | keep | 0 | Feb | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-02-20 04:53 | 2022-02-20 06:48 | 1681 | 001:55 | T | DESGANCHE | SE SECCIONALIZO POR BAMBU EN LINEA CARGA POR EL 1303-04 SJ-220220-0 | S22022000014 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-02-20 | 193315 | keep | 0 | Feb | 2022 | 0.13167 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-20 04:53 | 2022-02-20 06:48 | 1598 | 001:55 | T | DESGANCHE | BAMBU SOBRE LINEA PRIMARIA CARGA POR EL 1303-04 SW-220220-0 | S22022000014 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-02-20 | 183770 | keep | 0 | Feb | 2022 | 0.12516 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2022-02-20 06:12 | 2022-02-20 09:21 | 150 | 003:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C2202200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-02-20 | 28350 | keep | 0 | Feb | 2022 | 0.019309 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-02-20 06:31 | 2022-02-20 07:54 | 10 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22022000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-02-20 | 830 | keep | 0 | Feb | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-20 06:48 | 2022-02-20 07:32 | 168 | 000:44 | P | DESGANCHE | SECCIONALIZO EN CAMINO LOS GUANOS SE DESGANCHO CARGA POR EL 1303-04 | S22022000014 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-02-20 | 7392 | keep | 0 | Feb | 2022 | 0.0050347 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-20 06:49 | 2022-02-20 09:19 | 14 | 002:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y 2 X 5 EN BANCO DE TRANSFORMADORES CRUCE POR CULEBRA | R22022000002 | New_Event |  |  | Include | Wildlife | 150 | 2022-02-20 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2022-02-20 07:04 | 2022-02-20 11:15 | 2 | 004:11 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO CAUSA | C22022000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2022-02-20 | 502 | keep | 0 | Feb | 2022 | 0.00034191 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-02-20 07:22 | 2022-02-20 07:23 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22022000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 2696 | keep | 0 | Feb | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
HUMACAO | 2022-02-20 07:27 | 2022-02-20 10:33 | 40 | 003:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22022000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-02-20 | 7440 | keep | 0 | Feb | 2022 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-20 07:44 | 2022-02-20 09:38 | 20 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22022000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-02-20 | 2280 | keep | 0 | Feb | 2022 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-20 07:46 | 2022-02-20 11:33 | 60 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22022000065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-02-20 | 13620 | keep | 0 | Feb | 2022 | 0.0092765 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-20 07:58 | 2022-02-20 10:54 | 86 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN SU-3 MAL TIEMPO | R22022000004 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2022-02-20 | 15136 | keep | 0 | Feb | 2022 | 0.010309 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BAYAMON | 2022-02-20 08:24 | 2022-02-20 12:53 | 5961 | 004:29 | T | DESCONECTIVO DEFECTUOSO | SE REALIZO CAMBIO DE MACHETE QUEMADO CON GOI BY-220220-01 INTERRUPTOR 1713-05 LLEVA 95% 1717-02 | B22022000015 | New_Event | Switch Failure | Include | Include | Equipment | 269 | 2022-02-20 | 1603509 | keep | 0 | Feb | 2022 | 1.0921 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-02-20 08:24 | 2022-02-20 12:53 | 865 | 004:29 | P | DESCONECTIVO DEFECTUOSO | SE REALIZO CAMBIO DE MACHETE QUEMADO CON GOI BY-220220-01 INTERRUPTOR 1713-05 LLEVA 95% 1717-02 | B22022000015 | New_Event | Switch Failure | Include | Include | Equipment | 269 | 2022-02-20 | 232685 | keep | 0 | Feb | 2022 | 0.15848 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-02-20 08:40 | 2022-02-20 08:42 | 478 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22022000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-20 | 956 | keep | 0 | Feb | 2022 | 0.00065113 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-02-20 08:40 | 2022-02-20 08:42 | 865 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1705-01 LLEVANDO 90% 1705-03 | B22022000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-20 | 1730 | keep | 0 | Feb | 2022 | 0.0011783 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
CAGUAS | 2022-02-20 09:01 | 2022-02-20 11:08 | 3 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | C22022000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2022-02-20 | 381 | keep | 0 | Feb | 2022 | 0.0002595 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-02-20 09:01 | 2022-02-20 11:08 | 16 | 002:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | C22022000011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 127 | 2022-02-20 | 2032 | keep | 0 | Feb | 2022 | 0.001384 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-02-20 10:07 | 2022-02-20 17:21 | 2565 | 007:14 | P | CABLE SOTERRADO AVERIADO | SE ABRIO MH-19 A SU-20 PARA REPARAR PIN HOLE EN SU-20, SE ENERGIZO SE VA A TRABAJAR MANANA REMPLAZO CABLE ESTO POR AVERIA DEL 1111-2 | S22022000089 | New_Event | UG Cable Fault | Include | Include | Equipment | 434 | 2022-02-20 | 1113210 | keep | 0 | Feb | 2022 | 0.7582 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
ARECIBO | 2022-02-20 10:09 | 2022-02-20 11:51 | 30 | 001:42 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA REQUIERE DESGANCHE | A22022000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-02-20 | 3060 | keep | 0 | Feb | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-20 10:37 | 2022-02-20 17:21 | 17 | 006:44 | T | CABLE SOTERRADO AVERIADO | SE ABRIO MH-19 A SU-20 PARA REPARAR PIN HOLE EN SU-20, SE ENERGIZO SE VA A TRABAJAR MANANA REMPLAZO CABLE SU CARGA POR 1111-1 | S22022000089 | New_Event | UG Cable Fault | Include | Include | Equipment | 404 | 2022-02-20 | 6868 | keep | 0 | Feb | 2022 | 0.0046778 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2022-02-20 10:39 | 2022-02-20 14:03 | 150 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-1 | S22022000116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-02-20 | 30600 | keep | 0 | Feb | 2022 | 0.020842 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-02-20 10:48 | 2022-02-20 11:04 | 1 | 000:16 | P | OTRAS CAUSAS | 1 X 30 EN TRANSCLOUSER PROBLEMA DEL CLIENTE | C22022000027 | New_Event | Other Causes | Include | Include | Other | 16 | 2022-02-20 | 16 | keep | 0 | Feb | 2022 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-20 10:55 | 2022-02-20 10:56 | 2440 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22022000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 2440 | keep | 0 | Feb | 2022 | 0.0016619 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
BAYAMON | 2022-02-20 10:55 | 2022-02-20 10:56 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22022000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 2605 | keep | 0 | Feb | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
PONCE | 2022-02-20 10:56 | 2022-02-20 11:41 | 8 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA Y CONECTORES SECUNDARIOS | P22022000031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-02-20 | 360 | keep | 0 | Feb | 2022 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-02-20 11:31 | 2022-02-20 11:45 | 10 | 000:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B22022000236 | New_Event | Secondary Wire Down | Include | Include | Equipment | 14 | 2022-02-20 | 140 | keep | 0 | Feb | 2022 | 9.5353e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-20 11:41 | 2022-02-20 13:22 | 40 | 001:41 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA. SE REALIZO DESGANCHE | S22022000143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-02-20 | 4040 | keep | 0 | Feb | 2022 | 0.0027516 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-20 11:47 | 2022-02-20 16:08 | 85 | 004:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CHANGO CRUZO FASE | S22022000144 | New_Event |  |  | Include | Wildlife | 261 | 2022-02-20 | 22185 | keep | 0 | Feb | 2022 | 0.01511 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-02-20 11:55 | 2022-02-21 10:27 | 12 | 022:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25 KVA POR 50 KVA | S22022000151 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1352 | 2022-02-20 | 16224 | keep | 0 | Feb | 2022 | 0.01105 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-02-20 12:34 | 2022-02-20 13:45 | 1093 | 001:11 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE ALIMENTADOR NO CERRO POR CONTROL DE SCADA SE CERRO MANUAL ELECTRICAMENTE | P22022000047 | New_Event | Bad Weather | Include | Include | Weather | 71 | 2022-02-20 | 77603 | keep | 0 | Feb | 2022 | 0.052855 | 0.00074444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1093
BARRANQUITAS | 2022-02-20 12:52 | 2022-02-20 15:17 | 50 | 002:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO DISCO | C22022000033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 145 | 2022-02-20 | 7250 | keep | 0 | Feb | 2022 | 0.0049379 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-20 13:29 | 2022-02-20 15:49 | 100 | 002:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22022000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-02-20 | 14000 | keep | 0 | Feb | 2022 | 0.0095353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-20 13:45 | 2022-02-20 14:00 | 55 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | SE ABREN MACHETES PARA SECCIONALIZAR Y COLOCAR INTERRUPTOR EN SERVICIO | P22022000055 | Partial_restoration | Bad Weather | Include | Include | Weather | 15 | 2022-02-20 | 825 | keep | 0 | Feb | 2022 | 0.0005619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-20 14:00 | 2022-02-20 15:38 | 100 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE BRISA | P22022000066 | Additional_clients | Bad Weather | Include | Include | Weather | 98 | 2022-02-20 | 9800 | keep | 0 | Feb | 2022 | 0.0066747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-20 14:10 | 2022-02-20 16:05 | 85 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE BRISA | P22022000067 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2022-02-20 | 9775 | keep | 0 | Feb | 2022 | 0.0066577 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-02-20 14:25 | 2022-02-20 17:58 | 30 | 003:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y SE CERRO PUENTE ABIERTO (NO FUNDIO FUSIBLE) | B22022000304 | New_Event | Cutout Failure | Include | Include | Equipment | 213 | 2022-02-20 | 6390 | keep | 0 | Feb | 2022 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-20 14:29 | 2022-02-20 16:23 | 8 | 001:54 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y DESGANCHAR | M22022000151 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 114 | 2022-02-20 | 912 | keep | 0 | Feb | 2022 | 0.00062116 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-20 14:57 | 2022-02-20 22:03 | 12 | 007:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN CORTE DE LINEA Y SE REMPLAZO PORTAFUSIBLE | S22022200187 | New_Event | Cutout Failure | Include | Include | Equipment | 426 | 2022-02-20 | 5112 | keep | 0 | Feb | 2022 | 0.0034818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-20 15:09 | 2022-02-20 21:00 | 12 | 005:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO T-10 Y SE REPARO NEUTRAL ABIERTO | B22022000318 | New_Event | Secondary Wire Down | Include | Include | Equipment | 351 | 2022-02-20 | 4212 | keep | 0 | Feb | 2022 | 0.0028688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-20 15:35 | 2022-02-20 17:53 | 10 | 002:18 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | B22022200150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-02-20 | 1380 | keep | 0 | Feb | 2022 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-20 15:47 | 2022-02-20 15:48 | 776 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22022000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 776 | keep | 0 | Feb | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
AGUADILLA | 2022-02-20 15:50 | 2022-02-20 16:14 | 4 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22022000155 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-02-20 | 96 | keep | 0 | Feb | 2022 | 6.5385e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-02-20 16:06 | 2022-02-20 17:46 | 40 | 001:40 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA CRUZANDO LINEAS PRIMARIAS | A22022000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-02-20 | 4000 | keep | 0 | Feb | 2022 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-20 16:13 | 2022-02-20 20:36 | 10 | 004:23 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE MONTURA PARA RELOCALIZAR SECUNDARIA POSTE EN MALAS CONDICIONES | S22022000213 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 263 | 2022-02-20 | 2630 | keep | 0 | Feb | 2022 | 0.0017913 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-20 16:27 | 2022-02-20 17:45 | 75 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE BRISA | P22022000072 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2022-02-20 | 5850 | keep | 0 | Feb | 2022 | 0.0039844 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-20 17:07 | 2022-02-20 18:44 | 100 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L FUERTES LLUVIAS | B22022000335 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2022-02-20 | 9700 | keep | 0 | Feb | 2022 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-20 17:44 | 2022-02-21 13:19 | 25 | 019:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22022000342 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1175 | 2022-02-20 | 29375 | keep | 0 | Feb | 2022 | 0.020007 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-20 17:57 | 2022-02-20 17:58 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 281 | keep | 0 | Feb | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-02-20 17:57 | 2022-02-20 17:58 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 1252 | keep | 0 | Feb | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-02-20 17:57 | 2022-02-20 17:58 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 595 | keep | 0 | Feb | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-02-20 17:57 | 2022-02-20 17:58 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 51 | keep | 0 | Feb | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-02-20 17:57 | 2022-02-20 17:58 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 721 | keep | 0 | Feb | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-02-20 17:57 | 2022-02-20 17:58 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 1382 | keep | 0 | Feb | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-02-20 17:57 | 2022-02-20 17:58 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22022000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-20 | 654 | keep | 0 | Feb | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
BAYAMON | 2022-02-20 18:18 | 2022-02-21 18:15 | 20 | 023:57 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B22022000352 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1437 | 2022-02-20 | 28740 | keep | 0 | Feb | 2022 | 0.019575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-02-20 18:23 | 2022-02-20 21:28 | 20 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22022000167 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2022-02-20 | 3700 | keep | 0 | Feb | 2022 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-02-20 18:50 | 2022-02-21 08:45 | 8 | 013:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A22022000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 835 | 2022-02-20 | 6680 | keep | 0 | Feb | 2022 | 0.0045497 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-02-20 19:04 | 2022-02-20 20:01 | 20 | 000:57 | P | DESGANCHE | 1 X 40 EN C/L | R22022000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-02-20 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-20 19:32 | 2022-02-20 22:38 | 10 | 003:06 | P | NO SE REPORTO CAUSA | 1X20 EN TRANSFORMADOR | B22022000360 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2022-02-20 | 1860 | keep | 0 | Feb | 2022 | 0.0012668 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-20 19:43 | 2022-02-20 19:44 | 492 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 492 | keep | 0 | Feb | 2022 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
CAGUAS | 2022-02-20 19:43 | 2022-02-21 10:08 | 50 | 014:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22022000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 865 | 2022-02-20 | 43250 | keep | 0 | Feb | 2022 | 0.029457 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-20 20:09 | 2022-02-21 08:03 | 15 | 011:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22022000024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 714 | 2022-02-20 | 10710 | keep | 0 | Feb | 2022 | 0.0072945 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-20 20:38 | 2022-02-20 20:39 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022000045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-20 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-02-20 20:42 | 2022-02-21 11:30 | 90 | 014:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C22022000046 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 888 | 2022-02-20 | 79920 | keep | 0 | Feb | 2022 | 0.054433 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-02-20 21:00 | 2022-02-20 22:55 | 40 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA Y DISCO NO FUNDIO | R22022000028 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2022-02-20 | 4600 | keep | 0 | Feb | 2022 | 0.003133 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-20 22:34 | 2022-02-21 13:19 | 10 | 014:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22022000374 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 885 | 2022-02-20 | 8850 | keep | 0 | Feb | 2022 | 0.0060277 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-02-21 00:13 | 2022-02-21 14:05 | 145 | 013:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | REEMPLAZO DE POSTE PARTIDO POR AUTO | P22022100001 | New_Event |  |  | Include | Wildlife | 832 | 2022-02-21 | 120640 | keep | 0 | Feb | 2022 | 0.082167 | 9.8759e-05 | Sustained | FALSE | FALSE | TMED_Event | 145
BAYAMON | 2022-02-21 00:48 | 2022-02-21 00:50 | 3708 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22022100000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-21 | 7416 | keep | 0 | Feb | 2022 | 0.005051 | 0.0025255 | Momentary | FALSE | FALSE | TMED_Event | 3708
BAYAMON | 2022-02-21 00:50 | 2022-02-21 02:36 | 1224 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO A LA SALIDA DE RISER HACIA EL AEREO | S22022100000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 106 | 2022-02-21 | 129744 | keep | 0 | Feb | 2022 | 0.088368 | 0.00083366 | Sustained | FALSE | FALSE | TMED_Event | 1224
BAYAMON | 2022-02-21 01:12 | 2022-02-21 04:21 | 4089 | 003:09 | T | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO ALIMENTADOR POR OVERHEAD LINEA 38 KV CAYO EN ALIMENTADOR 30% EN SERVICIO BY-220221-01 | B22022100001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2022-02-21 | 772821 | keep | 0 | Feb | 2022 | 0.52636 | 0.002785 | Sustained | FALSE | FALSE | TMED_Event | 4089
UTUADO | 2022-02-21 01:23 | 2022-02-21 09:30 | 50 | 008:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A22022100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2022-02-21 | 24350 | keep | 0 | Feb | 2022 | 0.016585 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | TMED_Event | 2100
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | TMED_Event | 922
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | TMED_Event | 1676
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | TMED_Event | 2844
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | TMED_Event | 2775
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | TMED_Event | 1457
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | TMED_Event | 1086
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | TMED_Event | 2134
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | TMED_Event | 1464
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | TMED_Event | 1833
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | TMED_Event | 1565
GUAYAMA | 2022-02-21 01:24 | 2022-02-21 01:25 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-21 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | TMED_Event | 977
YAUCO | 2022-02-21 02:13 | 2022-02-21 02:14 | 968 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22022100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | TMED_Event | 968
BAYAMON | 2022-02-21 02:36 | 2022-02-21 02:56 | 3708 | 000:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO A LA SALIDA DE RISER HACIA EL AEREO | S22022100000 | Additional_clients | Wire Down | Include | Include | Equipment | 20 | 2022-02-21 | 74160 | keep | 0 | Feb | 2022 | 0.05051 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
ARECIBO | 2022-02-21 02:37 | 2022-02-21 09:09 | 50 | 006:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A22022100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-02-21 | 19600 | keep | 0 | Feb | 2022 | 0.013349 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-02-21 02:56 | 2022-02-21 04:06 | 2225 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO A LA SALIDA DE RISER HACIA EL AEREO | S22022100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 70 | 2022-02-21 | 155750 | keep | 0 | Feb | 2022 | 0.10608 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-02-21 03:40 | 2022-02-21 11:34 | 25 | 007:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE REMPLAZO CAJA PRIMARIA | B22022100018 | New_Event | Cutout Failure | Include | Include | Equipment | 474 | 2022-02-21 | 11850 | keep | 0 | Feb | 2022 | 0.008071 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
HUMACAO | 2022-02-21 03:44 | 2022-02-21 09:19 | 110 | 005:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C22022100007 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2022-02-21 | 36850 | keep | 0 | Feb | 2022 | 0.025098 | 7.492e-05 | Sustained | FALSE | FALSE | TMED_Event | 110
BAYAMON | 2022-02-21 04:21 | 2022-02-21 06:01 | 2862 | 001:40 | P | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD DE LA LINEA 9600 Y SE CERRARON LOS MACHETES | B22022100001 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2022-02-21 | 286200 | keep | 0 | Feb | 2022 | 0.19493 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
HUMACAO | 2022-02-21 04:32 | 2022-02-21 04:37 | 2126 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO | C22022100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-21 | 10630 | keep | 0 | Feb | 2022 | 0.00724 | 0.001448 | Momentary | FALSE | FALSE | TMED_Event | 2126
BAYAMON | 2022-02-21 05:04 | 2022-02-21 09:41 | 60 | 004:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER SE RETIRO GLOBO METALICO | B22022100029 | New_Event |  |  | Include | Wildlife | 277 | 2022-02-21 | 16620 | keep | 0 | Feb | 2022 | 0.01132 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
SAN JUAN | 2022-02-21 05:10 | 2022-02-21 05:11 | 50 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | S22022100009 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-21 | 50 | keep | 0 | Feb | 2022 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | TMED_Event | 50
HUMACAO | 2022-02-21 05:18 | 2022-02-21 05:19 | 327 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CARGAS X 2603-06 | C22022100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 327 | keep | 0 | Feb | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | TMED_Event | 327
BAYAMON | 2022-02-21 05:19 | 2022-02-21 08:49 | 3295 | 003:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22022100031 | New_Event | Wire Down | Include | Include | Equipment | 210 | 2022-02-21 | 691950 | keep | 0 | Feb | 2022 | 0.47128 | 0.0022442 | Sustained | FALSE | FALSE | TMED_Event | 3295
ARECIBO | 2022-02-21 05:30 | 2022-02-21 07:50 | 150 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 1 X 40 SE REMPLAZO CAJA QUEMADA | A22022100010 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2022-02-21 | 21000 | keep | 0 | Feb | 2022 | 0.014303 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
BAYAMON | 2022-02-21 05:57 | 2022-02-21 11:10 | 30 | 005:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S22022100037 | New_Event | Cutout Failure | Include | Include | Equipment | 313 | 2022-02-21 | 9390 | keep | 0 | Feb | 2022 | 0.0063955 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
SAN JUAN | 2022-02-21 06:01 | 2022-02-21 10:08 | 80 | 004:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22022100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-02-21 | 19760 | keep | 0 | Feb | 2022 | 0.013458 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
BAYAMON | 2022-02-21 06:34 | 2022-02-21 13:19 | 20 | 006:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA FUERTE | B22022100042 | New_Event | Bad Weather | Include | Include | Weather | 405 | 2022-02-21 | 8100 | keep | 0 | Feb | 2022 | 0.0055169 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
VEGA BAJA | 2022-02-21 06:36 | 2022-02-21 12:01 | 20 | 005:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22022100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2022-02-21 | 6500 | keep | 0 | Feb | 2022 | 0.0044271 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2022-02-21 06:58 | 2022-02-21 13:19 | 25 | 006:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22022100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2022-02-21 | 9525 | keep | 0 | Feb | 2022 | 0.0064874 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BAYAMON | 2022-02-21 07:27 | 2022-02-21 13:25 | 1 | 005:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE | B22022100055 | New_Event |  |  | Include | Wildlife | 358 | 2022-02-21 | 358 | keep | 0 | Feb | 2022 | 0.00024383 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 07:28 | 2022-02-21 10:06 | 10 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 15 EN AEREO PROVISIONAL HACIA T 51 | B22022100056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-02-21 | 1580 | keep | 0 | Feb | 2022 | 0.0010761 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-02-21 07:32 | 2022-02-21 07:34 | 723 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 SE CERRO POR SCADA | B22022100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-21 | 1446 | keep | 0 | Feb | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2022-02-21 07:32 | 2022-02-21 07:34 | 1976 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 SE CERRO POR SCADA | B22022100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-21 | 3952 | keep | 0 | Feb | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | TMED_Event | 1976
SAN JUAN | 2022-02-21 07:46 | 2022-02-21 13:17 | 12 | 005:31 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN SU-1 SE REPARO TERMINACION | S22022100065 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 331 | 2022-02-21 | 3972 | keep | 0 | Feb | 2022 | 0.0027053 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
YAUCO | 2022-02-21 07:46 | 2022-02-21 09:42 | 10 | 001:56 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR CLIENTE CON PROBLEMA INTERNO | P22022100012 | New_Event | Other Causes | Include | Include | Other | 116 | 2022-02-21 | 1160 | keep | 0 | Feb | 2022 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-02-21 07:58 | 2022-02-21 16:42 | 2 | 008:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTE DE LINEA 3 X 25 EN RISER SE REMPLAZO CAJA PRIMARIA Y AISLADOR | S22022100048 | New_Event | Cutout Failure | Include | Include | Equipment | 524 | 2022-02-21 | 1048 | keep | 0 | Feb | 2022 | 0.00071379 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-02-21 08:20 | 2022-02-21 13:19 | 10 | 004:59 | P | NO SE REPORTO CAUSA | 1X20 EN TRANSCLOSURE DE CLIENTE | S22022100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-02-21 | 2990 | keep | 0 | Feb | 2022 | 0.0020365 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2022-02-21 08:21 | 2022-02-21 11:40 | 2 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | A22022100011 | New_Event |  |  | Include | Wildlife | 199 | 2022-02-21 | 398 | keep | 0 | Feb | 2022 | 0.00027108 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
ARECIBO | 2022-02-21 08:28 | 2022-02-21 09:45 | 60 | 001:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CAMION CAUSO CRUCE DE FASES | A22022100013 | New_Event |  |  | Include | Wildlife | 77 | 2022-02-21 | 4620 | keep | 0 | Feb | 2022 | 0.0031467 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
FAJARDO | 2022-02-21 08:29 | 2022-02-21 09:17 | 15 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R22022000017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2022-02-21 | 720 | keep | 0 | Feb | 2022 | 0.00049039 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
VEGA BAJA | 2022-02-21 08:32 | 2022-02-21 10:25 | 10 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22022100077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-02-21 | 1130 | keep | 0 | Feb | 2022 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
VEGA BAJA | 2022-02-21 08:37 | 2022-02-21 09:35 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO BAJANTE SECUNDARIO | B22022000376 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-21 | 580 | keep | 0 | Feb | 2022 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
GUAYAMA | 2022-02-21 08:40 | 2022-02-21 09:08 | 5 | 000:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE CAMBIO CAJA PRIMARIA DE 100A EN TRANSFORMADOR | P22022100016 | New_Event | Cutout Failure | Include | Include | Equipment | 28 | 2022-02-21 | 140 | keep | 0 | Feb | 2022 | 9.5353e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-02-21 08:49 | 2022-02-21 12:19 | 2306 | 003:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN TRONCAL CON GOI BY-220221-02A | B22022100090 | Partial_restoration | Wire Down | Include | Include | Equipment | 210 | 2022-02-21 | 484260 | keep | 0 | Feb | 2022 | 0.32983 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2022-02-21 08:56 | 2022-02-21 12:17 | 30 | 003:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | R22022100017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2022-02-21 | 6030 | keep | 0 | Feb | 2022 | 0.004107 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
MAYAGÃœEZ | 2022-02-21 09:02 | 2022-02-21 09:05 | 1287 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M22022100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-21 | 3861 | keep | 0 | Feb | 2022 | 0.0026297 | 0.00087657 | Momentary | FALSE | FALSE | TMED_Event | 1287
BAYAMON | 2022-02-21 09:11 | 2022-02-21 12:14 | 5 | 003:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22022100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-02-21 | 915 | keep | 0 | Feb | 2022 | 0.0006232 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CAGUAS | 2022-02-21 09:15 | 2022-02-21 12:11 | 150 | 002:56 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C22022100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-02-21 | 26400 | keep | 0 | Feb | 2022 | 0.017981 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
FAJARDO | 2022-02-21 09:18 | 2022-02-21 10:15 | 20 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22022100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-02-21 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
CAGUAS | 2022-02-21 09:25 | 2022-02-21 11:18 | 50 | 001:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR AISLADORES ROTOS Y RETEZAR LINEA PRIMARIA | C22021900130 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2022-02-21 | 5650 | keep | 0 | Feb | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
UTUADO | 2022-02-21 09:30 | 2022-02-21 16:40 | 20 | 007:10 | P | LINEA DE TRANSMISION 115KV | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA 36100 | A22022100022 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 430 | 2022-02-21 | 8600 | keep | 0 | Feb | 2022 | 0.0058574 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
CAGUAS | 2022-02-21 09:35 | 2022-02-21 13:17 | 16 | 003:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR SECUNDARIA AVERIADA. | C22022100050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 222 | 2022-02-21 | 3552 | keep | 0 | Feb | 2022 | 0.0024193 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
MAYAGÃœEZ | 2022-02-21 09:45 | 2022-02-21 13:20 | 10 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22022000152 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2022-02-21 | 2150 | keep | 0 | Feb | 2022 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-02-21 09:53 | 2022-02-21 09:54 | 2435 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE INTERRUPTOR 1909-08 LLEVANDO 1907-05 | B22022100000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-02-21 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | TMED_Event | 2435
BAYAMON | 2022-02-21 09:53 | 2022-02-21 09:54 | 2956 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE INTERRUPTOR 1909-08 LLEVANDO 1907-05 | B22022100000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-02-21 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | TMED_Event | 2956
BAYAMON | 2022-02-21 09:54 | 2022-02-21 12:36 | 40 | 002:42 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO DEFECTUOSO | S22022100085 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 162 | 2022-02-21 | 6480 | keep | 0 | Feb | 2022 | 0.0044135 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
GUAYAMA | 2022-02-21 09:57 | 2022-02-21 10:32 | 1 | 000:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22022100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2022-02-21 | 35 | keep | 0 | Feb | 2022 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2022-02-21 10:25 | 2022-02-22 12:45 | 10 | 026:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS Y LINEAS SECUNDARIAS | A22022100028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1580 | 2022-02-21 | 15800 | keep | 0 | Feb | 2022 | 0.010761 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
HUMACAO | 2022-02-21 10:28 | 2022-02-21 21:42 | 20 | 011:14 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22022100059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 674 | 2022-02-21 | 13480 | keep | 0 | Feb | 2022 | 0.0091812 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
CANOVANAS | 2022-02-21 10:38 | 2022-02-21 13:19 | 20 | 002:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-02-21 | 3220 | keep | 0 | Feb | 2022 | 0.0021931 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
FAJARDO | 2022-02-21 10:40 | 2022-02-21 11:26 | 15 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA DE PEDESTAL | R22022100022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-02-21 | 690 | keep | 0 | Feb | 2022 | 0.00046996 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2022-02-21 10:43 | 2022-02-21 10:45 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S22022100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-21 | 344 | keep | 0 | Feb | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | TMED_Event | 172
CAGUAS | 2022-02-21 10:52 | 2022-02-21 13:59 | 5 | 003:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO XMR PARA RETEZAR LINEA PRIMARIA | C22022100068 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2022-02-21 | 935 | keep | 0 | Feb | 2022 | 0.00063682 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CANOVANAS | 2022-02-21 11:01 | 2022-02-21 11:02 | 1894 | 000:01 | T | DESGANCHE | RECIERRE | R22022100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-21 | 1894 | keep | 0 | Feb | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | TMED_Event | 1894
CANOVANAS | 2022-02-21 11:02 | 2022-02-21 13:19 | 25 | 002:17 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022100026 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-02-21 | 3425 | keep | 0 | Feb | 2022 | 0.0023328 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
AGUADILLA | 2022-02-21 11:07 | 2022-02-21 15:15 | 8 | 004:08 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CAJA DE TRANSFORMADOR Y SE REEMPLAZO CRUZETA Y PARRARAYOS CLIENTES SIN SERVICIO ESE DIA AL ABRIR XMER | M22021800049 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 248 | 2022-02-21 | 1984 | keep | 0 | Feb | 2022 | 0.0013513 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
VEGA BAJA | 2022-02-21 11:20 | 2022-02-21 13:12 | 10 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA EN PEDESTAL | B22022100137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2022-02-21 | 1120 | keep | 0 | Feb | 2022 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-02-21 11:51 | 2022-02-21 12:54 | 2 | 001:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA SE RETIRO IGUANA Y SE REALIZO DESGANCHE | B22022100143 | New_Event |  |  | Include | Wildlife | 63 | 2022-02-21 | 126 | keep | 0 | Feb | 2022 | 8.5818e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-02-21 11:53 | 2022-02-21 14:29 | 10 | 002:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22022100075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 156 | 2022-02-21 | 1560 | keep | 0 | Feb | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
SAN JUAN | 2022-02-21 11:57 | 2022-02-21 18:04 | 12 | 006:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA | S22022100174 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 367 | 2022-02-21 | 4404 | keep | 0 | Feb | 2022 | 0.0029995 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-02-21 12:26 | 2022-02-21 12:30 | 473 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA CERRAR PUENTE PRIMARIO SU CARGA POR 1530-7 | S22022100189 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-02-21 | 1892 | keep | 0 | Feb | 2022 | 0.0012886 | 0.00032216 | Momentary | FALSE | FALSE | TMED_Event | 473
BAYAMON | 2022-02-21 12:26 | 2022-02-21 12:30 | 145 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE 1530-7 PARA ABRIR MACHETE PARA SECCIONALIZAR PUENTE PRIMARIO SU CARGA POR 1530-7 | S22022100189 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-02-21 | 580 | keep | 0 | Feb | 2022 | 0.00039504 | 9.8759e-05 | Momentary | FALSE | FALSE | TMED_Event | 145
BAYAMON | 2022-02-21 12:26 | 2022-02-21 12:30 | 643 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA ABRIR MACHETE Y SECCIONALIZAR PUENTE PRIMARIO ABIERTO 50% EN SERVICIO LLEVA 1530-6 Y 1526-2 | S22022100111 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-02-21 | 2572 | keep | 0 | Feb | 2022 | 0.0017518 | 0.00043794 | Momentary | FALSE | FALSE | TMED_Event | 643
BAYAMON | 2022-02-21 12:30 | 2022-02-21 13:17 | 1420 | 000:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO Y SE CERRO MACHETE 100% EN SERVICIO SU CARGA POR 1530-7 | S22022100189 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 47 | 2022-02-21 | 66740 | keep | 0 | Feb | 2022 | 0.045456 | 0.00096716 | Sustained | FALSE | FALSE | TMED_Event | 1420
BAYAMON | 2022-02-21 12:30 | 2022-02-21 13:17 | 437 | 000:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO Y SE CERRO N/O 100% EN SERVICIO | S22022100189 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 47 | 2022-02-21 | 20539 | keep | 0 | Feb | 2022 | 0.013989 | 0.00029764 | Sustained | FALSE | FALSE | TMED_Event | 437
BAYAMON | 2022-02-21 12:30 | 2022-02-21 13:17 | 321 | 000:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE TRAS PATIO Y SE CERRO MACHETE 100% EN SERVICIO | S22022100189 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 47 | 2022-02-21 | 15087 | keep | 0 | Feb | 2022 | 0.010276 | 0.00021863 | Sustained | FALSE | FALSE | TMED_Event | 321
AGUADILLA | 2022-02-21 12:37 | 2022-02-21 12:38 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22022100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 470 | keep | 0 | Feb | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | TMED_Event | 470
AGUADILLA | 2022-02-21 12:37 | 2022-02-21 12:38 | 1345 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 7003-01 QUE ESTA LLEVANDO LA CARGA DEL 7003-02 | M22022100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 1345 | keep | 0 | Feb | 2022 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | TMED_Event | 1345
VEGA BAJA | 2022-02-21 12:57 | 2022-02-21 16:58 | 60 | 004:01 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA | B22022100165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-02-21 | 14460 | keep | 0 | Feb | 2022 | 0.0098486 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
FAJARDO | 2022-02-21 12:58 | 2022-02-21 14:23 | 15 | 001:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON PROBLEMA DE VOLTAJE | R22022100000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2022-02-21 | 1275 | keep | 0 | Feb | 2022 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
VEGA BAJA | 2022-02-21 13:04 | 2022-02-21 13:55 | 1 | 000:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22022100173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-02-21 | 51 | keep | 0 | Feb | 2022 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:09 | 2022-02-21 15:03 | 266 | 001:54 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1112-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 114 | 2022-02-21 | 30324 | keep | 0 | Feb | 2022 | 0.020654 | 0.00018117 | Sustained | FALSE | FALSE | TMED_Event | 266
SAN JUAN | 2022-02-21 13:09 | 2022-02-21 15:25 | 533 | 002:16 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1414-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 136 | 2022-02-21 | 72488 | keep | 0 | Feb | 2022 | 0.049371 | 0.00036302 | Sustained | FALSE | FALSE | TMED_Event | 533
SAN JUAN | 2022-02-21 13:09 | 2022-02-21 15:25 | 451 | 002:16 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1414-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 136 | 2022-02-21 | 61336 | keep | 0 | Feb | 2022 | 0.041776 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
HUMACAO | 2022-02-21 13:18 | 2022-02-21 15:02 | 10 | 001:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRA DE PEDESTAL | C22022100090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 104 | 2022-02-21 | 1040 | keep | 0 | Feb | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:33 | 1 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR EL 1001-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 134 | keep | 0 | Feb | 2022 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:33 | 47 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR EL 1001-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 6298 | keep | 0 | Feb | 2022 | 0.0042895 | 3.2011e-05 | Sustained | FALSE | FALSE | TMED_Event | 47
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:33 | 245 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA EL 1001-01 Y EL 1002-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 32830 | keep | 0 | Feb | 2022 | 0.02236 | 0.00016687 | Sustained | FALSE | FALSE | TMED_Event | 245
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 35 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 4585 | keep | 0 | Feb | 2022 | 0.0031228 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 126 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1001-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 16506 | keep | 0 | Feb | 2022 | 0.011242 | 8.5818e-05 | Sustained | FALSE | FALSE | TMED_Event | 126
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 46 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 6026 | keep | 0 | Feb | 2022 | 0.0041043 | 3.133e-05 | Sustained | FALSE | FALSE | TMED_Event | 46
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 396 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 51876 | keep | 0 | Feb | 2022 | 0.035333 | 0.00026971 | Sustained | FALSE | FALSE | TMED_Event | 396
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 119 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 15589 | keep | 0 | Feb | 2022 | 0.010618 | 8.105e-05 | Sustained | FALSE | FALSE | TMED_Event | 119
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 290 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 37990 | keep | 0 | Feb | 2022 | 0.025875 | 0.00019752 | Sustained | FALSE | FALSE | TMED_Event | 290
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 390 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 51090 | keep | 0 | Feb | 2022 | 0.034797 | 0.00026563 | Sustained | FALSE | FALSE | TMED_Event | 390
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 719 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 94189 | keep | 0 | Feb | 2022 | 0.064152 | 0.00048971 | Sustained | FALSE | FALSE | TMED_Event | 719
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 67 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 8777 | keep | 0 | Feb | 2022 | 0.005978 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 1 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 131 | keep | 0 | Feb | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 275 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 36025 | keep | 0 | Feb | 2022 | 0.024536 | 0.0001873 | Sustained | FALSE | FALSE | TMED_Event | 275
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 142 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 18602 | keep | 0 | Feb | 2022 | 0.01267 | 9.6716e-05 | Sustained | FALSE | FALSE | TMED_Event | 142
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 45 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 5895 | keep | 0 | Feb | 2022 | 0.0040151 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 93 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 13671 | keep | 0 | Feb | 2022 | 0.0093113 | 6.3342e-05 | Sustained | FALSE | FALSE | TMED_Event | 93
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 418 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 61446 | keep | 0 | Feb | 2022 | 0.041851 | 0.0002847 | Sustained | FALSE | FALSE | TMED_Event | 418
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 295 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 43365 | keep | 0 | Feb | 2022 | 0.029536 | 0.00020092 | Sustained | FALSE | FALSE | TMED_Event | 295
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 948 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 139356 | keep | 0 | Feb | 2022 | 0.094915 | 0.00064568 | Sustained | FALSE | FALSE | TMED_Event | 948
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 350 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 45850 | keep | 0 | Feb | 2022 | 0.031228 | 0.00023838 | Sustained | FALSE | FALSE | TMED_Event | 350
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 215 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 28165 | keep | 0 | Feb | 2022 | 0.019183 | 0.00014644 | Sustained | FALSE | FALSE | TMED_Event | 215
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 262 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 34322 | keep | 0 | Feb | 2022 | 0.023377 | 0.00017845 | Sustained | FALSE | FALSE | TMED_Event | 262
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 90 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 11790 | keep | 0 | Feb | 2022 | 0.0080301 | 6.1299e-05 | Sustained | FALSE | FALSE | TMED_Event | 90
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 453 | 002:27 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 66591 | keep | 0 | Feb | 2022 | 0.045355 | 0.00030854 | Sustained | FALSE | FALSE | TMED_Event | 453
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 68 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 10064 | keep | 0 | Feb | 2022 | 0.0068545 | 4.6314e-05 | Sustained | FALSE | FALSE | TMED_Event | 68
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 171 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 25308 | keep | 0 | Feb | 2022 | 0.017237 | 0.00011647 | Sustained | FALSE | FALSE | TMED_Event | 171
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 1837 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 271876 | keep | 0 | Feb | 2022 | 0.18517 | 0.0012512 | Sustained | FALSE | FALSE | TMED_Event | 1837
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 536 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 79328 | keep | 0 | Feb | 2022 | 0.05403 | 0.00036507 | Sustained | FALSE | FALSE | TMED_Event | 536
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 348 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 51504 | keep | 0 | Feb | 2022 | 0.035079 | 0.00023702 | Sustained | FALSE | FALSE | TMED_Event | 348
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:30 | 641 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA A 1133-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 83971 | keep | 0 | Feb | 2022 | 0.057192 | 0.00043658 | Sustained | FALSE | FALSE | TMED_Event | 641
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 308 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA A 1133-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 40348 | keep | 0 | Feb | 2022 | 0.027481 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:42 | 3 | 000:23 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 23 | 2022-02-21 | 69 | keep | 0 | Feb | 2022 | 4.6996e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:42 | 1 | 000:23 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 23 | 2022-02-21 | 23 | keep | 0 | Feb | 2022 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:42 | 1964 | 000:23 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 23 | 2022-02-21 | 45172 | keep | 0 | Feb | 2022 | 0.030766 | 0.0013377 | Sustained | FALSE | FALSE | TMED_Event | 1964
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:42 | 733 | 000:23 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 23 | 2022-02-21 | 16859 | keep | 0 | Feb | 2022 | 0.011483 | 0.00049924 | Sustained | FALSE | FALSE | TMED_Event | 733
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 76 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 11172 | keep | 0 | Feb | 2022 | 0.0076092 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 626 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 92022 | keep | 0 | Feb | 2022 | 0.062676 | 0.00042637 | Sustained | FALSE | FALSE | TMED_Event | 626
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 1105 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 100555 | keep | 0 | Feb | 2022 | 0.068488 | 0.00075261 | Sustained | FALSE | FALSE | TMED_Event | 1105
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:50 | 181 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 16471 | keep | 0 | Feb | 2022 | 0.011218 | 0.00012328 | Sustained | FALSE | FALSE | TMED_Event | 181
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:50 | 351 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 31941 | keep | 0 | Feb | 2022 | 0.021755 | 0.00023906 | Sustained | FALSE | FALSE | TMED_Event | 351
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:50 | 570 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 51870 | keep | 0 | Feb | 2022 | 0.035328 | 0.00038822 | Sustained | FALSE | FALSE | TMED_Event | 570
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:27 | 218 | 002:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1113-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 128 | 2022-02-21 | 27904 | keep | 0 | Feb | 2022 | 0.019005 | 0.00014848 | Sustained | FALSE | FALSE | TMED_Event | 218
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:27 | 455 | 002:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1102-2 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 128 | 2022-02-21 | 58240 | keep | 0 | Feb | 2022 | 0.039667 | 0.0003099 | Sustained | FALSE | FALSE | TMED_Event | 455
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:27 | 610 | 002:08 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 40% POR 1113-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 128 | 2022-02-21 | 78080 | keep | 0 | Feb | 2022 | 0.05318 | 0.00041547 | Sustained | FALSE | FALSE | TMED_Event | 610
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:27 | 916 | 002:08 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 60% POR 1106-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 128 | 2022-02-21 | 117248 | keep | 0 | Feb | 2022 | 0.079857 | 0.00062388 | Sustained | FALSE | FALSE | TMED_Event | 916
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:27 | 283 | 002:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 128 | 2022-02-21 | 36224 | keep | 0 | Feb | 2022 | 0.024672 | 0.00019275 | Sustained | FALSE | FALSE | TMED_Event | 283
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 513 | 002:06 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 20% POR 1118-10 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 64638 | keep | 0 | Feb | 2022 | 0.044025 | 0.0003494 | Sustained | FALSE | FALSE | TMED_Event | 513
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:03 | 2566 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 5% 1115-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 266864 | keep | 0 | Feb | 2022 | 0.18176 | 0.0017477 | Sustained | FALSE | FALSE | TMED_Event | 2566
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:03 | 17 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 1768 | keep | 0 | Feb | 2022 | 0.0012042 | 1.1579e-05 | Sustained | FALSE | FALSE | TMED_Event | 17
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:03 | 1447 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA CARGA 1419-9 Y 12 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 150488 | keep | 0 | Feb | 2022 | 0.1025 | 0.00098555 | Sustained | FALSE | FALSE | TMED_Event | 1447
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:43 | 1268 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 30432 | keep | 0 | Feb | 2022 | 0.020727 | 0.00086363 | Sustained | FALSE | FALSE | TMED_Event | 1268
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:43 | 287 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 6888 | keep | 0 | Feb | 2022 | 0.0046914 | 0.00019547 | Sustained | FALSE | FALSE | TMED_Event | 287
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:43 | 32 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 768 | keep | 0 | Feb | 2022 | 0.00052308 | 2.1795e-05 | Sustained | FALSE | FALSE | TMED_Event | 32
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:43 | 553 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 13272 | keep | 0 | Feb | 2022 | 0.0090395 | 0.00037665 | Sustained | FALSE | FALSE | TMED_Event | 553
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:43 | 1021 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 24504 | keep | 0 | Feb | 2022 | 0.01669 | 0.0006954 | Sustained | FALSE | FALSE | TMED_Event | 1021
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:56 | 3708 | 002:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 157 | 2022-02-21 | 582156 | keep | 0 | Feb | 2022 | 0.3965 | 0.0025255 | Sustained | FALSE | FALSE | TMED_Event | 3708
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:56 | 24 | 002:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 70% DEL 1115-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 157 | 2022-02-21 | 3768 | keep | 0 | Feb | 2022 | 0.0025664 | 1.6346e-05 | Sustained | FALSE | FALSE | TMED_Event | 24
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:56 | 1 | 002:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 157 | 2022-02-21 | 157 | keep | 0 | Feb | 2022 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 118 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 7788 | keep | 0 | Feb | 2022 | 0.0053044 | 8.0369e-05 | Sustained | FALSE | FALSE | TMED_Event | 118
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 134 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 8844 | keep | 0 | Feb | 2022 | 0.0060236 | 9.1267e-05 | Sustained | FALSE | FALSE | TMED_Event | 134
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:56 | 94 | 002:37 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA 70% DEL 1115-04 X 1119-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 157 | 2022-02-21 | 14758 | keep | 0 | Feb | 2022 | 0.010052 | 6.4023e-05 | Sustained | FALSE | FALSE | TMED_Event | 94
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 114 | 001:06 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 7524 | keep | 0 | Feb | 2022 | 0.0051246 | 7.7645e-05 | Sustained | FALSE | FALSE | TMED_Event | 114
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:03 | 44 | 001:44 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 5% POR 1111-1 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 4576 | keep | 0 | Feb | 2022 | 0.0031167 | 2.9968e-05 | Sustained | FALSE | FALSE | TMED_Event | 44
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 867 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 57222 | keep | 0 | Feb | 2022 | 0.038974 | 0.00059051 | Sustained | FALSE | FALSE | TMED_Event | 867
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 343 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 22638 | keep | 0 | Feb | 2022 | 0.015419 | 0.00023362 | Sustained | FALSE | FALSE | TMED_Event | 343
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 996 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 65736 | keep | 0 | Feb | 2022 | 0.044772 | 0.00067837 | Sustained | FALSE | FALSE | TMED_Event | 996
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 169 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR EL 1116-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 11154 | keep | 0 | Feb | 2022 | 0.0075969 | 0.00011511 | Sustained | FALSE | FALSE | TMED_Event | 169
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 5 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA EL 1116-04 Y EL 1117-08 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 330 | keep | 0 | Feb | 2022 | 0.00022476 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:25 | 466 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR EL 1116-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 30756 | keep | 0 | Feb | 2022 | 0.020948 | 0.00031739 | Sustained | FALSE | FALSE | TMED_Event | 466
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 316 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 46452 | keep | 0 | Feb | 2022 | 0.031638 | 0.00021523 | Sustained | FALSE | FALSE | TMED_Event | 316
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1356 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 199332 | keep | 0 | Feb | 2022 | 0.13576 | 0.00092357 | Sustained | FALSE | FALSE | TMED_Event | 1356
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 2124 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1657-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 267624 | keep | 0 | Feb | 2022 | 0.18228 | 0.0014466 | Sustained | FALSE | FALSE | TMED_Event | 2124
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:25 | 1825 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1118-9 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 229950 | keep | 0 | Feb | 2022 | 0.15662 | 0.001243 | Sustained | FALSE | FALSE | TMED_Event | 1825
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:25 | 4398 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 554148 | keep | 0 | Feb | 2022 | 0.37743 | 0.0029955 | Sustained | FALSE | FALSE | TMED_Event | 4398
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 2782 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 20% DEL 1111-1 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 350532 | keep | 0 | Feb | 2022 | 0.23875 | 0.0018948 | Sustained | FALSE | FALSE | TMED_Event | 2782
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 863 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 126861 | keep | 0 | Feb | 2022 | 0.086404 | 0.00058779 | Sustained | FALSE | FALSE | TMED_Event | 863
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 2720 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 95% DEL 1115-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 399840 | keep | 0 | Feb | 2022 | 0.27233 | 0.0018526 | Sustained | FALSE | FALSE | TMED_Event | 2720
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:46 | 1 | 002:27 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 147 | 2022-02-21 | 147 | keep | 0 | Feb | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 620 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 81220 | keep | 0 | Feb | 2022 | 0.055319 | 0.00042228 | Sustained | FALSE | FALSE | TMED_Event | 620
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 451 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 59081 | keep | 0 | Feb | 2022 | 0.04024 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:30 | 333 | 002:11 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 131 | 2022-02-21 | 43623 | keep | 0 | Feb | 2022 | 0.029711 | 0.0002268 | Sustained | FALSE | FALSE | TMED_Event | 333
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 137 | 000:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 3836 | keep | 0 | Feb | 2022 | 0.0026127 | 9.331e-05 | Sustained | FALSE | FALSE | TMED_Event | 137
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 457 | 000:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 12796 | keep | 0 | Feb | 2022 | 0.0087153 | 0.00031126 | Sustained | FALSE | FALSE | TMED_Event | 457
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 1225 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA DEL 1203-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 94325 | keep | 0 | Feb | 2022 | 0.064244 | 0.00083434 | Sustained | FALSE | FALSE | TMED_Event | 1225
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 1452 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 111804 | keep | 0 | Feb | 2022 | 0.076149 | 0.00098895 | Sustained | FALSE | FALSE | TMED_Event | 1452
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 616 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1203-01 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 47432 | keep | 0 | Feb | 2022 | 0.032306 | 0.00041955 | Sustained | FALSE | FALSE | TMED_Event | 616
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 858 | 003:37 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 20% POR 1303-2 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 186186 | keep | 0 | Feb | 2022 | 0.12681 | 0.00058438 | Sustained | FALSE | FALSE | TMED_Event | 858
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:48 | 3433 | 000:29 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 80% POR PORTATIL #22 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 99557 | keep | 0 | Feb | 2022 | 0.067808 | 0.0023382 | Sustained | FALSE | FALSE | TMED_Event | 3433
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:48 | 552 | 000:29 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 40% POR PORTATIL #22 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 16008 | keep | 0 | Feb | 2022 | 0.010903 | 0.00037596 | Sustained | FALSE | FALSE | TMED_Event | 552
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 828 | 001:06 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 60% POR EL 1206-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 54648 | keep | 0 | Feb | 2022 | 0.037221 | 0.00056395 | Sustained | FALSE | FALSE | TMED_Event | 828
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 600 | 001:35 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 30% POR 1336-8 & 40% POR EL 1206-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 57000 | keep | 0 | Feb | 2022 | 0.038822 | 0.00040866 | Sustained | FALSE | FALSE | TMED_Event | 600
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 1977 | 001:06 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 30% POR 1336-8 & 40% POR EL 1206-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 130482 | keep | 0 | Feb | 2022 | 0.088871 | 0.0013465 | Sustained | FALSE | FALSE | TMED_Event | 1977
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 500 | 001:35 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR EL 1336-08 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 47500 | keep | 0 | Feb | 2022 | 0.032352 | 0.00034055 | Sustained | FALSE | FALSE | TMED_Event | 500
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 641 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 42306 | keep | 0 | Feb | 2022 | 0.028814 | 0.00043658 | Sustained | FALSE | FALSE | TMED_Event | 641
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 733 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 48378 | keep | 0 | Feb | 2022 | 0.03295 | 0.00049924 | Sustained | FALSE | FALSE | TMED_Event | 733
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 4133 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 272778 | keep | 0 | Feb | 2022 | 0.18579 | 0.002815 | Sustained | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 1799 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 40% DEL 1204-04 Y 60% 1204-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 118734 | keep | 0 | Feb | 2022 | 0.080869 | 0.0012253 | Sustained | FALSE | FALSE | TMED_Event | 1799
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 1061 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 100795 | keep | 0 | Feb | 2022 | 0.068651 | 0.00072264 | Sustained | FALSE | FALSE | TMED_Event | 1061
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 302 | 001:41 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 40% POR 1335-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 30502 | keep | 0 | Feb | 2022 | 0.020775 | 0.00020569 | Sustained | FALSE | FALSE | TMED_Event | 302
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 440 | 001:35 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 60% 1437-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 41800 | keep | 0 | Feb | 2022 | 0.02847 | 0.00029968 | Sustained | FALSE | FALSE | TMED_Event | 440
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 998 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 94810 | keep | 0 | Feb | 2022 | 0.064575 | 0.00067973 | Sustained | FALSE | FALSE | TMED_Event | 998
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 1397 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 132715 | keep | 0 | Feb | 2022 | 0.090392 | 0.00095149 | Sustained | FALSE | FALSE | TMED_Event | 1397
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 1681 | 003:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 364777 | keep | 0 | Feb | 2022 | 0.24845 | 0.0011449 | Sustained | FALSE | FALSE | TMED_Event | 1681
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 2435 | 003:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 20% 1204-2 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 528395 | keep | 0 | Feb | 2022 | 0.35989 | 0.0016585 | Sustained | FALSE | FALSE | TMED_Event | 2435
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 726 | 003:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1346-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 157542 | keep | 0 | Feb | 2022 | 0.1073 | 0.00049448 | Sustained | FALSE | FALSE | TMED_Event | 726
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 225 | 003:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1303-1 Y 1346-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 48825 | keep | 0 | Feb | 2022 | 0.033254 | 0.00015325 | Sustained | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 870 | 003:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1303-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 188790 | keep | 0 | Feb | 2022 | 0.12858 | 0.00059255 | Sustained | FALSE | FALSE | TMED_Event | 870
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 627 | 000:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 17556 | keep | 0 | Feb | 2022 | 0.011957 | 0.00042705 | Sustained | FALSE | FALSE | TMED_Event | 627
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 293 | 000:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA DEL 1421-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 8204 | keep | 0 | Feb | 2022 | 0.0055877 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 761 | 000:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA DEL 1421-01 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 21308 | keep | 0 | Feb | 2022 | 0.014513 | 0.00051831 | Sustained | FALSE | FALSE | TMED_Event | 761
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 451 | 000:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 12628 | keep | 0 | Feb | 2022 | 0.0086009 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 7 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 168 | keep | 0 | Feb | 2022 | 0.00011442 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 277 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 6648 | keep | 0 | Feb | 2022 | 0.0045279 | 0.00018866 | Sustained | FALSE | FALSE | TMED_Event | 277
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:35 | 15 | 001:16 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 76 | 2022-02-21 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 5 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 120 | keep | 0 | Feb | 2022 | 8.1731e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 100 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 10100 | keep | 0 | Feb | 2022 | 0.0068791 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 644 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 65044 | keep | 0 | Feb | 2022 | 0.044301 | 0.00043863 | Sustained | FALSE | FALSE | TMED_Event | 644
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 525 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 53025 | keep | 0 | Feb | 2022 | 0.036115 | 0.00035758 | Sustained | FALSE | FALSE | TMED_Event | 525
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 45 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 4545 | keep | 0 | Feb | 2022 | 0.0030956 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 418 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 42218 | keep | 0 | Feb | 2022 | 0.028754 | 0.0002847 | Sustained | FALSE | FALSE | TMED_Event | 418
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 718 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 90% 1901-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 21540 | keep | 0 | Feb | 2022 | 0.014671 | 0.00048903 | Sustained | FALSE | FALSE | TMED_Event | 718
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 533 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 15990 | keep | 0 | Feb | 2022 | 0.010891 | 0.00036302 | Sustained | FALSE | FALSE | TMED_Event | 533
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 844 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 25320 | keep | 0 | Feb | 2022 | 0.017245 | 0.00057484 | Sustained | FALSE | FALSE | TMED_Event | 844
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 1384 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 139784 | keep | 0 | Feb | 2022 | 0.095206 | 0.00094264 | Sustained | FALSE | FALSE | TMED_Event | 1384
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 869 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 87769 | keep | 0 | Feb | 2022 | 0.059779 | 0.00059187 | Sustained | FALSE | FALSE | TMED_Event | 869
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 1208 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 122008 | keep | 0 | Feb | 2022 | 0.083099 | 0.00082276 | Sustained | FALSE | FALSE | TMED_Event | 1208
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 375 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 37875 | keep | 0 | Feb | 2022 | 0.025796 | 0.00025541 | Sustained | FALSE | FALSE | TMED_Event | 375
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 608 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 61408 | keep | 0 | Feb | 2022 | 0.041825 | 0.00041411 | Sustained | FALSE | FALSE | TMED_Event | 608
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 602 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 60802 | keep | 0 | Feb | 2022 | 0.041412 | 0.00041002 | Sustained | FALSE | FALSE | TMED_Event | 602
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:00 | 314 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 31714 | keep | 0 | Feb | 2022 | 0.0216 | 0.00021386 | Sustained | FALSE | FALSE | TMED_Event | 314
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 6481 | 001:35 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 30% POR 1619-2 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 615695 | keep | 0 | Feb | 2022 | 0.41935 | 0.0044142 | Sustained | FALSE | FALSE | TMED_Event | 6481
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 6244 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 593180 | keep | 0 | Feb | 2022 | 0.40401 | 0.0042528 | Sustained | FALSE | FALSE | TMED_Event | 6244
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 5290 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 30% 1204-4 LLEVA 1336-9 Y PARTE DEL 1204-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 502550 | keep | 0 | Feb | 2022 | 0.34228 | 0.003603 | Sustained | FALSE | FALSE | TMED_Event | 5290
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 207 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1336-8 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 19665 | keep | 0 | Feb | 2022 | 0.013394 | 0.00014099 | Sustained | FALSE | FALSE | TMED_Event | 207
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 403 | 001:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 85% POR 1620-01 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 38285 | keep | 0 | Feb | 2022 | 0.026076 | 0.00027448 | Sustained | FALSE | FALSE | TMED_Event | 403
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 255 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 7650 | keep | 0 | Feb | 2022 | 0.0052104 | 0.00017368 | Sustained | FALSE | FALSE | TMED_Event | 255
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 928 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 27840 | keep | 0 | Feb | 2022 | 0.018962 | 0.00063206 | Sustained | FALSE | FALSE | TMED_Event | 928
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 200 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 6000 | keep | 0 | Feb | 2022 | 0.0040866 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 185 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 5550 | keep | 0 | Feb | 2022 | 0.0037801 | 0.000126 | Sustained | FALSE | FALSE | TMED_Event | 185
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 73 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 2190 | keep | 0 | Feb | 2022 | 0.0014916 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:50 | 356 | 000:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 31 | 2022-02-21 | 11036 | keep | 0 | Feb | 2022 | 0.0075166 | 0.00024247 | Sustained | FALSE | FALSE | TMED_Event | 356
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:50 | 790 | 000:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 31 | 2022-02-21 | 24490 | keep | 0 | Feb | 2022 | 0.01668 | 0.00053807 | Sustained | FALSE | FALSE | TMED_Event | 790
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:50 | 29 | 000:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 31 | 2022-02-21 | 899 | keep | 0 | Feb | 2022 | 0.0006123 | 1.9752e-05 | Sustained | FALSE | FALSE | TMED_Event | 29
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:50 | 390 | 000:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 25% 1203-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 31 | 2022-02-21 | 12090 | keep | 0 | Feb | 2022 | 0.0082344 | 0.00026563 | Sustained | FALSE | FALSE | TMED_Event | 390
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 291 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1345-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 19206 | keep | 0 | Feb | 2022 | 0.013081 | 0.0001982 | Sustained | FALSE | FALSE | TMED_Event | 291
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:24 | 1825 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 118625 | keep | 0 | Feb | 2022 | 0.080795 | 0.001243 | Sustained | FALSE | FALSE | TMED_Event | 1825
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:24 | 47 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 3055 | keep | 0 | Feb | 2022 | 0.0020807 | 3.2011e-05 | Sustained | FALSE | FALSE | TMED_Event | 47
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:24 | 315 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 20475 | keep | 0 | Feb | 2022 | 0.013945 | 0.00021455 | Sustained | FALSE | FALSE | TMED_Event | 315
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:24 | 2 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 130 | keep | 0 | Feb | 2022 | 8.8542e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:24 | 2391 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 155415 | keep | 0 | Feb | 2022 | 0.10585 | 0.0016285 | Sustained | FALSE | FALSE | TMED_Event | 2391
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 660 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 43560 | keep | 0 | Feb | 2022 | 0.029669 | 0.00044952 | Sustained | FALSE | FALSE | TMED_Event | 660
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 435 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 28710 | keep | 0 | Feb | 2022 | 0.019554 | 0.00029628 | Sustained | FALSE | FALSE | TMED_Event | 435
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 259 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 17094 | keep | 0 | Feb | 2022 | 0.011643 | 0.0001764 | Sustained | FALSE | FALSE | TMED_Event | 259
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 686 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 45276 | keep | 0 | Feb | 2022 | 0.030837 | 0.00046723 | Sustained | FALSE | FALSE | TMED_Event | 686
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 953 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 62898 | keep | 0 | Feb | 2022 | 0.04284 | 0.00064908 | Sustained | FALSE | FALSE | TMED_Event | 953
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:08 | 1 | 000:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 49 | 2022-02-21 | 49 | keep | 0 | Feb | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:08 | 1844 | 000:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 49 | 2022-02-21 | 90356 | keep | 0 | Feb | 2022 | 0.061541 | 0.0012559 | Sustained | FALSE | FALSE | TMED_Event | 1844
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:08 | 2422 | 000:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 49 | 2022-02-21 | 118678 | keep | 0 | Feb | 2022 | 0.080831 | 0.0016496 | Sustained | FALSE | FALSE | TMED_Event | 2422
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 3932 | 003:37 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1303-3 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 853244 | keep | 0 | Feb | 2022 | 0.58114 | 0.0026781 | Sustained | FALSE | FALSE | TMED_Event | 3932
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:59 | 922 | 001:40 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1401-08 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 100 | 2022-02-21 | 92200 | keep | 0 | Feb | 2022 | 0.062797 | 0.00062797 | Sustained | FALSE | FALSE | TMED_Event | 922
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 16:56 | 1598 | 003:37 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1303-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 217 | 2022-02-21 | 346766 | keep | 0 | Feb | 2022 | 0.23618 | 0.0010884 | Sustained | FALSE | FALSE | TMED_Event | 1598
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 250 | 000:30 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA 20% DE LA CARGA POR PORTATIL | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 7500 | keep | 0 | Feb | 2022 | 0.0051082 | 0.00017027 | Sustained | FALSE | FALSE | TMED_Event | 250
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 1000 | 002:35 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1424-8 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 155000 | keep | 0 | Feb | 2022 | 0.10557 | 0.0006811 | Sustained | FALSE | FALSE | TMED_Event | 1000
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 278 | 002:35 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1424-8 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 43090 | keep | 0 | Feb | 2022 | 0.029348 | 0.00018934 | Sustained | FALSE | FALSE | TMED_Event | 278
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 1290 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 38700 | keep | 0 | Feb | 2022 | 0.026358 | 0.00087861 | Sustained | FALSE | FALSE | TMED_Event | 1290
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 7 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 168 | keep | 0 | Feb | 2022 | 0.00011442 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 17 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 408 | keep | 0 | Feb | 2022 | 0.00027789 | 1.1579e-05 | Sustained | FALSE | FALSE | TMED_Event | 17
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 2 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 48 | keep | 0 | Feb | 2022 | 3.2693e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 8 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 192 | keep | 0 | Feb | 2022 | 0.00013077 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 6 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 144 | keep | 0 | Feb | 2022 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 1 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 24 | keep | 0 | Feb | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:43 | 312 | 000:24 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 24 | 2022-02-21 | 7488 | keep | 0 | Feb | 2022 | 0.0051 | 0.0002125 | Sustained | FALSE | FALSE | TMED_Event | 312
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:27 | 837 | 001:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 68 | 2022-02-21 | 56916 | keep | 0 | Feb | 2022 | 0.038765 | 0.00057008 | Sustained | FALSE | FALSE | TMED_Event | 837
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:27 | 908 | 001:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 68 | 2022-02-21 | 61744 | keep | 0 | Feb | 2022 | 0.042054 | 0.00061843 | Sustained | FALSE | FALSE | TMED_Event | 908
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:27 | 135 | 001:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 68 | 2022-02-21 | 9180 | keep | 0 | Feb | 2022 | 0.0062525 | 9.1948e-05 | Sustained | FALSE | FALSE | TMED_Event | 135
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:27 | 1 | 001:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 68 | 2022-02-21 | 68 | keep | 0 | Feb | 2022 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:27 | 1295 | 001:08 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 68 | 2022-02-21 | 88060 | keep | 0 | Feb | 2022 | 0.059977 | 0.00088202 | Sustained | FALSE | FALSE | TMED_Event | 1295
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 143 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 11011 | keep | 0 | Feb | 2022 | 0.0074995 | 9.7397e-05 | Sustained | FALSE | FALSE | TMED_Event | 143
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 1357 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 104489 | keep | 0 | Feb | 2022 | 0.071167 | 0.00092425 | Sustained | FALSE | FALSE | TMED_Event | 1357
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 328 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 25256 | keep | 0 | Feb | 2022 | 0.017202 | 0.0002234 | Sustained | FALSE | FALSE | TMED_Event | 328
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 485 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1420-5 | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 37345 | keep | 0 | Feb | 2022 | 0.025436 | 0.00033033 | Sustained | FALSE | FALSE | TMED_Event | 485
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 23 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 2898 | keep | 0 | Feb | 2022 | 0.0019738 | 1.5665e-05 | Sustained | FALSE | FALSE | TMED_Event | 23
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 530 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 66780 | keep | 0 | Feb | 2022 | 0.045484 | 0.00036098 | Sustained | FALSE | FALSE | TMED_Event | 530
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 37 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 4662 | keep | 0 | Feb | 2022 | 0.0031753 | 2.5201e-05 | Sustained | FALSE | FALSE | TMED_Event | 37
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 929 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 117054 | keep | 0 | Feb | 2022 | 0.079725 | 0.00063274 | Sustained | FALSE | FALSE | TMED_Event | 929
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 21 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 2646 | keep | 0 | Feb | 2022 | 0.0018022 | 1.4303e-05 | Sustained | FALSE | FALSE | TMED_Event | 21
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:16 | 262 | 001:57 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1416-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 117 | 2022-02-21 | 30654 | keep | 0 | Feb | 2022 | 0.020878 | 0.00017845 | Sustained | FALSE | FALSE | TMED_Event | 262
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:16 | 296 | 001:57 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1416-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 117 | 2022-02-21 | 34632 | keep | 0 | Feb | 2022 | 0.023588 | 0.0002016 | Sustained | FALSE | FALSE | TMED_Event | 296
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:16 | 79 | 001:57 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1416-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 117 | 2022-02-21 | 9243 | keep | 0 | Feb | 2022 | 0.0062954 | 5.3807e-05 | Sustained | FALSE | FALSE | TMED_Event | 79
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:16 | 1129 | 001:57 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1416-1 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 117 | 2022-02-21 | 132093 | keep | 0 | Feb | 2022 | 0.089968 | 0.00076896 | Sustained | FALSE | FALSE | TMED_Event | 1129
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:16 | 1573 | 001:57 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 117 | 2022-02-21 | 184041 | keep | 0 | Feb | 2022 | 0.12535 | 0.0010714 | Sustained | FALSE | FALSE | TMED_Event | 1573
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 849 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 125652 | keep | 0 | Feb | 2022 | 0.085581 | 0.00057825 | Sustained | FALSE | FALSE | TMED_Event | 849
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 893 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 20% 1422-2 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 132164 | keep | 0 | Feb | 2022 | 0.090016 | 0.00060822 | Sustained | FALSE | FALSE | TMED_Event | 893
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 602 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 89096 | keep | 0 | Feb | 2022 | 0.060683 | 0.00041002 | Sustained | FALSE | FALSE | TMED_Event | 602
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 43 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 6364 | keep | 0 | Feb | 2022 | 0.0043345 | 2.9287e-05 | Sustained | FALSE | FALSE | TMED_Event | 43
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 1389 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 205572 | keep | 0 | Feb | 2022 | 0.14001 | 0.00094604 | Sustained | FALSE | FALSE | TMED_Event | 1389
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 1 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 66 | keep | 0 | Feb | 2022 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 1 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 66 | keep | 0 | Feb | 2022 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:03 | 73 | 001:44 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1112-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 7592 | keep | 0 | Feb | 2022 | 0.0051709 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 448 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 90% 1420-3 | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 29568 | keep | 0 | Feb | 2022 | 0.020139 | 0.00030513 | Sustained | FALSE | FALSE | TMED_Event | 448
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 1191 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 78606 | keep | 0 | Feb | 2022 | 0.053538 | 0.00081118 | Sustained | FALSE | FALSE | TMED_Event | 1191
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 60 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 3960 | keep | 0 | Feb | 2022 | 0.0026971 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 500 | 001:06 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 90% POR 1419-13 | S2202210000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 33000 | keep | 0 | Feb | 2022 | 0.022476 | 0.00034055 | Sustained | FALSE | FALSE | TMED_Event | 500
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 546 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 36036 | keep | 0 | Feb | 2022 | 0.024544 | 0.00037188 | Sustained | FALSE | FALSE | TMED_Event | 546
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:25 | 449 | 001:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 66 | 2022-02-21 | 29634 | keep | 0 | Feb | 2022 | 0.020184 | 0.00030581 | Sustained | FALSE | FALSE | TMED_Event | 449
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:36 | 4 | 001:17 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 308 | keep | 0 | Feb | 2022 | 0.00020978 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 1498 | 000:28 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1310-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 41944 | keep | 0 | Feb | 2022 | 0.028568 | 0.0010203 | Sustained | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:48 | 164 | 000:29 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1531-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 4756 | keep | 0 | Feb | 2022 | 0.0032393 | 0.0001117 | Sustained | FALSE | FALSE | TMED_Event | 164
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:47 | 766 | 000:28 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1310-03 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 28 | 2022-02-21 | 21448 | keep | 0 | Feb | 2022 | 0.014608 | 0.00052172 | Sustained | FALSE | FALSE | TMED_Event | 766
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 605 | 002:28 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 90% POR 1423-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 89540 | keep | 0 | Feb | 2022 | 0.060985 | 0.00041206 | Sustained | FALSE | FALSE | TMED_Event | 605
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 673 | 000:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1423-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 20190 | keep | 0 | Feb | 2022 | 0.013751 | 0.00045838 | Sustained | FALSE | FALSE | TMED_Event | 673
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 372 | 002:28 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1423-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 55056 | keep | 0 | Feb | 2022 | 0.037498 | 0.00025337 | Sustained | FALSE | FALSE | TMED_Event | 372
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 732 | 002:28 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1423-4 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 108336 | keep | 0 | Feb | 2022 | 0.073787 | 0.00049856 | Sustained | FALSE | FALSE | TMED_Event | 732
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:49 | 637 | 000:30 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1328-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 19110 | keep | 0 | Feb | 2022 | 0.013016 | 0.00043386 | Sustained | FALSE | FALSE | TMED_Event | 637
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 721 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 106708 | keep | 0 | Feb | 2022 | 0.072678 | 0.00049107 | Sustained | FALSE | FALSE | TMED_Event | 721
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 325 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 48100 | keep | 0 | Feb | 2022 | 0.032761 | 0.00022136 | Sustained | FALSE | FALSE | TMED_Event | 325
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 600 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 88800 | keep | 0 | Feb | 2022 | 0.060481 | 0.00040866 | Sustained | FALSE | FALSE | TMED_Event | 600
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 267 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1422-4 Y 1422-3 Y 90% DEL 1422-2 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 39516 | keep | 0 | Feb | 2022 | 0.026914 | 0.00018185 | Sustained | FALSE | FALSE | TMED_Event | 267
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:47 | 621 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 91908 | keep | 0 | Feb | 2022 | 0.062598 | 0.00042296 | Sustained | FALSE | FALSE | TMED_Event | 621
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 2203 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 341465 | keep | 0 | Feb | 2022 | 0.23257 | 0.0015005 | Sustained | FALSE | FALSE | TMED_Event | 2203
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 246 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 38130 | keep | 0 | Feb | 2022 | 0.02597 | 0.00016755 | Sustained | FALSE | FALSE | TMED_Event | 246
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 9 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1348-7 Y80% 1348-6 Y PARTE 1336-8 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 1395 | keep | 0 | Feb | 2022 | 0.00095013 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 601 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 93155 | keep | 0 | Feb | 2022 | 0.063447 | 0.00040934 | Sustained | FALSE | FALSE | TMED_Event | 601
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 640 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1437-1 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 99200 | keep | 0 | Feb | 2022 | 0.067565 | 0.0004359 | Sustained | FALSE | FALSE | TMED_Event | 640
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 1699 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 263345 | keep | 0 | Feb | 2022 | 0.17936 | 0.0011572 | Sustained | FALSE | FALSE | TMED_Event | 1699
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:54 | 445 | 001:35 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 60% DE LA CARGA DEL 1301-02 TRANSFERIDA AL 1437-04 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 95 | 2022-02-21 | 42275 | keep | 0 | Feb | 2022 | 0.028793 | 0.00030309 | Sustained | FALSE | FALSE | TMED_Event | 445
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:54 | 1066 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 165230 | keep | 0 | Feb | 2022 | 0.11254 | 0.00072605 | Sustained | FALSE | FALSE | TMED_Event | 1066
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:55 | 34 | 002:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 156 | 2022-02-21 | 5304 | keep | 0 | Feb | 2022 | 0.0036125 | 2.3157e-05 | Sustained | FALSE | FALSE | TMED_Event | 34
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:55 | 19 | 002:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 1910-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 156 | 2022-02-21 | 2964 | keep | 0 | Feb | 2022 | 0.0020188 | 1.2941e-05 | Sustained | FALSE | FALSE | TMED_Event | 19
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 534 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1519-5 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 82770 | keep | 0 | Feb | 2022 | 0.056374 | 0.0003637 | Sustained | FALSE | FALSE | TMED_Event | 534
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 790 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 122450 | keep | 0 | Feb | 2022 | 0.0834 | 0.00053807 | Sustained | FALSE | FALSE | TMED_Event | 790
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 193 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 80% POR 1910-01 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 29915 | keep | 0 | Feb | 2022 | 0.020375 | 0.00013145 | Sustained | FALSE | FALSE | TMED_Event | 193
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 433 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 67115 | keep | 0 | Feb | 2022 | 0.045712 | 0.00029491 | Sustained | FALSE | FALSE | TMED_Event | 433
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 558 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 86490 | keep | 0 | Feb | 2022 | 0.058908 | 0.00038005 | Sustained | FALSE | FALSE | TMED_Event | 558
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 514 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 79670 | keep | 0 | Feb | 2022 | 0.054263 | 0.00035008 | Sustained | FALSE | FALSE | TMED_Event | 514
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 681 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 105555 | keep | 0 | Feb | 2022 | 0.071893 | 0.00046383 | Sustained | FALSE | FALSE | TMED_Event | 681
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 752 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 116560 | keep | 0 | Feb | 2022 | 0.079388 | 0.00051218 | Sustained | FALSE | FALSE | TMED_Event | 752
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 68 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 10540 | keep | 0 | Feb | 2022 | 0.0071787 | 4.6314e-05 | Sustained | FALSE | FALSE | TMED_Event | 68
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 271 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 40379 | keep | 0 | Feb | 2022 | 0.027502 | 0.00018458 | Sustained | FALSE | FALSE | TMED_Event | 271
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 74 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 11026 | keep | 0 | Feb | 2022 | 0.0075098 | 5.0401e-05 | Sustained | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:36 | 771 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 59367 | keep | 0 | Feb | 2022 | 0.040435 | 0.00052512 | Sustained | FALSE | FALSE | TMED_Event | 771
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:36 | 946 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA AL 1525-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 72842 | keep | 0 | Feb | 2022 | 0.049612 | 0.00064432 | Sustained | FALSE | FALSE | TMED_Event | 946
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:36 | 590 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 45430 | keep | 0 | Feb | 2022 | 0.030942 | 0.00040185 | Sustained | FALSE | FALSE | TMED_Event | 590
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:36 | 1860 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 143220 | keep | 0 | Feb | 2022 | 0.097546 | 0.0012668 | Sustained | FALSE | FALSE | TMED_Event | 1860
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:36 | 937 | 001:17 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA 1525-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 77 | 2022-02-21 | 72149 | keep | 0 | Feb | 2022 | 0.04914 | 0.00063819 | Sustained | FALSE | FALSE | TMED_Event | 937
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 727 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 112685 | keep | 0 | Feb | 2022 | 0.076749 | 0.00049516 | Sustained | FALSE | FALSE | TMED_Event | 727
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 1420 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 220100 | keep | 0 | Feb | 2022 | 0.14991 | 0.00096716 | Sustained | FALSE | FALSE | TMED_Event | 1420
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 290 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 44950 | keep | 0 | Feb | 2022 | 0.030615 | 0.00019752 | Sustained | FALSE | FALSE | TMED_Event | 290
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 610 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 94550 | keep | 0 | Feb | 2022 | 0.064398 | 0.00041547 | Sustained | FALSE | FALSE | TMED_Event | 610
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:54 | 842 | 002:35 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 155 | 2022-02-21 | 130510 | keep | 0 | Feb | 2022 | 0.08889 | 0.00057348 | Sustained | FALSE | FALSE | TMED_Event | 842
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 1370 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 124670 | keep | 0 | Feb | 2022 | 0.084912 | 0.0009331 | Sustained | FALSE | FALSE | TMED_Event | 1370
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 1984 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA DE 1911-07 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 180544 | keep | 0 | Feb | 2022 | 0.12297 | 0.0013513 | Sustained | FALSE | FALSE | TMED_Event | 1984
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 199 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 18109 | keep | 0 | Feb | 2022 | 0.012334 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 1802 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 163982 | keep | 0 | Feb | 2022 | 0.11169 | 0.0012273 | Sustained | FALSE | FALSE | TMED_Event | 1802
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:14 | 437 | 001:55 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA CARGA 1526-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 115 | 2022-02-21 | 50255 | keep | 0 | Feb | 2022 | 0.034228 | 0.00029764 | Sustained | FALSE | FALSE | TMED_Event | 437
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:14 | 643 | 001:55 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 115 | 2022-02-21 | 73945 | keep | 0 | Feb | 2022 | 0.050364 | 0.00043794 | Sustained | FALSE | FALSE | TMED_Event | 643
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:14 | 1085 | 001:55 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 115 | 2022-02-21 | 124775 | keep | 0 | Feb | 2022 | 0.084984 | 0.00073899 | Sustained | FALSE | FALSE | TMED_Event | 1085
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:14 | 1310 | 001:55 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 115 | 2022-02-21 | 150650 | keep | 0 | Feb | 2022 | 0.10261 | 0.00089224 | Sustained | FALSE | FALSE | TMED_Event | 1310
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:14 | 411 | 001:55 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 115 | 2022-02-21 | 47265 | keep | 0 | Feb | 2022 | 0.032192 | 0.00027993 | Sustained | FALSE | FALSE | TMED_Event | 411
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:48 | 427 | 000:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 12383 | keep | 0 | Feb | 2022 | 0.008434 | 0.00029083 | Sustained | FALSE | FALSE | TMED_Event | 427
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:48 | 716 | 000:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA DEL 1421-02 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 20764 | keep | 0 | Feb | 2022 | 0.014142 | 0.00048766 | Sustained | FALSE | FALSE | TMED_Event | 716
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:48 | 867 | 000:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 25143 | keep | 0 | Feb | 2022 | 0.017125 | 0.00059051 | Sustained | FALSE | FALSE | TMED_Event | 867
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:48 | 353 | 000:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 29 | 2022-02-21 | 10237 | keep | 0 | Feb | 2022 | 0.0069724 | 0.00024043 | Sustained | FALSE | FALSE | TMED_Event | 353
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:28 | 763 | 002:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 129 | 2022-02-21 | 98427 | keep | 0 | Feb | 2022 | 0.067038 | 0.00051968 | Sustained | FALSE | FALSE | TMED_Event | 763
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:28 | 27 | 002:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 129 | 2022-02-21 | 3483 | keep | 0 | Feb | 2022 | 0.0023723 | 1.839e-05 | Sustained | FALSE | FALSE | TMED_Event | 27
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:28 | 1259 | 002:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 129 | 2022-02-21 | 162411 | keep | 0 | Feb | 2022 | 0.11062 | 0.0008575 | Sustained | FALSE | FALSE | TMED_Event | 1259
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:28 | 1051 | 002:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 129 | 2022-02-21 | 135579 | keep | 0 | Feb | 2022 | 0.092342 | 0.00071583 | Sustained | FALSE | FALSE | TMED_Event | 1051
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:28 | 188 | 002:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 129 | 2022-02-21 | 24252 | keep | 0 | Feb | 2022 | 0.016518 | 0.00012805 | Sustained | FALSE | FALSE | TMED_Event | 188
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:37 | 1862 | 002:18 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 138 | 2022-02-21 | 256956 | keep | 0 | Feb | 2022 | 0.17501 | 0.0012682 | Sustained | FALSE | FALSE | TMED_Event | 1862
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:37 | 1613 | 002:18 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 138 | 2022-02-21 | 222594 | keep | 0 | Feb | 2022 | 0.15161 | 0.0010986 | Sustained | FALSE | FALSE | TMED_Event | 1613
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:37 | 1448 | 002:18 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 138 | 2022-02-21 | 199824 | keep | 0 | Feb | 2022 | 0.1361 | 0.00098623 | Sustained | FALSE | FALSE | TMED_Event | 1448
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 9 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 1116 | keep | 0 | Feb | 2022 | 0.0007601 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 6 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 744 | keep | 0 | Feb | 2022 | 0.00050674 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 12 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 1488 | keep | 0 | Feb | 2022 | 0.0010135 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 3 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 372 | keep | 0 | Feb | 2022 | 0.00025337 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 7 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 868 | keep | 0 | Feb | 2022 | 0.00059119 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 4 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 496 | keep | 0 | Feb | 2022 | 0.00033782 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 4 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 496 | keep | 0 | Feb | 2022 | 0.00033782 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 331 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 41044 | keep | 0 | Feb | 2022 | 0.027955 | 0.00022544 | Sustained | FALSE | FALSE | TMED_Event | 331
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 1132 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 140368 | keep | 0 | Feb | 2022 | 0.095604 | 0.000771 | Sustained | FALSE | FALSE | TMED_Event | 1132
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 234 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 29016 | keep | 0 | Feb | 2022 | 0.019763 | 0.00015938 | Sustained | FALSE | FALSE | TMED_Event | 234
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 2179 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 270196 | keep | 0 | Feb | 2022 | 0.18403 | 0.0014841 | Sustained | FALSE | FALSE | TMED_Event | 2179
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:23 | 5062 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 627688 | keep | 0 | Feb | 2022 | 0.42752 | 0.0034477 | Sustained | FALSE | FALSE | TMED_Event | 5062
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:57 | 36 | 001:38 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 98 | 2022-02-21 | 3528 | keep | 0 | Feb | 2022 | 0.0024029 | 2.4519e-05 | Sustained | FALSE | FALSE | TMED_Event | 36
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:57 | 3718 | 001:38 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 98 | 2022-02-21 | 364364 | keep | 0 | Feb | 2022 | 0.24817 | 0.0025323 | Sustained | FALSE | FALSE | TMED_Event | 3718
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:57 | 1073 | 001:38 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA EL 1620-01 95% DEL 1336-10 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 98 | 2022-02-21 | 105154 | keep | 0 | Feb | 2022 | 0.07162 | 0.00073082 | Sustained | FALSE | FALSE | TMED_Event | 1073
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:57 | 172 | 001:38 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 98 | 2022-02-21 | 16856 | keep | 0 | Feb | 2022 | 0.011481 | 0.00011715 | Sustained | FALSE | FALSE | TMED_Event | 172
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:57 | 1615 | 001:38 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 98 | 2022-02-21 | 158270 | keep | 0 | Feb | 2022 | 0.1078 | 0.0011 | Sustained | FALSE | FALSE | TMED_Event | 1615
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:58 | 5668 | 000:39 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 39 | 2022-02-21 | 221052 | keep | 0 | Feb | 2022 | 0.15056 | 0.0038604 | Sustained | FALSE | FALSE | TMED_Event | 5668
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:58 | 1026 | 000:39 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 39 | 2022-02-21 | 40014 | keep | 0 | Feb | 2022 | 0.027253 | 0.0006988 | Sustained | FALSE | FALSE | TMED_Event | 1026
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:58 | 3046 | 000:39 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 39 | 2022-02-21 | 118794 | keep | 0 | Feb | 2022 | 0.08091 | 0.0020746 | Sustained | FALSE | FALSE | TMED_Event | 3046
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 13:58 | 2891 | 000:39 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 39 | 2022-02-21 | 112749 | keep | 0 | Feb | 2022 | 0.076793 | 0.001969 | Sustained | FALSE | FALSE | TMED_Event | 2891
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:44 | 99 | 001:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 85 | 2022-02-21 | 8415 | keep | 0 | Feb | 2022 | 0.0057314 | 6.7428e-05 | Sustained | FALSE | FALSE | TMED_Event | 99
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:44 | 31 | 001:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 85 | 2022-02-21 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 2.1114e-05 | Sustained | FALSE | FALSE | TMED_Event | 31
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:44 | 1474 | 001:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 85 | 2022-02-21 | 125290 | keep | 0 | Feb | 2022 | 0.085334 | 0.0010039 | Sustained | FALSE | FALSE | TMED_Event | 1474
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:44 | 2053 | 001:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 85 | 2022-02-21 | 174505 | keep | 0 | Feb | 2022 | 0.11885 | 0.0013983 | Sustained | FALSE | FALSE | TMED_Event | 2053
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:44 | 61 | 001:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 85 | 2022-02-21 | 5185 | keep | 0 | Feb | 2022 | 0.0035315 | 4.1547e-05 | Sustained | FALSE | FALSE | TMED_Event | 61
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:29 | 614 | 002:10 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 130 | 2022-02-21 | 79820 | keep | 0 | Feb | 2022 | 0.054365 | 0.00041819 | Sustained | FALSE | FALSE | TMED_Event | 614
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:29 | 770 | 002:10 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 130 | 2022-02-21 | 100100 | keep | 0 | Feb | 2022 | 0.068178 | 0.00052444 | Sustained | FALSE | FALSE | TMED_Event | 770
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:29 | 1271 | 002:10 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 130 | 2022-02-21 | 165230 | keep | 0 | Feb | 2022 | 0.11254 | 0.00086567 | Sustained | FALSE | FALSE | TMED_Event | 1271
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:29 | 247 | 002:10 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 130 | 2022-02-21 | 32110 | keep | 0 | Feb | 2022 | 0.02187 | 0.00016823 | Sustained | FALSE | FALSE | TMED_Event | 247
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 165 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 20790 | keep | 0 | Feb | 2022 | 0.01416 | 0.00011238 | Sustained | FALSE | FALSE | TMED_Event | 165
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 437 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 55062 | keep | 0 | Feb | 2022 | 0.037502 | 0.00029764 | Sustained | FALSE | FALSE | TMED_Event | 437
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 363 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 45738 | keep | 0 | Feb | 2022 | 0.031152 | 0.00024724 | Sustained | FALSE | FALSE | TMED_Event | 363
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 14 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 1764 | keep | 0 | Feb | 2022 | 0.0012015 | 9.5353e-06 | Sustained | FALSE | FALSE | TMED_Event | 14
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 2245 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 282870 | keep | 0 | Feb | 2022 | 0.19266 | 0.0015291 | Sustained | FALSE | FALSE | TMED_Event | 2245
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 1 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 126 | keep | 0 | Feb | 2022 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 15:25 | 1 | 002:06 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 126 | 2022-02-21 | 126 | keep | 0 | Feb | 2022 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 1 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 109 | keep | 0 | Feb | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 81 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 8829 | keep | 0 | Feb | 2022 | 0.0060134 | 5.5169e-05 | Sustained | FALSE | FALSE | TMED_Event | 81
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:00 | 1633 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 164933 | keep | 0 | Feb | 2022 | 0.11234 | 0.0011122 | Sustained | FALSE | FALSE | TMED_Event | 1633
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:00 | 1243 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 125543 | keep | 0 | Feb | 2022 | 0.085507 | 0.0008466 | Sustained | FALSE | FALSE | TMED_Event | 1243
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:00 | 1300 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 131300 | keep | 0 | Feb | 2022 | 0.089428 | 0.00088542 | Sustained | FALSE | FALSE | TMED_Event | 1300
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:00 | 41 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 4141 | keep | 0 | Feb | 2022 | 0.0028204 | 2.7925e-05 | Sustained | FALSE | FALSE | TMED_Event | 41
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1399 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 153890 | keep | 0 | Feb | 2022 | 0.10481 | 0.00095285 | Sustained | FALSE | FALSE | TMED_Event | 1399
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 302 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 33220 | keep | 0 | Feb | 2022 | 0.022626 | 0.00020569 | Sustained | FALSE | FALSE | TMED_Event | 302
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1048 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 115280 | keep | 0 | Feb | 2022 | 0.078517 | 0.00071379 | Sustained | FALSE | FALSE | TMED_Event | 1048
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 573 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 63030 | keep | 0 | Feb | 2022 | 0.042929 | 0.00039027 | Sustained | FALSE | FALSE | TMED_Event | 573
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1313 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 144430 | keep | 0 | Feb | 2022 | 0.098371 | 0.00089428 | Sustained | FALSE | FALSE | TMED_Event | 1313
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 478 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 51624 | keep | 0 | Feb | 2022 | 0.035161 | 0.00032556 | Sustained | FALSE | FALSE | TMED_Event | 478
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 679 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 73332 | keep | 0 | Feb | 2022 | 0.049946 | 0.00046246 | Sustained | FALSE | FALSE | TMED_Event | 679
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 949 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 102492 | keep | 0 | Feb | 2022 | 0.069807 | 0.00064636 | Sustained | FALSE | FALSE | TMED_Event | 949
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 67 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 7236 | keep | 0 | Feb | 2022 | 0.0049284 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 637 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 68796 | keep | 0 | Feb | 2022 | 0.046857 | 0.00043386 | Sustained | FALSE | FALSE | TMED_Event | 637
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 959 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 104531 | keep | 0 | Feb | 2022 | 0.071196 | 0.00065317 | Sustained | FALSE | FALSE | TMED_Event | 959
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 1382 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 150638 | keep | 0 | Feb | 2022 | 0.1026 | 0.00094127 | Sustained | FALSE | FALSE | TMED_Event | 1382
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 663 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 72267 | keep | 0 | Feb | 2022 | 0.049221 | 0.00045157 | Sustained | FALSE | FALSE | TMED_Event | 663
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 1935 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADORES ESTAN POR SUBESTACION PORTATIL. 1707-01 LLEVA PARTE 1708-02 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 208980 | keep | 0 | Feb | 2022 | 0.14234 | 0.0013179 | Sustained | FALSE | FALSE | TMED_Event | 1935
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 3 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADORES ESTAN POR SUBESTACION PORTATIL | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 324 | keep | 0 | Feb | 2022 | 0.00022067 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 61 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADORES ESTAN POR SUBESTACION PORTATIL | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 6588 | keep | 0 | Feb | 2022 | 0.0044871 | 4.1547e-05 | Sustained | FALSE | FALSE | TMED_Event | 61
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 1501 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADORES ESTAN POR SUBESTACION PORTATIL | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 162108 | keep | 0 | Feb | 2022 | 0.11041 | 0.0010223 | Sustained | FALSE | FALSE | TMED_Event | 1501
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 546 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADORES ESTAN POR SUBESTACION PORTATIL | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 58968 | keep | 0 | Feb | 2022 | 0.040163 | 0.00037188 | Sustained | FALSE | FALSE | TMED_Event | 546
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 715 | 001:48 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1707-01 LLEVA PARTE 1708-02 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 77220 | keep | 0 | Feb | 2022 | 0.052594 | 0.00048698 | Sustained | FALSE | FALSE | TMED_Event | 715
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1000 | 001:50 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1707-01 LLEVA PARTE 1708-02 ALIMENTADOR TRANSFERIDO AL 1708-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 110000 | keep | 0 | Feb | 2022 | 0.07492 | 0.0006811 | Sustained | FALSE | FALSE | TMED_Event | 1000
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1498 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA PARTE DE LA CARGA 1708-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 164780 | keep | 0 | Feb | 2022 | 0.11223 | 0.0010203 | Sustained | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1221 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 134310 | keep | 0 | Feb | 2022 | 0.091478 | 0.00083162 | Sustained | FALSE | FALSE | TMED_Event | 1221
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1100 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 121000 | keep | 0 | Feb | 2022 | 0.082413 | 0.0007492 | Sustained | FALSE | FALSE | TMED_Event | 1100
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 2402 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA CARGA 1720-08 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 259416 | keep | 0 | Feb | 2022 | 0.17669 | 0.001636 | Sustained | FALSE | FALSE | TMED_Event | 2402
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 750 | 001:48 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 50 % DE SU CARGA POR 1909-07. LLEVA CARGA 1709-05 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 81000 | keep | 0 | Feb | 2022 | 0.055169 | 0.00051082 | Sustained | FALSE | FALSE | TMED_Event | 750
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 753 | 002:28 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADOR 1709-03 50 % DE SU CARGA POR 1909-07 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 111444 | keep | 0 | Feb | 2022 | 0.075904 | 0.00051286 | Sustained | FALSE | FALSE | TMED_Event | 753
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 2364 | 001:48 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR 1709-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 255312 | keep | 0 | Feb | 2022 | 0.17389 | 0.0016101 | Sustained | FALSE | FALSE | TMED_Event | 2364
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 5809 | 001:19 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. TRANSFERIDO AL 1716-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 458911 | keep | 0 | Feb | 2022 | 0.31256 | 0.0039565 | Sustained | FALSE | FALSE | TMED_Event | 5809
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:49 | 3941 | 002:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 150 | 2022-02-21 | 591150 | keep | 0 | Feb | 2022 | 0.40263 | 0.0026842 | Sustained | FALSE | FALSE | TMED_Event | 3941
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:49 | 3871 | 002:30 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 150 | 2022-02-21 | 580650 | keep | 0 | Feb | 2022 | 0.39548 | 0.0026365 | Sustained | FALSE | FALSE | TMED_Event | 3871
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 2191 | 001:26 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1718-03 LLEVA 40% DE LA CARGA 1710-05 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 188426 | keep | 0 | Feb | 2022 | 0.12834 | 0.0014923 | Sustained | FALSE | FALSE | TMED_Event | 2191
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:49 | 3000 | 002:30 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 40 % DE SU CARGA POR 1718-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 150 | 2022-02-21 | 450000 | keep | 0 | Feb | 2022 | 0.30649 | 0.0020433 | Sustained | FALSE | FALSE | TMED_Event | 3000
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:35 | 1588 | 001:16 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 76 | 2022-02-21 | 120688 | keep | 0 | Feb | 2022 | 0.0822 | 0.0010816 | Sustained | FALSE | FALSE | TMED_Event | 1588
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:35 | 723 | 001:16 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 76 | 2022-02-21 | 54948 | keep | 0 | Feb | 2022 | 0.037425 | 0.00049243 | Sustained | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:35 | 13 | 001:16 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA PARTE 1716-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 76 | 2022-02-21 | 988 | keep | 0 | Feb | 2022 | 0.00067292 | 8.8542e-06 | Sustained | FALSE | FALSE | TMED_Event | 13
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:35 | 1983 | 001:16 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1801-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 76 | 2022-02-21 | 150708 | keep | 0 | Feb | 2022 | 0.10265 | 0.0013506 | Sustained | FALSE | FALSE | TMED_Event | 1983
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:35 | 1976 | 001:16 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 76 | 2022-02-21 | 150176 | keep | 0 | Feb | 2022 | 0.10228 | 0.0013458 | Sustained | FALSE | FALSE | TMED_Event | 1976
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 5252 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 782548 | keep | 0 | Feb | 2022 | 0.53299 | 0.0035771 | Sustained | FALSE | FALSE | TMED_Event | 5252
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 77 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 11473 | keep | 0 | Feb | 2022 | 0.0078142 | 5.2444e-05 | Sustained | FALSE | FALSE | TMED_Event | 77
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 5961 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1713-05 LLEVA 95% 1717-02 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 888189 | keep | 0 | Feb | 2022 | 0.60494 | 0.00406 | Sustained | FALSE | FALSE | TMED_Event | 5961
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 1408 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 111232 | keep | 0 | Feb | 2022 | 0.07576 | 0.00095898 | Sustained | FALSE | FALSE | TMED_Event | 1408
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 455 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 35945 | keep | 0 | Feb | 2022 | 0.024482 | 0.0003099 | Sustained | FALSE | FALSE | TMED_Event | 455
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 878 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 69362 | keep | 0 | Feb | 2022 | 0.047242 | 0.000598 | Sustained | FALSE | FALSE | TMED_Event | 878
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 98 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 10682 | keep | 0 | Feb | 2022 | 0.0072755 | 6.6747e-05 | Sustained | FALSE | FALSE | TMED_Event | 98
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 74 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 8066 | keep | 0 | Feb | 2022 | 0.0054937 | 5.0401e-05 | Sustained | FALSE | FALSE | TMED_Event | 74
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 776 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 84584 | keep | 0 | Feb | 2022 | 0.05761 | 0.00052853 | Sustained | FALSE | FALSE | TMED_Event | 776
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 450 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 35550 | keep | 0 | Feb | 2022 | 0.024213 | 0.00030649 | Sustained | FALSE | FALSE | TMED_Event | 450
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 130 | 002:29 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1717-04 LLEVA 20% 1716-02 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 19370 | keep | 0 | Feb | 2022 | 0.013193 | 8.8542e-05 | Sustained | FALSE | FALSE | TMED_Event | 130
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 521 | 001:19 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 20% DE SU CARGA POR 1717-04 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 41159 | keep | 0 | Feb | 2022 | 0.028033 | 0.00035485 | Sustained | FALSE | FALSE | TMED_Event | 521
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 1500 | 001:19 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. PARTE DE SU CARGA POR 1711-03 Y LLEVA CARGA 1710-01 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 118500 | keep | 0 | Feb | 2022 | 0.08071 | 0.0010216 | Sustained | FALSE | FALSE | TMED_Event | 1500
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 4080 | 002:29 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 10% DE SU CARGA POR 1806-02. LLEVA CARGA 1717-05 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 607920 | keep | 0 | Feb | 2022 | 0.41405 | 0.0027789 | Sustained | FALSE | FALSE | TMED_Event | 4080
BAYAMON | 2022-02-21 13:19 | 2022-02-21 16:19 | 46 | 003:00 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 95% DE SU CARGA POR 1713-05. ALIMENTADOR SE CERRO POR SCADA | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 180 | 2022-02-21 | 8280 | keep | 0 | Feb | 2022 | 0.0056395 | 3.133e-05 | Sustained | FALSE | FALSE | TMED_Event | 46
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 865 | 002:29 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1713-05 LLEVA 95% DE CARGA 1717-02 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 128885 | keep | 0 | Feb | 2022 | 0.087783 | 0.00058915 | Sustained | FALSE | FALSE | TMED_Event | 865
BAYAMON | 2022-02-21 13:19 | 2022-02-21 16:09 | 4431 | 002:50 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. ALIMENTADOR SE CERRO POR SCADA | B22022100180 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 170 | 2022-02-21 | 753270 | keep | 0 | Feb | 2022 | 0.51305 | 0.0030179 | Sustained | FALSE | FALSE | TMED_Event | 4431
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 1362 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1717-04 LLEVA 20% 1716-02 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 202938 | keep | 0 | Feb | 2022 | 0.13822 | 0.00092765 | Sustained | FALSE | FALSE | TMED_Event | 1362
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 341 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR 1717-01 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 50809 | keep | 0 | Feb | 2022 | 0.034606 | 0.00023225 | Sustained | FALSE | FALSE | TMED_Event | 341
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 1210 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 104060 | keep | 0 | Feb | 2022 | 0.070875 | 0.00082413 | Sustained | FALSE | FALSE | TMED_Event | 1210
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 3438 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 295668 | keep | 0 | Feb | 2022 | 0.20138 | 0.0023416 | Sustained | FALSE | FALSE | TMED_Event | 3438
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 2605 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 40% DE LA CARGA 1710-05 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 224030 | keep | 0 | Feb | 2022 | 0.15259 | 0.0017743 | Sustained | FALSE | FALSE | TMED_Event | 2605
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 73 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 6278 | keep | 0 | Feb | 2022 | 0.0042759 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:34 | 3597 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 269775 | keep | 0 | Feb | 2022 | 0.18374 | 0.0024499 | Sustained | FALSE | FALSE | TMED_Event | 3597
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:34 | 492 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 36900 | keep | 0 | Feb | 2022 | 0.025132 | 0.0003351 | Sustained | FALSE | FALSE | TMED_Event | 492
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:34 | 4028 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 302100 | keep | 0 | Feb | 2022 | 0.20576 | 0.0027435 | Sustained | FALSE | FALSE | TMED_Event | 4028
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:34 | 2617 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 196275 | keep | 0 | Feb | 2022 | 0.13368 | 0.0017824 | Sustained | FALSE | FALSE | TMED_Event | 2617
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 6136 | 001:48 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. INTERRUPTOR 1709-01 LLEVA CARGA 1720-07 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 662688 | keep | 0 | Feb | 2022 | 0.45135 | 0.0041792 | Sustained | FALSE | FALSE | TMED_Event | 6136
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:07 | 1 | 001:48 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. INTERRUPTOR 1709-02 LLEVA CARGA 1720-08 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 108 | 2022-02-21 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 1514 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 165026 | keep | 0 | Feb | 2022 | 0.1124 | 0.0010312 | Sustained | FALSE | FALSE | TMED_Event | 1514
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 1105 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 120445 | keep | 0 | Feb | 2022 | 0.082035 | 0.00075261 | Sustained | FALSE | FALSE | TMED_Event | 1105
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:55 | 966 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 92736 | keep | 0 | Feb | 2022 | 0.063162 | 0.00065794 | Sustained | FALSE | FALSE | TMED_Event | 966
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:55 | 186 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 17856 | keep | 0 | Feb | 2022 | 0.012162 | 0.00012668 | Sustained | FALSE | FALSE | TMED_Event | 186
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:55 | 1746 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 167616 | keep | 0 | Feb | 2022 | 0.11416 | 0.0011892 | Sustained | FALSE | FALSE | TMED_Event | 1746
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:55 | 112 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 10752 | keep | 0 | Feb | 2022 | 0.0073231 | 7.6283e-05 | Sustained | FALSE | FALSE | TMED_Event | 112
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:56 | 748 | 001:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 97 | 2022-02-21 | 72556 | keep | 0 | Feb | 2022 | 0.049418 | 0.00050946 | Sustained | FALSE | FALSE | TMED_Event | 748
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:56 | 33 | 001:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 97 | 2022-02-21 | 3201 | keep | 0 | Feb | 2022 | 0.0021802 | 2.2476e-05 | Sustained | FALSE | FALSE | TMED_Event | 33
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:56 | 67 | 001:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 97 | 2022-02-21 | 6499 | keep | 0 | Feb | 2022 | 0.0044264 | 4.5633e-05 | Sustained | FALSE | FALSE | TMED_Event | 67
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:56 | 1587 | 001:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 97 | 2022-02-21 | 153939 | keep | 0 | Feb | 2022 | 0.10485 | 0.0010809 | Sustained | FALSE | FALSE | TMED_Event | 1587
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:56 | 521 | 001:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 97 | 2022-02-21 | 50537 | keep | 0 | Feb | 2022 | 0.034421 | 0.00035485 | Sustained | FALSE | FALSE | TMED_Event | 521
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:56 | 1307 | 001:37 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 97 | 2022-02-21 | 126779 | keep | 0 | Feb | 2022 | 0.086349 | 0.00089019 | Sustained | FALSE | FALSE | TMED_Event | 1307
BAYAMON | 2022-02-21 13:19 | 2022-02-21 16:22 | 3798 | 003:03 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 183 | 2022-02-21 | 695034 | keep | 0 | Feb | 2022 | 0.47338 | 0.0025868 | Sustained | FALSE | FALSE | TMED_Event | 3798
BAYAMON | 2022-02-21 13:19 | 2022-02-21 16:22 | 4622 | 003:03 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA 10% 1717-01 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 183 | 2022-02-21 | 845826 | keep | 0 | Feb | 2022 | 0.57609 | 0.003148 | Sustained | FALSE | FALSE | TMED_Event | 4622
BAYAMON | 2022-02-21 13:19 | 2022-02-21 16:22 | 4089 | 003:03 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 183 | 2022-02-21 | 748287 | keep | 0 | Feb | 2022 | 0.50965 | 0.002785 | Sustained | FALSE | FALSE | TMED_Event | 4089
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 959 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA ESTA POR SUBESTACION PROVISIONAL 1904-00 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 105490 | keep | 0 | Feb | 2022 | 0.071849 | 0.00065317 | Sustained | FALSE | FALSE | TMED_Event | 959
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1297 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA ESTA POR SUBESTACION PROVISIONAL 1904-00 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 142670 | keep | 0 | Feb | 2022 | 0.097172 | 0.00088338 | Sustained | FALSE | FALSE | TMED_Event | 1297
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 451 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA ESTA POR SUBESTACION PROVISIONAL 1904-00 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 49610 | keep | 0 | Feb | 2022 | 0.033789 | 0.00030717 | Sustained | FALSE | FALSE | TMED_Event | 451
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 1264 | 001:50 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA ESTA POR SUBESTACION PROVISIONAL 1904-00 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 139040 | keep | 0 | Feb | 2022 | 0.0947 | 0.0008609 | Sustained | FALSE | FALSE | TMED_Event | 1264
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:09 | 62 | 001:50 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA ESTA POR SUBESTACION PROVISIONAL 1904-00 90% TRANSFERIDA A 1330-01 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 110 | 2022-02-21 | 6820 | keep | 0 | Feb | 2022 | 0.0046451 | 4.2228e-05 | Sustained | FALSE | FALSE | TMED_Event | 62
BAYAMON | 2022-02-21 13:19 | 2022-02-21 13:49 | 558 | 000:30 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA ESTA POR SUBESTACION PROVISIONAL 1904-00 90% TRANSFERIDA A 1330-01 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 30 | 2022-02-21 | 16740 | keep | 0 | Feb | 2022 | 0.011402 | 0.00038005 | Sustained | FALSE | FALSE | TMED_Event | 558
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 293 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 25198 | keep | 0 | Feb | 2022 | 0.017162 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 315 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 27090 | keep | 0 | Feb | 2022 | 0.018451 | 0.00021455 | Sustained | FALSE | FALSE | TMED_Event | 315
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 216 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 18576 | keep | 0 | Feb | 2022 | 0.012652 | 0.00014712 | Sustained | FALSE | FALSE | TMED_Event | 216
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:45 | 1310 | 001:26 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 86 | 2022-02-21 | 112660 | keep | 0 | Feb | 2022 | 0.076732 | 0.00089224 | Sustained | FALSE | FALSE | TMED_Event | 1310
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 222 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 32856 | keep | 0 | Feb | 2022 | 0.022378 | 0.0001512 | Sustained | FALSE | FALSE | TMED_Event | 222
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 2466 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 364968 | keep | 0 | Feb | 2022 | 0.24858 | 0.0016796 | Sustained | FALSE | FALSE | TMED_Event | 2466
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 2435 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1909-08 LLEVA 1907-05 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 360380 | keep | 0 | Feb | 2022 | 0.24545 | 0.0016585 | Sustained | FALSE | FALSE | TMED_Event | 2435
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:38 | 3 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 237 | keep | 0 | Feb | 2022 | 0.00016142 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:38 | 3957 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 312603 | keep | 0 | Feb | 2022 | 0.21291 | 0.0026951 | Sustained | FALSE | FALSE | TMED_Event | 3957
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:38 | 58 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 4582 | keep | 0 | Feb | 2022 | 0.0031208 | 3.9504e-05 | Sustained | FALSE | FALSE | TMED_Event | 58
SAN JUAN | 2022-02-21 13:19 | 2022-02-21 14:38 | 386 | 001:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 79 | 2022-02-21 | 30494 | keep | 0 | Feb | 2022 | 0.020769 | 0.0002629 | Sustained | FALSE | FALSE | TMED_Event | 386
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 1139 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1909-07 LLEVA 50% 1709-03 | S2022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 168572 | keep | 0 | Feb | 2022 | 0.11481 | 0.00077577 | Sustained | FALSE | FALSE | TMED_Event | 1139
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 2956 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA LA CARGA 1907-05 | S2022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 437488 | keep | 0 | Feb | 2022 | 0.29797 | 0.0020133 | Sustained | FALSE | FALSE | TMED_Event | 2956
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:47 | 4456 | 002:28 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S2022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 148 | 2022-02-21 | 659488 | keep | 0 | Feb | 2022 | 0.44917 | 0.003035 | Sustained | FALSE | FALSE | TMED_Event | 4456
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:52 | 37 | 001:33 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA PARTE 1519-05 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 93 | 2022-02-21 | 3441 | keep | 0 | Feb | 2022 | 0.0023436 | 2.5201e-05 | Sustained | FALSE | FALSE | TMED_Event | 37
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:52 | 7 | 001:33 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 93 | 2022-02-21 | 651 | keep | 0 | Feb | 2022 | 0.00044339 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:52 | 2 | 001:33 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 93 | 2022-02-21 | 186 | keep | 0 | Feb | 2022 | 0.00012668 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 577 | 001:31 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA TRANSFERIDA A 1529-12 | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 52507 | keep | 0 | Feb | 2022 | 0.035762 | 0.00039299 | Sustained | FALSE | FALSE | TMED_Event | 577
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 57 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 5187 | keep | 0 | Feb | 2022 | 0.0035328 | 3.8822e-05 | Sustained | FALSE | FALSE | TMED_Event | 57
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 212 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION.DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO AREA NORTE Y ESTE | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 19292 | keep | 0 | Feb | 2022 | 0.01314 | 0.00014439 | Sustained | FALSE | FALSE | TMED_Event | 212
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 72 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO AREA NORTE Y ESTE | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 6552 | keep | 0 | Feb | 2022 | 0.0044625 | 4.9039e-05 | Sustained | FALSE | FALSE | TMED_Event | 72
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 5 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO AREA NORTE Y ESTE | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 455 | keep | 0 | Feb | 2022 | 0.0003099 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 45 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO AREA NORTE Y ESTE | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 4095 | keep | 0 | Feb | 2022 | 0.0027891 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:50 | 686 | 001:31 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO AREA NORTE Y ESTE | S22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 91 | 2022-02-21 | 62426 | keep | 0 | Feb | 2022 | 0.042518 | 0.00046723 | Sustained | FALSE | FALSE | TMED_Event | 686
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:00 | 1571 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 158671 | keep | 0 | Feb | 2022 | 0.10807 | 0.00107 | Sustained | FALSE | FALSE | TMED_Event | 1571
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:00 | 2041 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 206141 | keep | 0 | Feb | 2022 | 0.1404 | 0.0013901 | Sustained | FALSE | FALSE | TMED_Event | 2041
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:00 | 625 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 63125 | keep | 0 | Feb | 2022 | 0.042994 | 0.00042568 | Sustained | FALSE | FALSE | TMED_Event | 625
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:00 | 1463 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 147763 | keep | 0 | Feb | 2022 | 0.10064 | 0.00099644 | Sustained | FALSE | FALSE | TMED_Event | 1463
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 1902 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 256770 | keep | 0 | Feb | 2022 | 0.17488 | 0.0012954 | Sustained | FALSE | FALSE | TMED_Event | 1902
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 970 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 130950 | keep | 0 | Feb | 2022 | 0.089189 | 0.00066066 | Sustained | FALSE | FALSE | TMED_Event | 970
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 3003 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 405405 | keep | 0 | Feb | 2022 | 0.27612 | 0.0020453 | Sustained | FALSE | FALSE | TMED_Event | 3003
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:33 | 1394 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 186796 | keep | 0 | Feb | 2022 | 0.12723 | 0.00094945 | Sustained | FALSE | FALSE | TMED_Event | 1394
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:33 | 412 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 55208 | keep | 0 | Feb | 2022 | 0.037602 | 0.00028061 | Sustained | FALSE | FALSE | TMED_Event | 412
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:34 | 424 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 31800 | keep | 0 | Feb | 2022 | 0.021659 | 0.00028878 | Sustained | FALSE | FALSE | TMED_Event | 424
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:34 | 240 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 18000 | keep | 0 | Feb | 2022 | 0.01226 | 0.00016346 | Sustained | FALSE | FALSE | TMED_Event | 240
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:34 | 2722 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 204150 | keep | 0 | Feb | 2022 | 0.13905 | 0.0018539 | Sustained | FALSE | FALSE | TMED_Event | 2722
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:34 | 1234 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 92550 | keep | 0 | Feb | 2022 | 0.063035 | 0.00084047 | Sustained | FALSE | FALSE | TMED_Event | 1234
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:34 | 76 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 5700 | keep | 0 | Feb | 2022 | 0.0038822 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:33 | 2286 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 306324 | keep | 0 | Feb | 2022 | 0.20864 | 0.001557 | Sustained | FALSE | FALSE | TMED_Event | 2286
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:33 | 693 | 002:14 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 134 | 2022-02-21 | 92862 | keep | 0 | Feb | 2022 | 0.063248 | 0.000472 | Sustained | FALSE | FALSE | TMED_Event | 693
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:31 | 4098 | 001:12 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 72 | 2022-02-21 | 295056 | keep | 0 | Feb | 2022 | 0.20096 | 0.0027911 | Sustained | FALSE | FALSE | TMED_Event | 4098
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:42 | 956 | 002:23 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 143 | 2022-02-21 | 136708 | keep | 0 | Feb | 2022 | 0.093111 | 0.00065113 | Sustained | FALSE | FALSE | TMED_Event | 956
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 2343 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 316305 | keep | 0 | Feb | 2022 | 0.21543 | 0.0015958 | Sustained | FALSE | FALSE | TMED_Event | 2343
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 1830 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 247050 | keep | 0 | Feb | 2022 | 0.16826 | 0.0012464 | Sustained | FALSE | FALSE | TMED_Event | 1830
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 710 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 95850 | keep | 0 | Feb | 2022 | 0.065283 | 0.00048358 | Sustained | FALSE | FALSE | TMED_Event | 710
FAJARDO | 2022-02-21 13:19 | 2022-02-21 15:34 | 1197 | 002:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 135 | 2022-02-21 | 161595 | keep | 0 | Feb | 2022 | 0.11006 | 0.00081527 | Sustained | FALSE | FALSE | TMED_Event | 1197
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 1894 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 268948 | keep | 0 | Feb | 2022 | 0.18318 | 0.00129 | Sustained | FALSE | FALSE | TMED_Event | 1894
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 4154 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 589868 | keep | 0 | Feb | 2022 | 0.40176 | 0.0028293 | Sustained | FALSE | FALSE | TMED_Event | 4154
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 424 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 60208 | keep | 0 | Feb | 2022 | 0.041007 | 0.00028878 | Sustained | FALSE | FALSE | TMED_Event | 424
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 2708 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 384536 | keep | 0 | Feb | 2022 | 0.26191 | 0.0018444 | Sustained | FALSE | FALSE | TMED_Event | 2708
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 2524 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 358408 | keep | 0 | Feb | 2022 | 0.24411 | 0.0017191 | Sustained | FALSE | FALSE | TMED_Event | 2524
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 1648 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 234016 | keep | 0 | Feb | 2022 | 0.15939 | 0.0011224 | Sustained | FALSE | FALSE | TMED_Event | 1648
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 14:34 | 539 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 40425 | keep | 0 | Feb | 2022 | 0.027533 | 0.00036711 | Sustained | FALSE | FALSE | TMED_Event | 539
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 14:34 | 3012 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 225900 | keep | 0 | Feb | 2022 | 0.15386 | 0.0020515 | Sustained | FALSE | FALSE | TMED_Event | 3012
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 14:34 | 2106 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 157950 | keep | 0 | Feb | 2022 | 0.10758 | 0.0014344 | Sustained | FALSE | FALSE | TMED_Event | 2106
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 14:34 | 635 | 001:15 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 75 | 2022-02-21 | 47625 | keep | 0 | Feb | 2022 | 0.032437 | 0.0004325 | Sustained | FALSE | FALSE | TMED_Event | 635
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:38 | 3766 | 002:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 139 | 2022-02-21 | 523474 | keep | 0 | Feb | 2022 | 0.35654 | 0.002565 | Sustained | FALSE | FALSE | TMED_Event | 3766
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:38 | 1380 | 002:19 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 139 | 2022-02-21 | 191820 | keep | 0 | Feb | 2022 | 0.13065 | 0.00093991 | Sustained | FALSE | FALSE | TMED_Event | 1380
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 3838 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 544996 | keep | 0 | Feb | 2022 | 0.37119 | 0.002614 | Sustained | FALSE | FALSE | TMED_Event | 3838
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 817 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 116014 | keep | 0 | Feb | 2022 | 0.079017 | 0.00055645 | Sustained | FALSE | FALSE | TMED_Event | 817
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:41 | 1124 | 002:22 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 142 | 2022-02-21 | 159608 | keep | 0 | Feb | 2022 | 0.10871 | 0.00076555 | Sustained | FALSE | FALSE | TMED_Event | 1124
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 2039 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 205939 | keep | 0 | Feb | 2022 | 0.14026 | 0.0013888 | Sustained | FALSE | FALSE | TMED_Event | 2039
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 4188 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 422988 | keep | 0 | Feb | 2022 | 0.2881 | 0.0028524 | Sustained | FALSE | FALSE | TMED_Event | 4188
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 4085 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 412585 | keep | 0 | Feb | 2022 | 0.28101 | 0.0027823 | Sustained | FALSE | FALSE | TMED_Event | 4085
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:44 | 2580 | 002:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 145 | 2022-02-21 | 374100 | keep | 0 | Feb | 2022 | 0.2548 | 0.0017572 | Sustained | FALSE | FALSE | TMED_Event | 2580
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:44 | 500 | 002:25 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 145 | 2022-02-21 | 72500 | keep | 0 | Feb | 2022 | 0.049379 | 0.00034055 | Sustained | FALSE | FALSE | TMED_Event | 500
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 3464 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 349864 | keep | 0 | Feb | 2022 | 0.23829 | 0.0023593 | Sustained | FALSE | FALSE | TMED_Event | 3464
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 7621 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 769721 | keep | 0 | Feb | 2022 | 0.52425 | 0.0051906 | Sustained | FALSE | FALSE | TMED_Event | 7621
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 3699 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 373599 | keep | 0 | Feb | 2022 | 0.25446 | 0.0025194 | Sustained | FALSE | FALSE | TMED_Event | 3699
CANOVANAS | 2022-02-21 13:19 | 2022-02-21 15:00 | 2675 | 001:41 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 101 | 2022-02-21 | 270175 | keep | 0 | Feb | 2022 | 0.18401 | 0.0018219 | Sustained | FALSE | FALSE | TMED_Event | 2675
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:32 | 1839 | 001:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 73 | 2022-02-21 | 134247 | keep | 0 | Feb | 2022 | 0.091435 | 0.0012525 | Sustained | FALSE | FALSE | TMED_Event | 1839
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:32 | 1778 | 001:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 73 | 2022-02-21 | 129794 | keep | 0 | Feb | 2022 | 0.088402 | 0.001211 | Sustained | FALSE | FALSE | TMED_Event | 1778
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:32 | 1376 | 001:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 73 | 2022-02-21 | 100448 | keep | 0 | Feb | 2022 | 0.068415 | 0.00093719 | Sustained | FALSE | FALSE | TMED_Event | 1376
CAGUAS | 2022-02-21 13:19 | 2022-02-21 14:24 | 2276 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 147940 | keep | 0 | Feb | 2022 | 0.10076 | 0.0015502 | Sustained | FALSE | FALSE | TMED_Event | 2276
CAGUAS | 2022-02-21 13:19 | 2022-02-21 14:24 | 777 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 50505 | keep | 0 | Feb | 2022 | 0.034399 | 0.00052921 | Sustained | FALSE | FALSE | TMED_Event | 777
CAGUAS | 2022-02-21 13:19 | 2022-02-21 14:24 | 12 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 780 | keep | 0 | Feb | 2022 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2022-02-21 13:19 | 2022-02-21 14:24 | 1290 | 001:05 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | C22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 65 | 2022-02-21 | 83850 | keep | 0 | Feb | 2022 | 0.05711 | 0.00087861 | Sustained | FALSE | FALSE | TMED_Event | 1290
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:32 | 293 | 001:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 73 | 2022-02-21 | 21389 | keep | 0 | Feb | 2022 | 0.014568 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
FAJARDO | 2022-02-21 13:19 | 2022-02-21 14:32 | 1215 | 001:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. | R22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 73 | 2022-02-21 | 88695 | keep | 0 | Feb | 2022 | 0.06041 | 0.00082753 | Sustained | FALSE | FALSE | TMED_Event | 1215
PONCE | 2022-02-21 13:19 | 2022-02-21 13:20 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22022100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 1606 | keep | 0 | Feb | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | TMED_Event | 1606
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 2791 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 371203 | keep | 0 | Feb | 2022 | 0.25282 | 0.0019009 | Sustained | FALSE | FALSE | TMED_Event | 2791
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 1464 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 194712 | keep | 0 | Feb | 2022 | 0.13262 | 0.00099712 | Sustained | FALSE | FALSE | TMED_Event | 1464
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 759 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 100947 | keep | 0 | Feb | 2022 | 0.068755 | 0.00051695 | Sustained | FALSE | FALSE | TMED_Event | 759
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 1500 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 199500 | keep | 0 | Feb | 2022 | 0.13588 | 0.0010216 | Sustained | FALSE | FALSE | TMED_Event | 1500
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 2132 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 283556 | keep | 0 | Feb | 2022 | 0.19313 | 0.0014521 | Sustained | FALSE | FALSE | TMED_Event | 2132
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 2366 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 314678 | keep | 0 | Feb | 2022 | 0.21433 | 0.0016115 | Sustained | FALSE | FALSE | TMED_Event | 2366
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 1976 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 262808 | keep | 0 | Feb | 2022 | 0.179 | 0.0013458 | Sustained | FALSE | FALSE | TMED_Event | 1976
ARECIBO | 2022-02-21 13:19 | 2022-02-21 15:32 | 3688 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | A22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 490504 | keep | 0 | Feb | 2022 | 0.33408 | 0.0025119 | Sustained | FALSE | FALSE | TMED_Event | 3688
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:55 | 4027 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 386592 | keep | 0 | Feb | 2022 | 0.26331 | 0.0027428 | Sustained | FALSE | FALSE | TMED_Event | 4027
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:55 | 2468 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 236928 | keep | 0 | Feb | 2022 | 0.16137 | 0.0016809 | Sustained | FALSE | FALSE | TMED_Event | 2468
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:55 | 1494 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 143424 | keep | 0 | Feb | 2022 | 0.097685 | 0.0010176 | Sustained | FALSE | FALSE | TMED_Event | 1494
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 2368 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 248640 | keep | 0 | Feb | 2022 | 0.16935 | 0.0016128 | Sustained | FALSE | FALSE | TMED_Event | 2368
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 538 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 56490 | keep | 0 | Feb | 2022 | 0.038475 | 0.00036643 | Sustained | FALSE | FALSE | TMED_Event | 538
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 1284 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 134820 | keep | 0 | Feb | 2022 | 0.091825 | 0.00087453 | Sustained | FALSE | FALSE | TMED_Event | 1284
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:55 | 1310 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 125760 | keep | 0 | Feb | 2022 | 0.085655 | 0.00089224 | Sustained | FALSE | FALSE | TMED_Event | 1310
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:55 | 215 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 20640 | keep | 0 | Feb | 2022 | 0.014058 | 0.00014644 | Sustained | FALSE | FALSE | TMED_Event | 215
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:55 | 1 | 001:36 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 96 | 2022-02-21 | 96 | keep | 0 | Feb | 2022 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 652 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 68460 | keep | 0 | Feb | 2022 | 0.046628 | 0.00044407 | Sustained | FALSE | FALSE | TMED_Event | 652
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 2704 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 283920 | keep | 0 | Feb | 2022 | 0.19338 | 0.0018417 | Sustained | FALSE | FALSE | TMED_Event | 2704
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:03 | 1526 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 158704 | keep | 0 | Feb | 2022 | 0.10809 | 0.0010394 | Sustained | FALSE | FALSE | TMED_Event | 1526
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:03 | 308 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 32032 | keep | 0 | Feb | 2022 | 0.021817 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:03 | 1397 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 145288 | keep | 0 | Feb | 2022 | 0.098955 | 0.00095149 | Sustained | FALSE | FALSE | TMED_Event | 1397
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:03 | 2926 | 001:44 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 104 | 2022-02-21 | 304304 | keep | 0 | Feb | 2022 | 0.20726 | 0.0019929 | Sustained | FALSE | FALSE | TMED_Event | 2926
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:51 | 1834 | 001:32 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 92 | 2022-02-21 | 168728 | keep | 0 | Feb | 2022 | 0.11492 | 0.0012491 | Sustained | FALSE | FALSE | TMED_Event | 1834
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:51 | 2324 | 001:32 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 92 | 2022-02-21 | 213808 | keep | 0 | Feb | 2022 | 0.14562 | 0.0015829 | Sustained | FALSE | FALSE | TMED_Event | 2324
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 14:51 | 1570 | 001:32 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 92 | 2022-02-21 | 144440 | keep | 0 | Feb | 2022 | 0.098377 | 0.0010693 | Sustained | FALSE | FALSE | TMED_Event | 1570
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 27 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 2835 | keep | 0 | Feb | 2022 | 0.0019309 | 1.839e-05 | Sustained | FALSE | FALSE | TMED_Event | 27
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 603 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 63315 | keep | 0 | Feb | 2022 | 0.043124 | 0.0004107 | Sustained | FALSE | FALSE | TMED_Event | 603
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 6 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 630 | keep | 0 | Feb | 2022 | 0.00042909 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 325 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 34125 | keep | 0 | Feb | 2022 | 0.023242 | 0.00022136 | Sustained | FALSE | FALSE | TMED_Event | 325
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:04 | 172 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 18060 | keep | 0 | Feb | 2022 | 0.012301 | 0.00011715 | Sustained | FALSE | FALSE | TMED_Event | 172
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:48 | 31 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 4619 | keep | 0 | Feb | 2022 | 0.003146 | 2.1114e-05 | Sustained | FALSE | FALSE | TMED_Event | 31
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:48 | 1859 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 276991 | keep | 0 | Feb | 2022 | 0.18866 | 0.0012662 | Sustained | FALSE | FALSE | TMED_Event | 1859
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:48 | 7 | 002:29 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 149 | 2022-02-21 | 1043 | keep | 0 | Feb | 2022 | 0.00071038 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:04 | 2861 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 300405 | keep | 0 | Feb | 2022 | 0.2046 | 0.0019486 | Sustained | FALSE | FALSE | TMED_Event | 2861
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:04 | 2096 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 220080 | keep | 0 | Feb | 2022 | 0.1499 | 0.0014276 | Sustained | FALSE | FALSE | TMED_Event | 2096
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:04 | 493 | 001:45 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 105 | 2022-02-21 | 51765 | keep | 0 | Feb | 2022 | 0.035257 | 0.00033578 | Sustained | FALSE | FALSE | TMED_Event | 493
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:23 | 941 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. LLEVA CARGA 9405-09 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 116684 | keep | 0 | Feb | 2022 | 0.079473 | 0.00064091 | Sustained | FALSE | FALSE | TMED_Event | 941
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:23 | 1 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 124 | keep | 0 | Feb | 2022 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:23 | 2678 | 002:04 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 332072 | keep | 0 | Feb | 2022 | 0.22617 | 0.001824 | Sustained | FALSE | FALSE | TMED_Event | 2678
VEGA BAJA | 2022-02-21 13:19 | 2022-02-21 15:05 | 425 | 001:46 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 106 | 2022-02-21 | 45050 | keep | 0 | Feb | 2022 | 0.030683 | 0.00028947 | Sustained | FALSE | FALSE | TMED_Event | 425
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:28 | 3511 | 001:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 69 | 2022-02-21 | 242259 | keep | 0 | Feb | 2022 | 0.165 | 0.0023913 | Sustained | FALSE | FALSE | TMED_Event | 3511
BAYAMON | 2022-02-21 13:19 | 2022-02-21 14:28 | 1 | 001:09 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 69 | 2022-02-21 | 69 | keep | 0 | Feb | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:23 | 136 | 002:04 | T | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. CARGA POR 9403-01 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 124 | 2022-02-21 | 16864 | keep | 0 | Feb | 2022 | 0.011486 | 9.2629e-05 | Sustained | FALSE | FALSE | TMED_Event | 136
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 3070 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 408310 | keep | 0 | Feb | 2022 | 0.2781 | 0.002091 | Sustained | FALSE | FALSE | TMED_Event | 3070
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 2735 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 363755 | keep | 0 | Feb | 2022 | 0.24775 | 0.0018628 | Sustained | FALSE | FALSE | TMED_Event | 2735
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 1070 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 142310 | keep | 0 | Feb | 2022 | 0.096927 | 0.00072877 | Sustained | FALSE | FALSE | TMED_Event | 1070
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 1647 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 219051 | keep | 0 | Feb | 2022 | 0.14919 | 0.0011218 | Sustained | FALSE | FALSE | TMED_Event | 1647
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 3295 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 438235 | keep | 0 | Feb | 2022 | 0.29848 | 0.0022442 | Sustained | FALSE | FALSE | TMED_Event | 3295
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 1180 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 156940 | keep | 0 | Feb | 2022 | 0.10689 | 0.00080369 | Sustained | FALSE | FALSE | TMED_Event | 1180
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 320 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 42560 | keep | 0 | Feb | 2022 | 0.028987 | 0.00021795 | Sustained | FALSE | FALSE | TMED_Event | 320
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:32 | 2234 | 002:13 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 133 | 2022-02-21 | 297122 | keep | 0 | Feb | 2022 | 0.20237 | 0.0015216 | Sustained | FALSE | FALSE | TMED_Event | 2234
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 4176 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 455184 | keep | 0 | Feb | 2022 | 0.31002 | 0.0028443 | Sustained | FALSE | FALSE | TMED_Event | 4176
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 252 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 27468 | keep | 0 | Feb | 2022 | 0.018708 | 0.00017164 | Sustained | FALSE | FALSE | TMED_Event | 252
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 2147 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 234023 | keep | 0 | Feb | 2022 | 0.15939 | 0.0014623 | Sustained | FALSE | FALSE | TMED_Event | 2147
BAYAMON | 2022-02-21 13:19 | 2022-02-21 15:08 | 2858 | 001:49 | S | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 109 | 2022-02-21 | 311522 | keep | 0 | Feb | 2022 | 0.21218 | 0.0019466 | Sustained | FALSE | FALSE | TMED_Event | 2858
CAGUAS | 2022-02-21 13:34 | 2022-02-21 15:17 | 70 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | C22022100094 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-02-21 | 7210 | keep | 0 | Feb | 2022 | 0.0049107 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
PONCE | 2022-02-21 14:15 | 2022-02-21 14:18 | 1556 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P22022100042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-21 | 4668 | keep | 0 | Feb | 2022 | 0.0031794 | 0.0010598 | Momentary | FALSE | FALSE | TMED_Event | 1556
BAYAMON | 2022-02-21 14:24 | 2022-02-22 12:29 | 25 | 022:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22022100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1325 | 2022-02-21 | 33125 | keep | 0 | Feb | 2022 | 0.022561 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
CAGUAS | 2022-02-21 14:40 | 2022-02-21 14:41 | 718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | C22022100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-21 | 718 | keep | 0 | Feb | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | TMED_Event | 718
ARECIBO | 2022-02-21 14:40 | 2022-02-21 15:00 | 10 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22022100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-02-21 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2022-02-21 14:41 | 2022-02-21 17:29 | 200 | 002:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN C/L CRUCE POR GATO | C22022100122 | 1st_after_momentary |  |  | Include | Wildlife | 168 | 2022-02-21 | 33600 | keep | 0 | Feb | 2022 | 0.022885 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
AGUADILLA | 2022-02-21 14:45 | 2022-02-21 14:46 | 3041 | 000:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | M22022100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-21 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | TMED_Event | 3041
AGUADILLA | 2022-02-21 14:46 | 2022-02-21 15:53 | 3041 | 001:07 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE ABRIO MACHETES PARA SECCIONALIZAR BAMBUA SOBRE LINEA Y SE CERRO EL INTERRUPTOR | M22022100037 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-02-21 | 203747 | keep | 0 | Feb | 2022 | 0.13877 | 0.0020712 | Sustained | FALSE | FALSE | TMED_Event | 3041
SAN JUAN | 2022-02-21 14:54 | 2022-02-22 09:13 | 1061 | 018:19 | T | DESCONECTIVO DEFECTUOSO | DISPARO LOCALMENTE CON INDICACION POR SCADA CERRADO TIENIA (HMA) DAÃ‘ADO SE PASO PARTE AL 1301-3 | S22022100561 | New_Event | Switch Failure | Include | Include | Equipment | 1099 | 2022-02-21 | 1166039 | keep | 0 | Feb | 2022 | 0.79418 | 0.00072264 | Sustained | FALSE | FALSE | TMED_Event | 1061
SAN JUAN | 2022-02-21 14:54 | 2022-02-21 15:54 | 500 | 001:00 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. SU CARGA POR 1424-8 | S22022100000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 60 | 2022-02-21 | 30000 | keep | 0 | Feb | 2022 | 0.020433 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-02-21 14:54 | 2022-02-21 14:57 | 383 | 000:03 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO APAGON EN EL AREA NORTE Y ESTE DE LA ISLA. 95% DE SU CARGA TRANSFERIDA AL 1620-01 | S22022100000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 3 | 2022-02-21 | 1149 | keep | 0 | Feb | 2022 | 0.00078258 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2022-02-21 15:00 | 2022-02-21 15:27 | 20 | 000:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022100023 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 27 | 2022-02-21 | 540 | keep | 0 | Feb | 2022 | 0.00036779 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
VEGA BAJA | 2022-02-21 15:04 | 2022-02-21 20:26 | 10 | 005:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22022000374 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 322 | 2022-02-21 | 3220 | keep | 0 | Feb | 2022 | 0.0021931 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-02-21 15:07 | 2022-02-21 21:08 | 20 | 006:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA FUERTE | B22022100042 | New_Event | Bad Weather | Include | Include | Weather | 361 | 2022-02-21 | 7220 | keep | 0 | Feb | 2022 | 0.0049175 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2022-02-21 15:08 | 2022-02-21 19:47 | 25 | 004:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22022000342 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-02-21 | 6975 | keep | 0 | Feb | 2022 | 0.0047506 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-02-21 15:23 | 2022-02-21 15:39 | 30 | 000:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE AISLADOR Y RETEZAR LINEA PRIMARIA | R22021600052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 16 | 2022-02-21 | 480 | keep | 0 | Feb | 2022 | 0.00032693 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
CANOVANAS | 2022-02-21 15:32 | 2022-02-21 15:46 | 30 | 000:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022100136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-02-21 | 420 | keep | 0 | Feb | 2022 | 0.00028606 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
UTUADO | 2022-02-21 15:36 | 2022-02-21 15:37 | 1054 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A22022100067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 1054 | keep | 0 | Feb | 2022 | 0.00071787 | 0.00071787 | Momentary | FALSE | FALSE | TMED_Event | 1054
CAGUAS | 2022-02-21 15:39 | 2022-02-21 18:15 | 25 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C22022100000 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-02-21 | 3900 | keep | 0 | Feb | 2022 | 0.0026563 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
CANOVANAS | 2022-02-21 15:41 | 2022-02-21 18:00 | 25 | 002:19 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022100026 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-02-21 | 3475 | keep | 0 | Feb | 2022 | 0.0023668 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-02-21 15:46 | 2022-02-21 17:46 | 418 | 002:00 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO SU-20 A MH-22 Y SE TRANSFIRIO 75% DE LA CARGA AL 1014-16 | S22022100382 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2022-02-21 | 50160 | keep | 0 | Feb | 2022 | 0.034164 | 0.0002847 | Sustained | FALSE | FALSE | TMED_Event | 418
BAYAMON | 2022-02-21 15:48 | 2022-02-21 16:22 | 453 | 000:34 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 10% DE SU CARGA POR 1806-02. LLEVA CARGA 1717-05 | B22022100000 | Partial_restoration | 230 kV Transmission Line Source | Include | Include | Power Supply | 34 | 2022-02-21 | 15402 | keep | 0 | Feb | 2022 | 0.01049 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
AGUADILLA | 2022-02-21 15:53 | 2022-02-21 16:37 | 500 | 000:44 | P | DESGANCHE | SE RETIRO BAMBUA Y SE CERRO LOS MACHETES QUE SE ABRIERON PARA SECCIONALIZAR AVERIA | M22022100037 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-02-21 | 22000 | keep | 0 | Feb | 2022 | 0.014984 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-02-21 15:56 | 2022-02-21 22:41 | 10 | 006:45 | P | NO SE REPORTO CAUSA | 1X20 EN TRANSCLOSURE DE CLIENTE | S22022100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 405 | 2022-02-21 | 4050 | keep | 0 | Feb | 2022 | 0.0027584 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2022-02-21 16:00 | 2022-02-21 16:54 | 3 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA AJUSTAR VOLTAJE SECUNDARIO Y REPARAR BAJANTE SECUNDARIO | A22022100068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-02-21 | 162 | keep | 0 | Feb | 2022 | 0.00011034 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
CAGUAS | 2022-02-21 16:01 | 2022-02-21 18:17 | 25 | 002:16 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | C22022100118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-02-21 | 3400 | keep | 0 | Feb | 2022 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BARRANQUITAS | 2022-02-21 16:01 | 2022-02-21 19:10 | 50 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22022100117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-02-21 | 9450 | keep | 0 | Feb | 2022 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
MAYAGÃœEZ | 2022-02-21 16:41 | 2022-02-21 19:08 | 70 | 002:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22022100051 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2022-02-21 | 10290 | keep | 0 | Feb | 2022 | 0.0070085 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
ARECIBO | 2022-02-21 16:52 | 2022-02-21 17:32 | 80 | 000:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22022100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-02-21 | 3200 | keep | 0 | Feb | 2022 | 0.0021795 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
MAYAGÃœEZ | 2022-02-21 17:03 | 2022-02-21 21:20 | 50 | 004:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22022100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2022-02-21 | 12850 | keep | 0 | Feb | 2022 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
SAN JUAN | 2022-02-21 17:14 | 2022-02-21 17:15 | 3 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22022100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-21 | 3 | keep | 0 | Feb | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | TMED_Event | 3
AGUADILLA | 2022-02-21 17:27 | 2022-02-21 18:05 | 10 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22022100063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-02-21 | 380 | keep | 0 | Feb | 2022 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2022-02-21 17:29 | 2022-02-21 17:30 | 718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | C22022100000 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-02-21 | 718 | keep | 0 | Feb | 2022 | 0.00048903 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-02-21 17:30 | 2022-02-21 17:40 | 200 | 000:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN C/L CRUCE POR GATO | C22022100122 | 1st_after_momentary |  |  | Include | Wildlife | 10 | 2022-02-21 | 2000 | keep | 0 | Feb | 2022 | 0.0013622 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
ARECIBO | 2022-02-21 17:31 | 2022-02-21 19:14 | 12 | 001:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | A22022100093 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2022-02-21 | 1236 | keep | 0 | Feb | 2022 | 0.00084183 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BAYAMON | 2022-02-21 17:32 | 2022-02-21 23:59 | 80 | 006:27 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22022100563 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 387 | 2022-02-21 | 30960 | keep | 0 | Feb | 2022 | 0.021087 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
MAYAGÃœEZ | 2022-02-21 17:33 | 2022-02-21 22:45 | 50 | 005:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22022100065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-02-21 | 15600 | keep | 0 | Feb | 2022 | 0.010625 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-02-21 17:33 | 2022-02-21 18:29 | 30 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22022100453 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2022-02-21 | 1680 | keep | 0 | Feb | 2022 | 0.0011442 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
ARECIBO | 2022-02-21 17:35 | 2022-02-21 18:39 | 1105 | 001:04 | T | DESGANCHE | SE ABRIO MACHETES PARA CONTINUAR PATRULLANDO | A22022100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-02-21 | 70720 | keep | 0 | Feb | 2022 | 0.048167 | 0.00075261 | Sustained | FALSE | FALSE | TMED_Event | 1105
BAYAMON | 2022-02-21 17:46 | 2022-02-21 18:59 | 105 | 001:13 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO INTERRUPTOR | S22022100382 | Partial_restoration | Switch Failure | Include | Include | Equipment | 73 | 2022-02-21 | 7665 | keep | 0 | Feb | 2022 | 0.0052206 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-02-21 18:05 | 2022-02-21 18:06 | 718 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION DE REINER LICIAGA SE SECCIONALIZO CONDUCTOR PRIMARIO ABIERTO | C22022100071 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-21 | 718 | keep | 0 | Feb | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | TMED_Event | 718
CAGUAS | 2022-02-21 18:06 | 2022-02-21 19:49 | 600 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR PRIMARIO ABIERTO | C22022100071 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 103 | 2022-02-21 | 61800 | keep | 0 | Feb | 2022 | 0.042092 | 0.00040866 | Sustained | FALSE | FALSE | TMED_Event | 600
BAYAMON | 2022-02-21 18:15 | 2022-02-21 22:41 | 50 | 004:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X100 EN CORTE DE LINEA Y SE LLEVO ALAMBRE PRIMARIO A SU LUGAR SE HABIA SOLTADO DE LA CAJA | B22022100479 | New_Event | Wire Down | Include | Include | Equipment | 266 | 2022-02-21 | 13300 | keep | 0 | Feb | 2022 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-02-21 18:15 | 2022-02-21 23:42 | 170 | 005:27 | P | NO SE REPORTO CAUSA | 1X100 EN CORTE DE LINEA Y 1X65 EN EL MISMO CORTE DE LINEA | B22022100480 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2022-02-21 | 55590 | keep | 0 | Feb | 2022 | 0.037862 | 0.00011579 | Sustained | FALSE | FALSE | TMED_Event | 170
SAN JUAN | 2022-02-21 18:29 | 2022-02-21 18:32 | 2565 | 000:03 | P | CABLE SOTERRADO AVERIADO | SE ABRIO N/O PARA NORMALIZAR CARGAS | S22022100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2022-02-21 | 7695 | keep | 0 | Feb | 2022 | 0.005241 | 0.001747 | Momentary | FALSE | FALSE | TMED_Event | 2565
SAN JUAN | 2022-02-21 18:29 | 2022-02-21 19:20 | 17 | 000:51 | T | CABLE SOTERRADO AVERIADO | SE REMPLAZO SALIDA SOTERRADO Y SE NORMALIZO CARGA | S22022100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 51 | 2022-02-21 | 867 | keep | 0 | Feb | 2022 | 0.00059051 | 1.1579e-05 | Sustained | FALSE | FALSE | TMED_Event | 17
HUMACAO | 2022-02-21 18:31 | 2022-02-21 20:51 | 45 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y X 50 EN C/L CRUCE POR AVE | C22022100180 | New_Event |  |  | Include | Wildlife | 140 | 2022-02-21 | 6300 | keep | 0 | Feb | 2022 | 0.0042909 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
ARECIBO | 2022-02-21 18:39 | 2022-02-21 19:13 | 300 | 000:34 | P | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS PRIMARIAS Y SE CERRO MACHETES | A22022100095 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 34 | 2022-02-21 | 10200 | keep | 0 | Feb | 2022 | 0.0069472 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-02-21 18:59 | 2022-02-21 19:28 | 84 | 000:29 | P | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR DEL MH-9A A MH-14 CALLE COMERCIO | S22022100382 | Partial_restoration | Switch Failure | Include | Include | Equipment | 29 | 2022-02-21 | 2436 | keep | 0 | Feb | 2022 | 0.0016591 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BARRANQUITAS | 2022-02-21 19:12 | 2022-02-22 09:06 | 50 | 013:54 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22022100198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 834 | 2022-02-21 | 41700 | keep | 0 | Feb | 2022 | 0.028402 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
CAGUAS | 2022-02-21 19:18 | 2022-02-21 21:24 | 120 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22022100203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-02-21 | 15120 | keep | 0 | Feb | 2022 | 0.010298 | 8.1731e-05 | Sustained | FALSE | FALSE | TMED_Event | 120
BAYAMON | 2022-02-21 19:28 | 2022-02-21 19:51 | 63 | 000:23 | P | CABLE SOTERRADO AVERIADO | ALIMENTADOR SECCIONALIZADO | S22022100382 | New_Event | UG Cable Fault | Include | Include | Equipment | 23 | 2022-02-21 | 1449 | keep | 0 | Feb | 2022 | 0.00098691 | 4.2909e-05 | Sustained | FALSE | FALSE | TMED_Event | 63
MAYAGÃœEZ | 2022-02-21 19:34 | 2022-02-22 03:50 | 5 | 008:16 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIA Y VIENTO | M22022100095 | New_Event | Bad Weather | Include | Include | Weather | 496 | 2022-02-21 | 2480 | keep | 0 | Feb | 2022 | 0.0016891 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
UTUADO | 2022-02-21 19:35 | 2022-02-22 09:28 | 40 | 013:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRARON BAMBUAS SOBRE LA LINEA | A22022100115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 833 | 2022-02-21 | 33320 | keep | 0 | Feb | 2022 | 0.022694 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BAYAMON | 2022-02-21 19:36 | 2022-02-22 12:04 | 15 | 016:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU 4 | B22022100501 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 988 | 2022-02-21 | 14820 | keep | 0 | Feb | 2022 | 0.010094 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2022-02-21 19:37 | 2022-02-21 20:22 | 60 | 000:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022100245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-02-21 | 2700 | keep | 0 | Feb | 2022 | 0.001839 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
HUMACAO | 2022-02-21 19:43 | 2022-02-22 09:40 | 60 | 013:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22022100212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 837 | 2022-02-21 | 50220 | keep | 0 | Feb | 2022 | 0.034205 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
MAYAGÃœEZ | 2022-02-21 19:50 | 2022-02-22 00:20 | 90 | 004:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA EN CORTE DE LINEA | M22022100102 | New_Event | Cutout Failure | Include | Include | Equipment | 270 | 2022-02-21 | 24300 | keep | 0 | Feb | 2022 | 0.016551 | 6.1299e-05 | Sustained | FALSE | FALSE | TMED_Event | 90
BAYAMON | 2022-02-21 19:51 | 2022-02-21 19:52 | 105 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR MH-9A A MH-16 | S22022100382 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-02-21 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 7.1515e-05 | Momentary | FALSE | FALSE | TMED_Event | 105
BAYAMON | 2022-02-21 19:52 | 2022-02-21 19:58 | 63 | 000:06 | P | DESCONECTIVO DEFECTUOSO | ALIMENTADOR SECCIONALIZADO | S22022100382 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 6 | 2022-02-21 | 378 | keep | 0 | Feb | 2022 | 0.00025745 | 4.2909e-05 | Sustained | FALSE | FALSE | TMED_Event | 63
ARECIBO | 2022-02-21 19:57 | 2022-02-22 08:27 | 50 | 012:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES LLUVIAS | A22022100118 | New_Event | Bad Weather | Include | Include | Weather | 750 | 2022-02-21 | 37500 | keep | 0 | Feb | 2022 | 0.025541 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-02-21 19:58 | 2022-02-21 19:59 | 105 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR MH-20 A MH-16 75% POR 1014-16 | S22022100382 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-02-21 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
VEGA BAJA | 2022-02-21 20:09 | 2022-02-22 09:55 | 20 | 013:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22022100508 | New_Event | Vegetation Contact | Include | Include | Vegetation | 826 | 2022-02-21 | 16520 | keep | 0 | Feb | 2022 | 0.011252 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
VEGA BAJA | 2022-02-21 20:10 | 2022-02-22 16:25 | 12 | 020:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37 KVA Y SE RETEZO NEUTRAL PRIMARIO | B20222100509 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1215 | 2022-02-21 | 14580 | keep | 0 | Feb | 2022 | 0.0099304 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CANOVANAS | 2022-02-21 20:16 | 2022-02-21 22:15 | 150 | 001:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO 2 CAJAS AVERIADAS | R22022100252 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2022-02-21 | 17850 | keep | 0 | Feb | 2022 | 0.012158 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
BAYAMON | 2022-02-21 20:18 | 2022-02-22 10:38 | 86 | 014:20 | P | DESGANCHE | SE REPUSO 1 X 50 EN CORTE DE LINEA PRINCIPAL Y SE DEJO CORTE DE LINEA INTERMEDIO ABIERTO PARA REALIZAR DESGANCHE. SE QUEDARON 36 CLIENTES FUERA | B22022100511 | New_Event | Vegetation Contact | Include | Include | Vegetation | 860 | 2022-02-21 | 73960 | keep | 0 | Feb | 2022 | 0.050374 | 5.8574e-05 | Sustained | FALSE | FALSE | TMED_Event | 86
BAYAMON | 2022-02-21 20:30 | 2022-02-21 20:31 | 313 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO DEL 1014-16 QUE ESTA LLEVANDO 75% DE LA CARGA DEL 1013-13 | S22022100382 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-02-21 | 313 | keep | 0 | Feb | 2022 | 0.00021318 | 0.00021318 | Momentary | FALSE | FALSE | TMED_Event | 313
BAYAMON | 2022-02-21 20:30 | 2022-02-21 20:31 | 295 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR MH-20 A MH-16 LLEVA 75% DEL 1013-13 | S22022100382 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-02-21 | 295 | keep | 0 | Feb | 2022 | 0.00020092 | 0.00020092 | Momentary | FALSE | FALSE | TMED_Event | 295
AGUADILLA | 2022-02-21 20:52 | 2022-02-21 22:42 | 470 | 001:50 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO CONECTOR DE PLANCHA AVERIADO EN AUXILIAR DE BARRA | M22022100062 | New_Event | Switch Failure | Include | Include | Equipment | 110 | 2022-02-21 | 51700 | keep | 0 | Feb | 2022 | 0.035213 | 0.00032011 | Sustained | FALSE | FALSE | TMED_Event | 470
AGUADILLA | 2022-02-21 20:52 | 2022-02-21 22:42 | 1345 | 001:50 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO CONECTOR DE PLANCHA AVERIADO EN AUXILIAR DE BARRA DEL 7003-01 QUE ESTA LLEVANDO LA CARGA DEL 7003-02 | M22022100062 | New_Event | Switch Failure | Include | Include | Equipment | 110 | 2022-02-21 | 147950 | keep | 0 | Feb | 2022 | 0.10077 | 0.00091607 | Sustained | FALSE | FALSE | TMED_Event | 1345
BAYAMON | 2022-02-21 21:04 | 2022-02-21 21:05 | 313 | 000:01 | P | CABLE SOTERRADO AVERIADO | DISPARO DEL 1014-16 QUE ESTA LLEVANDO 75% DE LA CARGA DEL 1013-13 | S22022100382 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-02-21 | 313 | keep | 0 | Feb | 2022 | 0.00021318 | 0.00021318 | Momentary | FALSE | FALSE | TMED_Event | 313
BAYAMON | 2022-02-21 21:04 | 2022-02-21 21:05 | 295 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR MH-16 AL MH-14 LLEVA 75% DEL 1013-13 | S22022100382 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2022-02-21 | 295 | keep | 0 | Feb | 2022 | 0.00020092 | 0.00020092 | Momentary | FALSE | FALSE | TMED_Event | 295
BAYAMON | 2022-02-21 21:05 | 2022-02-21 21:16 | 63 | 000:11 | P | DESCONECTIVO DEFECTUOSO | ALIMENTADOR SECCIONALIZADO | S22022100382 | New_Event | Switch Failure | Include | Include | Equipment | 11 | 2022-02-21 | 693 | keep | 0 | Feb | 2022 | 0.000472 | 4.2909e-05 | Sustained | FALSE | FALSE | TMED_Event | 63
BAYAMON | 2022-02-21 21:06 | 2022-02-21 21:07 | 500 | 000:01 | P | LINEA DE TRANSMISION | BAJO INVESTIGACION. DISTURBIO EN EL SISTEMA CAUSO INTERRUPCION EN EL SISTEMA ELECTRICO EN EL AREA NORTE Y ESTE DE LA ISLA. 1711 -03 LLEVA PARTE 1716-03 | B22022100000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-02-21 | 500 | keep | 0 | Feb | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | TMED_Event | 500
BAYAMON | 2022-02-21 21:16 | 2022-02-22 17:15 | 4 | 019:59 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO V.S. MH-14 Y SE DEJO N/O EN MH-16 100% EN SERVICIO | S22022100382 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1199 | 2022-02-21 | 4796 | keep | 0 | Feb | 2022 | 0.0032665 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
UTUADO | 2022-02-21 21:37 | 2022-02-22 13:27 | 6 | 015:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REEMPLAZARON CAJAS PRIMARIAS DE 100AMP | A22022100128 | New_Event | Cutout Failure | Include | Include | Equipment | 950 | 2022-02-21 | 5700 | keep | 0 | Feb | 2022 | 0.0038822 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
ARECIBO | 2022-02-21 21:52 | 2022-02-22 00:37 | 3 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22022100129 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2022-02-21 | 495 | keep | 0 | Feb | 2022 | 0.00033714 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
CAGUAS | 2022-02-21 21:58 | 2022-02-21 22:00 | 315 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22022100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-21 | 630 | keep | 0 | Feb | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | TMED_Event | 315
FAJARDO | 2022-02-21 22:54 | 2022-02-22 09:03 | 15 | 010:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | R22022100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 609 | 2022-02-21 | 9135 | keep | 0 | Feb | 2022 | 0.0062218 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2022-02-21 23:31 | 2022-02-22 14:28 | 50 | 014:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22022100761 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 897 | 2022-02-21 | 44850 | keep | 0 | Feb | 2022 | 0.030547 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
ARECIBO | 2022-02-21 23:43 | 2022-02-22 07:22 | 10 | 007:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR FUERTES LLUVIAS | A22022100131 | New_Event | Bad Weather | Include | Include | Weather | 459 | 2022-02-21 | 4590 | keep | 0 | Feb | 2022 | 0.0031262 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2022-02-21 23:45 | 2022-02-22 08:08 | 2 | 008:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR Y 1 X 20 EN CORTE DE LINEA POR FUERTES LLUVIAS | A22022100132 | New_Event | Bad Weather | Include | Include | Weather | 503 | 2022-02-21 | 1006 | keep | 0 | Feb | 2022 | 0.00068518 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
CAGUAS | 2022-02-22 01:48 | 2022-02-22 10:23 | 9 | 008:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA POR CAMION | C22022200019 | New_Event |  |  | Include | Wildlife | 515 | 2022-02-22 | 4635 | keep | 0 | Feb | 2022 | 0.0031569 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-02-22 01:48 | 2022-02-22 17:56 | 180 | 016:08 | P | DESGANCHE | 2 X 65 EN C/L SE RETIRO ARBOL SOBRE LINEA Y SE REEMPLAZARON 2 POSTES PARTIDOS | C22022200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 968 | 2022-02-22 | 174240 | keep | 0 | Feb | 2022 | 0.11867 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BARRANQUITAS | 2022-02-22 02:53 | 2022-02-22 02:54 | 3565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 3565 | keep | 0 | Feb | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
CAGUAS | 2022-02-22 03:45 | 2022-02-22 09:18 | 10 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22022200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2022-02-22 | 3330 | keep | 0 | Feb | 2022 | 0.002268 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-22 04:23 | 2022-02-22 04:24 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-22 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
MAYAGÃœEZ | 2022-02-22 04:40 | 2022-02-22 04:41 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22022200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 2999 | keep | 0 | Feb | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
FAJARDO | 2022-02-22 05:15 | 2022-02-22 05:16 | 693 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22022200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-22 | 693 | keep | 0 | Feb | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
FAJARDO | 2022-02-22 05:16 | 2022-02-22 12:21 | 100 | 007:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | R22022200009 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 425 | 2022-02-22 | 42500 | keep | 0 | Feb | 2022 | 0.028947 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-22 05:35 | 2022-02-22 05:36 | 316 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A22022200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-22 | 316 | keep | 0 | Feb | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-02-22 05:36 | 2022-02-22 09:39 | 11 | 004:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A22022200002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-02-22 | 2673 | keep | 0 | Feb | 2022 | 0.0018206 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-02-22 06:05 | 2022-02-22 09:37 | 20 | 003:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | R22022200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2022-02-22 | 4240 | keep | 0 | Feb | 2022 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-02-22 06:10 | 2022-02-22 09:40 | 55 | 003:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22022200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-02-22 | 11550 | keep | 0 | Feb | 2022 | 0.0078667 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-02-22 06:37 | 2022-02-22 06:38 | 17 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 17 | keep | 0 | Feb | 2022 | 1.1579e-05 | 1.1579e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2022-02-22 06:58 | 2022-02-22 09:07 | 7 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTA CAUSA | P22022200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-02-22 | 903 | keep | 0 | Feb | 2022 | 0.00061503 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-02-22 07:08 | 2022-02-22 09:13 | 15 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R22022200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-02-22 | 1875 | keep | 0 | Feb | 2022 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-22 07:16 | 2022-02-22 15:31 | 5 | 008:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA SE RETIRO IGUANA CRUZANDO LINEAS | B22022200003 | New_Event |  |  | Include | Wildlife | 495 | 2022-02-22 | 2475 | keep | 0 | Feb | 2022 | 0.0016857 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-22 07:17 | 2022-02-22 19:15 | 13 | 011:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE LEVANTO PRIMARIA Y SE DESGANCHO | S22022200027 | New_Event | Wire Down | Include | Include | Equipment | 718 | 2022-02-22 | 9334 | keep | 0 | Feb | 2022 | 0.0063573 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-02-22 07:45 | 2022-02-22 14:28 | 1 | 006:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 25 EN BANCO DE TRANSFORMADOR SE CERRO PUENTE DE LINEA A CAJA | B22022200004 | New_Event | Wire Down | Include | Include | Equipment | 403 | 2022-02-22 | 403 | keep | 0 | Feb | 2022 | 0.00027448 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-22 07:45 | 2022-02-22 11:55 | 1 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | M22022200003 | New_Event |  |  | Include | Wildlife | 250 | 2022-02-22 | 250 | keep | 0 | Feb | 2022 | 0.00017027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-22 08:01 | 2022-02-22 14:36 | 6 | 006:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 15 EN BOVEDA | B22022200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2022-02-22 | 2370 | keep | 0 | Feb | 2022 | 0.0016142 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-22 08:07 | 2022-02-22 10:26 | 35 | 002:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M22022200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-02-22 | 4865 | keep | 0 | Feb | 2022 | 0.0033135 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-02-22 08:12 | 2022-02-22 10:16 | 130 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR CONTACTO DE AVE | P22022200008 | New_Event |  |  | Include | Wildlife | 124 | 2022-02-22 | 16120 | keep | 0 | Feb | 2022 | 0.010979 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2022-02-22 08:31 | 2022-02-22 18:06 | 15 | 009:35 | P | LINEA DE TRANSMISION 115KV | SE ABRIO CORTE DE LINEA PARA QUE INGENIERIA TRABAJE EN LINEA 36100 | A22022200009 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 575 | 2022-02-22 | 8625 | keep | 0 | Feb | 2022 | 0.0058744 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-02-22 08:37 | 2022-02-22 09:01 | 1 | 000:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN C/L CULEBRA | R22022200013 | New_Event |  |  | Include | Wildlife | 24 | 2022-02-22 | 24 | keep | 0 | Feb | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-22 08:47 | 2022-02-22 15:01 | 20 | 006:14 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S22022200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 374 | 2022-02-22 | 7480 | keep | 0 | Feb | 2022 | 0.0050946 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-22 09:12 | 2022-02-22 20:40 | 30 | 011:28 | P | DESGANCHE | 3 X 80 Y 3 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22022200070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 688 | 2022-02-22 | 20640 | keep | 0 | Feb | 2022 | 0.014058 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-22 09:13 | 2022-02-22 10:04 | 877 | 000:51 | P | DESCONECTIVO DEFECTUOSO | DISPARO LOCALMENTE CON INDICACION POR SCADA CERRADO TIENIA (HMA) DAÃ‘ADO SE PASO PARTE POR 1335-1 | S22022100561 | New_Event | Switch Failure | Include | Include | Equipment | 51 | 2022-02-22 | 44727 | keep | 0 | Feb | 2022 | 0.030463 | 0.00059732 | Sustained | FALSE | FALSE | Not_TMED_Event | 877
SAN JUAN | 2022-02-22 09:29 | 2022-02-22 15:42 | 12 | 006:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA | S22022200062 | New_Event | Cutout Failure | Include | Include | Equipment | 373 | 2022-02-22 | 4476 | keep | 0 | Feb | 2022 | 0.0030486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-02-22 09:29 | 2022-02-22 12:27 | 15 | 002:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R22022200009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 178 | 2022-02-22 | 2670 | keep | 0 | Feb | 2022 | 0.0018185 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-22 09:37 | 2022-02-22 14:10 | 15 | 004:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA AVERIADO | R22022200019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 273 | 2022-02-22 | 4095 | keep | 0 | Feb | 2022 | 0.0027891 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-02-22 09:42 | 2022-02-22 12:47 | 50 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO CAUSA | C22022200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-02-22 | 9250 | keep | 0 | Feb | 2022 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-22 09:48 | 2022-02-22 13:20 | 40 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22022200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-02-22 | 8480 | keep | 0 | Feb | 2022 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-22 09:55 | 2022-02-22 09:56 | 492 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR 1719-16 AL HACER PRUEBA DE SU HACIA SUBESTACION PRIVADA ( UNIVERSIDAD INTERAMERICANA) | B22022200000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-02-22 | 492 | keep | 0 | Feb | 2022 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
SAN JUAN | 2022-02-22 10:04 | 2022-02-22 10:30 | 312 | 000:26 | P | DESCONECTIVO DEFECTUOSO | DISPARO LOCALMENTE CON INDICACION POR SCADA CERRADO TIENIA (HMA) DAÃ‘ADO SE PASO PARTE POR 1652-4 | S22022100561 | New_Event | Switch Failure | Include | Include | Equipment | 26 | 2022-02-22 | 8112 | keep | 0 | Feb | 2022 | 0.005525 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
HUMACAO | 2022-02-22 10:20 | 2022-02-22 10:44 | 1 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER @ TRANSCLOSURE NO CAUSA | C22022200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-02-22 | 24 | keep | 0 | Feb | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-02-22 10:22 | 2022-02-22 16:25 | 40 | 006:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA PRIMARIA | A22022200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2022-02-22 | 14520 | keep | 0 | Feb | 2022 | 0.0098895 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-22 10:38 | 2022-02-22 12:22 | 36 | 001:44 | P | DESGANCHE | SE REPUSO 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22022100511 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-02-22 | 3744 | keep | 0 | Feb | 2022 | 0.00255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-02-22 10:43 | 2022-02-22 11:25 | 25 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22022200016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-02-22 | 1050 | keep | 0 | Feb | 2022 | 0.00071515 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-22 10:57 | 2022-02-22 13:42 | 1 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C22022200044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-02-22 | 165 | keep | 0 | Feb | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-02-22 11:08 | 2022-02-22 13:53 | 5 | 002:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | P22022200017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 165 | 2022-02-22 | 825 | keep | 0 | Feb | 2022 | 0.0005619 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-22 11:09 | 2022-02-22 11:10 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
PONCE | 2022-02-22 11:14 | 2022-02-22 11:55 | 1 | 000:41 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN MONTURA TRIFASICA POR PARARRAYO DEFECTUOSO | P22022200019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 41 | 2022-02-22 | 41 | keep | 0 | Feb | 2022 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-22 11:42 | 2022-02-22 11:43 | 100 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 1 X 40 EN C/L NO CAUSA | R22022200021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 100 | keep | 0 | Feb | 2022 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-02-22 11:46 | 2022-02-22 15:46 | 20 | 004:00 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22022200189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-02-22 | 4800 | keep | 0 | Feb | 2022 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-22 12:04 | 2022-02-22 12:06 | 3798 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22022200031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-22 | 7596 | keep | 0 | Feb | 2022 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
SAN JUAN | 2022-02-22 12:09 | 2022-02-22 23:57 | 1 | 011:48 | P | NO SE REPORTO CAUSA | 2X25 EN BANCO DE TRANSFORMADORES | S22022200091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 708 | 2022-02-22 | 708 | keep | 0 | Feb | 2022 | 0.00048222 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-02-22 12:09 | 2022-02-22 14:11 | 20 | 002:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR ROTO | C22022200062 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 122 | 2022-02-22 | 2440 | keep | 0 | Feb | 2022 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-22 12:11 | 2022-02-22 13:54 | 100 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | M22022200033 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-02-22 | 10300 | keep | 0 | Feb | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-22 12:16 | 2022-02-22 22:30 | 60 | 010:14 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU 14A Y 1 X 30 EN C/L CONSTRUYO AEREO PROVICIONAL | R22022200035 | New_Event | UG Cable Fault | Include | Include | Equipment | 614 | 2022-02-22 | 36840 | keep | 0 | Feb | 2022 | 0.025092 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-02-22 12:22 | 2022-02-22 13:46 | 1089 | 001:24 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 3000 JUNCOS @ RIO BLANCO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-02-22 | 91476 | keep | 0 | Feb | 2022 | 0.062304 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-02-22 12:22 | 2022-02-22 13:46 | 3896 | 001:24 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 3000 JUNCOS @ RIO BLANCO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-02-22 | 327264 | keep | 0 | Feb | 2022 | 0.2229 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-02-22 12:22 | 2022-02-22 13:46 | 1467 | 001:24 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 3000 JUNCOS @ RIO BLANCO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-02-22 | 123228 | keep | 0 | Feb | 2022 | 0.08393 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
PONCE | 2022-02-22 12:27 | 2022-02-22 14:16 | 1 | 001:49 | P | PARARRAYOS DEFECTUOSO | 4 X 50 EN RISER 3 X 65 EN CORTE DE LINEA SE ELIMINO PARARRAYO CRUZADO | P22022200023 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 109 | 2022-02-22 | 109 | keep | 0 | Feb | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 1153 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 2306 | keep | 0 | Feb | 2022 | 0.0015706 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 1709 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 3418 | keep | 0 | Feb | 2022 | 0.002328 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 1320 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 2640 | keep | 0 | Feb | 2022 | 0.0017981 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 2276 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 4552 | keep | 0 | Feb | 2022 | 0.0031003 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 777 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 1554 | keep | 0 | Feb | 2022 | 0.0010584 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 12 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 24 | keep | 0 | Feb | 2022 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:35 | 1290 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-22 | 2580 | keep | 0 | Feb | 2022 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-02-22 12:33 | 2022-02-22 12:34 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 1702 | keep | 0 | Feb | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
VEGA BAJA | 2022-02-22 12:33 | 2022-02-22 13:43 | 10 | 001:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y SE REMPLAZO AISLADOR PRIMARIO | B22022200032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 70 | 2022-02-22 | 700 | keep | 0 | Feb | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-22 12:35 | 2022-02-22 13:31 | 1 | 000:56 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P22022200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-02-22 | 56 | keep | 0 | Feb | 2022 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-22 12:36 | 2022-02-23 11:19 | 12 | 022:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR SE REMPLAZO CAJA PRIMARIA | S22022200094 | New_Event | Cutout Failure | Include | Include | Equipment | 1363 | 2022-02-22 | 16356 | keep | 0 | Feb | 2022 | 0.01114 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-02-22 13:05 | 2022-02-22 13:06 | 108 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1203-3 | S22022200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-22 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-02-22 13:05 | 2022-02-22 13:06 | 616 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 1203-01 LLEVANDO 1203-3 | S22022200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-22 | 616 | keep | 0 | Feb | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-02-22 13:06 | 2022-02-22 22:23 | 50 | 009:17 | P | DESGANCHE | 1X100 EN CORTE DE LINEA | S22022200130 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 557 | 2022-02-22 | 27850 | keep | 0 | Feb | 2022 | 0.018969 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-02-22 13:22 | 2022-02-22 15:25 | 5 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO LA CAUSA | P22022200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-02-22 | 615 | keep | 0 | Feb | 2022 | 0.00041887 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-02-22 13:26 | 2022-02-23 10:05 | 448 | 020:39 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA Y SE CERRO PUENTE PRIMARIO | C22022200159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1239 | 2022-02-22 | 555072 | keep | 0 | Feb | 2022 | 0.37806 | 0.00030513 | Sustained | FALSE | FALSE | Not_TMED_Event | 448
CAGUAS | 2022-02-22 13:58 | 2022-02-22 15:51 | 30 | 001:53 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22022200189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-02-22 | 3390 | keep | 0 | Feb | 2022 | 0.0023089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-22 14:01 | 2022-02-22 21:44 | 72 | 007:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL | S22022200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2022-02-22 | 33336 | keep | 0 | Feb | 2022 | 0.022705 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2022-02-22 14:09 | 2022-02-22 17:10 | 30 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22022200109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-02-22 | 5430 | keep | 0 | Feb | 2022 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-02-22 14:13 | 2022-02-22 20:02 | 2 | 005:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22022200060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 349 | 2022-02-22 | 698 | keep | 0 | Feb | 2022 | 0.0004754 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-02-22 14:14 | 2022-02-22 15:04 | 9 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22022200061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-02-22 | 450 | keep | 0 | Feb | 2022 | 0.00030649 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2022-02-22 14:39 | 2022-02-22 17:14 | 20 | 002:35 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22022200204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-02-22 | 3100 | keep | 0 | Feb | 2022 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-22 14:45 | 2022-02-22 14:46 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE INTERRUPTOR LINEAS CRUZADAS POR GLOBO | M22022200000 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-22 | 4641 | keep | 0 | Feb | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-02-22 14:46 | 2022-02-22 17:00 | 150 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA LINEAS CUZADAS POR GLOBO | M22022200065 | 1st_after_momentary |  |  | Include | Wildlife | 134 | 2022-02-22 | 20100 | keep | 0 | Feb | 2022 | 0.01369 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-02-22 15:26 | 2022-02-22 16:06 | 10 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO SECUNDARIA | A22022200038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-02-22 | 400 | keep | 0 | Feb | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-02-22 15:42 | 2022-02-22 18:48 | 40 | 003:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-02-22 | 7440 | keep | 0 | Feb | 2022 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-22 15:49 | 2022-02-22 18:40 | 25 | 002:51 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22022200219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-02-22 | 4275 | keep | 0 | Feb | 2022 | 0.0029117 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-02-22 16:03 | 2022-02-22 17:26 | 40 | 001:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022200049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-02-22 | 3320 | keep | 0 | Feb | 2022 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-22 16:05 | 2022-02-23 12:01 | 22 | 019:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22022200228 | New_Event | Bad Weather | Include | Include | Weather | 1196 | 2022-02-22 | 26312 | keep | 0 | Feb | 2022 | 0.017921 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2022-02-22 16:18 | 2022-02-22 22:41 | 10 | 006:23 | P | DESGANCHE | 1X20 EN TRANSFORMADOR | S22022200124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-02-22 | 3830 | keep | 0 | Feb | 2022 | 0.0026086 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-02-22 16:21 | 2022-02-22 19:23 | 18 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO PUENTE PRIMARIO A CAJA DE TRANSFORMADOR | P22022200041 | New_Event | Wire Down | Include | Include | Equipment | 182 | 2022-02-22 | 3276 | keep | 0 | Feb | 2022 | 0.0022313 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-02-22 16:22 | 2022-02-22 19:26 | 45 | 003:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA | P22022200042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-02-22 | 8280 | keep | 0 | Feb | 2022 | 0.0056395 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-02-22 16:29 | 2022-02-22 18:14 | 1 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO HACIA BOMBAS AAA | B22022200048 | New_Event | Wire Down | Include | Include | Equipment | 105 | 2022-02-22 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-22 16:34 | 2022-02-22 21:05 | 256 | 004:31 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE REMPLAZO MACHETE QUEMADO AVE. BARTOLOME DE LAS CASAS Y SE CERRO INTERRUPTOR 10% POR 1118-10 | S22022200204 | New_Event | Switch Failure | Include | Include | Equipment | 271 | 2022-02-22 | 69376 | keep | 0 | Feb | 2022 | 0.047252 | 0.00017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 256
SAN JUAN | 2022-02-22 16:34 | 2022-02-22 21:05 | 2782 | 004:31 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE REMPLAZO MACHETE QUEMADO AVE. BARTOLOME DE LAS CASAS Y SE CERRO INTERRUPTOR | S22022200204 | New_Event | Switch Failure | Include | Include | Equipment | 271 | 2022-02-22 | 753922 | keep | 0 | Feb | 2022 | 0.51349 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
CAGUAS | 2022-02-22 16:34 | 2022-02-23 14:31 | 30 | 021:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE RETEZO LINEA PRIMARIA | C22022200236 | New_Event | Wire Down | Include | Include | Equipment | 1317 | 2022-02-22 | 39510 | keep | 0 | Feb | 2022 | 0.02691 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-02-22 16:44 | 2022-02-22 17:52 | 50 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO | R22022200057 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-02-22 | 3400 | keep | 0 | Feb | 2022 | 0.0023157 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-22 17:21 | 2022-02-22 20:33 | 259 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO PUENTE SAFADO EN CORTE DE LINEA | P22022200049 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2022-02-22 | 49728 | keep | 0 | Feb | 2022 | 0.03387 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2022-02-22 17:31 | 2022-02-22 21:44 | 12 | 004:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR AVE CRUZO FASE | S22022200163 | New_Event |  |  | Include | Wildlife | 253 | 2022-02-22 | 3036 | keep | 0 | Feb | 2022 | 0.0020678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-02-22 17:31 | 2022-02-22 20:50 | 10 | 003:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | B22022200051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 199 | 2022-02-22 | 1990 | keep | 0 | Feb | 2022 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-22 17:48 | 2022-02-22 21:25 | 15 | 003:37 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P22022200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-02-22 | 3255 | keep | 0 | Feb | 2022 | 0.002217 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-22 17:48 | 2022-02-22 19:40 | 40 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B22022200057 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2022-02-22 | 4480 | keep | 0 | Feb | 2022 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-22 17:52 | 2022-02-22 18:48 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22022200046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-02-22 | 560 | keep | 0 | Feb | 2022 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-22 18:00 | 2022-02-22 18:01 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 3046 | keep | 0 | Feb | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-02-22 18:21 | 2022-02-22 18:24 | 1825 | 000:03 | S | LINEA DE TRANSMISION 38KV | SE ABRE L-3000 PARA SECCIONALIZAR TRAMO POR PUENTE ABIERTO 3091B A 3029A | S22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-22 | 5475 | keep | 0 | Feb | 2022 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-02-22 18:21 | 2022-02-22 18:24 | 47 | 000:03 | S | LINEA DE TRANSMISION 38KV | SE ABRE L-3000 PARA SECCIONALIZAR TRAMO POR PUENTE ABIERTO 3091B A 3029A | S22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-22 | 141 | keep | 0 | Feb | 2022 | 9.6034e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-02-22 18:21 | 2022-02-22 18:24 | 315 | 000:03 | S | LINEA DE TRANSMISION 38KV | SE ABRE L-3000 PARA SECCIONALIZAR TRAMO POR PUENTE ABIERTO 3091B A 3029A | S22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-22 | 945 | keep | 0 | Feb | 2022 | 0.00064364 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-02-22 18:21 | 2022-02-22 18:24 | 2 | 000:03 | S | LINEA DE TRANSMISION 38KV | SE ABRE L-3000 PARA SECCIONALIZAR TRAMO POR PUENTE ABIERTO 3091B A 3029A | S22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-22 | 6 | keep | 0 | Feb | 2022 | 4.0866e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-02-22 18:21 | 2022-02-22 18:24 | 2391 | 000:03 | S | LINEA DE TRANSMISION 38KV | SE ABRE L-3000 PARA SECCIONALIZAR TRAMO POR PUENTE ABIERTO 3091B A 3029A | S22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-22 | 7173 | keep | 0 | Feb | 2022 | 0.0048855 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 1153 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 10377 | keep | 0 | Feb | 2022 | 0.0070677 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 1709 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 15381 | keep | 0 | Feb | 2022 | 0.010476 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 1320 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 11880 | keep | 0 | Feb | 2022 | 0.0080914 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 2276 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 20484 | keep | 0 | Feb | 2022 | 0.013952 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 777 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 6993 | keep | 0 | Feb | 2022 | 0.0047629 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 12 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-22 18:21 | 2022-02-22 18:30 | 1290 | 000:09 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO DISPARO LA LINEA 3000 PARA SECCIONALIZAR PUENTE ABIERTO | C22022200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-02-22 | 11610 | keep | 0 | Feb | 2022 | 0.0079075 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
ARECIBO | 2022-02-22 18:38 | 2022-02-22 19:02 | 8 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO CONEXIONES EN SECUNDARIA | A22022200049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-02-22 | 192 | keep | 0 | Feb | 2022 | 0.00013077 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-22 18:39 | 2022-02-23 15:31 | 70 | 020:52 | P | ESTRUCTURA AVERIADA | SE REEMPLAZARON DOS POSTES Y SE REALIZO DESGANCHE | S22022200618 | New_Event | Defective Pole | Include | Include | Equipment | 1252 | 2022-02-22 | 87640 | keep | 0 | Feb | 2022 | 0.059691 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-02-22 18:50 | 2022-02-23 15:23 | 25 | 020:33 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22022200295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1233 | 2022-02-22 | 30825 | keep | 0 | Feb | 2022 | 0.020995 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-02-22 18:51 | 2022-02-23 06:18 | 60 | 011:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22022200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 687 | 2022-02-22 | 41220 | keep | 0 | Feb | 2022 | 0.028075 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-22 19:30 | 2022-02-22 21:04 | 1 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU C HACIA PISTA DE LEVITTOWN | B22022200067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-02-22 | 94 | keep | 0 | Feb | 2022 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-22 19:47 | 2022-02-22 19:50 | 988 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1336-8 | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-22 | 2964 | keep | 0 | Feb | 2022 | 0.0020188 | 0.00067292 | Momentary | FALSE | FALSE | Not_TMED_Event | 988
SAN JUAN | 2022-02-22 19:47 | 2022-02-22 19:50 | 300 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1336-8 | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-22 | 900 | keep | 0 | Feb | 2022 | 0.00061299 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-02-22 19:47 | 2022-02-22 19:50 | 3703 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1336-9 LLEVA 30% 1204-4 Y PARTE DEL 1204-5 | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-22 | 11109 | keep | 0 | Feb | 2022 | 0.0075663 | 0.0025221 | Momentary | FALSE | FALSE | Not_TMED_Event | 3703
SAN JUAN | 2022-02-22 19:47 | 2022-02-22 19:50 | 207 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1336-8 | S22022200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-22 | 621 | keep | 0 | Feb | 2022 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
PONCE | 2022-02-22 19:50 | 2022-02-23 06:47 | 75 | 010:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22022200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 657 | 2022-02-22 | 49275 | keep | 0 | Feb | 2022 | 0.033561 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-02-22 19:57 | 2022-02-22 23:17 | 4 | 003:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X30 EN BANCO DE TRANSFORMADORES Y SE REMPLAZO PORTAFUSIBLE | S22022200025 | New_Event | Cutout Failure | Include | Include | Equipment | 200 | 2022-02-22 | 800 | keep | 0 | Feb | 2022 | 0.00054488 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-22 20:20 | 2022-02-22 20:48 | 10 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22022200036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-02-22 | 280 | keep | 0 | Feb | 2022 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-22 20:57 | 2022-02-22 20:58 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22022200074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-02-22 21:05 | 2022-02-22 23:12 | 2435 | 002:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SUBIO/FIJO NEUTRAL QUE SE SALIO DEL AISLADOR CARGA TRANSFERIDA AL 1909-08 | S22022200293 | New_Event | Wire Down | Include | Include | Equipment | 127 | 2022-02-22 | 309245 | keep | 0 | Feb | 2022 | 0.21063 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-22 21:05 | 2022-02-22 23:02 | 2956 | 001:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SUBIO/FIJO NEUTRAL QUE SE SALIO DEL AISLADOR LLEVA LA CARGA DEL 1907-05 | S22022200293 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2022-02-22 | 345852 | keep | 0 | Feb | 2022 | 0.23556 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2022-02-22 21:22 | 2022-02-22 21:24 | 2228 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 8007-04 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022200063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-22 | 4456 | keep | 0 | Feb | 2022 | 0.003035 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-22 21:22 | 2022-02-22 21:24 | 438 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | A22022200063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-22 | 876 | keep | 0 | Feb | 2022 | 0.00059664 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-22 21:25 | 2022-02-22 21:26 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022200064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-22 21:25 | 2022-02-22 21:26 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22022200064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-22 21:28 | 2022-02-22 21:29 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022200065 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-22 21:28 | 2022-02-22 21:29 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22022200065 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-22 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-22 22:23 | 2022-02-23 13:55 | 262 | 015:32 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUCETA PARTIDA MEDIANTE GOI BY-220223-01 | B22022200071 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 932 | 2022-02-22 | 244184 | keep | 0 | Feb | 2022 | 0.16631 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
MAYAGÃœEZ | 2022-02-22 22:34 | 2022-02-23 03:45 | 30 | 005:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22022200077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-02-22 | 9330 | keep | 0 | Feb | 2022 | 0.0063546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-22 22:58 | 2022-02-23 11:32 | 1 | 012:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO | C22022200356 | New_Event | Bad Weather | Include | Include | Weather | 754 | 2022-02-22 | 754 | keep | 0 | Feb | 2022 | 0.00051355 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-22 23:03 | 2022-02-22 23:55 | 40 | 000:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN CORTE DE LINEA Y SE REMPLAZO EL PORTAFUSIBLE | S22022200410 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2022-02-22 | 2080 | keep | 0 | Feb | 2022 | 0.0014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-23 01:19 | 2022-02-23 01:21 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22022300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-23 | 2002 | keep | 0 | Feb | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
ARECIBO | 2022-02-23 01:35 | 2022-02-23 12:58 | 1 | 011:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | A22022300001 | New_Event | Wire Down | Include | Include | Equipment | 683 | 2022-02-23 | 683 | keep | 0 | Feb | 2022 | 0.00046519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-23 01:51 | 2022-02-23 02:53 | 95 | 001:02 | P | NO SE REPORTO CAUSA | 1X65 EN CORTE DE LINEA | B22022300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-02-23 | 5890 | keep | 0 | Feb | 2022 | 0.0040117 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
UTUADO | 2022-02-23 03:40 | 2022-02-23 09:57 | 40 | 006:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22022300002 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2022-02-23 | 15080 | keep | 0 | Feb | 2022 | 0.010271 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-23 03:43 | 2022-02-23 03:45 | 651 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | B22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-23 | 1302 | keep | 0 | Feb | 2022 | 0.00088679 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
ARECIBO | 2022-02-23 04:17 | 2022-02-23 04:18 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 LLEVA LA CARGA DEL 8007-03 | A22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 04:17 | 2022-02-23 04:18 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
MAYAGÃœEZ | 2022-02-23 04:32 | 2022-02-23 04:33 | 108 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M22022300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-23 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-02-23 04:33 | 2022-02-23 06:30 | 50 | 001:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA BAMBUA ENCIMA DE LINEA PRIMARIA | M22022300001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-02-23 | 5850 | keep | 0 | Feb | 2022 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-23 04:43 | 2022-02-23 05:02 | 40 | 000:19 | P | NO SE REPORTO CAUSA | 1X80 EN CORTE DE LINEA | B22022300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-02-23 | 760 | keep | 0 | Feb | 2022 | 0.00051763 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-23 05:06 | 2022-02-23 05:07 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 LLEVA LA CARGA DEL 8007-03 | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 05:06 | 2022-02-23 05:07 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-23 05:23 | 2022-02-23 12:20 | 45 | 006:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 10 EN XMR | B22022300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2022-02-23 | 18765 | keep | 0 | Feb | 2022 | 0.012781 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-02-23 05:44 | 2022-02-23 05:45 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 LLEVA LA CARGA DEL 8007-03 | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 05:44 | 2022-02-23 05:45 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
CAGUAS | 2022-02-23 05:57 | 2022-02-23 12:38 | 47 | 006:41 | P | DESGANCHE | 1 X 65 Y 1 X 20 EN CORTES DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22022300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2022-02-23 | 18847 | keep | 0 | Feb | 2022 | 0.012837 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2022-02-23 06:30 | 2022-02-23 13:45 | 17 | 007:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 50 KVA AVERIADO | C22022300010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 435 | 2022-02-23 | 7395 | keep | 0 | Feb | 2022 | 0.0050367 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2022-02-23 06:31 | 2022-02-23 09:33 | 40 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22022300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-02-23 | 7280 | keep | 0 | Feb | 2022 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-23 06:37 | 2022-02-23 06:46 | 6136 | 000:09 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR DE EMERGENCIA POR VEHICULO EN FUEGO LUEGO DE IMPACTAR POSTE DE METAL | S22022300011 | New_Event |  |  | Include | Wildlife | 9 | 2022-02-23 | 55224 | keep | 0 | Feb | 2022 | 0.037613 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-02-23 06:46 | 2022-02-23 15:40 | 14 | 008:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L SE LLEVO LINEA A AISLADOR CAUSADO POR IMPACTO DE VEHICULO CON POSTE Y SE REALIZO DESGANCHE | B22022300014 | Partial_restoration |  |  | Include | Wildlife | 534 | 2022-02-23 | 7476 | keep | 0 | Feb | 2022 | 0.0050919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-23 06:46 | 2022-02-23 06:47 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 06:46 | 2022-02-23 06:47 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-23 06:53 | 2022-02-23 06:54 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 06:53 | 2022-02-23 06:54 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-23 07:08 | 2022-02-23 07:09 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 07:08 | 2022-02-23 07:09 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-23 07:44 | 2022-02-23 11:16 | 60 | 003:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22022300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2022-02-23 | 12720 | keep | 0 | Feb | 2022 | 0.0086635 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-23 07:51 | 2022-02-23 12:06 | 50 | 004:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLASDOR ROTO | A22022300024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 255 | 2022-02-23 | 12750 | keep | 0 | Feb | 2022 | 0.008684 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-23 07:51 | 2022-02-23 07:52 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 07:51 | 2022-02-23 07:52 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-23 07:59 | 2022-02-23 08:00 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300029 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 07:59 | 2022-02-23 08:00 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300029 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-23 08:05 | 2022-02-23 21:13 | 40 | 013:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22022300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 788 | 2022-02-23 | 31520 | keep | 0 | Feb | 2022 | 0.021468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-23 08:07 | 2022-02-23 08:08 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 08:07 | 2022-02-23 08:08 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-23 08:11 | 2022-02-23 13:01 | 1 | 004:50 | P | NO SE REPORTO CAUSA | 1 X 15 EN PM | S22022300033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2022-02-23 | 290 | keep | 0 | Feb | 2022 | 0.00019752 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-23 08:20 | 2022-02-23 08:21 | 1474 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22022300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 1474 | keep | 0 | Feb | 2022 | 0.0010039 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
VEGA BAJA | 2022-02-23 08:21 | 2022-02-23 09:14 | 6 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22022200070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-02-23 | 318 | keep | 0 | Feb | 2022 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-02-23 08:36 | 2022-02-23 14:32 | 25 | 005:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22022300044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 356 | 2022-02-23 | 8900 | keep | 0 | Feb | 2022 | 0.0060617 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-23 08:40 | 2022-02-23 09:07 | 6 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S22022300003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-02-23 | 162 | keep | 0 | Feb | 2022 | 0.00011034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-02-23 08:46 | 2022-02-23 08:47 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022300055 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 08:46 | 2022-02-23 08:47 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22022300055 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-23 08:51 | 2022-02-23 13:43 | 15 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22022200050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2022-02-23 | 4380 | keep | 0 | Feb | 2022 | 0.0029832 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-23 09:00 | 2022-02-23 14:15 | 25 | 005:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22022300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2022-02-23 | 7875 | keep | 0 | Feb | 2022 | 0.0053636 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-02-23 09:08 | 2022-02-23 11:37 | 11 | 002:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BAJANTE Y SECUNDARIA | C22022300050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 149 | 2022-02-23 | 1639 | keep | 0 | Feb | 2022 | 0.0011163 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-02-23 09:11 | 2022-02-23 09:12 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 1909-08 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2435 | keep | 0 | Feb | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-02-23 09:11 | 2022-02-23 09:12 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1907-05 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2956 | keep | 0 | Feb | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2022-02-23 09:31 | 2022-02-23 17:11 | 20 | 007:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | C22022300056 | New_Event | Bad Weather | Include | Include | Weather | 460 | 2022-02-23 | 9200 | keep | 0 | Feb | 2022 | 0.0062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-02-23 09:35 | 2022-02-23 10:45 | 20 | 001:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22022300076 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2022-02-23 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-23 09:39 | 2022-02-23 10:14 | 1 | 000:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22022300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2022-02-23 | 35 | keep | 0 | Feb | 2022 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-23 10:01 | 2022-02-23 19:56 | 150 | 009:55 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 100 EN CORTE DE LINEA | S22022300054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 595 | 2022-02-23 | 89250 | keep | 0 | Feb | 2022 | 0.060788 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-23 10:01 | 2022-02-24 13:11 | 15 | 027:10 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZAO PISTOLA Y SE CERRO HACIA MH-9A | S22022300054 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1630 | 2022-02-23 | 24450 | keep | 0 | Feb | 2022 | 0.016653 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-02-23 10:01 | 2022-02-23 11:41 | 5 | 001:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR UNO DE LA MISMA CAPACIDAD | M22022300012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2022-02-23 | 500 | keep | 0 | Feb | 2022 | 0.00034055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-02-23 10:07 | 2022-02-23 10:23 | 6 | 000:16 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | C22022300078 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 16 | 2022-02-23 | 96 | keep | 0 | Feb | 2022 | 6.5385e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-23 10:09 | 2022-02-23 10:10 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22022300080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2203 | keep | 0 | Feb | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
MAYAGÃœEZ | 2022-02-23 10:11 | 2022-02-23 17:24 | 3 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | M22022300013 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2022-02-23 | 1299 | keep | 0 | Feb | 2022 | 0.00088474 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-02-23 10:17 | 2022-02-23 12:20 | 40 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22022300085 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2022-02-23 | 4920 | keep | 0 | Feb | 2022 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-23 10:28 | 2022-02-23 13:45 | 30 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22022300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-02-23 | 5910 | keep | 0 | Feb | 2022 | 0.0040253 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-23 10:29 | 2022-02-23 20:16 | 5 | 009:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN SU MAL TIEMPO | C22022300089 | New_Event | Bad Weather | Include | Include | Weather | 587 | 2022-02-23 | 2935 | keep | 0 | Feb | 2022 | 0.001999 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-23 10:32 | 2022-02-23 15:56 | 70 | 005:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | M22022300018 | New_Event | Wire Down | Include | Include | Equipment | 324 | 2022-02-23 | 22680 | keep | 0 | Feb | 2022 | 0.015447 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-02-23 10:35 | 2022-02-23 13:12 | 50 | 002:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22022300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-02-23 | 7850 | keep | 0 | Feb | 2022 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-23 10:50 | 2022-02-23 20:30 | 5 | 009:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22022300091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 580 | 2022-02-23 | 2900 | keep | 0 | Feb | 2022 | 0.0019752 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-23 10:53 | 2022-02-23 10:54 | 250 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE 1620-02 Y SE CERRO POR SCADA LLEVA PARTE DEL 1206-03 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 250 | keep | 0 | Feb | 2022 | 0.00017027 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-02-23 10:53 | 2022-02-23 10:54 | 383 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE 1620-02 Y SE CERRO POR SCADA LLEVA 95% DEL 1336-10 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 383 | keep | 0 | Feb | 2022 | 0.00026086 | 0.00026086 | Momentary | FALSE | FALSE | Not_TMED_Event | 383
SAN JUAN | 2022-02-23 10:53 | 2022-02-23 10:54 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-02 Y SE CERRO POR SCADA LLEVA 1620-01 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 36 | keep | 0 | Feb | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-02-23 10:53 | 2022-02-23 10:54 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-02 Y SE CERRO POR SCADA LLEVA 1620-01 95% DEL 1336-10 Y PARTE DEL 1206-03 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 3718 | keep | 0 | Feb | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
UTUADO | 2022-02-23 11:03 | 2022-02-23 11:41 | 40 | 000:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22022300093 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2022-02-23 | 1520 | keep | 0 | Feb | 2022 | 0.0010353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-02-23 11:10 | 2022-02-23 16:37 | 10 | 005:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 50KVA | M22022300021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 327 | 2022-02-23 | 3270 | keep | 0 | Feb | 2022 | 0.0022272 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-02-23 11:15 | 2022-02-23 13:24 | 65 | 002:09 | P | DESGANCHE | 2 X 140 EN C/L DESGANCHE | B22022300044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-02-23 | 8385 | keep | 0 | Feb | 2022 | 0.005711 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-02-23 11:16 | 2022-02-23 13:32 | 40 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22022300095 | New_Event |  |  | Include | Wildlife | 136 | 2022-02-23 | 5440 | keep | 0 | Feb | 2022 | 0.0037052 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-23 11:22 | 2022-02-23 11:23 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-04 Y SE CERRO POR SCADA LLEVA 1303-01 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 1681 | keep | 0 | Feb | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-02-23 11:22 | 2022-02-23 11:23 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-04 Y SE CERRO POR SCADA LLEVA 1346-06 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 1598 | keep | 0 | Feb | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2022-02-23 11:30 | 2022-02-23 13:00 | 70 | 001:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22022300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-02-23 | 6300 | keep | 0 | Feb | 2022 | 0.0042909 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-02-23 11:39 | 2022-02-23 15:30 | 40 | 003:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA DE TRANSFORMADOR | R22022300031 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2022-02-23 | 9240 | keep | 0 | Feb | 2022 | 0.0062933 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-02-23 11:54 | 2022-02-23 13:02 | 60 | 001:08 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN RISER POR AVERIA SOTERRADA DEL T-33 AL T-34 SE CONSTRUYO PROVICIONAL AEREO | P22022300021 | New_Event | UG Cable Fault | Include | Include | Equipment | 68 | 2022-02-23 | 4080 | keep | 0 | Feb | 2022 | 0.0027789 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-23 11:57 | 2022-02-23 12:00 | 50 | 000:03 | P | NO SE REPORTO CAUSA | 2 X 50 Y 1 X 65 EN C/L | C22022300130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 150 | keep | 0 | Feb | 2022 | 0.00010216 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-23 12:00 | 2022-02-23 12:02 | 1089 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C22022300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-23 | 2178 | keep | 0 | Feb | 2022 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-02-23 12:00 | 2022-02-23 12:02 | 3896 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C22022300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-23 | 7792 | keep | 0 | Feb | 2022 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-02-23 12:00 | 2022-02-23 12:02 | 1467 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C22022300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-23 | 2934 | keep | 0 | Feb | 2022 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
GUAYAMA | 2022-02-23 12:01 | 2022-02-23 12:43 | 15 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | P22022300023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-02-23 | 630 | keep | 0 | Feb | 2022 | 0.00042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-02-23 12:02 | 2022-02-23 14:40 | 50 | 002:38 | P | NO SE REPORTO CAUSA | 2 X 50 Y 1 X 65 EN C/L | C22022300130 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-02-23 | 7900 | keep | 0 | Feb | 2022 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-02-23 12:13 | 2022-02-23 15:01 | 8 | 002:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR Y 1 X 40 EN C/L CRUCE POR LAGARTO | C22022300139 | New_Event |  |  | Include | Wildlife | 168 | 2022-02-23 | 1344 | keep | 0 | Feb | 2022 | 0.00091539 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-23 12:16 | 2022-02-23 18:57 | 97 | 006:41 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA | B22022300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2022-02-23 | 38897 | keep | 0 | Feb | 2022 | 0.026493 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
FAJARDO | 2022-02-23 12:28 | 2022-02-23 13:30 | 3 | 001:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REEMPLAZO PORTAFUSIBLE | R22022300045 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2022-02-23 | 186 | keep | 0 | Feb | 2022 | 0.00012668 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-02-23 12:29 | 2022-02-23 20:39 | 50 | 008:10 | P | DESGANCHE | 1 X 40 Y 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22022300105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 490 | 2022-02-23 | 24500 | keep | 0 | Feb | 2022 | 0.016687 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-23 12:30 | 2022-02-23 22:13 | 19 | 009:43 | P | NO SE REPORTO CAUSA | 1X25 EN TRANSFORMADOR | S22022300110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 583 | 2022-02-23 | 11077 | keep | 0 | Feb | 2022 | 0.0075445 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-02-23 12:48 | 2022-02-23 15:17 | 100 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M22022300026 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-02-23 | 14900 | keep | 0 | Feb | 2022 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-23 12:58 | 2022-02-23 12:59 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1620-05 Y SE CERRO POR SCADA LLEVA PARTE DEL 1206-03 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 300 | keep | 0 | Feb | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-02-23 12:58 | 2022-02-23 12:59 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-05 Y SE CERRO POR SCADA LLEVA PARTE DEL 1206-03 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 1615 | keep | 0 | Feb | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
FAJARDO | 2022-02-23 13:02 | 2022-02-23 13:03 | 1571 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 1571 | keep | 0 | Feb | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
PONCE | 2022-02-23 13:02 | 2022-02-23 18:12 | 12 | 005:10 | P | CABLE SOTERRADO AVERIADO | AVERIA DE CABLE SOTERRADO HACIA T-34 SE DIO SERVICIO POR PROVICIONAL AEREO | P22022300025 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 310 | 2022-02-23 | 3720 | keep | 0 | Feb | 2022 | 0.0025337 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-23 13:03 | 2022-02-23 14:32 | 30 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22022300054 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-02-23 | 2670 | keep | 0 | Feb | 2022 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-23 13:05 | 2022-02-23 15:42 | 10 | 002:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 25 X 25 KVA | B22022300065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 157 | 2022-02-23 | 1570 | keep | 0 | Feb | 2022 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-23 13:10 | 2022-02-24 08:27 | 25 | 019:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22022300132 | New_Event | Wire Down | Include | Include | Equipment | 1157 | 2022-02-23 | 28925 | keep | 0 | Feb | 2022 | 0.019701 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-23 13:17 | 2022-02-23 18:45 | 282 | 005:28 | P | DESGANCHE | 2 X 80 EN C/L Y 2 X 65 EN C/L SE DESGANCHO ARBOL, SE LEVANTO CONDUCTOR Y SE REEMPLAZO AISLADOR | B22022300138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2022-02-23 | 92496 | keep | 0 | Feb | 2022 | 0.062999 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
ARECIBO | 2022-02-23 13:29 | 2022-02-23 17:10 | 30 | 003:41 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22022300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-02-23 | 6630 | keep | 0 | Feb | 2022 | 0.0045157 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-23 13:35 | 2022-02-23 19:44 | 35 | 006:09 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA | C22022300157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-02-23 | 12915 | keep | 0 | Feb | 2022 | 0.0087963 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-02-23 13:35 | 2022-02-23 14:26 | 102 | 000:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22022300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-02-23 | 5202 | keep | 0 | Feb | 2022 | 0.0035431 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
CAGUAS | 2022-02-23 13:41 | 2022-02-23 19:00 | 20 | 005:19 | P | CABLE SOTERRADO AVERIADO | CABLE SOTERRADO AVERIADO DEL T-5 AL T-6 SE CONSTRUYO AEREO PROVISIONAL | C22022300176 | New_Event | UG Cable Fault | Include | Include | Equipment | 319 | 2022-02-23 | 6380 | keep | 0 | Feb | 2022 | 0.0043454 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-23 13:46 | 2022-02-23 16:00 | 1 | 002:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 15 X 15 KVA | B22022300071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2022-02-23 | 134 | keep | 0 | Feb | 2022 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-23 13:49 | 2022-02-23 15:51 | 15 | 002:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R22022300069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 122 | 2022-02-23 | 1830 | keep | 0 | Feb | 2022 | 0.0012464 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-23 13:51 | 2022-02-23 13:56 | 353 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-23 | 1765 | keep | 0 | Feb | 2022 | 0.0012021 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2022-02-23 13:54 | 2022-02-24 01:50 | 30 | 011:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22022300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 716 | 2022-02-23 | 21480 | keep | 0 | Feb | 2022 | 0.01463 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-23 13:56 | 2022-02-23 13:57 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22022300165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2178 | keep | 0 | Feb | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
GUAYAMA | 2022-02-23 13:56 | 2022-02-23 13:57 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P220223000XX | New_Event |  |  | Include | Wildlife | 1 | 2022-02-23 | 464 | keep | 0 | Feb | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-02-23 13:57 | 2022-02-23 15:07 | 50 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22022300031 | 1st_after_momentary |  |  | Include | Wildlife | 70 | 2022-02-23 | 3500 | keep | 0 | Feb | 2022 | 0.0023838 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-23 14:07 | 2022-02-23 15:37 | 45 | 001:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22022300035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-02-23 | 4050 | keep | 0 | Feb | 2022 | 0.0027584 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2022-02-23 14:16 | 2022-02-24 16:50 | 30 | 026:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN SU-2 SE REPARO TRAMO AVERIADO POR EXCAVACION DE AAA | C22022300170 | New_Event |  |  | Include | Wildlife | 1594 | 2022-02-23 | 47820 | keep | 0 | Feb | 2022 | 0.03257 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-23 14:16 | 2022-02-23 17:11 | 8 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 NX X 18 EN XMR SE SECCIONALIZO SECUNDARIA AVERIADA | C22022300170 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2022-02-23 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-02-23 14:50 | 2022-02-23 17:36 | 25 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C22022300185 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2022-02-23 | 4150 | keep | 0 | Feb | 2022 | 0.0028265 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-23 14:52 | 2022-02-23 14:53 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
BAYAMON | 2022-02-23 15:00 | 2022-02-23 17:08 | 10 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B22022200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2022-02-23 | 1280 | keep | 0 | Feb | 2022 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-23 15:15 | 2022-02-23 15:41 | 10 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22022300025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-02-23 | 260 | keep | 0 | Feb | 2022 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-23 15:18 | 2022-02-23 19:54 | 163 | 004:36 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN CORTE DE LINEA SE ELIMINO PARARRAYO CRUZADO | P22022300045 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 276 | 2022-02-23 | 44988 | keep | 0 | Feb | 2022 | 0.030641 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
SAN JUAN | 2022-02-23 15:27 | 2022-02-24 08:03 | 60 | 016:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22022300169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 996 | 2022-02-23 | 59760 | keep | 0 | Feb | 2022 | 0.040702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-23 15:27 | 2022-02-23 17:12 | 1 | 001:45 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 25KVA | B22022300082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 105 | 2022-02-23 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-23 15:28 | 2022-02-23 17:54 | 26 | 002:26 | P | TRANSFORMADOR AVERIADO | ABRIO CL PARA REEMPLAZAR TRANSFORMADOR T-52 DE 75KVA X 75KVA | S22022300171 | New_Event | Service Transformer Failure | Include | Include | Equipment | 146 | 2022-02-23 | 3796 | keep | 0 | Feb | 2022 | 0.0025854 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2022-02-23 15:38 | 2022-02-23 18:48 | 65 | 003:10 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22022300196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-02-23 | 12350 | keep | 0 | Feb | 2022 | 0.0084115 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-02-23 15:42 | 2022-02-23 18:26 | 12 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22022300128 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2022-02-23 | 1968 | keep | 0 | Feb | 2022 | 0.0013404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-23 15:46 | 2022-02-23 16:46 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22022300084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-02-23 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-02-23 15:52 | 2022-02-23 17:25 | 76 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | P22022300050 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2022-02-23 | 7068 | keep | 0 | Feb | 2022 | 0.004814 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
FAJARDO | 2022-02-23 15:53 | 2022-02-23 15:54 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 2722 | keep | 0 | Feb | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2022-02-23 15:54 | 2022-02-23 17:57 | 100 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | R22022300089 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-02-23 | 12300 | keep | 0 | Feb | 2022 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-23 16:14 | 2022-02-23 23:25 | 45 | 007:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN BOOSTER LLUVIA Y VIENTO | M22022300048 | New_Event | Bad Weather | Include | Include | Weather | 431 | 2022-02-23 | 19395 | keep | 0 | Feb | 2022 | 0.01321 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2022-02-23 16:18 | 2022-02-23 19:05 | 53 | 002:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22022300073 | New_Event |  |  | Include | Wildlife | 167 | 2022-02-23 | 8851 | keep | 0 | Feb | 2022 | 0.0060284 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2022-02-23 16:36 | 2022-02-23 17:40 | 75 | 001:04 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE DESGANCHO | S22022300188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-02-23 | 4800 | keep | 0 | Feb | 2022 | 0.0032693 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-02-23 16:43 | 2022-02-23 16:45 | 988 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1336-8 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-23 | 1976 | keep | 0 | Feb | 2022 | 0.0013458 | 0.00067292 | Momentary | FALSE | FALSE | Not_TMED_Event | 988
SAN JUAN | 2022-02-23 16:43 | 2022-02-23 16:45 | 300 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1336-8 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-23 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-02-23 16:43 | 2022-02-23 16:45 | 3703 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-23 | 7406 | keep | 0 | Feb | 2022 | 0.0050442 | 0.0025221 | Momentary | FALSE | FALSE | Not_TMED_Event | 3703
SAN JUAN | 2022-02-23 16:43 | 2022-02-23 16:45 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1336-8 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-23 | 414 | keep | 0 | Feb | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-02-23 16:44 | 2022-02-23 18:57 | 353 | 002:13 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO | S22022300192 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-02-23 | 46949 | keep | 0 | Feb | 2022 | 0.031977 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-02-23 16:45 | 2022-02-24 00:53 | 80 | 008:08 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22022300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2022-02-23 | 39040 | keep | 0 | Feb | 2022 | 0.02659 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-23 16:47 | 2022-02-23 16:50 | 1420 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1530-07 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 4260 | keep | 0 | Feb | 2022 | 0.0029015 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-02-23 16:47 | 2022-02-23 16:50 | 437 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1530-07 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 1311 | keep | 0 | Feb | 2022 | 0.00089292 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-02-23 16:47 | 2022-02-23 16:50 | 643 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1526-02 Y 1530-06 | S22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 1929 | keep | 0 | Feb | 2022 | 0.0013138 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2022-02-23 16:53 | 2022-02-23 16:56 | 59 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1117-09 | S22022300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 177 | keep | 0 | Feb | 2022 | 0.00012055 | 4.0185e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2022-02-23 16:53 | 2022-02-23 16:56 | 134 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1117-09 | S22022300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 402 | keep | 0 | Feb | 2022 | 0.0002738 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2022-02-23 16:53 | 2022-02-23 16:56 | 80 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1117-09 | S22022300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 240 | keep | 0 | Feb | 2022 | 0.00016346 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-23 16:53 | 2022-02-23 16:56 | 316 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 50% 1115-02, 100% DEL 1115-03, 30% DEL 1115-04 | S22022300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 948 | keep | 0 | Feb | 2022 | 0.00064568 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2022-02-23 16:58 | 2022-02-23 17:40 | 12 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R22022300094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-02-23 | 504 | keep | 0 | Feb | 2022 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-23 17:04 | 2022-02-23 18:24 | 1310 | 001:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO TRAMO | S22022300216 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2022-02-23 | 104800 | keep | 0 | Feb | 2022 | 0.071379 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2022-02-23 17:13 | 2022-02-23 21:03 | 65 | 003:50 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22022300235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-02-23 | 14950 | keep | 0 | Feb | 2022 | 0.010182 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2022-02-23 17:14 | 2022-02-23 22:14 | 16 | 005:00 | P | DESGANCHE | 1X30 EN CORTE DE LINEA | B22022300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-02-23 | 4800 | keep | 0 | Feb | 2022 | 0.0032693 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-02-23 17:15 | 2022-02-24 08:15 | 5 | 015:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C22022300236 | New_Event | Bad Weather | Include | Include | Weather | 900 | 2022-02-23 | 4500 | keep | 0 | Feb | 2022 | 0.0030649 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-02-23 17:21 | 2022-02-24 05:19 | 16 | 011:58 | P | DESGANCHE | 1X20 EN TRANSFORMADOR | S22022300224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 718 | 2022-02-23 | 11488 | keep | 0 | Feb | 2022 | 0.0078244 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-02-23 17:25 | 2022-02-23 22:47 | 2228 | 005:22 | T | LINEA DE TRANSMISION 38KV | SE REPARO CONDICION DE OVER HEAD DE LA LINEA 6900 CAIDO SOBRE EL ALIMENTADOR 8007-04 Y CAUSO QUE SE ROMPIERA AISLADOR DEL ALIMENTADOR ESTE ESTA LLEVANDO LA CARGA DEL 8007-03 | A22022300136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 322 | 2022-02-23 | 717416 | keep | 0 | Feb | 2022 | 0.48863 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-23 17:25 | 2022-02-23 22:47 | 438 | 005:22 | T | LINEA DE TRANSMISION 38KV | SE REPARO CONDICION DE OVER HEAD DE LA LINEA 6900 CAIDO SOBRE EL ALIMENTADOR CAUSO QUE SE ROMPIERA AISLADOR DEL ALIMENTADOR | A22022300136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 322 | 2022-02-23 | 141036 | keep | 0 | Feb | 2022 | 0.096059 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-02-23 17:28 | 2022-02-23 22:30 | 20 | 005:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22022300137 | New_Event | Bad Weather | Include | Include | Weather | 302 | 2022-02-23 | 6040 | keep | 0 | Feb | 2022 | 0.0041138 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-02-23 17:42 | 2022-02-23 18:44 | 250 | 001:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTE DE LINEA SE REEMPLAZARON TRES CAJAS PRIMARIAS QUEMADAS EN CORTE DE LINEA | P21022300062 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2022-02-23 | 15500 | keep | 0 | Feb | 2022 | 0.010557 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-02-23 17:49 | 2022-02-23 18:48 | 40 | 000:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-02-23 | 2360 | keep | 0 | Feb | 2022 | 0.0016074 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-23 18:01 | 2022-02-23 20:37 | 35 | 002:36 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22022300240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-02-23 | 5460 | keep | 0 | Feb | 2022 | 0.0037188 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-02-23 18:14 | 2022-02-23 22:44 | 10 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22022300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2022-02-23 | 2700 | keep | 0 | Feb | 2022 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-02-23 18:20 | 2022-02-23 20:23 | 15 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | R22022300116 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2022-02-23 | 1845 | keep | 0 | Feb | 2022 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-23 18:24 | 2022-02-23 18:59 | 650 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON LOS MACHETES | S22022300216 | Partial_restoration | Wire Down | Include | Include | Equipment | 35 | 2022-02-23 | 22750 | keep | 0 | Feb | 2022 | 0.015495 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-23 18:42 | 2022-02-23 21:26 | 250 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22022300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-02-23 | 41000 | keep | 0 | Feb | 2022 | 0.027925 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
GUAYAMA | 2022-02-23 18:44 | 2022-02-23 18:52 | 1945 | 000:08 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE ALIMENTADOR AL CERRAR CORTE DE LINEA RELACIONADO A EVENTO P22022300062 | P22022300075 | Additional_clients | Cutout Failure | Include | Include | Equipment | 8 | 2022-02-23 | 15560 | keep | 0 | Feb | 2022 | 0.010598 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-23 18:52 | 2022-02-23 21:35 | 250 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTE DE LINEA SE REEMPLAZARON TRES CAJAS PRIMARIAS QUEMADAS EN CORTE DE LINEA | P21022300062 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 163 | 2022-02-23 | 40750 | keep | 0 | Feb | 2022 | 0.027755 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-23 18:54 | 2022-02-23 21:43 | 100 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA ALGUNA | M22022300073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-02-23 | 16900 | keep | 0 | Feb | 2022 | 0.011511 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-23 18:57 | 2022-02-23 19:30 | 18 | 000:33 | P | NO SE REPORTO CAUSA | SE CERRARON LOS MACHETES | S22022300192 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 33 | 2022-02-23 | 594 | keep | 0 | Feb | 2022 | 0.00040457 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-23 19:25 | 2022-02-23 19:26 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22022300086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-23 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
CANOVANAS | 2022-02-23 19:37 | 2022-02-23 19:50 | 30 | 000:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22022300123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2022-02-23 | 390 | keep | 0 | Feb | 2022 | 0.00026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-23 19:51 | 2022-02-23 21:50 | 95 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P22022300091 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2022-02-23 | 11305 | keep | 0 | Feb | 2022 | 0.0076998 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2022-02-23 20:05 | 2022-02-24 01:35 | 125 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | M22022300107 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2022-02-23 | 41250 | keep | 0 | Feb | 2022 | 0.028095 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
UTUADO | 2022-02-23 20:50 | 2022-02-24 11:16 | 17 | 014:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22022300207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 866 | 2022-02-23 | 14722 | keep | 0 | Feb | 2022 | 0.010027 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2022-02-23 21:59 | 2022-02-23 22:01 | 5069 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR DE EMERGENCIA POR PUNTO CALIENTE EN TRONCAL DEL ALIMENTRADOR CONECTOR HOT CLAMP AVERIADO SE INSTALO PUENTE DE GOMA Y SE CERRO INTERRUPTOR | P220223000XX | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-23 | 10138 | keep | 0 | Feb | 2022 | 0.0069049 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
BAYAMON | 2022-02-23 22:14 | 2022-02-23 22:16 | 1310 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22022300275 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-02-23 | 2620 | keep | 0 | Feb | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-02-23 22:18 | 2022-02-23 22:23 | 1310 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22022300275 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 5 | 2022-02-23 | 6550 | keep | 0 | Feb | 2022 | 0.0044612 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-02-23 22:23 | 2022-02-23 23:17 | 1310 | 000:54 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR | S22022300275 | Partial_restoration | Wire Down | Include | Include | Equipment | 54 | 2022-02-23 | 70740 | keep | 0 | Feb | 2022 | 0.048181 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-23 22:25 | 2022-02-23 22:30 | 353 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22022300279 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-23 | 1765 | keep | 0 | Feb | 2022 | 0.0012021 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2022-02-23 22:35 | 2022-02-24 05:20 | 306 | 006:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO CARGA POR EL 1336-08 | S22022300448 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 405 | 2022-02-23 | 123930 | keep | 0 | Feb | 2022 | 0.084408 | 0.00020842 | Sustained | FALSE | FALSE | Not_TMED_Event | 306
SAN JUAN | 2022-02-23 22:35 | 2022-02-24 03:20 | 3703 | 004:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA CARGA TOTAL DEL 1336-09 Y 30% DEL 1204-05 QUEDO 50% DEL 1336-08 FUERA DE SERVICIO | S22022300448 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 285 | 2022-02-23 | 1055355 | keep | 0 | Feb | 2022 | 0.7188 | 0.0025221 | Sustained | FALSE | FALSE | Not_TMED_Event | 3703
SAN JUAN | 2022-02-23 22:35 | 2022-02-24 03:20 | 207 | 004:45 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO LLEVA CARGA TOTAL DEL 1336-09 Y 30% DEL 1204-05 QUEDO 50% DEL 1336-08 FUERA DE SERVICIO | S22022300448 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 285 | 2022-02-23 | 58995 | keep | 0 | Feb | 2022 | 0.040181 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-02-23 22:36 | 2022-02-24 01:41 | 1384 | 003:05 | S | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD GROUNDWIRE DE LA LINEA 1000 DE ENCIMA DEL CABLE DE TELEFONO, DEL 13KV Y DEL 4KV | S22022300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-02-23 | 256040 | keep | 0 | Feb | 2022 | 0.17439 | 0.00094264 | Sustained | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2022-02-23 22:36 | 2022-02-24 01:41 | 869 | 003:05 | S | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD GROUNDWIRE DE LA LINEA 1000 DE ENCIMA DEL CABLE DE TELEFONO, DEL 13KV Y DEL 4KV | S22022300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-02-23 | 160765 | keep | 0 | Feb | 2022 | 0.1095 | 0.00059187 | Sustained | FALSE | FALSE | Not_TMED_Event | 869
BAYAMON | 2022-02-23 22:45 | 2022-02-24 04:15 | 125 | 005:30 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION DE ALAMBRE PRIMARIO EN EL RISER | S22022300209 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 330 | 2022-02-23 | 41250 | keep | 0 | Feb | 2022 | 0.028095 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-02-23 22:46 | 2022-02-23 22:47 | 100 | 000:01 | P | DESGANCHE | 2X100 EN CORTE DE LINEA | S22022300187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-23 | 100 | keep | 0 | Feb | 2022 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-23 22:55 | 2022-02-24 06:08 | 100 | 007:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22022300336 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 433 | 2022-02-23 | 43300 | keep | 0 | Feb | 2022 | 0.029491 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-23 23:00 | 2022-02-24 00:05 | 48 | 001:05 | P | NO SE REPORTO CAUSA | 1X100 EN CORTE DE LINEA | B22022300114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-02-23 | 3120 | keep | 0 | Feb | 2022 | 0.002125 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
FAJARDO | 2022-02-23 23:09 | 2022-02-23 23:10 | 1571 | 000:01 | T | DESGANCHE | RECIERRE | R22022300126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-23 | 1571 | keep | 0 | Feb | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
FAJARDO | 2022-02-23 23:10 | 2022-02-24 00:59 | 66 | 001:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22022300128 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-02-23 | 7194 | keep | 0 | Feb | 2022 | 0.0048998 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-02-23 23:17 | 2022-02-23 23:47 | 650 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON MACHETES | S22022300275 | Partial_restoration | Wire Down | Include | Include | Equipment | 30 | 2022-02-23 | 19500 | keep | 0 | Feb | 2022 | 0.013281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-02-23 23:33 | 2022-02-23 23:34 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 1192 | keep | 0 | Feb | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
PONCE | 2022-02-23 23:44 | 2022-02-24 07:18 | 25 | 007:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22022300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 454 | 2022-02-23 | 11350 | keep | 0 | Feb | 2022 | 0.0077304 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-23 23:47 | 2022-02-23 23:58 | 500 | 000:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON MACHETES | S22022300275 | Partial_restoration | Wire Down | Include | Include | Equipment | 11 | 2022-02-23 | 5500 | keep | 0 | Feb | 2022 | 0.003746 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-23 23:48 | 2022-02-23 23:51 | 2216 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22022300121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-23 | 6648 | keep | 0 | Feb | 2022 | 0.0045279 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2022-02-23 23:48 | 2022-02-23 23:49 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22022300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 3332 | keep | 0 | Feb | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
FAJARDO | 2022-02-23 23:50 | 2022-02-24 02:03 | 50 | 002:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22022300131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-02-23 | 6650 | keep | 0 | Feb | 2022 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-23 23:56 | 2022-02-23 23:57 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22022300121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-23 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2022-02-23 23:58 | 2022-02-24 01:58 | 15 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PRIMARIO PARTIDO | S22022400012 | Partial_restoration | Wire Down | Include | Include | Equipment | 120 | 2022-02-23 | 1800 | keep | 0 | Feb | 2022 | 0.001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-24 00:02 | 2022-02-24 00:03 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-24 00:02 | 2022-02-24 00:03 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
VEGA BAJA | 2022-02-24 00:08 | 2022-02-24 10:41 | 25 | 010:33 | P | DESGANCHE | 1 X 40 EN C/L SE LEVANTO CONDUCTOR Y SE REALIZO DESGANCHE | B22022400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 633 | 2022-02-24 | 15825 | keep | 0 | Feb | 2022 | 0.010778 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-02-24 00:41 | 2022-02-24 00:42 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22022400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-02-24 01:15 | 2022-02-25 12:50 | 11 | 035:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 5 KVA POR 25 KVA | M22022400103 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2135 | 2022-02-24 | 23485 | keep | 0 | Feb | 2022 | 0.015996 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-02-24 01:17 | 2022-02-24 10:56 | 20 | 009:39 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | C22022400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 579 | 2022-02-24 | 11580 | keep | 0 | Feb | 2022 | 0.0078871 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-24 01:22 | 2022-02-24 12:15 | 10 | 010:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN XMR SE REMPLAZO CAJA PRIMARIA | S22022400039 | New_Event | Cutout Failure | Include | Include | Equipment | 653 | 2022-02-24 | 6530 | keep | 0 | Feb | 2022 | 0.0044476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-24 01:41 | 2022-02-24 01:42 | 1384 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD GROUNDWIRE DE LA LINEA 1000 DE ENCIMA DEL CABLE DE TELEFONO, DEL 13KV Y DEL 4KV (ALIMENTADOR OPERO INMEDIATAMENTE AL ENTRAR EN SERVICIO LA SUBESTACION) | S22022400043 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1384 | keep | 0 | Feb | 2022 | 0.00094264 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-24 01:57 | 2022-02-24 03:39 | 4 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES | R22022400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2022-02-24 | 408 | keep | 0 | Feb | 2022 | 0.00027789 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-24 01:58 | 2022-02-24 05:11 | 50 | 003:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L PARA SUBIR ALAMBRE PRIMARIO | S22022400012 | Additional_clients | Wire Down | Include | Include | Equipment | 193 | 2022-02-24 | 9650 | keep | 0 | Feb | 2022 | 0.0065726 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-24 03:00 | 2022-02-24 03:01 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
SAN JUAN | 2022-02-24 03:20 | 2022-02-24 05:12 | 1852 | 001:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO LLEVA CARGA TOTAL DEL 1336-09 Y 30% DEL 1204-05 QUEDADO EL 50% DEL 1336-08 Y FINALMENTE ENTRO | S22022300448 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2022-02-24 | 207424 | keep | 0 | Feb | 2022 | 0.14128 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-24 04:08 | 2022-02-24 09:21 | 50 | 005:13 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22022400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2022-02-24 | 15650 | keep | 0 | Feb | 2022 | 0.010659 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-24 04:15 | 2022-02-24 12:12 | 300 | 007:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22022400008 | New_Event | Bad Weather | Include | Include | Weather | 477 | 2022-02-24 | 143100 | keep | 0 | Feb | 2022 | 0.097465 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-02-24 06:16 | 2022-02-24 11:28 | 40 | 005:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-02-24 | 12480 | keep | 0 | Feb | 2022 | 0.0085001 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-24 06:28 | 2022-02-24 06:29 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2354 | keep | 0 | Feb | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
YAUCO | 2022-02-24 06:33 | 2022-02-24 09:22 | 50 | 002:49 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22022400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-02-24 | 8450 | keep | 0 | Feb | 2022 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-24 06:50 | 2022-02-24 08:29 | 50 | 001:39 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22022400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-02-24 | 4950 | keep | 0 | Feb | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-24 07:05 | 2022-02-24 09:50 | 12 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO PORTAFUSIBLE | C22022400012 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2022-02-24 | 1980 | keep | 0 | Feb | 2022 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-24 07:13 | 2022-02-24 07:16 | 1310 | 000:03 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | S22022400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-02-24 | 3930 | keep | 0 | Feb | 2022 | 0.0026767 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2022-02-24 07:22 | 2022-02-24 10:30 | 40 | 003:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REEMPLAZO AISLADOR | C22022400014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 188 | 2022-02-24 | 7520 | keep | 0 | Feb | 2022 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-24 07:30 | 2022-02-24 08:41 | 45 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL AEREO | S22022400103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-02-24 | 3195 | keep | 0 | Feb | 2022 | 0.0021761 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-02-24 07:40 | 2022-02-24 07:41 | 770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7801-04 | M22022400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 770 | keep | 0 | Feb | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2022-02-24 07:40 | 2022-02-24 07:41 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 7801-02 EL CUAL LLEVA LA CARGA DEL 7802-04 NO SE REPORTO CAUSA | M22022400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 1772 | keep | 0 | Feb | 2022 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
SAN JUAN | 2022-02-24 07:48 | 2022-02-24 09:56 | 12 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22022400107 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2022-02-24 | 1536 | keep | 0 | Feb | 2022 | 0.0010462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-24 07:49 | 2022-02-24 10:58 | 25 | 003:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22022400019 | New_Event | Bad Weather | Include | Include | Weather | 189 | 2022-02-24 | 4725 | keep | 0 | Feb | 2022 | 0.0032182 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-02-24 07:49 | 2022-02-24 09:26 | 20 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE LLEVO CONDUTOR AL AISLADOR | B22022400007 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2022-02-24 | 1940 | keep | 0 | Feb | 2022 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-24 08:01 | 2022-02-24 09:43 | 1 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C22022400017 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-02-24 | 102 | keep | 0 | Feb | 2022 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-24 08:04 | 2022-02-24 08:05 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 1590 | keep | 0 | Feb | 2022 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
ARECIBO | 2022-02-24 08:06 | 2022-02-24 09:50 | 80 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22022400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-02-24 | 8320 | keep | 0 | Feb | 2022 | 0.0056667 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-02-24 08:10 | 2022-02-24 11:55 | 10 | 003:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22022400007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 225 | 2022-02-24 | 2250 | keep | 0 | Feb | 2022 | 0.0015325 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-24 08:12 | 2022-02-24 11:17 | 40 | 003:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22022400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-02-24 | 7400 | keep | 0 | Feb | 2022 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-24 08:24 | 2022-02-24 08:25 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22022400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 108 | keep | 0 | Feb | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2022-02-24 08:24 | 2022-02-24 15:39 | 70 | 007:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA Y SE REEMPLAZO AISLADOR ROTO | A22022400012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 435 | 2022-02-24 | 30450 | keep | 0 | Feb | 2022 | 0.020739 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-02-24 08:33 | 2022-02-24 13:54 | 150 | 005:21 | P | DESGANCHE | 3 X 80 EN C/L DESGANHCHE | P22022400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-02-24 | 48150 | keep | 0 | Feb | 2022 | 0.032795 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-02-24 08:48 | 2022-02-24 08:49 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022400025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2635 | keep | 0 | Feb | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
ARECIBO | 2022-02-24 08:55 | 2022-02-24 09:16 | 1 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22022400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-02-24 | 21 | keep | 0 | Feb | 2022 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-24 09:13 | 2022-02-24 13:44 | 13 | 004:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22022400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2022-02-24 | 3523 | keep | 0 | Feb | 2022 | 0.0023995 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2022-02-24 09:28 | 2022-02-24 13:46 | 70 | 004:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22022400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-02-24 | 18060 | keep | 0 | Feb | 2022 | 0.012301 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-02-24 09:30 | 2022-02-24 18:18 | 100 | 008:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22022400128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 528 | 2022-02-24 | 52800 | keep | 0 | Feb | 2022 | 0.035962 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-24 09:30 | 2022-02-24 16:36 | 30 | 007:06 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LAS LINEAS | M22022400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 426 | 2022-02-24 | 12780 | keep | 0 | Feb | 2022 | 0.0087044 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-02-24 09:33 | 2022-02-24 13:19 | 50 | 003:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO AISLADOR Y DESGANCHO | C22022400038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 226 | 2022-02-24 | 11300 | keep | 0 | Feb | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-02-24 09:39 | 2022-02-24 10:56 | 3041 | 001:17 | T | ESTRUCTURA AVERIADA | SE ABRIO MACHETES PARA SECCIONALIZAR Y CONTINUAR PATRULLANDO | M22022400044 | New_Event | Defective Pole | Include | Include | Equipment | 77 | 2022-02-24 | 234157 | keep | 0 | Feb | 2022 | 0.15948 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2022-02-24 10:04 | 2022-02-24 12:56 | 20 | 002:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A22022400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-02-24 | 3440 | keep | 0 | Feb | 2022 | 0.002343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-24 10:07 | 2022-02-24 12:57 | 5 | 002:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22022400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-02-24 | 850 | keep | 0 | Feb | 2022 | 0.00057893 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-24 10:15 | 2022-02-24 10:16 | 1310 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | S22022400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-24 | 1310 | keep | 0 | Feb | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
PONCE | 2022-02-24 10:16 | 2022-02-24 11:11 | 35 | 000:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22022400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-02-24 | 1925 | keep | 0 | Feb | 2022 | 0.0013111 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2022-02-24 10:20 | 2022-02-24 10:21 | 2565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022400048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2565 | keep | 0 | Feb | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BAYAMON | 2022-02-24 10:34 | 2022-02-24 12:03 | 1310 | 001:29 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S22022400145 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-02-24 | 116590 | keep | 0 | Feb | 2022 | 0.079409 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2022-02-24 10:37 | 2022-02-24 10:38 | 2192 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2192 | keep | 0 | Feb | 2022 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
BAYAMON | 2022-02-24 10:45 | 2022-02-24 12:13 | 1984 | 001:28 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA LLEVA 1911-07 | S22022400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-02-24 | 174592 | keep | 0 | Feb | 2022 | 0.11891 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-02-24 10:45 | 2022-02-24 12:13 | 577 | 001:28 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA1529-12 QUE LLEVA 1911-07 | S22022400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-02-24 | 50776 | keep | 0 | Feb | 2022 | 0.034583 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
ARECIBO | 2022-02-24 10:46 | 2022-02-24 10:47 | 2756 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR NEUTRAL SOBRE LINEA | A22022400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-24 | 2756 | keep | 0 | Feb | 2022 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2022-02-24 10:47 | 2022-02-24 10:48 | 2756 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR NEUTRAL SOBRE LINEA | A22022400000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-24 | 2756 | keep | 0 | Feb | 2022 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2022-02-24 10:48 | 2022-02-24 12:31 | 2756 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO NEUTRAL SOBRE LINEA | A22022400041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 103 | 2022-02-24 | 283868 | keep | 0 | Feb | 2022 | 0.19334 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
BARRANQUITAS | 2022-02-24 10:48 | 2022-02-24 14:05 | 40 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22022400052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-02-24 | 7880 | keep | 0 | Feb | 2022 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-02-24 10:56 | 2022-02-24 11:19 | 2280 | 000:23 | P | ESTRUCTURA AVERIADA | PERSONAL INDICA NO IDENTIFICO CAUSA SE CERRO MACHETES | M20222400044 | New_Event | Defective Pole | Include | Include | Equipment | 23 | 2022-02-24 | 52440 | keep | 0 | Feb | 2022 | 0.035717 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
SAN JUAN | 2022-02-24 10:58 | 2022-02-24 16:58 | 100 | 006:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A CAJA | S22022400151 | New_Event | Wire Down | Include | Include | Equipment | 360 | 2022-02-24 | 36000 | keep | 0 | Feb | 2022 | 0.024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-02-24 10:59 | 2022-02-24 15:45 | 75 | 004:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE VA A ABRIR CORTE DE LINEA PARA REPARAR | M22022400164 | New_Event | Wire Down | Include | Include | Equipment | 286 | 2022-02-24 | 21450 | keep | 0 | Feb | 2022 | 0.014609 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-02-24 11:07 | 2022-02-25 08:53 | 10 | 021:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO CAJA PRIMARIA | S22022100155 | New_Event | Cutout Failure | Include | Include | Equipment | 1306 | 2022-02-24 | 13060 | keep | 0 | Feb | 2022 | 0.0088951 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-24 11:08 | 2022-02-24 12:57 | 1 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE BANCO DE XMR | S22022400159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-02-24 | 109 | keep | 0 | Feb | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-02-24 11:08 | 2022-02-24 14:24 | 7 | 003:16 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR DERRAMANDO DE 37.5 KVA X 37.5 KVA | R22022400015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 196 | 2022-02-24 | 1372 | keep | 0 | Feb | 2022 | 0.00093446 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-02-24 11:19 | 2022-02-24 16:20 | 15 | 005:01 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO CON TRANSFORMADOR | M22022400055 | Partial_restoration | Defective Pole | Include | Include | Equipment | 301 | 2022-02-24 | 4515 | keep | 0 | Feb | 2022 | 0.0030751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-24 11:26 | 2022-02-24 13:16 | 237 | 001:50 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C22022400060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-02-24 | 26070 | keep | 0 | Feb | 2022 | 0.017756 | 0.00016142 | Sustained | FALSE | FALSE | Not_TMED_Event | 237
BARRANQUITAS | 2022-02-24 11:37 | 2022-02-24 12:08 | 12 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR, NO FUNDIO FUSIBLE. | C22022400062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2022-02-24 | 372 | keep | 0 | Feb | 2022 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-02-24 11:47 | 2022-02-24 15:30 | 35 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | A22022400054 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-02-24 | 7805 | keep | 0 | Feb | 2022 | 0.0053159 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-02-24 11:48 | 2022-02-24 19:15 | 22 | 007:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22022400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2022-02-24 | 9834 | keep | 0 | Feb | 2022 | 0.0066979 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2022-02-24 12:02 | 2022-02-24 15:27 | 10 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B22022400018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-02-24 | 2050 | keep | 0 | Feb | 2022 | 0.0013962 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-24 12:03 | 2022-02-24 12:35 | 982 | 000:32 | P | DESGANCHE | SE SECCIONALIZO MACHETES CALLE CONSTITUCION Y SE CERRARON OTROS CALLE CORRIENTE PARA REALIZAR DESGANCHE | S22022400145 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 32 | 2022-02-24 | 31424 | keep | 0 | Feb | 2022 | 0.021403 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-24 12:04 | 2022-02-24 12:05 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22022400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 176 | keep | 0 | Feb | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-02-24 12:31 | 2022-02-24 15:23 | 20 | 002:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M22022400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-02-24 | 3440 | keep | 0 | Feb | 2022 | 0.002343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-24 12:31 | 2022-02-24 13:18 | 2147 | 000:47 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA | B22022400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-02-24 | 100909 | keep | 0 | Feb | 2022 | 0.068729 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-02-24 12:35 | 2022-02-24 13:50 | 328 | 001:15 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES EN CALLE CONSTITUCION | S22022400145 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-02-24 | 24600 | keep | 0 | Feb | 2022 | 0.016755 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-24 12:41 | 2022-02-24 18:53 | 60 | 006:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO | S22022400185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-02-24 | 22320 | keep | 0 | Feb | 2022 | 0.015202 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-24 12:43 | 2022-02-24 16:01 | 12 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C22022400069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-02-24 | 2376 | keep | 0 | Feb | 2022 | 0.0016183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-02-24 12:43 | 2022-02-24 12:44 | 393 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 6007-05 QUE LLEVA LA CARGA DEL 6007-04 LINEA PRIMARIA ARRIADA | M22022400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-24 | 393 | keep | 0 | Feb | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-02-24 12:43 | 2022-02-24 12:44 | 4 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M20222400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-24 | 4 | keep | 0 | Feb | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-24 12:44 | 2022-02-24 14:23 | 80 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA LINEA PRIMARIA ARRIADA | M22022400099 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 99 | 2022-02-24 | 7920 | keep | 0 | Feb | 2022 | 0.0053943 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-02-24 12:49 | 2022-02-24 13:36 | 15 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | P22022400071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2022-02-24 | 705 | keep | 0 | Feb | 2022 | 0.00048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-02-24 13:11 | 2022-02-25 13:30 | 3 | 024:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE A CAJA DE TRANSFORMADOR | P22022400238 | New_Event | Wire Down | Include | Include | Equipment | 1459 | 2022-02-24 | 4377 | keep | 0 | Feb | 2022 | 0.0029812 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-02-24 13:11 | 2022-02-24 19:26 | 100 | 006:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22022400101 | New_Event | Wire Down | Include | Include | Equipment | 375 | 2022-02-24 | 37500 | keep | 0 | Feb | 2022 | 0.025541 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-02-24 13:12 | 2022-02-24 14:29 | 50 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES VIENTOS | A22022400064 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2022-02-24 | 3850 | keep | 0 | Feb | 2022 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-24 13:23 | 2022-02-24 15:54 | 681 | 002:31 | T | DESGANCHE | DISPARO DE INTERRUPTOR DE REALIZO DESGANCHE SJ-220224-03 | S22022400192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-02-24 | 102831 | keep | 0 | Feb | 2022 | 0.070038 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
PONCE | 2022-02-24 13:32 | 2022-02-24 15:14 | 125 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA 1 X 100 EN CORTE DE LINEA | P22022400081 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2022-02-24 | 12750 | keep | 0 | Feb | 2022 | 0.008684 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-02-24 13:36 | 2022-02-25 01:20 | 50 | 011:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO PEGANDO CON CRUCETA MEDIANTE G.O.I. SJ-220224-04 | S22022400198 | New_Event | Wire Down | Include | Include | Equipment | 704 | 2022-02-24 | 35200 | keep | 0 | Feb | 2022 | 0.023975 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-02-24 13:36 | 2022-02-24 15:27 | 120 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22022400074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-02-24 | 13320 | keep | 0 | Feb | 2022 | 0.0090722 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-02-24 13:38 | 2022-02-24 18:42 | 150 | 005:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022400107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-02-24 | 45600 | keep | 0 | Feb | 2022 | 0.031058 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-02-24 13:39 | 2022-02-24 17:03 | 65 | 003:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | R22022400022 | New_Event |  |  | Include | Wildlife | 204 | 2022-02-24 | 13260 | keep | 0 | Feb | 2022 | 0.0090313 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-02-24 13:47 | 2022-02-24 16:25 | 7 | 002:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA AISLADOR SAFADO | P22022400085 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 158 | 2022-02-24 | 1106 | keep | 0 | Feb | 2022 | 0.00075329 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-02-24 14:02 | 2022-02-24 17:30 | 300 | 003:28 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022400120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-02-24 | 62400 | keep | 0 | Feb | 2022 | 0.0425 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-02-24 14:08 | 2022-02-24 17:23 | 30 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE CAJA A LINEA | C22022400080 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2022-02-24 | 5850 | keep | 0 | Feb | 2022 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-24 14:10 | 2022-02-24 17:49 | 350 | 003:39 | P | DESGANCHE | 1 X 80 2 X 100 Y 2 X 140 EN CORTES DE LINEA DESGANCHO Y RETEZO LINEAS | R22022400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-02-24 | 76650 | keep | 0 | Feb | 2022 | 0.052206 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
ARECIBO | 2022-02-24 14:12 | 2022-02-24 15:24 | 1 | 001:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y SE CERRO PUENTE | A22022400066 | New_Event | Wire Down | Include | Include | Equipment | 72 | 2022-02-24 | 72 | keep | 0 | Feb | 2022 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-24 14:13 | 2022-02-24 18:42 | 67 | 004:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA QUEMADA | B22022400037 | New_Event | Cutout Failure | Include | Include | Equipment | 269 | 2022-02-24 | 18023 | keep | 0 | Feb | 2022 | 0.012275 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-02-24 14:19 | 2022-02-24 14:21 | 1310 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTORN SE CERRO POR SCADA | S22022400212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-02-24 | 2620 | keep | 0 | Feb | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-02-24 14:20 | 2022-02-24 14:53 | 10 | 000:33 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO PEDESTAL | B22022400039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 33 | 2022-02-24 | 330 | keep | 0 | Feb | 2022 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-24 14:21 | 2022-02-24 15:59 | 4 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO SECUNDARIA | A22022400019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-02-24 | 392 | keep | 0 | Feb | 2022 | 0.00026699 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-02-24 14:29 | 2022-02-24 14:36 | 1310 | 000:07 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22022400217 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-02-24 | 9170 | keep | 0 | Feb | 2022 | 0.0062456 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-02-24 14:36 | 2022-02-24 17:16 | 60 | 002:40 | P | DESGANCHE | 2 X 40 EN C/L SE REALIZO DESGANCHE DE ARBOL | B22022400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-02-24 | 9600 | keep | 0 | Feb | 2022 | 0.0065385 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-24 14:45 | 2022-02-24 15:10 | 1310 | 000:25 | T | DESGANCHE | DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220224-04 | S22022400223 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 25 | 2022-02-24 | 32750 | keep | 0 | Feb | 2022 | 0.022306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 386 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 7720 | keep | 0 | Feb | 2022 | 0.0052581 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 610 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 12200 | keep | 0 | Feb | 2022 | 0.0083094 | 0.00041547 | Sustained | FALSE | FALSE | Not_TMED_Event | 610
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 1785 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 35700 | keep | 0 | Feb | 2022 | 0.024315 | 0.0012158 | Sustained | FALSE | FALSE | Not_TMED_Event | 1785
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 1233 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 24660 | keep | 0 | Feb | 2022 | 0.016796 | 0.00083979 | Sustained | FALSE | FALSE | Not_TMED_Event | 1233
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 584 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400106 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 11680 | keep | 0 | Feb | 2022 | 0.0079552 | 0.00039776 | Sustained | FALSE | FALSE | Not_TMED_Event | 584
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 1658 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400106 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 33160 | keep | 0 | Feb | 2022 | 0.022585 | 0.0011293 | Sustained | FALSE | FALSE | Not_TMED_Event | 1658
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 630 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P22022400106 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 12600 | keep | 0 | Feb | 2022 | 0.0085818 | 0.00042909 | Sustained | FALSE | FALSE | Not_TMED_Event | 630
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 1173 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 23460 | keep | 0 | Feb | 2022 | 0.015978 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 215 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 4300 | keep | 0 | Feb | 2022 | 0.0029287 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:09 | 464 | 000:20 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 100 | P220224000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-02-24 | 9280 | keep | 0 | Feb | 2022 | 0.0063206 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 2100 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400112 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 39900 | keep | 0 | Feb | 2022 | 0.027176 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 922 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400112 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 17518 | keep | 0 | Feb | 2022 | 0.011931 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 1676 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400112 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 31844 | keep | 0 | Feb | 2022 | 0.021689 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 2844 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400112 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 54036 | keep | 0 | Feb | 2022 | 0.036804 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 2775 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 52725 | keep | 0 | Feb | 2022 | 0.035911 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 1457 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 27683 | keep | 0 | Feb | 2022 | 0.018855 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 1086 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 20634 | keep | 0 | Feb | 2022 | 0.014054 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 2134 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 40546 | keep | 0 | Feb | 2022 | 0.027616 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 1464 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 27816 | keep | 0 | Feb | 2022 | 0.018945 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 1833 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 34827 | keep | 0 | Feb | 2022 | 0.023721 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 1565 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 29735 | keep | 0 | Feb | 2022 | 0.020252 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-24 14:49 | 2022-02-24 15:08 | 977 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-02-24 | 18563 | keep | 0 | Feb | 2022 | 0.012643 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
CANOVANAS | 2022-02-24 14:51 | 2022-02-24 17:36 | 30 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22022400025 | New_Event |  |  | Include | Wildlife | 165 | 2022-02-24 | 4950 | keep | 0 | Feb | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-24 14:54 | 2022-02-24 15:21 | 10 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B22022400041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-02-24 | 270 | keep | 0 | Feb | 2022 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-24 14:55 | 2022-02-24 16:29 | 80 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M22022400130 | Partial_restoration | Wire Down | Include | Include | Equipment | 94 | 2022-02-24 | 7520 | keep | 0 | Feb | 2022 | 0.0051218 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-24 15:00 | 2022-02-24 15:01 | 637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6703-03 | M22022400133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 637 | keep | 0 | Feb | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-02-24 15:00 | 2022-02-24 15:01 | 1491 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6703-02 LLEVA LA CARGA DEL 6703-03 | M22022400133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 1491 | keep | 0 | Feb | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-02-24 15:07 | 2022-02-25 00:15 | 100 | 009:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO UNA CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22022400139 | New_Event | Cutout Failure | Include | Include | Equipment | 548 | 2022-02-24 | 54800 | keep | 0 | Feb | 2022 | 0.037324 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-24 15:10 | 2022-02-24 16:08 | 650 | 000:58 | P | DESGANCHE | SE REALIZO DESGANCHE EN CALLE AUSTRIA SJ-220224-04 | S22022400223 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-02-24 | 37700 | keep | 0 | Feb | 2022 | 0.025677 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-02-24 15:10 | 2022-02-24 18:26 | 90 | 003:16 | P | DESGANCHE | 2 X 100 EN C/L SE DESGANCHARON DOS ARBOLES | B22022400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-02-24 | 17640 | keep | 0 | Feb | 2022 | 0.012015 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-02-24 15:11 | 2022-02-24 15:12 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2354 | keep | 0 | Feb | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
ARECIBO | 2022-02-24 15:18 | 2022-02-24 16:57 | 8 | 001:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A22022400081 | New_Event | Cutout Failure | Include | Include | Equipment | 99 | 2022-02-24 | 792 | keep | 0 | Feb | 2022 | 0.00053943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 2100 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 35700 | keep | 0 | Feb | 2022 | 0.024315 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 922 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 15674 | keep | 0 | Feb | 2022 | 0.010675 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 1676 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 28492 | keep | 0 | Feb | 2022 | 0.019406 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 2844 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400139 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 48348 | keep | 0 | Feb | 2022 | 0.03293 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 2775 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 47175 | keep | 0 | Feb | 2022 | 0.032131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 1457 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 24769 | keep | 0 | Feb | 2022 | 0.01687 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 1086 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 18462 | keep | 0 | Feb | 2022 | 0.012574 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 2134 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 36278 | keep | 0 | Feb | 2022 | 0.024709 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 1464 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400141 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 24888 | keep | 0 | Feb | 2022 | 0.016951 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 1833 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400141 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 31161 | keep | 0 | Feb | 2022 | 0.021224 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 1565 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400141 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 26605 | keep | 0 | Feb | 2022 | 0.018121 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 15:21 | 2022-02-24 15:38 | 977 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400141 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-02-24 | 16609 | keep | 0 | Feb | 2022 | 0.011312 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-24 15:25 | 2022-02-24 16:39 | 36 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22022400082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-02-24 | 2664 | keep | 0 | Feb | 2022 | 0.0018144 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BARRANQUITAS | 2022-02-24 15:25 | 2022-02-24 18:01 | 100 | 002:36 | P | DESGANCHE | 2 X 65 EN C/L SE DEGANCHO BAMBUAS | C22022400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-02-24 | 15600 | keep | 0 | Feb | 2022 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-02-24 15:38 | 2022-02-24 15:39 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1089 | keep | 0 | Feb | 2022 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-02-24 15:38 | 2022-02-24 15:39 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 3896 | keep | 0 | Feb | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-02-24 15:38 | 2022-02-24 15:39 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22022400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1467 | keep | 0 | Feb | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2022-02-24 15:38 | 2022-02-25 01:20 | 25 | 009:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22022400151 | New_Event | Bad Weather | Include | Include | Weather | 582 | 2022-02-24 | 14550 | keep | 0 | Feb | 2022 | 0.0099099 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-02-24 15:45 | 2022-02-24 16:18 | 100 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | M22022400164 | Additional_clients | Wire Down | Include | Include | Equipment | 33 | 2022-02-24 | 3300 | keep | 0 | Feb | 2022 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-24 16:06 | 2022-02-24 17:56 | 3 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR VIENTOS | A22022400085 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2022-02-24 | 330 | keep | 0 | Feb | 2022 | 0.00022476 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-02-24 16:07 | 2022-02-24 17:26 | 5 | 001:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE | R22022400030 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2022-02-24 | 395 | keep | 0 | Feb | 2022 | 0.00026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-24 16:12 | 2022-02-24 16:17 | 353 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22022400239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-24 | 1765 | keep | 0 | Feb | 2022 | 0.0012021 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 2100 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400168 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 4200 | keep | 0 | Feb | 2022 | 0.0028606 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 922 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400168 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 1844 | keep | 0 | Feb | 2022 | 0.0012559 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 1676 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400168 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 3352 | keep | 0 | Feb | 2022 | 0.002283 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 2844 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400168 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 5688 | keep | 0 | Feb | 2022 | 0.0038741 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 2775 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P21022400170 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 5550 | keep | 0 | Feb | 2022 | 0.0037801 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 1457 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P21022400170 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 2914 | keep | 0 | Feb | 2022 | 0.0019847 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 1086 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P21022400170 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 2172 | keep | 0 | Feb | 2022 | 0.0014793 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 2134 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P21022400170 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 4268 | keep | 0 | Feb | 2022 | 0.0029069 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 1464 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 2928 | keep | 0 | Feb | 2022 | 0.0019942 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 1833 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 3666 | keep | 0 | Feb | 2022 | 0.0024969 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 3130 | keep | 0 | Feb | 2022 | 0.0021318 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-02-24 16:27 | 2022-02-24 16:29 | 977 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22022400173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-24 | 1954 | keep | 0 | Feb | 2022 | 0.0013309 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-02-24 16:27 | 2022-02-24 16:29 | 2113 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE | P22022400166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-24 | 4226 | keep | 0 | Feb | 2022 | 0.0028783 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-02-24 16:27 | 2022-02-24 16:28 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22022400166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 1478 | keep | 0 | Feb | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
MAYAGÃœEZ | 2022-02-24 16:28 | 2022-02-24 16:29 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22022400173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 176 | keep | 0 | Feb | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-02-24 16:29 | 2022-02-24 16:30 | 393 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR CARGA POR 6007-05 MAL TIEMPO VIENTOS FUERTES LINEA PRIMARIA ARRIADA | M22022400174 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-02-24 | 393 | keep | 0 | Feb | 2022 | 0.00026767 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-24 16:29 | 2022-02-24 16:30 | 4 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES LLEVA LA CARGA DEL 6007-04 | M22022400174 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-24 | 4 | keep | 0 | Feb | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-24 16:30 | 2022-02-24 19:14 | 80 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES LINEA PRIMARIA ARRIADA | M20022400226 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 164 | 2022-02-24 | 13120 | keep | 0 | Feb | 2022 | 0.008936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-24 16:32 | 2022-02-24 21:56 | 8 | 005:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22022400108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 324 | 2022-02-24 | 2592 | keep | 0 | Feb | 2022 | 0.0017654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-02-24 16:33 | 2022-02-24 20:53 | 40 | 004:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22022400243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2022-02-24 | 10400 | keep | 0 | Feb | 2022 | 0.0070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-02-24 16:50 | 2022-02-24 19:45 | 50 | 002:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M20022400191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-02-24 | 8750 | keep | 0 | Feb | 2022 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-24 16:53 | 2022-02-25 02:11 | 40 | 009:18 | P | DESGANCHE | 1X80 EN CORTE DE LINEA | S22022400025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 558 | 2022-02-24 | 22320 | keep | 0 | Feb | 2022 | 0.015202 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-24 16:56 | 2022-02-25 14:40 | 30 | 021:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M22022400194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1304 | 2022-02-24 | 39120 | keep | 0 | Feb | 2022 | 0.026644 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-02-24 17:07 | 2022-02-24 18:04 | 36 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22022400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-02-24 | 2052 | keep | 0 | Feb | 2022 | 0.0013976 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-02-24 17:09 | 2022-02-24 19:30 | 2 | 002:21 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022400201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-02-24 | 282 | keep | 0 | Feb | 2022 | 0.00019207 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-24 17:11 | 2022-02-24 21:00 | 80 | 003:49 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN RISER Y 1 X 65 EN AEREO PROVISIONAL HACIA SU-3. SU-3 PODRIDO Y CON PUNTO CALIENTE | B22022400052 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 229 | 2022-02-24 | 18320 | keep | 0 | Feb | 2022 | 0.012478 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-24 17:12 | 2022-02-24 20:30 | 125 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22022400202 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2022-02-24 | 24750 | keep | 0 | Feb | 2022 | 0.016857 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-02-24 17:13 | 2022-02-24 20:27 | 100 | 003:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022400203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-02-24 | 19400 | keep | 0 | Feb | 2022 | 0.013213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400185 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2100 | keep | 0 | Feb | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400185 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 922 | keep | 0 | Feb | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400185 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1676 | keep | 0 | Feb | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400185 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2844 | keep | 0 | Feb | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400189 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2775 | keep | 0 | Feb | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400189 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1457 | keep | 0 | Feb | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400189 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1086 | keep | 0 | Feb | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400189 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 2134 | keep | 0 | Feb | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400190 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400190 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1833 | keep | 0 | Feb | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400190 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 1565 | keep | 0 | Feb | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-02-24 17:23 | 2022-02-24 17:24 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22022400190 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-24 | 977 | keep | 0 | Feb | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
CAGUAS | 2022-02-24 17:24 | 2022-02-24 18:09 | 50 | 000:45 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | C22022400116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-02-24 | 2250 | keep | 0 | Feb | 2022 | 0.0015325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-02-24 17:34 | 2022-02-24 20:37 | 50 | 003:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 25 EN TRANSFORMADOR SE LEVANTO SECUNDARIA | S22022400256 | New_Event | Secondary Wire Down | Include | Include | Equipment | 183 | 2022-02-24 | 9150 | keep | 0 | Feb | 2022 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-24 17:41 | 2022-02-24 19:17 | 20 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | R22022400033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-02-24 | 1920 | keep | 0 | Feb | 2022 | 0.0013077 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-02-24 17:42 | 2022-02-24 22:30 | 15 | 004:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO LA CAUSA | P22022400214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2022-02-24 | 4320 | keep | 0 | Feb | 2022 | 0.0029423 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-24 17:50 | 2022-02-24 18:42 | 1 | 000:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN XMR SE REEMPLAZO CAJA QUEMADA | S22022400260 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2022-02-24 | 52 | keep | 0 | Feb | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-24 17:52 | 2022-02-25 04:37 | 89 | 010:45 | P | DESGANCHE | 2X65 EN CORTE DE LINEA | S22022400262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2022-02-24 | 57405 | keep | 0 | Feb | 2022 | 0.039098 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BARRANQUITAS | 2022-02-24 17:52 | 2022-02-24 19:54 | 619 | 002:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRONCAL | C22022400122 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-02-24 | 75518 | keep | 0 | Feb | 2022 | 0.051435 | 0.0004216 | Sustained | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2022-02-24 18:01 | 2022-02-24 19:42 | 60 | 001:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22022400089 | New_Event |  |  | Include | Wildlife | 101 | 2022-02-24 | 6060 | keep | 0 | Feb | 2022 | 0.0041274 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-24 18:15 | 2022-02-24 18:20 | 353 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22022400265 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-24 | 1765 | keep | 0 | Feb | 2022 | 0.0012021 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-24 18:31 | 2022-02-25 05:22 | 1290 | 010:51 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S22022400271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 651 | 2022-02-24 | 839790 | keep | 0 | Feb | 2022 | 0.57198 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
UTUADO | 2022-02-24 18:48 | 2022-02-25 16:36 | 20 | 021:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA SE REPARO TENSOR PARTIDO | A22022400092 | New_Event |  |  | Include | Wildlife | 1308 | 2022-02-24 | 26160 | keep | 0 | Feb | 2022 | 0.017817 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-02-24 19:08 | 2022-02-24 19:09 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P220224000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 1173 | keep | 0 | Feb | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
ARECIBO | 2022-02-24 19:17 | 2022-02-24 22:51 | 20 | 003:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22022400094 | New_Event | Bad Weather | Include | Include | Weather | 214 | 2022-02-24 | 4280 | keep | 0 | Feb | 2022 | 0.0029151 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-02-24 19:19 | 2022-02-24 22:23 | 300 | 003:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE SECCIONALIZO CONDUCTOR DEL SUELO | C22022400143 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2022-02-24 | 55200 | keep | 0 | Feb | 2022 | 0.037596 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
YAUCO | 2022-02-24 19:30 | 2022-02-25 07:21 | 300 | 011:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22022400220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 711 | 2022-02-24 | 213300 | keep | 0 | Feb | 2022 | 0.14528 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
YAUCO | 2022-02-24 19:35 | 2022-02-25 09:10 | 17 | 013:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22022400222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2022-02-24 | 13855 | keep | 0 | Feb | 2022 | 0.0094366 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2022-02-24 19:49 | 2022-02-24 19:50 | 519 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 519 | keep | 0 | Feb | 2022 | 0.00035349 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
BARRANQUITAS | 2022-02-24 19:54 | 2022-02-24 20:03 | 1437 | 000:09 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA LLEVAR CONDUCTOR ZAFADO ENCIMA DE CRUCETA EN MALAS CONDICIONES Y REMPLAZAR CAJA PRIMARIA | C22022400154 | Additional_clients | Cutout Failure | Include | Include | Equipment | 9 | 2022-02-24 | 12933 | keep | 0 | Feb | 2022 | 0.0088086 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-02-24 20:22 | 2022-02-24 23:44 | 2747 | 003:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PRIMARIA EN EL PISO EN TRONCAL DEL ALIMENTADOR | P22022400235 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-02-24 | 554894 | keep | 0 | Feb | 2022 | 0.37794 | 0.001871 | Sustained | FALSE | FALSE | Not_TMED_Event | 2747
VEGA BAJA | 2022-02-24 20:24 | 2022-02-24 22:02 | 37 | 001:38 | P | NO SE REPORTO CAUSA | 1X80 EN CORTE DE LINEA | B22022400065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-02-24 | 3626 | keep | 0 | Feb | 2022 | 0.0024697 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
MAYAGÃœEZ | 2022-02-24 21:05 | 2022-02-24 21:37 | 75 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22022400279 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2022-02-24 | 2400 | keep | 0 | Feb | 2022 | 0.0016346 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-02-24 21:05 | 2022-02-24 22:10 | 3 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22022400241 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-02-24 | 195 | keep | 0 | Feb | 2022 | 0.00013281 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-02-24 21:24 | 2022-02-24 21:29 | 353 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22022400281 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-02-24 | 1765 | keep | 0 | Feb | 2022 | 0.0012021 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-24 21:57 | 2022-02-25 10:34 | 5 | 012:37 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22022400162 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 757 | 2022-02-24 | 3785 | keep | 0 | Feb | 2022 | 0.0025779 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-02-24 22:09 | 2022-02-25 09:29 | 80 | 011:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22022400255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 680 | 2022-02-24 | 54400 | keep | 0 | Feb | 2022 | 0.037052 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-02-24 22:14 | 2022-02-25 03:05 | 30 | 004:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22022400283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2022-02-24 | 8730 | keep | 0 | Feb | 2022 | 0.005946 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-02-24 22:23 | 2022-02-25 19:18 | 21 | 020:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO Y SE REALIZO DESGANCHE | C22022400163 | Partial_restoration | Wire Down | Include | Include | Equipment | 1255 | 2022-02-24 | 26355 | keep | 0 | Feb | 2022 | 0.01795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-02-24 23:16 | 2022-02-24 23:17 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 8007-04 | A22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 2228 | keep | 0 | Feb | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-02-24 23:16 | 2022-02-24 23:17 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22022400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-24 | 438 | keep | 0 | Feb | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2022-02-24 23:54 | 2022-02-25 02:31 | 16 | 002:37 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | B22022400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-02-24 | 2512 | keep | 0 | Feb | 2022 | 0.0017109 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-02-25 00:23 | 2022-02-25 12:18 | 120 | 011:55 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE | S22022500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2022-02-25 | 85800 | keep | 0 | Feb | 2022 | 0.058438 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-02-25 00:23 | 2022-02-25 16:17 | 12 | 015:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22022500001 | New_Event | Wire Down | Include | Include | Equipment | 954 | 2022-02-25 | 11448 | keep | 0 | Feb | 2022 | 0.0077972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-02-25 00:56 | 2022-02-25 00:57 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 2605 | keep | 0 | Feb | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2022-02-25 01:02 | 2022-02-25 03:59 | 22 | 002:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X50 EN CORTE DE LINEA SE REMPLAZO AISLADOR DE PORCELANA POR POLIMERO SE REPARO/LEVANTO CONDUCTOR PRIMARIO QUE HABIA CAIDO AL SUELO | S22022500007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 177 | 2022-02-25 | 3894 | keep | 0 | Feb | 2022 | 0.0026522 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2022-02-25 02:08 | 2022-02-25 09:24 | 30 | 007:16 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO RAMA | R22022500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2022-02-25 | 13080 | keep | 0 | Feb | 2022 | 0.0089087 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-02-25 02:09 | 2022-02-25 02:10 | 1173 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P220225000XX | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-02-25 | 1173 | keep | 0 | Feb | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2022-02-25 02:12 | 2022-02-25 02:13 | 1173 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P220225000XX | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-02-25 | 1173 | keep | 0 | Feb | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2022-02-25 02:14 | 2022-02-25 02:15 | 1173 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P220225000XX | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-02-25 | 1173 | keep | 0 | Feb | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2022-02-25 02:16 | 2022-02-25 03:34 | 1173 | 001:18 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR POR MACHETE QUEMADO SE ABREN MACHETES EN TRONCAL DEL ALIMENTADOR PARA SECCIONALIZAR AVERIA | P220225000XX | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 78 | 2022-02-25 | 91494 | keep | 0 | Feb | 2022 | 0.062316 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
MAYAGÃœEZ | 2022-02-25 02:57 | 2022-02-25 06:41 | 80 | 003:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | M22022500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-02-25 | 17920 | keep | 0 | Feb | 2022 | 0.012205 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-02-25 03:34 | 2022-02-25 04:22 | 532 | 000:48 | P | DESCONECTIVO DEFECTUOSO | SE INSTALO PUENTE EN MACHETE QUEMADO Y SE CERRO MACHETE EN TRONCAL DEL ALIMENTADOR | P22022500015 | Partial_restoration | Switch Failure | Include | Include | Equipment | 48 | 2022-02-25 | 25536 | keep | 0 | Feb | 2022 | 0.017392 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-02-25 03:40 | 2022-02-25 07:15 | 60 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L Y 1 X 50 EN C/L SE LEVANTO CONDUCTOR | R22022500002 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2022-02-25 | 12900 | keep | 0 | Feb | 2022 | 0.0087861 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-02-25 05:05 | 2022-02-25 15:13 | 30 | 010:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE | C22022500001 | New_Event |  |  | Include | Wildlife | 608 | 2022-02-25 | 18240 | keep | 0 | Feb | 2022 | 0.012423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-25 06:24 | 2022-02-25 06:25 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22022500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 3718 | keep | 0 | Feb | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2022-02-25 07:32 | 2022-02-25 10:35 | 50 | 003:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L Y 1 X 65 EN C/L SE REPARO AISLADOR Y NEUTRAL | R22022500012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 183 | 2022-02-25 | 9150 | keep | 0 | Feb | 2022 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-02-25 07:44 | 2022-02-25 12:47 | 60 | 005:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTE | P22022500023 | New_Event | Wire Down | Include | Include | Equipment | 303 | 2022-02-25 | 18180 | keep | 0 | Feb | 2022 | 0.012382 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-02-25 08:04 | 2022-02-25 17:24 | 30 | 009:20 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | C22022500007 | New_Event | Defective Pole | Include | Include | Equipment | 560 | 2022-02-25 | 16800 | keep | 0 | Feb | 2022 | 0.011442 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-25 08:08 | 2022-02-25 14:35 | 30 | 006:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M22022500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 387 | 2022-02-25 | 11610 | keep | 0 | Feb | 2022 | 0.0079075 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-02-25 08:09 | 2022-02-25 08:10 | 908 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 908 | keep | 0 | Feb | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
CAGUAS | 2022-02-25 08:13 | 2022-02-25 08:14 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 4634 | keep | 0 | Feb | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
VEGA BAJA | 2022-02-25 08:29 | 2022-02-25 10:25 | 25 | 001:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA | B22022500006 | New_Event | Wire Down | Include | Include | Equipment | 116 | 2022-02-25 | 2900 | keep | 0 | Feb | 2022 | 0.0019752 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-02-25 08:34 | 2022-02-25 11:31 | 1 | 002:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22022500005 | New_Event | Cutout Failure | Include | Include | Equipment | 177 | 2022-02-25 | 177 | keep | 0 | Feb | 2022 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-25 08:47 | 2022-02-25 08:48 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C22022500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 1879 | keep | 0 | Feb | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2022-02-25 08:54 | 2022-02-25 12:44 | 170 | 003:50 | P | DESGANCHE | 2 X 100 EN C/L | C22022500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-02-25 | 39100 | keep | 0 | Feb | 2022 | 0.026631 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
BAYAMON | 2022-02-25 09:06 | 2022-02-25 14:19 | 65 | 005:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 50 EN CORTES DE LINEA SE ESCONTRO AVE | B22022500008 | New_Event |  |  | Include | Wildlife | 313 | 2022-02-25 | 20345 | keep | 0 | Feb | 2022 | 0.013857 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-02-25 09:13 | 2022-02-25 11:35 | 15 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | M22022500019 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2022-02-25 | 2130 | keep | 0 | Feb | 2022 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-25 09:37 | 2022-02-25 11:50 | 1 | 002:13 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L Y 3 X 15 EN SUBESTACION PRIVADA | B22022500011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-02-25 | 133 | keep | 0 | Feb | 2022 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-25 09:38 | 2022-02-25 09:39 | 396 | 000:01 | T | PROTECCION DEFECTUOSA | DISPARO INTERRUPTOR 5016-03 AL REALIZAR PRUEBA DE TRIP POR PERSONAL DE CONSERVACION EN 5016-01 SEÃ‘AL DE DISPARO CRUZADA | P22022500035 | New_Event | Protection Miscoordination | Include | Include | Other | 1 | 2022-02-25 | 396 | keep | 0 | Feb | 2022 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
AGUADILLA | 2022-02-25 09:39 | 2022-02-25 12:35 | 20 | 002:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22022500021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 176 | 2022-02-25 | 3520 | keep | 0 | Feb | 2022 | 0.0023975 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-25 09:46 | 2022-02-25 18:17 | 6 | 008:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNADRIA | S22022500022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 511 | 2022-02-25 | 3066 | keep | 0 | Feb | 2022 | 0.0020882 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-25 09:46 | 2022-02-25 16:01 | 60 | 006:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 SE RETIRO GLOBO DE LINEA | B22022500013 | New_Event |  |  | Include | Wildlife | 375 | 2022-02-25 | 22500 | keep | 0 | Feb | 2022 | 0.015325 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-02-25 10:03 | 2022-02-25 11:15 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR PEDESTAL EN MAL ESTADO | R22022500024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2022-02-25 | 720 | keep | 0 | Feb | 2022 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-25 10:09 | 2022-02-25 10:12 | 1117 | 000:03 | T | NO SE REPORTO CAUSA | CARGA POR 6404-02 | M22022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-25 | 3351 | keep | 0 | Feb | 2022 | 0.0022824 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-02-25 10:09 | 2022-02-25 10:12 | 1671 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6404-01 | M22022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-02-25 | 5013 | keep | 0 | Feb | 2022 | 0.0034143 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
ARECIBO | 2022-02-25 10:13 | 2022-02-25 12:15 | 7 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22022500014 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2022-02-25 | 854 | keep | 0 | Feb | 2022 | 0.00058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-02-25 10:25 | 2022-02-25 11:23 | 6 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22022500015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-25 | 348 | keep | 0 | Feb | 2022 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-02-25 10:33 | 2022-02-25 10:34 | 5063 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR RELIZA UNA OPERACION Y QUEDA EN SERVICIO | P22022500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 5063 | keep | 0 | Feb | 2022 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2022-02-25 10:36 | 2022-02-25 12:30 | 100 | 001:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | P22022500043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 114 | 2022-02-25 | 11400 | keep | 0 | Feb | 2022 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-02-25 10:44 | 2022-02-25 17:07 | 30 | 006:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22022500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 383 | 2022-02-25 | 11490 | keep | 0 | Feb | 2022 | 0.0078258 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-25 10:45 | 2022-02-25 12:04 | 20 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22022500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-02-25 | 1580 | keep | 0 | Feb | 2022 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-25 11:00 | 2022-02-25 11:01 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 1085 | keep | 0 | Feb | 2022 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
MAYAGÃœEZ | 2022-02-25 11:00 | 2022-02-25 14:43 | 15 | 003:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M22022500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 223 | 2022-02-25 | 3345 | keep | 0 | Feb | 2022 | 0.0022783 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-25 11:04 | 2022-02-25 11:05 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22022500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 1 | keep | 0 | Feb | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-25 11:08 | 2022-02-25 16:24 | 50 | 005:16 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO | B22022500007 | New_Event | UG Cable Fault | Include | Include | Equipment | 316 | 2022-02-25 | 15800 | keep | 0 | Feb | 2022 | 0.010761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-02-25 11:30 | 2022-02-25 12:56 | 10 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN XMR SE REPARO SECUNDARIA | R22022500018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2022-02-25 | 860 | keep | 0 | Feb | 2022 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-25 12:11 | 2022-02-25 15:02 | 200 | 002:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE LLEVO CONDUCTOR A AISLADOR | B22022500041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 171 | 2022-02-25 | 34200 | keep | 0 | Feb | 2022 | 0.023293 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-02-25 12:15 | 2022-02-25 12:16 | 30 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22022500012 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-25 | 30 | keep | 0 | Feb | 2022 | 2.0433e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-02-25 12:38 | 2022-02-25 14:16 | 50 | 001:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22022500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-02-25 | 4900 | keep | 0 | Feb | 2022 | 0.0033374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-25 13:05 | 2022-02-25 13:44 | 14 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22022500029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-02-25 | 546 | keep | 0 | Feb | 2022 | 0.00037188 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-02-25 13:06 | 2022-02-25 15:20 | 10 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S22022500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-02-25 | 1340 | keep | 0 | Feb | 2022 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-25 13:12 | 2022-02-25 16:20 | 1 | 003:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | M22022500035 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2022-02-25 | 188 | keep | 0 | Feb | 2022 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-25 13:25 | 2022-02-25 19:25 | 100 | 006:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR EN EL SUELO | B22022500037 | New_Event | Wire Down | Include | Include | Equipment | 360 | 2022-02-25 | 36000 | keep | 0 | Feb | 2022 | 0.024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-25 13:33 | 2022-02-25 15:19 | 80 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE CORTE DE LINEA NO SE REPUSO FUSIBLE | P22022500065 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2022-02-25 | 8480 | keep | 0 | Feb | 2022 | 0.0057757 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-02-25 13:38 | 2022-02-25 13:39 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO | C22022500053 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-25 | 1702 | keep | 0 | Feb | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
HUMACAO | 2022-02-25 13:39 | 2022-02-25 17:48 | 1 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22022500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-02-25 | 249 | keep | 0 | Feb | 2022 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-02-25 13:39 | 2022-02-25 15:02 | 35 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO AVE Y SE REALIZO DESGANCHE | C22022500065 | 1st_after_momentary |  |  | Include | Wildlife | 83 | 2022-02-25 | 2905 | keep | 0 | Feb | 2022 | 0.0019786 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-02-25 13:39 | 2022-02-25 16:31 | 100 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA EN CORTE DE LINEA QUEMADA | P22022500067 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-02-25 | 17200 | keep | 0 | Feb | 2022 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-25 13:47 | 2022-02-25 16:02 | 10 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | C22022500054 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2022-02-25 | 1350 | keep | 0 | Feb | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-25 13:47 | 2022-02-25 13:48 | 638 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22022500055 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-25 | 638 | keep | 0 | Feb | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-02-25 13:48 | 2022-02-25 17:10 | 40 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO IGUANA | C22022500057 | 1st_after_momentary |  |  | Include | Wildlife | 202 | 2022-02-25 | 8080 | keep | 0 | Feb | 2022 | 0.0055033 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-25 13:51 | 2022-02-25 19:58 | 30 | 006:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 50KVA X 37.5 KVA | B22022500055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 367 | 2022-02-25 | 11010 | keep | 0 | Feb | 2022 | 0.0074989 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-02-25 14:07 | 2022-02-25 16:35 | 230 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABREN PUENTES EN CORTE DE LINEA PARA SECCIONALIZAR AVERIA Y LEVANTAR LINEA PRIMARIA | P22022500071 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2022-02-25 | 34040 | keep | 0 | Feb | 2022 | 0.023184 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
CAGUAS | 2022-02-25 14:17 | 2022-02-25 17:47 | 30 | 003:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LINEA | C22022500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-02-25 | 6300 | keep | 0 | Feb | 2022 | 0.0042909 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-02-25 14:18 | 2022-02-25 16:28 | 10 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE RETIRO IGUANA Y SE REALIZO DESGANCHE | C22022500066 | New_Event |  |  | Include | Wildlife | 130 | 2022-02-25 | 1300 | keep | 0 | Feb | 2022 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-25 14:45 | 2022-02-25 16:53 | 20 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA EN RISER | C22022500066 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-02-25 | 2560 | keep | 0 | Feb | 2022 | 0.0017436 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-25 14:57 | 2022-02-26 02:15 | 10 | 011:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE RETEZO LINEA SECUNDARIA ABIERTA | S22022500041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 678 | 2022-02-25 | 6780 | keep | 0 | Feb | 2022 | 0.0046178 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-25 15:04 | 2022-02-25 15:33 | 15 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B22022400024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-02-25 | 435 | keep | 0 | Feb | 2022 | 0.00029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-02-25 15:05 | 2022-02-25 18:30 | 6 | 003:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL PARTIDO | M22022500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 205 | 2022-02-25 | 1230 | keep | 0 | Feb | 2022 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-02-25 15:12 | 2022-02-25 15:18 | 50 | 000:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22022500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-02-25 | 300 | keep | 0 | Feb | 2022 | 0.00020433 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-25 15:15 | 2022-02-25 16:14 | 12 | 000:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M22022500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-02-25 | 708 | keep | 0 | Feb | 2022 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-02-25 15:35 | 2022-02-25 16:44 | 10 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO | M22022500047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2022-02-25 | 690 | keep | 0 | Feb | 2022 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-02-25 15:55 | 2022-02-25 16:38 | 20 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO | M22022500054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-02-25 | 860 | keep | 0 | Feb | 2022 | 0.00058574 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-25 15:55 | 2022-02-25 21:13 | 100 | 005:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22022500075 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2022-02-25 | 31800 | keep | 0 | Feb | 2022 | 0.021659 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-02-25 16:09 | 2022-02-25 17:19 | 60 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22022500084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-02-25 | 4200 | keep | 0 | Feb | 2022 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-02-25 16:10 | 2022-02-25 19:05 | 120 | 002:55 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA POR DESGANCHE | P22022500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-02-25 | 21000 | keep | 0 | Feb | 2022 | 0.014303 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-02-25 16:10 | 2022-02-25 17:06 | 20 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22022500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2022-02-25 | 1120 | keep | 0 | Feb | 2022 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-25 16:11 | 2022-02-25 17:09 | 30 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | B22022500069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-25 | 1740 | keep | 0 | Feb | 2022 | 0.0011851 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-25 16:31 | 2022-02-25 21:24 | 20 | 004:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO PORTAFUSIBLE SE ENCONTRO ABIERTO NO FUNDIO | S22022500053 | New_Event | Cutout Failure | Include | Include | Equipment | 293 | 2022-02-25 | 5860 | keep | 0 | Feb | 2022 | 0.0039912 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-25 16:35 | 2022-02-25 17:42 | 10 | 001:07 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR PARA INSTALAR PARARRAYO | R22022500041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 67 | 2022-02-25 | 670 | keep | 0 | Feb | 2022 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-02-25 16:35 | 2022-02-25 17:50 | 30 | 001:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO Y SE CERRARON PUENTES PRIMARIOS | P22022500071 | Partial_restoration | Wire Down | Include | Include | Equipment | 75 | 2022-02-25 | 2250 | keep | 0 | Feb | 2022 | 0.0015325 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-02-25 16:51 | 2022-02-25 17:25 | 10 | 000:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22022500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2022-02-25 | 340 | keep | 0 | Feb | 2022 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-25 17:07 | 2022-02-25 18:57 | 2635 | 001:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE PASO CARGA AL 9902-03 POR APARENTE BOBINA QUEMADA | C22022500086 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-02-25 | 289850 | keep | 0 | Feb | 2022 | 0.19742 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
CAGUAS | 2022-02-25 17:22 | 2022-02-26 08:45 | 40 | 015:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22022500090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 923 | 2022-02-25 | 36920 | keep | 0 | Feb | 2022 | 0.025146 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-02-25 17:24 | 2022-02-26 09:56 | 40 | 016:32 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 80 EN SU#5 | C22022500094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 992 | 2022-02-25 | 39680 | keep | 0 | Feb | 2022 | 0.027026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-02-25 17:48 | 2022-02-25 17:49 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON | M22022500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-25 | 1287 | keep | 0 | Feb | 2022 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
BAYAMON | 2022-02-25 17:54 | 2022-02-25 19:33 | 100 | 001:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y SE REEMPLAZO CAJA PRIMARIA | B22022500075 | New_Event | Cutout Failure | Include | Include | Equipment | 99 | 2022-02-25 | 9900 | keep | 0 | Feb | 2022 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-25 18:22 | 2022-02-26 09:19 | 50 | 014:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE | C22022500119 | New_Event | Cutout Failure | Include | Include | Equipment | 897 | 2022-02-25 | 44850 | keep | 0 | Feb | 2022 | 0.030547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-25 18:57 | 2022-02-25 20:31 | 10 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22022500048 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-02-25 | 940 | keep | 0 | Feb | 2022 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-25 18:57 | 2022-02-25 23:07 | 34 | 004:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22022500112 | Partial_restoration | Wire Down | Include | Include | Equipment | 250 | 2022-02-25 | 8500 | keep | 0 | Feb | 2022 | 0.0057893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-25 19:19 | 2022-02-25 19:39 | 10 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22022500040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-02-25 | 200 | keep | 0 | Feb | 2022 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-25 19:23 | 2022-02-25 21:55 | 50 | 002:32 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS | C22022500130 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 152 | 2022-02-25 | 7600 | keep | 0 | Feb | 2022 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-02-25 19:25 | 2022-02-26 08:05 | 6 | 012:40 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA POR ARBOL | P22022500103 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 760 | 2022-02-25 | 4560 | keep | 0 | Feb | 2022 | 0.0031058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-25 19:34 | 2022-02-25 22:25 | 80 | 002:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-02-25 | 13680 | keep | 0 | Feb | 2022 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-02-25 20:20 | 2022-02-26 12:41 | 40 | 016:21 | P | ERROR HUMANO | CONTRATISTA PRIVADO INTERCAMBIA FASES PRIMARIAS DURANTE VIA LIBRE D2022-00369 REV.1 SE ABRIERON MONTURAS TRIFASICAS Y SE CORRIGIO FASEO V/L DEL DIA ANTERIOR | P22022600016 | New_Event | Human Error | Include | Include | Other | 981 | 2022-02-25 | 39240 | keep | 0 | Feb | 2022 | 0.026726 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-25 20:37 | 2022-02-25 22:46 | 20 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S22022500064 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2022-02-25 | 2580 | keep | 0 | Feb | 2022 | 0.0017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-02-25 20:38 | 2022-02-25 22:48 | 2379 | 002:10 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR DESGANCHE | P22022500120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-02-25 | 309270 | keep | 0 | Feb | 2022 | 0.21064 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2022-02-25 20:56 | 2022-02-25 21:27 | 30 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR CONECTORES DE BAJANTE SECUNDARIO | B22022500073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2022-02-25 | 930 | keep | 0 | Feb | 2022 | 0.00063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-02-25 21:40 | 2022-02-26 17:15 | 8 | 019:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON BAJANTES SECUNDARIOS DE TRANSFORMADOR | P22022500136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1175 | 2022-02-25 | 9400 | keep | 0 | Feb | 2022 | 0.0064023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-02-25 22:46 | 2022-02-26 00:55 | 90 | 002:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22022500075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-02-25 | 11610 | keep | 0 | Feb | 2022 | 0.0079075 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-02-25 23:01 | 2022-02-26 00:57 | 10 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22022500183 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2022-02-25 | 1160 | keep | 0 | Feb | 2022 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-25 23:06 | 2022-02-26 01:22 | 40 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | B22022500085 | New_Event | Wire Down | Include | Include | Equipment | 136 | 2022-02-25 | 5440 | keep | 0 | Feb | 2022 | 0.0037052 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-25 23:10 | 2022-02-26 10:22 | 100 | 011:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN C/L SE REEMPLAZO AISLADOR PARTIDO | C22022500159 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 672 | 2022-02-25 | 67200 | keep | 0 | Feb | 2022 | 0.04577 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-25 23:26 | 2022-02-26 02:37 | 20 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S22022500067 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2022-02-25 | 3820 | keep | 0 | Feb | 2022 | 0.0026018 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-02-26 02:30 | 2022-02-26 02:31 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR 9203-04 | B22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 1570 | keep | 0 | Feb | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
AGUADILLA | 2022-02-26 02:31 | 2022-02-26 02:32 | 1827 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22022600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-02-26 | 1827 | keep | 0 | Feb | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-02-26 02:32 | 2022-02-26 15:15 | 20 | 012:43 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA POR DESGANCHE | M22022600027 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 763 | 2022-02-26 | 15260 | keep | 0 | Feb | 2022 | 0.010394 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-02-26 02:38 | 2022-02-26 02:40 | 600 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1346-03 LLEVANDO 30% 1346-02 | S22022600000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-02-26 | 1200 | keep | 0 | Feb | 2022 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-02-26 02:38 | 2022-02-26 02:40 | 2422 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1346-03 LLEVANDO 30% 1346-02 | S22022600000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-02-26 | 4844 | keep | 0 | Feb | 2022 | 0.0032992 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
SAN JUAN | 2022-02-26 02:44 | 2022-02-26 04:11 | 600 | 001:27 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1346-03 LLEVANDO 30% 1346-02 SE REMPLAZO MACHETE | S22022600005 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 87 | 2022-02-26 | 52200 | keep | 0 | Feb | 2022 | 0.035553 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-02-26 02:44 | 2022-02-26 04:11 | 2422 | 001:27 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1346-03 LLEVANDO 30% 1346-02 SE REMPLAZO MACHETE QUEMADO | S22022600005 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 87 | 2022-02-26 | 210714 | keep | 0 | Feb | 2022 | 0.14352 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
CANOVANAS | 2022-02-26 03:10 | 2022-02-26 03:11 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 1648 | keep | 0 | Feb | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-02-26 03:11 | 2022-02-26 05:32 | 130 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R22022600001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 141 | 2022-02-26 | 18330 | keep | 0 | Feb | 2022 | 0.012484 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2022-02-26 03:11 | 2022-02-26 13:43 | 25 | 010:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRIMARIA Y DESGANCHE | C22022600009 | New_Event | Cutout Failure | Include | Include | Equipment | 632 | 2022-02-26 | 15800 | keep | 0 | Feb | 2022 | 0.010761 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-02-26 03:33 | 2022-02-26 03:34 | 3833 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 3833 | keep | 0 | Feb | 2022 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2022-02-26 03:34 | 2022-02-26 12:02 | 70 | 008:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO PORTAFUSIBLE | C22022600075 | New_Event | Cutout Failure | Include | Include | Equipment | 508 | 2022-02-26 | 35560 | keep | 0 | Feb | 2022 | 0.02422 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-02-26 03:34 | 2022-02-26 11:00 | 40 | 007:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | C22022600014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 446 | 2022-02-26 | 17840 | keep | 0 | Feb | 2022 | 0.012151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-02-26 04:01 | 2022-02-26 11:17 | 6 | 007:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS QUEMADOS | P22022600001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 436 | 2022-02-26 | 2616 | keep | 0 | Feb | 2022 | 0.0017817 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-02-26 04:46 | 2022-02-26 13:14 | 5 | 008:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22022600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 508 | 2022-02-26 | 2540 | keep | 0 | Feb | 2022 | 0.00173 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-02-26 06:10 | 2022-02-26 18:54 | 300 | 012:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65, 1 X 100, 1 X 80 EN CORTES DE LINEA Y SE LEVANTO CONDUCTOR | B22022600003 | New_Event | Wire Down | Include | Include | Equipment | 764 | 2022-02-26 | 229200 | keep | 0 | Feb | 2022 | 0.15611 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-02-26 06:16 | 2022-02-26 09:26 | 40 | 003:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L SE RETIRO AVE | R22022600002 | New_Event |  |  | Include | Wildlife | 190 | 2022-02-26 | 7600 | keep | 0 | Feb | 2022 | 0.0051763 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-02-26 07:06 | 2022-02-26 10:28 | 30 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22022600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-02-26 | 6060 | keep | 0 | Feb | 2022 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-02-26 07:20 | 2022-02-26 07:21 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22022600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-02-26 07:29 | 2022-02-26 07:30 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22022600008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
MAYAGÃœEZ | 2022-02-26 07:30 | 2022-02-26 07:31 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 179 | keep | 0 | Feb | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
VEGA BAJA | 2022-02-26 07:35 | 2022-02-26 08:38 | 22 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22022600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-02-26 | 1386 | keep | 0 | Feb | 2022 | 0.000944 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2022-02-26 07:41 | 2022-02-26 07:42 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 1702 | keep | 0 | Feb | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BARRANQUITAS | 2022-02-26 07:57 | 2022-02-26 16:45 | 6 | 008:48 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L ELIMINO PARARRAYO | C22022600041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 528 | 2022-02-26 | 3168 | keep | 0 | Feb | 2022 | 0.0021577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-02-26 07:58 | 2022-02-26 07:59 | 4279 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22022600002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-02-26 | 4279 | keep | 0 | Feb | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-02-26 07:59 | 2022-02-26 10:42 | 6 | 002:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PAD MOUNTED T-14 DE 37.5 KVA A 7.62 KV CON LIQUEO DE ACEITE | P22022600009 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 163 | 2022-02-26 | 978 | keep | 0 | Feb | 2022 | 0.00066611 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-26 08:41 | 2022-02-26 13:36 | 15 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22022600015 | New_Event | Wire Down | Include | Include | Equipment | 295 | 2022-02-26 | 4425 | keep | 0 | Feb | 2022 | 0.0030138 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-26 08:54 | 2022-02-26 08:55 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 2605 | keep | 0 | Feb | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
YAUCO | 2022-02-26 09:05 | 2022-02-26 10:42 | 40 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22022600008 | New_Event |  |  | Include | Wildlife | 97 | 2022-02-26 | 3880 | keep | 0 | Feb | 2022 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-02-26 09:05 | 2022-02-26 09:57 | 6 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO CONEXIONES | B22022500056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-02-26 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-26 09:07 | 2022-02-26 09:26 | 5 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO EN PM Y SE REPARO EN PEDESTAL | B22022600013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2022-02-26 | 95 | keep | 0 | Feb | 2022 | 6.4704e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-02-26 09:46 | 2022-02-26 11:22 | 6 | 001:36 | P | NO SE REPORTO CAUSA | SE ABRIO XMR Y SE AJUSTO VOLTAJE | B22022600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-02-26 | 576 | keep | 0 | Feb | 2022 | 0.00039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-26 09:49 | 2022-02-26 13:03 | 60 | 003:14 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | S22022600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-02-26 | 11640 | keep | 0 | Feb | 2022 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-02-26 10:19 | 2022-02-26 11:02 | 25 | 000:43 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER SE TIRO AEREO PROVISIONAL HACIA T-16 | R22022600004 | New_Event | UG Cable Fault | Include | Include | Equipment | 43 | 2022-02-26 | 1075 | keep | 0 | Feb | 2022 | 0.00073218 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-02-26 10:44 | 2022-02-26 10:47 | 293 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED | B22022600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-26 | 879 | keep | 0 | Feb | 2022 | 0.00059868 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2022-02-26 10:44 | 2022-02-26 10:47 | 315 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED | B22022600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-26 | 945 | keep | 0 | Feb | 2022 | 0.00064364 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2022-02-26 10:44 | 2022-02-26 10:47 | 216 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED | B22022600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-26 | 648 | keep | 0 | Feb | 2022 | 0.00044135 | 0.00014712 | Momentary | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2022-02-26 10:44 | 2022-02-26 10:47 | 1310 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED | B22022600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-02-26 | 3930 | keep | 0 | Feb | 2022 | 0.0026767 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
MAYAGÃœEZ | 2022-02-26 10:45 | 2022-02-26 18:00 | 10 | 007:15 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE MASIVO | M22022600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2022-02-26 | 4350 | keep | 0 | Feb | 2022 | 0.0029628 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-02-26 11:02 | 2022-02-26 11:03 | 3003 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO AL PROBAR FUSIBLE EN EVENTO R22022600004 | R22022600000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-02-26 | 3003 | keep | 0 | Feb | 2022 | 0.0020453 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-26 11:03 | 2022-02-26 21:48 | 25 | 010:45 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER SE TIRO AEREO PROVISIONAL HACIA T-16 | R22022600004 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 645 | 2022-02-26 | 16125 | keep | 0 | Feb | 2022 | 0.010983 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-02-26 11:28 | 2022-02-26 11:29 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 1702 | keep | 0 | Feb | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2022-02-26 11:39 | 2022-02-26 12:05 | 293 | 000:26 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED SE LE RETIRO CARGA A SUBESTACION SE REMPLAZO FUSIBLE Y SE ENERGIZO Y NORMALIZO LA CARGA CON BY-220226-01 | S22022600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-02-26 | 7618 | keep | 0 | Feb | 2022 | 0.0051886 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2022-02-26 11:39 | 2022-02-26 12:05 | 315 | 000:26 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED SE LE RETIRO CARGA A SUBESTACION SE REMPLAZO FUSIBLE Y SE ENERGIZO Y NORMALIZO LA CARGA CON BY-220226-01 | S22022600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-02-26 | 8190 | keep | 0 | Feb | 2022 | 0.0055782 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2022-02-26 11:39 | 2022-02-26 12:05 | 216 | 000:26 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED SE LE RETIRO CARGA A SUBESTACION SE REMPLAZO FUSIBLE Y SE ENERGIZO Y NORMALIZO LA CARGA CON BY-220226-01 | S22022600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-02-26 | 5616 | keep | 0 | Feb | 2022 | 0.003825 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2022-02-26 11:39 | 2022-02-26 12:05 | 1310 | 000:26 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 4300 FUNDIO FUSIBLE EN LA ALTA 125 SLOW SPEED SE LE RETIRO CARGA A SUBESTACION SE REMPLAZO FUSIBLE Y SE ENERGIZO Y NORMALIZO LA CARGA CON BY-220226-01 | S22022600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-02-26 | 34060 | keep | 0 | Feb | 2022 | 0.023198 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2022-02-26 11:47 | 2022-02-26 13:41 | 35 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22022600081 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2022-02-26 | 3990 | keep | 0 | Feb | 2022 | 0.0027176 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-02-26 12:04 | 2022-02-26 17:24 | 50 | 005:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A22022600012 | New_Event | Wire Down | Include | Include | Equipment | 320 | 2022-02-26 | 16000 | keep | 0 | Feb | 2022 | 0.010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-02-26 12:36 | 2022-02-26 14:58 | 60 | 002:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22022600019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-02-26 | 8520 | keep | 0 | Feb | 2022 | 0.0058029 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-02-26 12:47 | 2022-02-26 14:33 | 20 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22022600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-02-26 | 2120 | keep | 0 | Feb | 2022 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-02-26 12:58 | 2022-02-26 16:55 | 5 | 003:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO QUEMADO | M22022600025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 237 | 2022-02-26 | 1185 | keep | 0 | Feb | 2022 | 0.0008071 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-02-26 12:59 | 2022-02-26 17:11 | 5 | 004:12 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22022600089 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 252 | 2022-02-26 | 1260 | keep | 0 | Feb | 2022 | 0.00085818 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-26 13:42 | 2022-02-26 13:43 | 60 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22022600007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-02-26 | 60 | keep | 0 | Feb | 2022 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-02-26 13:49 | 2022-02-26 15:48 | 70 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22022600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-02-26 | 8330 | keep | 0 | Feb | 2022 | 0.0056735 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-02-26 13:51 | 2022-02-26 16:40 | 153 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO TRONCAL | S22022600061 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2022-02-26 | 25857 | keep | 0 | Feb | 2022 | 0.017611 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
CANOVANAS | 2022-02-26 14:00 | 2022-02-26 15:00 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22022600009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-02-26 | 600 | keep | 0 | Feb | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-26 14:07 | 2022-02-26 16:35 | 180 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 100 EN C/L'S CRUCE X AVE | C22022600092 | New_Event |  |  | Include | Wildlife | 148 | 2022-02-26 | 26640 | keep | 0 | Feb | 2022 | 0.018144 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
PONCE | 2022-02-26 14:10 | 2022-02-27 08:30 | 30 | 018:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22022600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1100 | 2022-02-26 | 33000 | keep | 0 | Feb | 2022 | 0.022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-26 14:15 | 2022-02-26 19:22 | 9 | 005:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y SE HIZO DESGANCHE | S22022600010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 307 | 2022-02-26 | 2763 | keep | 0 | Feb | 2022 | 0.0018819 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-02-26 14:28 | 2022-02-26 16:05 | 40 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22022600093 | New_Event |  |  | Include | Wildlife | 97 | 2022-02-26 | 3880 | keep | 0 | Feb | 2022 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-26 15:07 | 2022-02-26 17:34 | 10 | 002:27 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | A22022600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-02-26 | 1470 | keep | 0 | Feb | 2022 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-26 15:39 | 2022-02-26 22:26 | 10 | 006:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER HACIA TRANSFORMADOR | S22022600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 407 | 2022-02-26 | 4070 | keep | 0 | Feb | 2022 | 0.0027721 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-02-26 15:39 | 2022-02-26 21:25 | 400 | 005:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A22022600018 | New_Event | Wire Down | Include | Include | Equipment | 346 | 2022-02-26 | 138400 | keep | 0 | Feb | 2022 | 0.094264 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-02-26 15:43 | 2022-02-26 18:17 | 100 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARAR BAJANTE LINEA A CAJA | B22022600039 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2022-02-26 | 15400 | keep | 0 | Feb | 2022 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-26 15:56 | 2022-02-26 18:16 | 300 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B22022600045 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2022-02-26 | 42000 | keep | 0 | Feb | 2022 | 0.028606 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-02-26 16:09 | 2022-02-26 18:47 | 60 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTES DE LINEA | B22022600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-02-26 | 9480 | keep | 0 | Feb | 2022 | 0.0064568 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-26 16:25 | 2022-02-26 19:13 | 100 | 002:48 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S22022600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-02-26 | 16800 | keep | 0 | Feb | 2022 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-02-26 16:38 | 2022-02-26 16:39 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1206-03 QUE ESTA LLEVANDO PARTE DEL 1204-05 | S22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 1500 | keep | 0 | Feb | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-02-26 16:38 | 2022-02-26 16:39 | 3133 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE POR EL 1620-05 LLEVA PARTE 1204-5 | S22022600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-26 | 3133 | keep | 0 | Feb | 2022 | 0.0021339 | 0.0021339 | Momentary | FALSE | FALSE | Not_TMED_Event | 3133
SAN JUAN | 2022-02-26 16:40 | 2022-02-26 17:40 | 380 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE SE REPARO PUENTE PRIMARIO TRONCAL TRAS PATIO | S22022600061 | Additional_clients | Wire Down | Include | Include | Equipment | 60 | 2022-02-26 | 22800 | keep | 0 | Feb | 2022 | 0.015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-02-26 16:43 | 2022-02-26 18:34 | 5 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN XMR REMPLAZO SECUNDARIA QUEMADA | C22022600104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2022-02-26 | 555 | keep | 0 | Feb | 2022 | 0.00037801 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-02-26 17:14 | 2022-02-26 22:30 | 20 | 005:16 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LEVANTO LINEA PRIMARIA DEL PISO | P22022600041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2022-02-26 | 6320 | keep | 0 | Feb | 2022 | 0.0043045 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-02-26 17:19 | 2022-02-26 17:21 | 2900 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22022600109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-26 | 5800 | keep | 0 | Feb | 2022 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BAYAMON | 2022-02-26 17:54 | 2022-02-26 19:29 | 150 | 001:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE RETIRO GLOBO DE LINEA | B22022600058 | New_Event |  |  | Include | Wildlife | 95 | 2022-02-26 | 14250 | keep | 0 | Feb | 2022 | 0.0097056 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-02-26 18:11 | 2022-02-26 22:14 | 10 | 004:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR. SE RETIRO CULEBRA CRUZANDO CAJA TRANSFORMADOR | B22022600060 | New_Event |  |  | Include | Wildlife | 243 | 2022-02-26 | 2430 | keep | 0 | Feb | 2022 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-26 18:14 | 2022-02-26 20:00 | 100 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 50 EN CORTE DE LINEA | B22022600061 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2022-02-26 | 10600 | keep | 0 | Feb | 2022 | 0.0072196 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-02-26 18:14 | 2022-02-27 10:14 | 6 | 016:00 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22022600113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 960 | 2022-02-26 | 5760 | keep | 0 | Feb | 2022 | 0.0039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-02-26 18:19 | 2022-02-27 15:10 | 30 | 020:51 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN DIFERENTES CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M22022600039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1251 | 2022-02-26 | 37530 | keep | 0 | Feb | 2022 | 0.025562 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-26 18:42 | 2022-02-26 18:44 | 1000 | 000:02 | P | DESGANCHE | DISPARO 1620-05 LLEVANDO PARTE DEL 1206-03 | S22022600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-02-26 | 2000 | keep | 0 | Feb | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-02-26 18:42 | 2022-02-26 18:44 | 1615 | 000:02 | T | DESGANCHE | DISPARO 1620-05 LLEVANDO PARTE DEL 1206-3 Y SE CERRO POR SCADA | S22022600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-02-26 | 3230 | keep | 0 | Feb | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2022-02-26 18:44 | 2022-02-26 20:29 | 40 | 001:45 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE RAMA | R22022600019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-02-26 | 4200 | keep | 0 | Feb | 2022 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-02-26 20:56 | 2022-02-27 08:21 | 50 | 011:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22022600131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 685 | 2022-02-26 | 34250 | keep | 0 | Feb | 2022 | 0.023328 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-26 21:04 | 2022-02-26 21:55 | 20 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONECTORES Y PUENTE SECUNDARIO | S22022600106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-02-26 | 1020 | keep | 0 | Feb | 2022 | 0.00069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-26 21:43 | 2022-02-27 07:13 | 55 | 009:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | M22022600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 570 | 2022-02-26 | 31350 | keep | 0 | Feb | 2022 | 0.021352 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
AGUADILLA | 2022-02-26 22:10 | 2022-02-26 23:15 | 4 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO | M22022600043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-02-26 | 260 | keep | 0 | Feb | 2022 | 0.00017708 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-27 02:00 | 2022-02-27 02:01 | 3147 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR POSTE PRIMARIO PARTIDO | M22022700001 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2022-02-27 | 3147 | keep | 0 | Feb | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-02-27 02:01 | 2022-02-27 10:30 | 40 | 008:29 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA POSTE PRIMARIO PARTIDO SE SECCIONALIZO | M22022700003 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 509 | 2022-02-27 | 20360 | keep | 0 | Feb | 2022 | 0.013867 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-27 02:58 | 2022-02-27 07:24 | 154 | 004:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO CAJA PRIMARIA Y PORTA FUSIBLE | C22022700006 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2022-02-27 | 40964 | keep | 0 | Feb | 2022 | 0.0279 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
BAYAMON | 2022-02-27 03:25 | 2022-02-27 05:15 | 83 | 001:50 | P | OTRAS CAUSAS | SE ABRIO DE MH-11 A MH-9 Y SE CERRO INTERRUPTOR 20% EN SERVICIO PROA SOLO LLEVANDO EL 25% DE SU CARGA | S22022700002 | New_Event | Other Causes | Include | Include | Other | 110 | 2022-02-27 | 9130 | keep | 0 | Feb | 2022 | 0.0062184 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
HUMACAO | 2022-02-27 03:25 | 2022-02-27 09:14 | 2 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22022700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2022-02-27 | 698 | keep | 0 | Feb | 2022 | 0.0004754 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-02-27 04:02 | 2022-02-27 05:04 | 100 | 001:02 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B22022700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-02-27 | 6200 | keep | 0 | Feb | 2022 | 0.0042228 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-27 04:02 | 2022-02-27 08:53 | 6 | 004:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22022700001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 291 | 2022-02-27 | 1746 | keep | 0 | Feb | 2022 | 0.0011892 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-02-27 05:15 | 2022-02-27 06:28 | 17 | 001:13 | P | OTRAS CAUSAS | SE CERRO DE MH-9A MH-14A Y SE INSTALO TAG PARA VERIFICAR CAJAS SECAS MH-14A 23% EN SERVICIO PROA | S22022700002 | Partial_restoration | Other Causes | Include | Include | Other | 73 | 2022-02-27 | 1241 | keep | 0 | Feb | 2022 | 0.00084524 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-02-27 05:57 | 2022-02-27 09:43 | 20 | 003:46 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR SE REMPLAZO BUSHING | S22022700003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 226 | 2022-02-27 | 4520 | keep | 0 | Feb | 2022 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-02-27 06:12 | 2022-02-27 09:10 | 80 | 002:58 | P | DESGANCHE | 1 X 80 EN C/L | R22022700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-02-27 | 14240 | keep | 0 | Feb | 2022 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-02-27 06:28 | 2022-02-27 16:58 | 3 | 010:30 | P | OTRAS CAUSAS | SE ABRIO DE MH-9A A MH-14A Y SE RETIRO TOMA DE MH-14A A SUBEST. DONA FELA CLIENTE TIENE QUE REPARAR PROA | S22022700002 | Partial_restoration | Other Causes | Include | Include | Other | 630 | 2022-02-27 | 1890 | keep | 0 | Feb | 2022 | 0.0012873 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-02-27 06:59 | 2022-02-27 11:00 | 50 | 004:01 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22022700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-02-27 | 12050 | keep | 0 | Feb | 2022 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-02-27 07:30 | 2022-02-27 07:31 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-27 | 5630 | keep | 0 | Feb | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-02-27 07:30 | 2022-02-27 07:32 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22022700017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-02-27 | 4252 | keep | 0 | Feb | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2022-02-27 07:32 | 2022-02-27 10:37 | 100 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22022700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-02-27 | 18500 | keep | 0 | Feb | 2022 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-02-27 07:54 | 2022-02-27 10:24 | 3 | 002:30 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22022700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-02-27 | 450 | keep | 0 | Feb | 2022 | 0.00030649 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-02-27 08:04 | 2022-02-27 08:05 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-27 | 4634 | keep | 0 | Feb | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
AGUADILLA | 2022-02-27 08:17 | 2022-02-27 09:45 | 1057 | 001:28 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR CLIENTE PROVOCO RAMA CAYERA SOBRE LINEA | M22022700017 | New_Event |  |  | Include | Wildlife | 88 | 2022-02-27 | 93016 | keep | 0 | Feb | 2022 | 0.063353 | 0.00071992 | Sustained | FALSE | FALSE | Not_TMED_Event | 1057
CANOVANAS | 2022-02-27 08:24 | 2022-02-27 09:41 | 40 | 001:17 | P | DESGANCHE | 1 X 25 EN C/L | R22022700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-02-27 | 3080 | keep | 0 | Feb | 2022 | 0.0020978 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-27 08:49 | 2022-02-27 14:03 | 40 | 005:14 | P | DESGANCHE | 1 X 80 EN C/L | R22022700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-02-27 | 12560 | keep | 0 | Feb | 2022 | 0.0085546 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-02-27 08:52 | 2022-02-27 11:15 | 150 | 002:23 | P | DESGANCHE | 2 X 65 EN C/L | R22022700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-02-27 | 21450 | keep | 0 | Feb | 2022 | 0.014609 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-02-27 09:11 | 2022-02-27 12:09 | 126 | 002:58 | P | OTRAS CAUSAS | 1 X 80 EN SMU-20 CONTAMINACION SUBEST. PRIVADA | S22022700021 | New_Event | Other Causes | Include | Include | Other | 178 | 2022-02-27 | 22428 | keep | 0 | Feb | 2022 | 0.015276 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
CANOVANAS | 2022-02-27 09:36 | 2022-02-27 11:18 | 100 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN C/LS CRUCE X AVE REMPLAZO PIN POLE TOP | R22022700044 | New_Event |  |  | Include | Wildlife | 102 | 2022-02-27 | 10200 | keep | 0 | Feb | 2022 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-27 09:45 | 2022-02-27 11:41 | 60 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22022700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-02-27 | 6960 | keep | 0 | Feb | 2022 | 0.0047404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-02-27 09:46 | 2022-02-27 13:44 | 693 | 003:58 | T | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO DISCO PARTIDO Y TERMINACION EN EL RISER DE SALIDA | R22022700058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 238 | 2022-02-27 | 164934 | keep | 0 | Feb | 2022 | 0.11234 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
MAYAGÃœEZ | 2022-02-27 09:53 | 2022-02-27 16:50 | 1 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRO RECLOSER EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22022700032 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2022-02-27 | 417 | keep | 0 | Feb | 2022 | 0.00028402 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-27 10:12 | 2022-02-27 12:24 | 50 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22022700033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-02-27 | 6600 | keep | 0 | Feb | 2022 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-02-27 10:29 | 2022-02-27 14:16 | 400 | 003:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 80 SMU 20 EN SU -1 1 X 65 Y 2 X 25 EN C/LS REMPLAZO 1 CAJA QUEMADA Y 2 AVERIADAS | R22022700065 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2022-02-27 | 90800 | keep | 0 | Feb | 2022 | 0.061843 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2022-02-27 10:30 | 2022-02-27 15:47 | 30 | 005:17 | P | ESTRUCTURA AVERIADA | 3 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M22022700039 | New_Event | Defective Pole | Include | Include | Equipment | 317 | 2022-02-27 | 9510 | keep | 0 | Feb | 2022 | 0.0064772 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-02-27 10:43 | 2022-02-27 13:40 | 12 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE LEVANTO SECUNDARIA | S22022700039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2022-02-27 | 2124 | keep | 0 | Feb | 2022 | 0.0014466 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-02-27 10:52 | 2022-02-27 12:11 | 7 | 001:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22022700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-02-27 | 553 | keep | 0 | Feb | 2022 | 0.00037665 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-02-27 10:54 | 2022-02-27 15:30 | 39 | 004:36 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR MANUAL ELECTRICO | M22022700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-02-27 | 10764 | keep | 0 | Feb | 2022 | 0.0073313 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2022-02-27 10:58 | 2022-02-27 11:06 | 55 | 000:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22022700044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-02-27 | 440 | keep | 0 | Feb | 2022 | 0.00029968 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2022-02-27 11:00 | 2022-02-27 12:21 | 6 | 001:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 4.16 KV AVERIADO Y SE NORMALIZO CARGA SECUNDARIA LA CUAL HABIA SIDO TRANSFERIDA A TRANSFORMADOR ALEDAÃ‘O | P22022700006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2022-02-27 | 486 | keep | 0 | Feb | 2022 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-02-27 11:03 | 2022-02-27 11:04 | 1307 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22022700052 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-27 | 1307 | keep | 0 | Feb | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-02-27 11:04 | 2022-02-27 12:08 | 111 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L GLOBO DE CUMPLEAÃ‘OS CRUZO LA LINEA | C22022700057 | 1st_after_momentary |  |  | Include | Wildlife | 64 | 2022-02-27 | 7104 | keep | 0 | Feb | 2022 | 0.0048385 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
MAYAGÃœEZ | 2022-02-27 11:36 | 2022-02-28 10:44 | 60 | 023:08 | P | DESGANCHE | 1 X 65 EN CORTRE DE LINEA REQUIERE DESGANCHE | M22022700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1388 | 2022-02-27 | 83280 | keep | 0 | Feb | 2022 | 0.056722 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-27 11:43 | 2022-02-27 12:22 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR SE REPARO SECUNDARIA | B22022700018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-02-27 | 390 | keep | 0 | Feb | 2022 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-02-27 12:04 | 2022-02-27 13:02 | 6 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22022700057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-02-27 | 348 | keep | 0 | Feb | 2022 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-02-27 12:11 | 2022-02-27 15:43 | 2 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS Y CONECTORES | P22022700010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2022-02-27 | 424 | keep | 0 | Feb | 2022 | 0.00028878 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-02-27 12:28 | 2022-02-27 13:41 | 1 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN C/L CRUCE POR AVE | C22022700059 | New_Event |  |  | Include | Wildlife | 73 | 2022-02-27 | 73 | keep | 0 | Feb | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-02-27 12:31 | 2022-02-27 15:24 | 30 | 002:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE DESGANCHO | B22022700021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-02-27 | 5190 | keep | 0 | Feb | 2022 | 0.0035349 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-02-27 13:13 | 2022-02-27 18:25 | 253 | 005:12 | P | HERRAJE ROTO O PODRIDO | SE ABRE CORTE DE LINEA PARA REMPLAZAR CRUCETA Y SE REMPLAZO TRANSFORMADOR 37.5KVA | S22022700054 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 312 | 2022-02-27 | 78936 | keep | 0 | Feb | 2022 | 0.053763 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
BAYAMON | 2022-02-27 13:27 | 2022-02-27 14:34 | 100 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22022700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-02-27 | 6700 | keep | 0 | Feb | 2022 | 0.0045633 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-27 13:36 | 2022-02-27 15:25 | 15 | 001:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO | B22022700032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 109 | 2022-02-27 | 1635 | keep | 0 | Feb | 2022 | 0.0011136 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-27 13:36 | 2022-02-27 15:25 | 75 | 001:49 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA Y SE DESGANCHO | B22022700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-02-27 | 8175 | keep | 0 | Feb | 2022 | 0.005568 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-02-27 13:52 | 2022-02-27 13:53 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22022700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-27 | 4035 | keep | 0 | Feb | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
CANOVANAS | 2022-02-27 14:11 | 2022-02-27 15:31 | 60 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 50 EN C/L CRUCE X AVE | R22022700103 | New_Event |  |  | Include | Wildlife | 80 | 2022-02-27 | 4800 | keep | 0 | Feb | 2022 | 0.0032693 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-02-27 14:32 | 2022-02-27 14:50 | 5 | 000:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22022700106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2022-02-27 | 90 | keep | 0 | Feb | 2022 | 6.1299e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-02-27 14:34 | 2022-02-27 21:30 | 60 | 006:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M22022700074 | New_Event | Wire Down | Include | Include | Equipment | 416 | 2022-02-27 | 24960 | keep | 0 | Feb | 2022 | 0.017 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-02-27 14:34 | 2022-02-27 17:37 | 100 | 003:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22022700075 | New_Event | Bad Weather | Include | Include | Weather | 183 | 2022-02-27 | 18300 | keep | 0 | Feb | 2022 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-02-27 14:48 | 2022-02-27 15:23 | 5 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA CAMBIAR BAJANTES SECUNDARIOS Y CONECTORES | P22022700014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-02-27 | 175 | keep | 0 | Feb | 2022 | 0.00011919 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-02-27 15:05 | 2022-02-27 15:06 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22022700084 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-27 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-02-27 15:10 | 2022-02-27 15:11 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22022700085 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-02-27 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-02-27 15:16 | 2022-02-27 15:17 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22022700086 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2022-02-27 | 3041 | keep | 0 | Feb | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-02-27 15:17 | 2022-02-27 18:25 | 4 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN RISER LLUVIA Y FUERTES VIENTOS | M22022700135 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 188 | 2022-02-27 | 752 | keep | 0 | Feb | 2022 | 0.00051218 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-02-27 15:24 | 2022-02-27 20:30 | 100 | 005:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22022700097 | New_Event | Bad Weather | Include | Include | Weather | 306 | 2022-02-27 | 30600 | keep | 0 | Feb | 2022 | 0.020842 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-27 15:36 | 2022-02-28 15:58 | 50 | 024:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A22022700011 | New_Event | Wire Down | Include | Include | Equipment | 1462 | 2022-02-27 | 73100 | keep | 0 | Feb | 2022 | 0.049788 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-02-27 15:52 | 2022-02-27 17:03 | 15 | 001:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 50KVA POR OTRO DE 50KVA | A22022700017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 71 | 2022-02-27 | 1065 | keep | 0 | Feb | 2022 | 0.00072537 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-02-27 16:31 | 2022-02-27 17:40 | 10 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R22022700111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2022-02-27 | 690 | keep | 0 | Feb | 2022 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-02-27 16:54 | 2022-02-27 21:17 | 122 | 004:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA GLOBO CRUZO FASE | S22022700067 | New_Event |  |  | Include | Wildlife | 263 | 2022-02-27 | 32086 | keep | 0 | Feb | 2022 | 0.021854 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
UTUADO | 2022-02-27 17:10 | 2022-02-27 17:59 | 3502 | 000:49 | S | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO CARGA A LA SUBESTACION POR AVE QUE CRUZO LINEAS Y QUEMO AISLACION EN MACHETES SOLIDOS | A22022700031 | New_Event |  |  | Include | Wildlife | 49 | 2022-02-27 | 171598 | keep | 0 | Feb | 2022 | 0.11687 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-02-27 17:10 | 2022-02-27 17:59 | 1241 | 000:49 | S | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO CARGA A LA SUBESTACION POR AVE QUE CRUZO LINEAS Y QUEMO AISLACION EN MACHETES SOLIDOS | A22022700031 | New_Event |  |  | Include | Wildlife | 49 | 2022-02-27 | 60809 | keep | 0 | Feb | 2022 | 0.041417 | 0.00084524 | Sustained | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-02-27 17:10 | 2022-02-27 17:59 | 650 | 000:49 | S | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO CARGA A LA SUBESTACION POR AVE QUE CRUZO LINEAS Y QUEMO AISLACION EN MACHETES SOLIDOS | A22022700031 | New_Event |  |  | Include | Wildlife | 49 | 2022-02-27 | 31850 | keep | 0 | Feb | 2022 | 0.021693 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 2791 | keep | 0 | Feb | 2022 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1464 | keep | 0 | Feb | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 759 | keep | 0 | Feb | 2022 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1500 | keep | 0 | Feb | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 2132 | keep | 0 | Feb | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 2366 | keep | 0 | Feb | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1976 | keep | 0 | Feb | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2022-02-27 17:30 | 2022-02-27 17:31 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 3688 | keep | 0 | Feb | 2022 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 3070 | keep | 0 | Feb | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 2735 | keep | 0 | Feb | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1070 | keep | 0 | Feb | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1647 | keep | 0 | Feb | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 3295 | keep | 0 | Feb | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1180 | keep | 0 | Feb | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 320 | keep | 0 | Feb | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-02-27 17:30 | 2022-02-27 17:31 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 2234 | keep | 0 | Feb | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2022-02-27 17:38 | 2022-02-27 17:39 | 614 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 614 | keep | 0 | Feb | 2022 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-02-27 17:38 | 2022-02-27 17:39 | 770 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 770 | keep | 0 | Feb | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-02-27 17:38 | 2022-02-27 17:39 | 1271 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1271 | keep | 0 | Feb | 2022 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-02-27 17:38 | 2022-02-27 17:39 | 247 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 247 | keep | 0 | Feb | 2022 | 0.00016823 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
BAYAMON | 2022-02-27 17:40 | 2022-02-28 04:02 | 3070 | 010:22 | S | ESTRUCTURA AVERIADA | SE LE HIZO PRUEBA A TRANSFORMADOR Y SE REMPLAZARON FUSIBLES DE ALTA. SE REPARO MACHETE DE BARRA DE 9501-02 Y SE NORMALIZO SU CARGA. CARGA DE 9501-01 SE TRANSFIRIO AL 9501-03 POR BARRA INSPECCION POR BUSHING DE BARRA DE 9501-01 QUEMADOS. | B22022700065 | New_Event | Defective Pole | Include | Include | Equipment | 622 | 2022-02-27 | 1909540 | keep | 0 | Feb | 2022 | 1.3006 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-02-27 17:40 | 2022-02-28 04:02 | 2735 | 010:22 | S | ESTRUCTURA AVERIADA | SE LE HIZO PRUEBA A TRANSFORMADOR Y SE REMPLAZARON FUSIBLES DE ALTA. SE REPARO MACHETE DE BARRA DE 9501-02 Y SE NORMALIZO SU CARGA. CARGA DE 9501-01 SE TRANSFIRIO AL 9501-03 POR BARRA INSPECCION POR BUSHING DE BARRA DE 9501-01 QUEMADOS. | B22022700065 | New_Event | Defective Pole | Include | Include | Equipment | 622 | 2022-02-27 | 1701170 | keep | 0 | Feb | 2022 | 1.1587 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-02-27 17:40 | 2022-02-28 04:02 | 1070 | 010:22 | S | ESTRUCTURA AVERIADA | SE LE HIZO PRUEBA A TRANSFORMADOR Y SE REMPLAZARON FUSIBLES DE ALTA. SE REPARO MACHETE DE BARRA DE 9501-02 Y SE NORMALIZO SU CARGA. CARGA DE 9501-01 SE TRANSFIRIO AL 9501-03 POR BARRA INSPECCION POR BUSHING DE BARRA DE 9501-01 QUEMADOS. | B22022700065 | New_Event | Defective Pole | Include | Include | Equipment | 622 | 2022-02-27 | 665540 | keep | 0 | Feb | 2022 | 0.4533 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-02-27 17:40 | 2022-02-27 17:41 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINE 36100 | B22022700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1647 | keep | 0 | Feb | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-02-27 17:40 | 2022-02-27 17:41 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINE 36100 | B22022700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 3295 | keep | 0 | Feb | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-02-27 17:40 | 2022-02-27 17:41 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINE 36100 | B22022700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 1180 | keep | 0 | Feb | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-02-27 17:40 | 2022-02-27 17:41 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 320 | keep | 0 | Feb | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-02-27 17:40 | 2022-02-27 17:41 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22022700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-02-27 | 2234 | keep | 0 | Feb | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-02-27 17:42 | 2022-02-27 19:42 | 3597 | 002:00 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUAL EN EL CAMPO | B22022700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-02-27 | 431640 | keep | 0 | Feb | 2022 | 0.29399 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
FAJARDO | 2022-02-27 17:42 | 2022-02-27 18:28 | 20 | 000:46 | P | DESGANCHE | 1 X 30 EN C/L | R22022700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2022-02-27 | 920 | keep | 0 | Feb | 2022 | 0.00062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-27 17:52 | 2022-02-28 00:45 | 100 | 006:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22022700129 | New_Event | Cutout Failure | Include | Include | Equipment | 413 | 2022-02-27 | 41300 | keep | 0 | Feb | 2022 | 0.028129 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-27 17:55 | 2022-02-28 12:38 | 60 | 018:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22022700130 | New_Event | Bad Weather | Include | Include | Weather | 1123 | 2022-02-27 | 67380 | keep | 0 | Feb | 2022 | 0.045892 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-27 18:16 | 2022-02-28 09:35 | 10 | 015:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES LLUVIAS | A22022700050 | New_Event | Bad Weather | Include | Include | Weather | 919 | 2022-02-27 | 9190 | keep | 0 | Feb | 2022 | 0.0062593 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 574 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 37884 | keep | 0 | Feb | 2022 | 0.025803 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 2493 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 164538 | keep | 0 | Feb | 2022 | 0.11207 | 0.001698 | Sustained | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 1415 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 93390 | keep | 0 | Feb | 2022 | 0.063608 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 1428 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 94248 | keep | 0 | Feb | 2022 | 0.064192 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 1036 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 68376 | keep | 0 | Feb | 2022 | 0.046571 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 382 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 25212 | keep | 0 | Feb | 2022 | 0.017172 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 19:23 | 39 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2022-02-27 | 2574 | keep | 0 | Feb | 2022 | 0.0017531 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 23:03 | 2366 | 004:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 286 | 2022-02-27 | 676676 | keep | 0 | Feb | 2022 | 0.46088 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-02-27 18:17 | 2022-02-27 23:03 | 1337 | 004:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 286 | 2022-02-27 | 382382 | keep | 0 | Feb | 2022 | 0.26044 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-02-27 18:17 | 2022-02-27 23:03 | 709 | 004:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22022700167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 286 | 2022-02-27 | 202774 | keep | 0 | Feb | 2022 | 0.13811 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
MAYAGÃœEZ | 2022-02-27 18:33 | 2022-02-27 18:35 | 281 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 562 | keep | 0 | Feb | 2022 | 0.00038278 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-02-27 18:33 | 2022-02-27 18:35 | 1252 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 2504 | keep | 0 | Feb | 2022 | 0.0017055 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-02-27 18:33 | 2022-02-27 18:35 | 595 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 1190 | keep | 0 | Feb | 2022 | 0.0008105 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-02-27 18:33 | 2022-02-27 18:35 | 51 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 102 | keep | 0 | Feb | 2022 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-02-27 18:33 | 2022-02-27 18:35 | 721 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 1442 | keep | 0 | Feb | 2022 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-02-27 18:33 | 2022-02-27 18:35 | 1382 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 2764 | keep | 0 | Feb | 2022 | 0.0018825 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-02-27 18:33 | 2022-02-27 18:35 | 654 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22022700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-02-27 | 1308 | keep | 0 | Feb | 2022 | 0.00089087 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
HUMACAO | 2022-02-27 19:18 | 2022-02-28 06:20 | 30 | 011:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22022700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 662 | 2022-02-27 | 19860 | keep | 0 | Feb | 2022 | 0.013527 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-02-27 19:28 | 2022-02-27 19:29 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22022700291 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-02-27 | 1827 | keep | 0 | Feb | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-02-27 19:29 | 2022-02-28 00:46 | 150 | 005:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES LLUVIAS | M22022700294 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 317 | 2022-02-27 | 47550 | keep | 0 | Feb | 2022 | 0.032386 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-02-27 20:55 | 2022-02-28 16:36 | 60 | 019:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M22022700351 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1181 | 2022-02-27 | 70860 | keep | 0 | Feb | 2022 | 0.048262 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-02-27 22:19 | 2022-02-28 10:13 | 100 | 011:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22022700070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 714 | 2022-02-27 | 71400 | keep | 0 | Feb | 2022 | 0.04863 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-27 23:26 | 2022-02-28 10:18 | 100 | 010:52 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS AVERIADO | M22022700388 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 652 | 2022-02-27 | 65200 | keep | 0 | Feb | 2022 | 0.044407 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-02-28 00:30 | 2022-02-28 11:07 | 150 | 010:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | A22022800001 | New_Event | Cutout Failure | Include | Include | Equipment | 637 | 2022-02-28 | 95550 | keep | 0 | Feb | 2022 | 0.065079 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-02-28 01:09 | 2022-02-28 03:09 | 406 | 002:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA PODER REPARAR LINEA PRIMARIA PARTIDA EN TRONCAL DEL INTERRUPTOR | M22022800003 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2022-02-28 | 48720 | keep | 0 | Feb | 2022 | 0.033183 | 0.00027652 | Sustained | FALSE | FALSE | Not_TMED_Event | 406
MAYAGÃœEZ | 2022-02-28 05:01 | 2022-02-28 10:47 | 30 | 005:46 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22022800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2022-02-28 | 10380 | keep | 0 | Feb | 2022 | 0.0070698 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-02-28 05:37 | 2022-02-28 10:40 | 100 | 005:03 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA LOS FUSIBLES FUNDIDOS | M22022800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2022-02-28 | 30300 | keep | 0 | Feb | 2022 | 0.020637 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-28 06:31 | 2022-02-28 07:32 | 1 | 001:01 | P | NO SE REPORTO CAUSA | 1X30 EN CORTE DE LINEA | B22022800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-02-28 | 61 | keep | 0 | Feb | 2022 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-28 06:50 | 2022-02-28 06:51 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE IINTERRUPTOR | M22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 312 | keep | 0 | Feb | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
PONCE | 2022-02-28 06:59 | 2022-02-28 08:57 | 40 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | P22022800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-02-28 | 4720 | keep | 0 | Feb | 2022 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-02-28 07:13 | 2022-02-28 07:14 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22022800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 2302 | keep | 0 | Feb | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
BAYAMON | 2022-02-28 07:15 | 2022-02-28 13:17 | 50 | 006:02 | P | DESGANCHE | 1X10 EN CORTE DE LINEA | S22022800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-02-28 | 18100 | keep | 0 | Feb | 2022 | 0.012328 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-02-28 07:24 | 2022-02-28 10:19 | 8 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22022800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2022-02-28 | 1400 | keep | 0 | Feb | 2022 | 0.00095353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-02-28 07:32 | 2022-02-28 10:31 | 172 | 002:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO PRIMARIA | S22022800005 | New_Event | Wire Down | Include | Include | Equipment | 179 | 2022-02-28 | 30788 | keep | 0 | Feb | 2022 | 0.02097 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2022-02-28 07:56 | 2022-02-28 11:50 | 5 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22022800011 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2022-02-28 | 1170 | keep | 0 | Feb | 2022 | 0.00079688 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-02-28 08:15 | 2022-02-28 19:17 | 10 | 011:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZA TRANSFORMADOR AVERIADO DE 50KVA A 2.4KV POR UNO DE LA MISMA CAPACIDAD | P22022800003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 662 | 2022-02-28 | 6620 | keep | 0 | Feb | 2022 | 0.0045089 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-28 08:31 | 2022-02-28 12:46 | 1 | 004:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22022800015 | New_Event |  |  | Include | Wildlife | 255 | 2022-02-28 | 255 | keep | 0 | Feb | 2022 | 0.00017368 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-02-28 08:35 | 2022-02-28 12:07 | 382 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 100 Y 1 X 140 EN CORTE DE LINEA SE ENDERESO POSTE CAMION BASURA SE ENREDO CABLE TV Y VIRO POSTE LUMA Y CRUZO FASE | S22022800011 | New_Event |  |  | Include | Wildlife | 212 | 2022-02-28 | 80984 | keep | 0 | Feb | 2022 | 0.055158 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
CAGUAS | 2022-02-28 08:39 | 2022-02-28 10:46 | 1 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22022800004 | New_Event |  |  | Include | Wildlife | 127 | 2022-02-28 | 127 | keep | 0 | Feb | 2022 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-02-28 08:39 | 2022-02-28 11:11 | 10 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO REPORTO CAUSA | A22022800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-02-28 | 1520 | keep | 0 | Feb | 2022 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-02-28 09:01 | 2022-02-28 15:44 | 7 | 006:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22022800006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 403 | 2022-02-28 | 2821 | keep | 0 | Feb | 2022 | 0.0019214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-02-28 09:11 | 2022-02-28 17:57 | 60 | 008:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22022800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 526 | 2022-02-28 | 31560 | keep | 0 | Feb | 2022 | 0.021495 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-02-28 09:11 | 2022-02-28 11:36 | 20 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X40 EN CORTE DE LINEA Y SE REMPLAZO BAJANTE PRIMARIO | B22022800014 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2022-02-28 | 2900 | keep | 0 | Feb | 2022 | 0.0019752 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-02-28 09:22 | 2022-02-28 11:17 | 16 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRONCAL SECUNDARIO | B22022700019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2022-02-28 | 1840 | keep | 0 | Feb | 2022 | 0.0012532 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-02-28 09:25 | 2022-02-28 13:09 | 12 | 003:44 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA | A22022800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-02-28 | 2688 | keep | 0 | Feb | 2022 | 0.0018308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-02-28 09:28 | 2022-02-28 12:58 | 25 | 003:30 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L REMPLAZO PARARRAYO | C22022800008 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 210 | 2022-02-28 | 5250 | keep | 0 | Feb | 2022 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-02-28 09:42 | 2022-02-28 10:05 | 70 | 000:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A22022800028 | New_Event | Bad Weather | Include | Include | Weather | 23 | 2022-02-28 | 1610 | keep | 0 | Feb | 2022 | 0.0010966 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-02-28 09:49 | 2022-02-28 11:12 | 10 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | R22022800005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-02-28 | 830 | keep | 0 | Feb | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-02-28 10:01 | 2022-02-28 15:24 | 100 | 005:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M22022800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2022-02-28 | 32300 | keep | 0 | Feb | 2022 | 0.021999 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-02-28 10:07 | 2022-02-28 12:11 | 40 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22022800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-02-28 | 4960 | keep | 0 | Feb | 2022 | 0.0033782 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-02-28 10:14 | 2022-02-28 11:50 | 15 | 001:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE QUEMADO | A22022800034 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2022-02-28 | 1440 | keep | 0 | Feb | 2022 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-02-28 10:44 | 2022-02-28 11:09 | 1 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | R22020800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-02-28 | 25 | keep | 0 | Feb | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-28 10:45 | 2022-02-28 12:18 | 115 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22022800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-02-28 | 10695 | keep | 0 | Feb | 2022 | 0.0072843 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
MAYAGÃœEZ | 2022-02-28 11:17 | 2022-02-28 16:00 | 1 | 004:43 | P | DESGANCHE | 1 X 5 EN TRANSFORMADOR POR DESGANCHE | M22022800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2022-02-28 | 283 | keep | 0 | Feb | 2022 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-02-28 11:32 | 2022-02-28 16:35 | 1 | 005:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M22022800049 | New_Event | Wire Down | Include | Include | Equipment | 303 | 2022-02-28 | 303 | keep | 0 | Feb | 2022 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-02-28 11:44 | 2022-02-28 15:08 | 80 | 003:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22022800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-02-28 | 16320 | keep | 0 | Feb | 2022 | 0.011115 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-02-28 11:47 | 2022-02-28 15:00 | 11 | 003:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA IMPACTADA POR CAMION | R22022800015 | New_Event |  |  | Include | Wildlife | 193 | 2022-02-28 | 2123 | keep | 0 | Feb | 2022 | 0.001446 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2022-02-28 11:50 | 2022-02-28 12:25 | 3 | 000:35 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR PEDESTAL SECUNDARIO | P22022800017 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 35 | 2022-02-28 | 105 | keep | 0 | Feb | 2022 | 7.1515e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-02-28 11:50 | 2022-02-28 12:21 | 2 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN MONTURA TRIFASICA PARA REMPLAZAR CONECTORES EN BAJANTES SECUNDARIOS | P22022800019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2022-02-28 | 62 | keep | 0 | Feb | 2022 | 4.2228e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-02-28 11:53 | 2022-02-28 12:55 | 57 | 001:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22022800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-02-28 | 3534 | keep | 0 | Feb | 2022 | 0.002407 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
CAGUAS | 2022-02-28 12:03 | 2022-02-28 13:41 | 80 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22022800018 | New_Event |  |  | Include | Wildlife | 98 | 2022-02-28 | 7840 | keep | 0 | Feb | 2022 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-02-28 12:10 | 2022-02-28 13:41 | 1 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO | A22022800047 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2022-02-28 | 91 | keep | 0 | Feb | 2022 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-02-28 12:17 | 2022-02-28 14:45 | 1 | 002:28 | P | DESGANCHE | 1 X 40 EN RISER POR DESGANCHE | M22022800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-02-28 | 148 | keep | 0 | Feb | 2022 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-02-28 12:20 | 2022-02-28 12:21 | 968 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO LLEVA LA CARGA DEL 5302-03 | P22022800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 12:20 | 2022-02-28 12:21 | 680 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO LA CARGA POR EL 5302-02 | P22022800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 680 | keep | 0 | Feb | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
CAGUAS | 2022-02-28 12:29 | 2022-02-28 12:30 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22022800030 | New_Event |  |  | Include | Wildlife | 1 | 2022-02-28 | 1702 | keep | 0 | Feb | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-02-28 12:30 | 2022-02-28 18:26 | 40 | 005:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L Y 1 X 15 EN XMR CRUCE X GLOBO | C22022800043 | 1st_after_momentary |  |  | Include | Wildlife | 356 | 2022-02-28 | 14240 | keep | 0 | Feb | 2022 | 0.0096988 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-02-28 12:32 | 2022-02-28 12:33 | 968 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO LLEVA LA CARGA DEL 5302-03 | P22022800025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 12:32 | 2022-02-28 12:33 | 680 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO LA CARGA POR EL 5302-02 | P22022800025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 680 | keep | 0 | Feb | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
HUMACAO | 2022-02-28 12:33 | 2022-02-28 12:34 | 1467 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C22022800025 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 1467 | keep | 0 | Feb | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-02-28 12:34 | 2022-02-28 20:26 | 1070 | 007:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUTOR NO FUNDIO | C22022800027 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 472 | 2022-02-28 | 505040 | keep | 0 | Feb | 2022 | 0.34398 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
AGUADILLA | 2022-02-28 12:46 | 2022-02-28 17:48 | 60 | 005:02 | P | DESGANCHE | 1 X 50 EN RISER POR DESGANCHE | M22022800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-02-28 | 18120 | keep | 0 | Feb | 2022 | 0.012341 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 1500 | 000:09 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH PARTE POR 1424-8 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 13500 | keep | 0 | Feb | 2022 | 0.0091948 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 1000 | 000:09 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC 80% POR 1424-8 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 9000 | keep | 0 | Feb | 2022 | 0.0061299 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 278 | 000:09 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC SU CARGA POR 1424-8 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 2502 | keep | 0 | Feb | 2022 | 0.0017041 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 849 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 56883 | keep | 0 | Feb | 2022 | 0.038743 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 893 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 59831 | keep | 0 | Feb | 2022 | 0.040751 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 602 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 40334 | keep | 0 | Feb | 2022 | 0.027471 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 43 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 2881 | keep | 0 | Feb | 2022 | 0.0019622 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 1389 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 93063 | keep | 0 | Feb | 2022 | 0.063385 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:06 | 134 | 001:08 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC 20% POR EL 1418-02 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 68 | 2022-02-28 | 9112 | keep | 0 | Feb | 2022 | 0.0062061 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 539 | 001:07 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC 80% POR EL 1423-04 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 36113 | keep | 0 | Feb | 2022 | 0.024596 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 372 | 001:07 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC CARGA POR EL 1423-04 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 24924 | keep | 0 | Feb | 2022 | 0.016976 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 721 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 48307 | keep | 0 | Feb | 2022 | 0.032902 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 325 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 21775 | keep | 0 | Feb | 2022 | 0.014831 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 600 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 40200 | keep | 0 | Feb | 2022 | 0.02738 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 267 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 17889 | keep | 0 | Feb | 2022 | 0.012184 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 14:05 | 621 | 001:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 67 | 2022-02-28 | 41607 | keep | 0 | Feb | 2022 | 0.028338 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 2203 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 19827 | keep | 0 | Feb | 2022 | 0.013504 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 246 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 2214 | keep | 0 | Feb | 2022 | 0.0015079 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 9 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC LLEVA CARGA 1348-7, 80% 1348-6 Y PARTE 1336-8 | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 81 | keep | 0 | Feb | 2022 | 5.5169e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 601 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 5409 | keep | 0 | Feb | 2022 | 0.003684 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 640 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 5760 | keep | 0 | Feb | 2022 | 0.0039231 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 1699 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 15291 | keep | 0 | Feb | 2022 | 0.010415 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 892 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 8028 | keep | 0 | Feb | 2022 | 0.0054678 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-02-28 12:58 | 2022-02-28 13:07 | 1066 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC | S22022800000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-02-28 | 9594 | keep | 0 | Feb | 2022 | 0.0065344 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2022-02-28 13:06 | 2022-02-28 13:07 | 1935 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1708-02 | B20022800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 1935 | keep | 0 | Feb | 2022 | 0.0013179 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-02-28 13:06 | 2022-02-28 13:07 | 1715 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE BREAKER CARGA TRANSFERIDA AL 1707-01 | B22022800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 1715 | keep | 0 | Feb | 2022 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2022-02-28 13:07 | 2022-02-28 18:04 | 400 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22022800036 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 297 | 2022-02-28 | 118800 | keep | 0 | Feb | 2022 | 0.080914 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-02-28 13:08 | 2022-02-28 14:44 | 837 | 001:36 | T | NO SE REPORTO CAUSA | SE CERRARON MACHETES PREVIAMENTE ABIERTOS CARGA POR EL 1401-07 | S22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-02-28 | 80352 | keep | 0 | Feb | 2022 | 0.054727 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-02-28 13:08 | 2022-02-28 14:27 | 908 | 001:19 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE ABRIO MACHETES DE AMARRE CONTRA EL 1401-06 Y SE CERRO | S22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-02-28 | 71732 | keep | 0 | Feb | 2022 | 0.048856 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
YAUCO | 2022-02-28 13:21 | 2022-02-28 13:22 | 968 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO LLEVA LA CARGA DEL 5302-03 | P22022800026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 13:21 | 2022-02-28 13:22 | 680 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO LA CARGA POR EL 5302-02 | P22022800026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 680 | keep | 0 | Feb | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
VEGA BAJA | 2022-02-28 13:35 | 2022-02-28 15:36 | 2000 | 002:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO MEDIANTE GOI BY-220228-03 | B22022800026 | New_Event | Wire Down | Include | Include | Equipment | 121 | 2022-02-28 | 242000 | keep | 0 | Feb | 2022 | 0.16483 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-02-28 13:36 | 2022-02-28 13:37 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 112 | keep | 0 | Feb | 2022 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
SAN JUAN | 2022-02-28 13:47 | 2022-02-28 16:29 | 451 | 002:42 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO POR SCADA | S22022800143 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 162 | 2022-02-28 | 73062 | keep | 0 | Feb | 2022 | 0.049762 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
CAGUAS | 2022-02-28 13:50 | 2022-02-28 15:34 | 9 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22022800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-02-28 | 936 | keep | 0 | Feb | 2022 | 0.00063751 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-02-28 14:11 | 2022-02-28 17:08 | 200 | 002:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA POR TENSOR QUE CRUZO LINEAS | M22022800068 | New_Event |  |  | Include | Wildlife | 177 | 2022-02-28 | 35400 | keep | 0 | Feb | 2022 | 0.024111 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-02-28 14:23 | 2022-02-28 14:24 | 968 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA LA CARGA DEL 5302-03 | P22022800034 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 14:23 | 2022-02-28 14:24 | 680 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LA CARGA POR EL 5302-02 | P22022800034 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 680 | keep | 0 | Feb | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
SAN JUAN | 2022-02-28 14:44 | 2022-02-28 15:08 | 167 | 000:24 | P | NO SE REPORTO CAUSA | SE CERRARON MACHETES PREVIAMENTE ABIERTOS 100% EN SERVICIO | S22022800000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-02-28 | 4008 | keep | 0 | Feb | 2022 | 0.0027298 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-02-28 14:46 | 2022-02-28 17:56 | 6 | 003:10 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR SE REALIZO DESGANCHE | R22022800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-02-28 | 1140 | keep | 0 | Feb | 2022 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-02-28 14:46 | 2022-02-28 14:47 | 968 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA LA CARGA DEL 5302-03 | P22022800036 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 14:46 | 2022-02-28 14:47 | 680 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LA CARGA POR EL 5302-02 | P22022800036 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 680 | keep | 0 | Feb | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
SAN JUAN | 2022-02-28 14:48 | 2022-03-01 09:34 | 57 | 018:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POSSIBLE RELACION EVENTO POSTE VIRADO POR CAMION | S22022800184 | New_Event |  |  | Include | Wildlife | 1126 | 2022-02-28 | 64182 | keep | 0 | Feb | 2022 | 0.043714 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
YAUCO | 2022-02-28 14:48 | 2022-02-28 14:49 | 968 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA LA CARGA DEL 5302-03 | P22022800037 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 968 | keep | 0 | Feb | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 14:48 | 2022-02-28 14:49 | 680 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LA CARGA POR EL 5302-02 | P22022800034 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-02-28 | 680 | keep | 0 | Feb | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
ARECIBO | 2022-02-28 14:52 | 2022-03-01 09:43 | 1 | 018:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | A22022800054 | New_Event | Wire Down | Include | Include | Equipment | 1131 | 2022-02-28 | 1131 | keep | 0 | Feb | 2022 | 0.00077032 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-28 15:01 | 2022-02-28 16:12 | 15 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22022800065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-02-28 | 1065 | keep | 0 | Feb | 2022 | 0.00072537 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-02-28 15:06 | 2022-02-28 21:32 | 10 | 006:26 | P | NO SE REPORTO CAUSA | 1 X 60 EN C/L | S22022800190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 386 | 2022-02-28 | 3860 | keep | 0 | Feb | 2022 | 0.002629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-02-28 15:09 | 2022-03-01 08:12 | 360 | 017:03 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE Y SE REPARO LIGADURA | C22022800042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1023 | 2022-02-28 | 368280 | keep | 0 | Feb | 2022 | 0.25083 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
SAN JUAN | 2022-02-28 15:43 | 2022-02-28 16:43 | 3718 | 001:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERROPOR SCADA | S22022800000 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2022-02-28 | 223080 | keep | 0 | Feb | 2022 | 0.15194 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2022-02-28 15:46 | 2022-02-28 18:21 | 60 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22022800059 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2022-02-28 | 9300 | keep | 0 | Feb | 2022 | 0.0063342 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-02-28 15:48 | 2022-02-28 17:54 | 1 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22022800060 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2022-02-28 | 126 | keep | 0 | Feb | 2022 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-02-28 15:53 | 2022-02-28 15:54 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 2610 | keep | 0 | Feb | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
MAYAGÃœEZ | 2022-02-28 16:02 | 2022-02-28 22:46 | 100 | 006:44 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUAS | M22022800089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 404 | 2022-02-28 | 40400 | keep | 0 | Feb | 2022 | 0.027516 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-02-28 16:03 | 2022-02-28 23:17 | 20 | 007:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22022800090 | New_Event | Bad Weather | Include | Include | Weather | 434 | 2022-02-28 | 8680 | keep | 0 | Feb | 2022 | 0.0059119 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-02-28 16:08 | 2022-03-01 00:07 | 10 | 007:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22022800092 | New_Event | Bad Weather | Include | Include | Weather | 479 | 2022-02-28 | 4790 | keep | 0 | Feb | 2022 | 0.0032624 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-02-28 16:14 | 2022-02-28 21:15 | 150 | 005:01 | P | NO SE REPORTO CAUSA | SE LEVANTO CONDUCTOR | S22022800217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2022-02-28 | 45150 | keep | 0 | Feb | 2022 | 0.030751 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-02-28 16:20 | 2022-02-28 18:24 | 100 | 002:04 | P | DESGANCHE | 2 X 65 EN C/L | C22022800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-02-28 | 12400 | keep | 0 | Feb | 2022 | 0.0084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-02-28 16:42 | 2022-02-28 20:34 | 15 | 003:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | B22022800085 | New_Event | Cutout Failure | Include | Include | Equipment | 232 | 2022-02-28 | 3480 | keep | 0 | Feb | 2022 | 0.0023702 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-02-28 16:43 | 2022-02-28 18:06 | 1115 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESPEGO PUENTE DE POSTE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S22022800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 83 | 2022-02-28 | 92545 | keep | 0 | Feb | 2022 | 0.063032 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-02-28 16:45 | 2022-02-28 20:32 | 50 | 003:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M22022800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-02-28 | 11350 | keep | 0 | Feb | 2022 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-02-28 16:55 | 2022-02-28 23:06 | 40 | 006:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS | M22022800099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2022-02-28 | 14840 | keep | 0 | Feb | 2022 | 0.010107 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-02-28 17:02 | 2022-02-28 18:12 | 968 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA LLEVAR LINEA A AISLADOR EN TRONCAL DE ALIMENTADOR LLEVA LA CARGA DEL INTERRUPTOR 3 | P22022800052 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 70 | 2022-02-28 | 67760 | keep | 0 | Feb | 2022 | 0.046151 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-02-28 17:02 | 2022-02-28 18:12 | 680 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SU CARGA POR INTERRUPTOR 2 SE ABRE INTERRUPTOR PARA LLEVAR LINEA DE TRONCAL A AISLADOR | P22022800052 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 70 | 2022-02-28 | 47600 | keep | 0 | Feb | 2022 | 0.03242 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
BAYAMON | 2022-02-28 17:05 | 2022-02-28 20:44 | 5 | 003:39 | P | NO SE REPORTO CAUSA | 2 X 40 EN SU | S22022800240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-02-28 | 1095 | keep | 0 | Feb | 2022 | 0.0007458 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-02-28 17:10 | 2022-02-28 20:34 | 30 | 003:24 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | B22022800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-02-28 | 6120 | keep | 0 | Feb | 2022 | 0.0041683 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-02-28 17:14 | 2022-02-28 17:15 | 810 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22022800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 810 | keep | 0 | Feb | 2022 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
VEGA BAJA | 2022-02-28 17:24 | 2022-02-28 17:25 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 2704 | keep | 0 | Feb | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2022-02-28 18:20 | 2022-02-28 19:25 | 60 | 001:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE CAJA PRIMARIA TRASPATIO | B22022800035 | New_Event | Cutout Failure | Include | Include | Equipment | 65 | 2022-02-28 | 3900 | keep | 0 | Feb | 2022 | 0.0026563 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-02-28 21:21 | 2022-02-28 21:22 | 31 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22022800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-02-28 | 31 | keep | 0 | Feb | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2022-02-28 21:50 | 2022-03-01 03:04 | 35 | 005:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22022800116 | New_Event | Bad Weather | Include | Include | Weather | 314 | 2022-02-28 | 10990 | keep | 0 | Feb | 2022 | 0.0074852 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-02-28 22:05 | 2022-03-01 08:56 | 14 | 010:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | S22022800331 | New_Event | Cutout Failure | Include | Include | Equipment | 651 | 2022-02-28 | 9114 | keep | 0 | Feb | 2022 | 0.0062075 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2022-03-01 00:09 | 2022-03-01 07:17 | 100 | 007:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22030100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 428 | 2022-03-01 | 42800 | keep | 0 | Mar | 2022 | 0.029151 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-01 00:25 | 2022-03-01 02:18 | 60 | 001:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-03-01 | 6780 | keep | 0 | Mar | 2022 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-01 01:55 | 2022-03-01 01:56 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1713-05 LLEVANDO 95% DE LA CARGA 1717-02 | B22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 5961 | keep | 0 | Mar | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-03-01 01:55 | 2022-03-01 01:56 | 861 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1713-05 LLEVANDO 95% DE LA CARGA 1717-02 | B22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 861 | keep | 0 | Mar | 2022 | 0.00058642 | 0.00058642 | Momentary | FALSE | FALSE | Not_TMED_Event | 861
ARECIBO | 2022-03-01 02:16 | 2022-03-01 09:31 | 50 | 007:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22030100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2022-03-01 | 21750 | keep | 0 | Mar | 2022 | 0.014814 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-01 03:17 | 2022-03-01 08:18 | 60 | 005:01 | P | CABLE SOTERRADO AVERIADO | 1X50, 1X40 Y 1X30 EN DISTINTOS AEREOS PROVISIONALES SE QUEDO AVERIA SOTERRADA | B22030100001 | New_Event | UG Cable Fault | Include | Include | Equipment | 301 | 2022-03-01 | 18060 | keep | 0 | Mar | 2022 | 0.012301 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-03-01 03:35 | 2022-03-01 12:36 | 62 | 009:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L 1 X 50 EN RISER Y 2 X 40 EN RISER | C22030100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 541 | 2022-03-01 | 33542 | keep | 0 | Mar | 2022 | 0.022845 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BARRANQUITAS | 2022-03-01 04:27 | 2022-03-01 18:32 | 50 | 014:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22030100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 845 | 2022-03-01 | 42250 | keep | 0 | Mar | 2022 | 0.028776 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-01 05:19 | 2022-03-01 12:43 | 20 | 007:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA SE AÃ‘ADIO 10 PIES 3 1/0 ALUM. Y SE REGULO VOLTAJE 122/244 V | S22030100003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 444 | 2022-03-01 | 8880 | keep | 0 | Mar | 2022 | 0.0060481 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-03-01 05:55 | 2022-03-01 08:44 | 42 | 002:49 | P | NO SE REPORTO CAUSA | 1X50 EN CORTE DE LINEA Y 1X40 EN CORTE DE LINEA | B22030100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-03-01 | 7098 | keep | 0 | Mar | 2022 | 0.0048344 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
PONCE | 2022-03-01 06:51 | 2022-03-01 10:22 | 5 | 003:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22030100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-03-01 | 1055 | keep | 0 | Mar | 2022 | 0.00071856 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-01 07:08 | 2022-03-01 10:10 | 70 | 003:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-03-01 | 12740 | keep | 0 | Mar | 2022 | 0.0086772 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-03-01 07:36 | 2022-03-01 15:26 | 20 | 007:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22030100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 470 | 2022-03-01 | 9400 | keep | 0 | Mar | 2022 | 0.0064023 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-01 07:47 | 2022-03-01 08:42 | 1078 | 000:55 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR DEBIDO A DOS POSTES PRIMARIOS PARTIDOS SE ABRIERON MACHETES EN CARR 132 INT PR-9 BO CANAS Y SE COLOCO INTERRUPTOR EN SERVICIO | P22030100004 | New_Event | Defective Pole | Include | Include | Equipment | 55 | 2022-03-01 | 59290 | keep | 0 | Mar | 2022 | 0.040382 | 0.00073422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1078
MAYAGÃœEZ | 2022-03-01 08:17 | 2022-03-01 11:36 | 20 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22030100008 | New_Event |  |  | Include | Wildlife | 199 | 2022-03-01 | 3980 | keep | 0 | Mar | 2022 | 0.0027108 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-01 08:18 | 2022-03-01 08:19 | 1210 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B22030100000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-01 | 1210 | keep | 0 | Mar | 2022 | 0.00082413 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-01 08:19 | 2022-03-01 11:01 | 47 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X100 EN CORTE DE LINEA Y SE RETIRO GLOBO DE HULE DEL 13KV | B22030100010 | New_Event |  |  | Include | Wildlife | 162 | 2022-03-01 | 7614 | keep | 0 | Mar | 2022 | 0.0051859 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2022-03-01 08:19 | 2022-03-01 08:24 | 60 | 000:05 | P | CABLE SOTERRADO AVERIADO | 1X50, 1X40 Y 1X30 EN DISTINTOS AEREOS PROVISIONALES SE QUEDO AVERIA SOTERRADA | B22030100001 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 5 | 2022-03-01 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-01 08:20 | 2022-03-01 11:47 | 5 | 003:27 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHO Y RETIRO REPTIL | R22030100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-03-01 | 1035 | keep | 0 | Mar | 2022 | 0.00070493 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-03-01 08:20 | 2022-03-01 12:08 | 10 | 003:48 | P | SECUNDARIA/DESGANCHE | DESGANCHO Y REPARO SECUNDARIA | R22030100002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 228 | 2022-03-01 | 2280 | keep | 0 | Mar | 2022 | 0.0015529 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-01 08:24 | 2022-03-01 18:49 | 15 | 010:25 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO AL T-24 | B22030100001 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 625 | 2022-03-01 | 9375 | keep | 0 | Mar | 2022 | 0.0063853 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-01 08:26 | 2022-03-01 12:40 | 10 | 004:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22030100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-03-01 | 2540 | keep | 0 | Mar | 2022 | 0.00173 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-01 08:38 | 2022-03-01 08:39 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-01 | 281 | keep | 0 | Mar | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-03-01 08:38 | 2022-03-01 08:39 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-01 | 1252 | keep | 0 | Mar | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-03-01 08:38 | 2022-03-01 08:39 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-01 | 595 | keep | 0 | Mar | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-03-01 08:38 | 2022-03-01 08:39 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-01 | 51 | keep | 0 | Mar | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-01 08:38 | 2022-03-01 08:39 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-01 | 721 | keep | 0 | Mar | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
PONCE | 2022-03-01 08:42 | 2022-03-01 12:42 | 500 | 004:00 | P | ESTRUCTURA AVERIADA | SE ABRIERON PUENTES PRIMARIOS Y SE CERRO MACHETES | P22030100013 | Partial_restoration | Defective Pole | Include | Include | Equipment | 240 | 2022-03-01 | 120000 | keep | 0 | Mar | 2022 | 0.081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-01 09:06 | 2022-03-01 15:16 | 200 | 006:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2022-03-01 | 74000 | keep | 0 | Mar | 2022 | 0.050401 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-03-01 09:06 | 2022-03-01 11:52 | 20 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22030100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-03-01 | 3320 | keep | 0 | Mar | 2022 | 0.0022612 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-01 09:20 | 2022-03-01 09:56 | 12 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE Y SE DESGANCHO Y CONECTOR | S22022800208 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-03-01 | 432 | keep | 0 | Mar | 2022 | 0.00029423 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-03-01 09:30 | 2022-03-01 09:48 | 3 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22030100017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2022-03-01 | 54 | keep | 0 | Mar | 2022 | 3.6779e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-01 09:49 | 2022-03-01 09:50 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 4664 | keep | 0 | Mar | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
SAN JUAN | 2022-03-01 10:00 | 2022-03-01 13:28 | 12 | 003:28 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S22030100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-03-01 | 2496 | keep | 0 | Mar | 2022 | 0.0017 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-01 10:00 | 2022-03-01 10:01 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R22030100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-01 | 2708 | keep | 0 | Mar | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-03-01 10:01 | 2022-03-01 13:12 | 100 | 003:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN C/L CRUCE X AVE | R22030100014 | 1st_after_momentary |  |  | Include | Wildlife | 191 | 2022-03-01 | 19100 | keep | 0 | Mar | 2022 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-01 10:13 | 2022-03-01 13:35 | 62 | 003:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN CORTE DE LINEA, 1X30 EN MONTURA DE TRANSFORMADORES Y SE REMPLAZO CAJA PRIMARIA | B22030100022 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2022-03-01 | 12524 | keep | 0 | Mar | 2022 | 0.00853 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
UTUADO | 2022-03-01 10:22 | 2022-03-01 15:37 | 1 | 005:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA QUEMADA | A22030100017 | New_Event | Cutout Failure | Include | Include | Equipment | 315 | 2022-03-01 | 315 | keep | 0 | Mar | 2022 | 0.00021455 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-01 10:24 | 2022-03-01 10:50 | 1 | 000:26 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR POR SOBRE CARGA | A22030100016 | New_Event | Trip Due To Overload | Include | Include | Other | 26 | 2022-03-01 | 26 | keep | 0 | Mar | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-01 10:37 | 2022-03-01 14:43 | 30 | 004:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22030100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-03-01 | 7380 | keep | 0 | Mar | 2022 | 0.0050265 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-01 10:39 | 2022-03-01 12:10 | 1 | 001:31 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHO | R22030100021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 91 | 2022-03-01 | 91 | keep | 0 | Mar | 2022 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-01 10:49 | 2022-03-01 12:32 | 60 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES LLUVIA Y VIENTO | A22030100020 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2022-03-01 | 6180 | keep | 0 | Mar | 2022 | 0.0042092 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-01 10:50 | 2022-03-01 15:49 | 12 | 004:59 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22030100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-03-01 | 3588 | keep | 0 | Mar | 2022 | 0.0024438 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-01 11:24 | 2022-03-01 11:25 | 776 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22030100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-01 | 776 | keep | 0 | Mar | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
BAYAMON | 2022-03-01 11:25 | 2022-03-01 15:07 | 633 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22030100070 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 222 | 2022-03-01 | 140526 | keep | 0 | Mar | 2022 | 0.095712 | 0.00043113 | Sustained | FALSE | FALSE | Not_TMED_Event | 633
MAYAGÃœEZ | 2022-03-01 11:25 | 2022-03-01 15:27 | 1 | 004:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE RISER | M22030100035 | New_Event | Cutout Failure | Include | Include | Equipment | 242 | 2022-03-01 | 242 | keep | 0 | Mar | 2022 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-01 11:37 | 2022-03-01 14:39 | 30 | 003:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-03-01 | 5460 | keep | 0 | Mar | 2022 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-01 11:49 | 2022-03-01 12:00 | 1 | 000:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR POR AVE CRUZO FASE A TIERRA | A22030100028 | New_Event |  |  | Include | Wildlife | 11 | 2022-03-01 | 11 | keep | 0 | Mar | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-01 11:59 | 2022-03-01 20:06 | 80 | 008:07 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22030100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2022-03-01 | 38960 | keep | 0 | Mar | 2022 | 0.026535 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-03-01 12:06 | 2022-03-01 13:52 | 85 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L CRUCE X REPTIL | R22030100032 | New_Event |  |  | Include | Wildlife | 106 | 2022-03-01 | 9010 | keep | 0 | Mar | 2022 | 0.0061367 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-03-01 12:11 | 2022-03-02 15:57 | 30 | 027:46 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO DE T-7 AL T-6 | S22030100038 | New_Event | UG Cable Fault | Include | Include | Equipment | 1666 | 2022-03-01 | 49980 | keep | 0 | Mar | 2022 | 0.034041 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-03-01 12:11 | 2022-03-01 15:31 | 30 | 003:20 | P | CABLE SOTERRADO AVERIADO | 1 X 50 Y 1 X 25 EN CORTE DE LINEA SE SECCIONALIZO AVERIA SOTERRADA | B22030100038 | New_Event | UG Cable Fault | Include | Include | Equipment | 200 | 2022-03-01 | 6000 | keep | 0 | Mar | 2022 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-03-01 12:15 | 2022-03-01 12:26 | 3 | 000:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | P22030100035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 11 | 2022-03-01 | 33 | keep | 0 | Mar | 2022 | 2.2476e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-03-01 12:36 | 2022-03-01 12:38 | 2178 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22030100051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-01 | 4356 | keep | 0 | Mar | 2022 | 0.0029669 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
PONCE | 2022-03-01 12:42 | 2022-03-01 18:16 | 440 | 005:34 | P | ESTRUCTURA AVERIADA | SE LEVANTARON 2 POSTES PARTIDOS Y SE CERRARON MACHETES | P22030100013 | New_Event | Defective Pole | Include | Include | Equipment | 334 | 2022-03-01 | 146960 | keep | 0 | Mar | 2022 | 0.10009 | 0.00029968 | Sustained | FALSE | FALSE | Not_TMED_Event | 440
MAYAGÃœEZ | 2022-03-01 12:50 | 2022-03-01 14:13 | 9 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR RAPARAR LINEA ZAFADA DE "BUSHING" | M22030100049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-03-01 | 747 | keep | 0 | Mar | 2022 | 0.00050878 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-03-01 13:10 | 2022-03-01 13:19 | 20 | 000:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES EN BAJANTE SECUNDARIO | P22030100038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 9 | 2022-03-01 | 180 | keep | 0 | Mar | 2022 | 0.0001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-01 13:14 | 2022-03-01 14:43 | 45 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | R22030100044 | New_Event |  |  | Include | Wildlife | 89 | 2022-03-01 | 4005 | keep | 0 | Mar | 2022 | 0.0027278 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-03-01 13:24 | 2022-03-01 22:38 | 100 | 009:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M22030100054 | New_Event | Bad Weather | Include | Include | Weather | 554 | 2022-03-01 | 55400 | keep | 0 | Mar | 2022 | 0.037733 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-01 13:30 | 2022-03-01 13:31 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1530-7 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 1420 | keep | 0 | Mar | 2022 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-03-01 13:30 | 2022-03-01 13:31 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1530-7 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 437 | keep | 0 | Mar | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-03-01 13:30 | 2022-03-01 13:31 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA 1526-2 Y 1530-6 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 643 | keep | 0 | Mar | 2022 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2022-03-01 13:45 | 2022-03-01 13:46 | 5809 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE BREAKER 1716-03 LLEVA TRANFERIDA LA CARGA DEL 1710-01 | B22030100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-01 | 5809 | keep | 0 | Mar | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-03-01 13:45 | 2022-03-01 13:46 | 1812 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA LA CARGA DEL 1710-01 | B22030100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-01 | 1812 | keep | 0 | Mar | 2022 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-03-01 13:46 | 2022-03-01 16:48 | 1 | 003:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE RETIRO AVE | B22030100064 | 1st_after_momentary |  |  | Include | Wildlife | 182 | 2022-03-01 | 182 | keep | 0 | Mar | 2022 | 0.00012396 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-01 13:49 | 2022-03-01 15:41 | 10 | 001:52 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR REQUIERE DESGANCHE | A22030100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-03-01 | 1120 | keep | 0 | Mar | 2022 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-01 13:56 | 2022-03-01 13:57 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 752 | keep | 0 | Mar | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
UTUADO | 2022-03-01 13:59 | 2022-03-01 19:40 | 2 | 005:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO SAFADO DE CAJA PRIMARIA | A22030100035 | New_Event | Wire Down | Include | Include | Equipment | 341 | 2022-03-01 | 682 | keep | 0 | Mar | 2022 | 0.00046451 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-03-01 14:02 | 2022-03-01 17:15 | 15 | 003:13 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | C22030100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2022-03-01 | 2895 | keep | 0 | Mar | 2022 | 0.0019718 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-01 14:07 | 2022-03-01 15:30 | 100 | 001:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M22030100065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-03-01 | 8300 | keep | 0 | Mar | 2022 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-01 14:20 | 2022-03-01 16:58 | 20 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO 140' DE LINEA SECUNDARIA HURTADA | B22030100068 | New_Event |  |  | Include | Wildlife | 158 | 2022-03-01 | 3160 | keep | 0 | Mar | 2022 | 0.0021523 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-01 14:38 | 2022-03-01 16:47 | 80 | 002:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22030100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-03-01 | 10320 | keep | 0 | Mar | 2022 | 0.0070289 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-01 14:39 | 2022-03-01 16:45 | 25 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B22030100073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-03-01 | 3150 | keep | 0 | Mar | 2022 | 0.0021455 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-01 14:47 | 2022-03-02 11:01 | 1 | 020:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22030100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1214 | 2022-03-01 | 1214 | keep | 0 | Mar | 2022 | 0.00082685 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-01 14:54 | 2022-03-01 18:28 | 50 | 003:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-03-01 | 10700 | keep | 0 | Mar | 2022 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-01 15:12 | 2022-03-01 16:59 | 15 | 001:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-03-01 | 1605 | keep | 0 | Mar | 2022 | 0.0010932 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-01 15:15 | 2022-03-01 15:35 | 12 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE PM-21 PARA REPARAR BARA PEDESTAL | S22030100048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-03-01 | 240 | keep | 0 | Mar | 2022 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-01 15:21 | 2022-03-02 11:57 | 12 | 020:36 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO 50 KVA X 50 KVA | C22030100070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1236 | 2022-03-01 | 14832 | keep | 0 | Mar | 2022 | 0.010102 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-03-01 15:31 | 2022-03-01 15:32 | 908 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO | B22030100000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-01 | 908 | keep | 0 | Mar | 2022 | 0.00061843 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-01 15:32 | 2022-03-01 16:09 | 3522 | 000:37 | T | DESGANCHE | SE RETIRO RAMA SOBRE LINEA | M22030100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2022-03-01 | 130314 | keep | 0 | Mar | 2022 | 0.088756 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
VEGA BAJA | 2022-03-01 15:32 | 2022-03-01 17:28 | 30 | 001:56 | P | CABLE SOTERRADO AVERIADO | 1 X 50 Y 1 X 25 EN CORTE DE LINEA SE SECCIONALIZO AVERIA SOTERRADA | B22030100038 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 116 | 2022-03-01 | 3480 | keep | 0 | Mar | 2022 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-01 15:35 | 2022-03-01 15:36 | 4500 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE POR 1206-3 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 4500 | keep | 0 | Mar | 2022 | 0.0030649 | 0.0030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 4500
SAN JUAN | 2022-03-01 15:35 | 2022-03-01 15:36 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA PARTE DE 1204-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 4133 | keep | 0 | Mar | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-03-01 15:36 | 2022-03-01 16:20 | 12 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE PM-21 PARA REPARAR BARA PEDESTAL | S22030100048 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-03-01 | 528 | keep | 0 | Mar | 2022 | 0.00035962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-03-01 15:44 | 2022-03-01 19:23 | 55 | 003:39 | P | DESGANCHE | 1 X 65 EN C/L | R22030100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-03-01 | 12045 | keep | 0 | Mar | 2022 | 0.0082038 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2022-03-01 15:46 | 2022-03-01 16:09 | 603 | 000:23 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR POR CONTROL PARA FIJAR OPERADOR DE VACCUM SWITCH A PARED DE MAN HOLE | B22030100000 | New_Event | Switch Failure | Include | Include | Equipment | 23 | 2022-03-01 | 13869 | keep | 0 | Mar | 2022 | 0.0094461 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
ARECIBO | 2022-03-01 15:57 | 2022-03-01 18:25 | 10 | 002:28 | P | DESGANCHE | 1 X 10 EN RISER SE RETIRO ENREDADERA | A22030100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-03-01 | 1480 | keep | 0 | Mar | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-01 15:58 | 2022-03-01 17:02 | 80 | 001:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L CONTAMINACION | R22030100061 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2022-03-01 | 5120 | keep | 0 | Mar | 2022 | 0.0034872 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-01 15:59 | 2022-03-01 17:01 | 10 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C22030100035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2022-03-01 | 620 | keep | 0 | Mar | 2022 | 0.00042228 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-01 16:00 | 2022-03-01 17:24 | 40 | 001:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE LINEA A CAJA NO FUNDIO | R22030100063 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2022-03-01 | 3360 | keep | 0 | Mar | 2022 | 0.0022885 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-01 16:00 | 2022-03-01 16:23 | 20 | 000:23 | P | DESGANCHE | 1 X 20 EN C/L | R22030100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-03-01 | 460 | keep | 0 | Mar | 2022 | 0.0003133 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-01 16:02 | 2022-03-02 13:46 | 39 | 021:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA POR 37.5KVA | S22030100057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1304 | 2022-03-01 | 50856 | keep | 0 | Mar | 2022 | 0.034638 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
PONCE | 2022-03-01 16:06 | 2022-03-01 17:50 | 100 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON PUENTES PRIMARIOS | P22030100053 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2022-03-01 | 10400 | keep | 0 | Mar | 2022 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-01 16:12 | 2022-03-01 17:30 | 50 | 001:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22030100102 | New_Event |  |  | Include | Wildlife | 78 | 2022-03-01 | 3900 | keep | 0 | Mar | 2022 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-01 16:15 | 2022-03-01 18:47 | 10 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22030100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-03-01 | 1520 | keep | 0 | Mar | 2022 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-01 16:20 | 2022-03-01 16:50 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C22022800035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-03-01 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-01 16:24 | 2022-03-01 18:40 | 92 | 002:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22030100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-03-01 | 12512 | keep | 0 | Mar | 2022 | 0.0085219 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
HUMACAO | 2022-03-01 16:33 | 2022-03-01 17:02 | 50 | 000:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22030100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-03-01 | 1450 | keep | 0 | Mar | 2022 | 0.00098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-01 16:35 | 2022-03-01 17:03 | 15 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22030100037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-03-01 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-01 16:47 | 2022-03-01 16:48 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 4641 | keep | 0 | Mar | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
PONCE | 2022-03-01 16:50 | 2022-03-01 19:31 | 19 | 002:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO BAJANTE PRIMARIO Y CAJA DE TRANSFORMADOR | P22030100061 | New_Event | Cutout Failure | Include | Include | Equipment | 161 | 2022-03-01 | 3059 | keep | 0 | Mar | 2022 | 0.0020835 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2022-03-01 16:52 | 2022-03-01 19:06 | 50 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22030100104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-03-01 | 6700 | keep | 0 | Mar | 2022 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-01 17:28 | 2022-03-02 15:57 | 12 | 022:29 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO ENTRE T-6 Y T-7 | B22030100038 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1349 | 2022-03-01 | 16188 | keep | 0 | Mar | 2022 | 0.011026 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-01 17:34 | 2022-03-01 20:06 | 1 | 002:32 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | A22030100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-03-01 | 152 | keep | 0 | Mar | 2022 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-01 18:02 | 2022-03-01 18:34 | 15 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22030100094 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 32 | 2022-03-01 | 480 | keep | 0 | Mar | 2022 | 0.00032693 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-01 18:08 | 2022-03-01 21:04 | 60 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22030100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2022-03-01 | 10560 | keep | 0 | Mar | 2022 | 0.0071924 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-03-01 18:14 | 2022-03-01 21:56 | 2747 | 003:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE PRIMARIO EN EL PISO | P22030100080 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2022-03-01 | 609834 | keep | 0 | Mar | 2022 | 0.41536 | 0.001871 | Sustained | FALSE | FALSE | Not_TMED_Event | 2747
VEGA BAJA | 2022-03-01 18:21 | 2022-03-01 18:42 | 1 | 000:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE CAJA A LA CARGA | B22030100095 | New_Event | Wire Down | Include | Include | Equipment | 21 | 2022-03-01 | 21 | keep | 0 | Mar | 2022 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-01 18:30 | 2022-03-01 19:00 | 1 | 000:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETIRAR RAMA SOBRE LINEA | M22030100040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 30 | 2022-03-01 | 30 | keep | 0 | Mar | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-01 18:35 | 2022-03-02 17:17 | 24 | 022:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZO DE SECUNDARIA AVERIADA | M22030100112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1362 | 2022-03-01 | 32688 | keep | 0 | Mar | 2022 | 0.022264 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
FAJARDO | 2022-03-01 18:39 | 2022-03-01 19:24 | 40 | 000:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO AISLADOR Y CERRO PUENTE DE LINEA A CAJA | R22030100071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2022-03-01 | 1800 | keep | 0 | Mar | 2022 | 0.001226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-01 18:44 | 2022-03-01 19:54 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C22030100096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-03-01 | 700 | keep | 0 | Mar | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-03-01 19:05 | 2022-03-02 11:24 | 26 | 016:19 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C22030100119 | New_Event | Service Transformer Failure | Include | Include | Equipment | 979 | 2022-03-01 | 25454 | keep | 0 | Mar | 2022 | 0.017337 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2022-03-01 19:30 | 2022-03-01 22:14 | 10 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22030100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-03-01 | 1640 | keep | 0 | Mar | 2022 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-01 19:44 | 2022-03-01 21:24 | 60 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22030100077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-03-01 | 6000 | keep | 0 | Mar | 2022 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-01 19:44 | 2022-03-01 21:24 | 80 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO PARTIDO | A22030100048 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2022-03-01 | 8000 | keep | 0 | Mar | 2022 | 0.0054488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-01 20:14 | 2022-03-01 20:15 | 3432 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 3432 | keep | 0 | Mar | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
MAYAGÃœEZ | 2022-03-01 20:55 | 2022-03-02 00:44 | 40 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22030100119 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2022-03-01 | 9160 | keep | 0 | Mar | 2022 | 0.0062388 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-01 21:10 | 2022-03-02 03:24 | 30 | 006:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22030100121 | New_Event | Bad Weather | Include | Include | Weather | 374 | 2022-03-01 | 11220 | keep | 0 | Mar | 2022 | 0.0076419 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-01 21:13 | 2022-03-01 23:41 | 200 | 002:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE LLEVO ALAMBRE PRIMARIO A LA CAJA | B22030100105 | New_Event | Cutout Failure | Include | Include | Equipment | 148 | 2022-03-01 | 29600 | keep | 0 | Mar | 2022 | 0.02016 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-01 21:30 | 2022-03-01 22:33 | 5 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22030100123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-03-01 | 315 | keep | 0 | Mar | 2022 | 0.00021455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-03-01 21:36 | 2022-03-01 23:18 | 80 | 001:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22030100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-03-01 | 8160 | keep | 0 | Mar | 2022 | 0.0055577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-01 21:50 | 2022-03-01 22:36 | 45 | 000:46 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22030100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-03-01 | 2070 | keep | 0 | Mar | 2022 | 0.0014099 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-03-01 22:01 | 2022-03-01 22:04 | 922 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 LLEVANDO CARGA 1346-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-01 | 2766 | keep | 0 | Mar | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-01 22:01 | 2022-03-01 22:04 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 LLEVANDO CARGA 1346-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-01 | 405 | keep | 0 | Mar | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-03-01 22:04 | 2022-03-02 01:38 | 50 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S22030100111 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-03-01 | 10700 | keep | 0 | Mar | 2022 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-03-01 22:30 | 2022-03-01 23:20 | 6 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22030100125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-03-01 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-01 22:58 | 2022-03-02 09:26 | 8 | 010:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRAMO SECUNDARIO TRASPATIO | B22030100113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 628 | 2022-03-01 | 5024 | keep | 0 | Mar | 2022 | 0.0034218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-01 23:22 | 2022-03-01 23:24 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04 100% 1336-09 Y PARTE 1204-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-01 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-01 23:22 | 2022-03-01 23:24 | 4000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04 100% 1336-09 Y PARTE 1204-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-01 | 8000 | keep | 0 | Mar | 2022 | 0.0054488 | 0.0027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 4000
SAN JUAN | 2022-03-01 23:22 | 2022-03-01 23:24 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04 100% 1336-09 Y PARTE 1204-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-01 | 10580 | keep | 0 | Mar | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-01 23:22 | 2022-03-01 23:24 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO 30% 1204-04 100% 1336-09 Y PARTE 1204-05 | S22030100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-01 | 414 | keep | 0 | Mar | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
HUMACAO | 2022-03-01 23:42 | 2022-03-01 23:43 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030100125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-01 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
VEGA BAJA | 2022-03-02 01:12 | 2022-03-02 03:45 | 20 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR Y 1 X 30 EN CORTE DE LINEA | B22030200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-03-02 | 3060 | keep | 0 | Mar | 2022 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-03-02 01:42 | 2022-03-02 12:15 | 8 | 010:33 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | C22030200003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 633 | 2022-03-02 | 5064 | keep | 0 | Mar | 2022 | 0.0034491 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-02 01:58 | 2022-03-02 01:59 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 1597 | keep | 0 | Mar | 2022 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
PONCE | 2022-03-02 02:09 | 2022-03-02 12:46 | 150 | 010:37 | P | DESGANCHE | 1 X 80 Y 2 X 100 EN DISTINTOS CORTES DE LINEA POR DESGANCHE SE LEVANTO LINEA PRIMARIA DEL PISO | P22030200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 637 | 2022-03-02 | 95550 | keep | 0 | Mar | 2022 | 0.065079 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-03-02 03:22 | 2022-03-02 03:23 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 4132 | keep | 0 | Mar | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2022-03-02 04:48 | 2022-03-02 10:15 | 20 | 005:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22030200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2022-03-02 | 6540 | keep | 0 | Mar | 2022 | 0.0044544 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-02 06:24 | 2022-03-02 07:56 | 50 | 001:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22203020009 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2022-03-02 | 4600 | keep | 0 | Mar | 2022 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-02 06:40 | 2022-03-02 11:51 | 10 | 005:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C22030200005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 311 | 2022-03-02 | 3110 | keep | 0 | Mar | 2022 | 0.0021182 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-02 07:03 | 2022-03-02 13:37 | 60 | 006:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 Y 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22030200010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 394 | 2022-03-02 | 23640 | keep | 0 | Mar | 2022 | 0.016101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-03-02 07:25 | 2022-03-02 09:17 | 80 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | P22030200014 | New_Event |  |  | Include | Wildlife | 112 | 2022-03-02 | 8960 | keep | 0 | Mar | 2022 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-02 07:29 | 2022-03-02 07:32 | 3654 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR 2 CAJAS PRIMARIAS Y 2 PARARRAYOS AVERIADOS EN CONVERTIDOR | A22030200001 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2022-03-02 | 10962 | keep | 0 | Mar | 2022 | 0.0074662 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
ARECIBO | 2022-03-02 07:32 | 2022-03-02 08:54 | 200 | 001:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 CAJAS PRIMARIAS Y 2 PARARRAYOS AVERIADOS EN CONVERTIDOR | A22030200007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 82 | 2022-03-02 | 16400 | keep | 0 | Mar | 2022 | 0.01117 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-03-02 07:37 | 2022-03-02 10:00 | 100 | 002:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-03-02 | 14300 | keep | 0 | Mar | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-02 07:39 | 2022-03-02 11:36 | 1 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22030200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2022-03-02 | 237 | keep | 0 | Mar | 2022 | 0.00016142 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-02 07:55 | 2022-03-02 11:20 | 30 | 003:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-03-02 | 6150 | keep | 0 | Mar | 2022 | 0.0041887 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-02 08:02 | 2022-03-02 10:29 | 4 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22030200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-03-02 | 588 | keep | 0 | Mar | 2022 | 0.00040048 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-03-02 08:19 | 2022-03-02 08:20 | 553 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DEL 1529-15 QUE LLEVA EL 30% DEL 1346-02 | S22030200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 553 | keep | 0 | Mar | 2022 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-03-02 08:19 | 2022-03-02 08:20 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 30% DEL 1346-2 SE PROBO QUEDO EN SERVICIO | S22030200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 1802 | keep | 0 | Mar | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CANOVANAS | 2022-03-02 08:22 | 2022-03-02 09:49 | 15 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22030200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-03-02 | 1305 | keep | 0 | Mar | 2022 | 0.00088883 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-02 08:25 | 2022-03-02 08:26 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22030200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 5252 | keep | 0 | Mar | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
VEGA BAJA | 2022-03-02 08:47 | 2022-03-02 10:30 | 1 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X20 EN RISER Y SE RETIRO ROEDOR DE LA MONTURA | B22030200003 | New_Event |  |  | Include | Wildlife | 103 | 2022-03-02 | 103 | keep | 0 | Mar | 2022 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-02 08:48 | 2022-03-02 11:36 | 8 | 002:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B22030200004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 168 | 2022-03-02 | 1344 | keep | 0 | Mar | 2022 | 0.00091539 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-02 08:48 | 2022-03-02 20:22 | 30 | 011:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE REMPLAZO CRUCETA PARTIDA | M22030200046 | New_Event | Wire Down | Include | Include | Equipment | 694 | 2022-03-02 | 20820 | keep | 0 | Mar | 2022 | 0.01418 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-02 08:54 | 2022-03-02 09:54 | 3654 | 001:00 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 2 CAJAS PRIMARIAS Y 2 PARARRAYOS AVERIADOS EN CONVERTIDOR Y SE CERRO EL INTERRUPTOR | A22030200013 | Additional_clients | Cutout Failure | Include | Include | Equipment | 60 | 2022-03-02 | 219240 | keep | 0 | Mar | 2022 | 0.14932 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-02 08:59 | 2022-03-02 23:06 | 10 | 014:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C22030200061 | New_Event | Wire Down | Include | Include | Equipment | 847 | 2022-03-02 | 8470 | keep | 0 | Mar | 2022 | 0.0057689 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-02 09:02 | 2022-03-02 09:04 | 2524 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22030200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-02 | 5048 | keep | 0 | Mar | 2022 | 0.0034382 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
GUAYAMA | 2022-03-02 09:02 | 2022-03-02 09:03 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 922 | keep | 0 | Mar | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-03-02 09:03 | 2022-03-02 16:43 | 15 | 007:40 | P | ESTRUCTURA AVERIADA | INDICA OSVALDO GALIO SE MOVIO XMR NUEVO A POSTE NUEVO SE BAJO TAP | P22030200039 | New_Event | Defective Pole | Include | Include | Equipment | 460 | 2022-03-02 | 6900 | keep | 0 | Mar | 2022 | 0.0046996 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-02 09:27 | 2022-03-02 09:28 | 64 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22030200040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 64 | keep | 0 | Mar | 2022 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2022-03-02 09:30 | 2022-03-02 17:36 | 49 | 008:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO TRAMOS DE LINEA EN VARIOS TRAMOS SE DESGANCHO Y SE CERRO C/L | S22030200005 | New_Event | Wire Down | Include | Include | Equipment | 486 | 2022-03-02 | 23814 | keep | 0 | Mar | 2022 | 0.01622 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
PONCE | 2022-03-02 09:37 | 2022-03-02 09:38 | 5063 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P22030200035 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-02 | 5063 | keep | 0 | Mar | 2022 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2022-03-02 09:38 | 2022-03-02 13:10 | 100 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER IGUANA CRUZO FASE | P22030200036 | 1st_after_momentary |  |  | Include | Wildlife | 212 | 2022-03-02 | 21200 | keep | 0 | Mar | 2022 | 0.014439 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-03-02 09:58 | 2022-03-02 17:34 | 6 | 007:36 | P | LINEA DE TRANSMISION 115KV | 1 X 20 EN CORTE DE LINEA SE LEVANTO ALAMBRE DE 115 KV SOBRE EL 2305-02 | R22030200055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 456 | 2022-03-02 | 2736 | keep | 0 | Mar | 2022 | 0.0018635 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-03-02 09:59 | 2022-03-02 12:00 | 25 | 002:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L AISLADOR PARTIDO | R22030200040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 121 | 2022-03-02 | 3025 | keep | 0 | Mar | 2022 | 0.0020603 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-02 09:59 | 2022-03-03 12:37 | 15 | 026:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CERRO PUENTE ABIERTO EN LINEA | C22030200069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1598 | 2022-03-02 | 23970 | keep | 0 | Mar | 2022 | 0.016326 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-02 10:10 | 2022-03-02 11:12 | 6 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22030200026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2022-03-02 | 372 | keep | 0 | Mar | 2022 | 0.00025337 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-03-02 10:17 | 2022-03-02 11:45 | 9 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X AVE | R22030200047 | New_Event |  |  | Include | Wildlife | 88 | 2022-03-02 | 792 | keep | 0 | Mar | 2022 | 0.00053943 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-03-02 10:21 | 2022-03-02 13:49 | 40 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22030200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-03-02 | 8320 | keep | 0 | Mar | 2022 | 0.0056667 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-03-02 10:25 | 2022-03-02 11:25 | 7 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22030100070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-02 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-03-02 10:26 | 2022-03-02 14:05 | 70 | 003:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22030200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-03-02 | 15330 | keep | 0 | Mar | 2022 | 0.010441 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-03-02 10:31 | 2022-03-02 13:51 | 100 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CHANGO CRUZO FASE | S22030200028 | New_Event |  |  | Include | Wildlife | 200 | 2022-03-02 | 20000 | keep | 0 | Mar | 2022 | 0.013622 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-02 10:33 | 2022-03-02 13:09 | 30 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22030200050 | New_Event |  |  | Include | Wildlife | 156 | 2022-03-02 | 4680 | keep | 0 | Mar | 2022 | 0.0031875 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-02 10:42 | 2022-03-02 12:02 | 10 | 001:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA QUEMADA | B22030200009 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2022-03-02 | 800 | keep | 0 | Mar | 2022 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-02 11:06 | 2022-03-02 14:13 | 10 | 003:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22030200012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 187 | 2022-03-02 | 1870 | keep | 0 | Mar | 2022 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-02 11:43 | 2022-03-02 13:27 | 21 | 001:44 | P | NO SE REPORTO CAUSA | 1X25 EN MONTURA DE TRANSFORMADORES | B22030200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-03-02 | 2184 | keep | 0 | Mar | 2022 | 0.0014875 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-03-02 11:44 | 2022-03-02 11:45 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 281 | keep | 0 | Mar | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-03-02 11:44 | 2022-03-02 11:45 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 1252 | keep | 0 | Mar | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-03-02 11:44 | 2022-03-02 11:45 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 595 | keep | 0 | Mar | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-03-02 11:44 | 2022-03-02 11:45 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 51 | keep | 0 | Mar | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-02 11:44 | 2022-03-02 11:45 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 721 | keep | 0 | Mar | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-03-02 11:44 | 2022-03-02 11:45 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 1382 | keep | 0 | Mar | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-03-02 11:44 | 2022-03-02 11:45 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 654 | keep | 0 | Mar | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2022-03-02 11:50 | 2022-03-02 17:20 | 30 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030200054 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2022-03-02 | 9900 | keep | 0 | Mar | 2022 | 0.0067428 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-02 12:00 | 2022-03-02 12:45 | 15 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22030200035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-03-02 | 675 | keep | 0 | Mar | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-02 12:04 | 2022-03-02 14:55 | 12 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO SE REPORTO CAUSA | P22030200059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-03-02 | 2052 | keep | 0 | Mar | 2022 | 0.0013976 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-02 12:05 | 2022-03-02 12:06 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1303-05 LLEVANDO LA CARGA DEL 1303-04 | S22030200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 225 | keep | 0 | Mar | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-02 12:05 | 2022-03-02 12:06 | 870 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1303-05 LLEVANDO LA CARGA DEL 1303-04 | S22030200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 870 | keep | 0 | Mar | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2022-03-02 12:13 | 2022-03-02 13:22 | 1 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P22030200060 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2022-03-02 | 69 | keep | 0 | Mar | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-02 12:28 | 2022-03-02 14:37 | 30 | 002:09 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA CORTAR PEDAZO PARTIDO A POSTE Y BAJO LA LINEA | C22022400033 | New_Event | Defective Pole | Include | Include | Equipment | 129 | 2022-03-02 | 3870 | keep | 0 | Mar | 2022 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-03-02 12:40 | 2022-03-02 14:11 | 29 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22030200046 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2022-03-02 | 2639 | keep | 0 | Mar | 2022 | 0.0017974 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2022-03-02 12:53 | 2022-03-02 16:43 | 15 | 003:50 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE Y SE REEMPLAZO CAJA PRIMARIA QUEMADA | B22030200017 | New_Event | Defective Pole | Include | Include | Equipment | 230 | 2022-03-02 | 3450 | keep | 0 | Mar | 2022 | 0.0023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-02 12:57 | 2022-03-02 19:36 | 80 | 006:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030200064 | New_Event | Bad Weather | Include | Include | Weather | 399 | 2022-03-02 | 31920 | keep | 0 | Mar | 2022 | 0.021741 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-02 13:25 | 2022-03-02 13:26 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 1617 | keep | 0 | Mar | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-03-02 13:25 | 2022-03-02 13:26 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 1017 | keep | 0 | Mar | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-03-02 13:25 | 2022-03-02 13:26 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22030200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-02 | 828 | keep | 0 | Mar | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-03-02 13:25 | 2022-03-02 14:37 | 770 | 001:12 | T | DESGANCHE | SE RETIRO BAMBUA Y SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 7801-04 | M22030200066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-03-02 | 55440 | keep | 0 | Mar | 2022 | 0.03776 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2022-03-02 13:25 | 2022-03-02 14:37 | 1772 | 001:12 | T | DESGANCHE | CARGA POR 7801-02 | M22030200066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-03-02 | 127584 | keep | 0 | Mar | 2022 | 0.086897 | 0.0012069 | Sustained | FALSE | FALSE | Not_TMED_Event | 1772
SAN JUAN | 2022-03-02 13:30 | 2022-03-02 14:30 | 198 | 001:00 | P | ESTRUCTURA AVERIADA | SE ABRIO C/L PARA REMPLAZO DE POSTE PARTIDO | S22030200036 | New_Event | Defective Pole | Include | Include | Equipment | 60 | 2022-03-02 | 11880 | keep | 0 | Mar | 2022 | 0.0080914 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
FAJARDO | 2022-03-02 14:00 | 2022-03-02 15:12 | 22 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22030200061 | New_Event |  |  | Include | Wildlife | 72 | 2022-03-02 | 1584 | keep | 0 | Mar | 2022 | 0.0010789 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2022-03-02 14:06 | 2022-03-02 16:25 | 50 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L AVE CRUZO LINEAS | P22030200066 | New_Event |  |  | Include | Wildlife | 139 | 2022-03-02 | 6950 | keep | 0 | Mar | 2022 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-03-02 14:41 | 2022-03-02 16:27 | 70 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030200051 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2022-03-02 | 7420 | keep | 0 | Mar | 2022 | 0.0050537 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-03-02 14:50 | 2022-03-02 16:40 | 4 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22030200052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2022-03-02 | 440 | keep | 0 | Mar | 2022 | 0.00029968 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-03-02 14:57 | 2022-03-02 16:25 | 10 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | P22030200075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2022-03-02 | 880 | keep | 0 | Mar | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-03-02 15:00 | 2022-03-03 18:50 | 3 | 027:50 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PARTIDO | A22030200025 | New_Event | Defective Pole | Include | Include | Equipment | 1670 | 2022-03-02 | 5010 | keep | 0 | Mar | 2022 | 0.0034123 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-03-02 15:11 | 2022-03-02 19:00 | 30 | 003:49 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2022-03-02 | 6870 | keep | 0 | Mar | 2022 | 0.0046791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-02 15:12 | 2022-03-02 15:13 | 2770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030200027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 2770 | keep | 0 | Mar | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
PONCE | 2022-03-02 15:14 | 2022-03-02 18:00 | 527 | 002:46 | T | OTRAS CAUSAS | AVERIA DENTRO DEL ALBERGUE OLIMPICO SACABA EL BREAKER SE DEJO ABIERTO HACIA EL ALBERGUE OLIMPICO | P22030200076 | New_Event | Other Causes | Include | Include | Other | 166 | 2022-03-02 | 87482 | keep | 0 | Mar | 2022 | 0.059584 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2022-03-02 15:18 | 2022-03-03 01:02 | 60 | 009:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030200101 | New_Event | Bad Weather | Include | Include | Weather | 584 | 2022-03-02 | 35040 | keep | 0 | Mar | 2022 | 0.023866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-03-02 15:23 | 2022-03-02 16:51 | 15 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22030200079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2022-03-02 | 1320 | keep | 0 | Mar | 2022 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-02 15:35 | 2022-03-02 16:49 | 5 | 001:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C22030200028 | New_Event | Cutout Failure | Include | Include | Equipment | 74 | 2022-03-02 | 370 | keep | 0 | Mar | 2022 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-02 15:46 | 2022-03-02 17:03 | 10 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22030200016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-03-02 | 770 | keep | 0 | Mar | 2022 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-02 16:05 | 2022-03-02 17:58 | 6 | 001:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA POR UNO DE 50 KVA | A22030200060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 113 | 2022-03-02 | 678 | keep | 0 | Mar | 2022 | 0.00046178 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-03-02 16:05 | 2022-03-02 18:50 | 6 | 002:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030200061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-03-02 | 990 | keep | 0 | Mar | 2022 | 0.00067428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-02 16:09 | 2022-03-03 00:05 | 60 | 007:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030200105 | New_Event | Bad Weather | Include | Include | Weather | 476 | 2022-03-02 | 28560 | keep | 0 | Mar | 2022 | 0.019452 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-02 16:25 | 2022-03-02 16:32 | 770 | 000:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | GLOBO CRUZO LINEA PRIMARIA LLEVA LA CARGA DEL 7801-04 | M22030200111 | New_Event |  |  | Include | Wildlife | 7 | 2022-03-02 | 5390 | keep | 0 | Mar | 2022 | 0.0036711 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2022-03-02 16:25 | 2022-03-02 16:32 | 1772 | 000:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | GLOBO CRUZO LINEA PRIMARIA LA CARGA ESTA POR EL 7801-02 | M22030200111 | New_Event |  |  | Include | Wildlife | 7 | 2022-03-02 | 12404 | keep | 0 | Mar | 2022 | 0.0084483 | 0.0012069 | Sustained | FALSE | FALSE | Not_TMED_Event | 1772
ARECIBO | 2022-03-02 16:26 | 2022-03-02 20:20 | 50 | 003:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030200062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-03-02 | 11700 | keep | 0 | Mar | 2022 | 0.0079688 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-03-02 16:28 | 2022-03-03 13:26 | 4 | 020:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | C22030200033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1258 | 2022-03-02 | 5032 | keep | 0 | Mar | 2022 | 0.0034273 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-03-02 16:42 | 2022-03-02 16:43 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22030200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 2203 | keep | 0 | Mar | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
VEGA BAJA | 2022-03-02 16:52 | 2022-03-02 17:35 | 10 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22030200006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-03-02 | 430 | keep | 0 | Mar | 2022 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-02 16:55 | 2022-03-02 18:10 | 1 | 001:15 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22030200035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 75 | 2022-03-02 | 75 | keep | 0 | Mar | 2022 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-02 16:58 | 2022-03-02 21:40 | 60 | 004:42 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 3 X 80 EN C/L Y 3 X 65 EN RISER SE DEJO TOMA DE EDIFICIO ABANDONADO FUERA | S22030200062 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 282 | 2022-03-02 | 16920 | keep | 0 | Mar | 2022 | 0.011524 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-02 17:00 | 2022-03-02 20:36 | 25 | 003:36 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030200066 | New_Event | Bad Weather | Include | Include | Weather | 216 | 2022-03-02 | 5400 | keep | 0 | Mar | 2022 | 0.0036779 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-03-02 17:02 | 2022-03-02 20:07 | 10 | 003:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO SAFADO EN CAJA DE XMR | P22030200090 | New_Event | Wire Down | Include | Include | Equipment | 185 | 2022-03-02 | 1850 | keep | 0 | Mar | 2022 | 0.00126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-02 17:14 | 2022-03-02 19:22 | 30 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA | B22030200029 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-03-02 | 3840 | keep | 0 | Mar | 2022 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-02 17:17 | 2022-03-02 20:09 | 1444 | 002:52 | T | MAL TIEMPO/RAYOS/WET ASH | SE DISPARO INTERRUPTOR SE PATRULLO TOTAL Y SE CERRO POR SCADA MAL TIEMPO LLUVIA Y VIENTOS FUERTES LA CARGA ESTA POR 6014-02 | M22030200291 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2022-03-02 | 248368 | keep | 0 | Mar | 2022 | 0.16916 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-03-02 17:17 | 2022-03-02 20:09 | 3630 | 002:52 | T | MAL TIEMPO/RAYOS/WET ASH | SE DISPARO INTERRUPTOR SE PATRULLO TOTAL Y SE CERRO POR SCADA MAL TIEMPO LLUVIA Y VIENTOS FUERTES LLEVA LA CARGA DEL 6014-01 | M22030200291 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2022-03-02 | 624360 | keep | 0 | Mar | 2022 | 0.42525 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-03-02 17:42 | 2022-03-02 22:28 | 10 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030200193 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2022-03-02 | 2860 | keep | 0 | Mar | 2022 | 0.0019479 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-03-02 18:03 | 2022-03-03 15:53 | 30 | 021:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C22030200037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1310 | 2022-03-02 | 39300 | keep | 0 | Mar | 2022 | 0.026767 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-02 18:30 | 2022-03-02 19:31 | 6 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | S22030200068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-03-02 | 366 | keep | 0 | Mar | 2022 | 0.00024928 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-02 18:32 | 2022-03-02 20:32 | 30 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22030200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-03-02 | 3600 | keep | 0 | Mar | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-02 18:33 | 2022-03-02 20:57 | 10 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22030200034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2022-03-02 | 1440 | keep | 0 | Mar | 2022 | 0.00098078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-03-02 18:54 | 2022-03-02 18:55 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030200099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 1173 | keep | 0 | Mar | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
PONCE | 2022-03-02 19:11 | 2022-03-02 19:12 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | BKR DISPARO SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P22030200102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-02 | 1712 | keep | 0 | Mar | 2022 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-03-02 19:12 | 2022-03-02 21:02 | 110 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | P22030200103 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2022-03-02 | 12100 | keep | 0 | Mar | 2022 | 0.0082413 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2022-03-02 19:40 | 2022-03-03 11:50 | 15 | 016:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO LINEA SECUNDARIA DEL SUELO | C22030200043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 970 | 2022-03-02 | 14550 | keep | 0 | Mar | 2022 | 0.0099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-02 20:55 | 2022-03-03 08:54 | 69 | 011:59 | P | OTRAS CAUSAS | 1 X 10 EN CORTE DE LINEA PROBLEMA DEL CLIENTE | C22030200045 | New_Event | Other Causes | Include | Include | Other | 719 | 2022-03-02 | 49611 | keep | 0 | Mar | 2022 | 0.03379 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
ARECIBO | 2022-03-02 21:10 | 2022-03-02 21:48 | 7 | 000:38 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO AVERIADO | A22030200075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 38 | 2022-03-02 | 266 | keep | 0 | Mar | 2022 | 0.00018117 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-03-02 21:47 | 2022-03-02 23:02 | 15 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22030200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-03-02 | 1125 | keep | 0 | Mar | 2022 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-02 23:17 | 2022-03-03 01:03 | 10 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C22030200061 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-03-02 | 1060 | keep | 0 | Mar | 2022 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-02 23:23 | 2022-03-03 17:49 | 90 | 018:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C22030200078 | New_Event | Wire Down | Include | Include | Equipment | 1106 | 2022-03-02 | 99540 | keep | 0 | Mar | 2022 | 0.067796 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-03-03 01:05 | 2022-03-03 01:06 | 793 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 793 | keep | 0 | Mar | 2022 | 0.00054011 | 0.00054011 | Momentary | FALSE | FALSE | Not_TMED_Event | 793
CAGUAS | 2022-03-03 01:07 | 2022-03-03 15:55 | 10 | 014:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C22030200061 | Partial_restoration | Wire Down | Include | Include | Equipment | 888 | 2022-03-03 | 8880 | keep | 0 | Mar | 2022 | 0.0060481 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-03 01:43 | 2022-03-03 09:38 | 100 | 007:55 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTE POR LINEA PRIMARIA PARTIDA Y POSTE Y SE CERRO CORTE DE LINEA | A22030300009 | New_Event | Defective Pole | Include | Include | Equipment | 475 | 2022-03-03 | 47500 | keep | 0 | Mar | 2022 | 0.032352 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-03 03:44 | 2022-03-03 11:04 | 50 | 007:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22030300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 440 | 2022-03-03 | 22000 | keep | 0 | Mar | 2022 | 0.014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-03 05:19 | 2022-03-03 08:24 | 60 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR FUERTES LLUVIAS | A22030300012 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2022-03-03 | 11100 | keep | 0 | Mar | 2022 | 0.0075602 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-03-03 05:50 | 2022-03-03 07:51 | 2039 | 002:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR RAMA SOBRE LA LINEA EN TRONCAL DEL ALIMENTADOR | P22030300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-03-03 | 246719 | keep | 0 | Mar | 2022 | 0.16804 | 0.0013888 | Sustained | FALSE | FALSE | Not_TMED_Event | 2039
YAUCO | 2022-03-03 06:28 | 2022-03-03 16:33 | 175 | 010:05 | P | ESTRUCTURA AVERIADA | POSTE CEDIO Y LINEAS BAJARON Y SE CRUZARON | P22030300026 | New_Event | Defective Pole | Include | Include | Equipment | 605 | 2022-03-03 | 105875 | keep | 0 | Mar | 2022 | 0.072111 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BARRANQUITAS | 2022-03-03 07:07 | 2022-03-03 07:08 | 229 | 000:01 | T | DESGANCHE | DISPARO SE CERRO POR CONTROL | C22030300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-03 | 229 | keep | 0 | Mar | 2022 | 0.00015597 | 0.00015597 | Momentary | FALSE | FALSE | Not_TMED_Event | 229
BARRANQUITAS | 2022-03-03 07:07 | 2022-03-03 07:08 | 1246 | 000:01 | T | DESGANCHE | DISPARO SE CERRO POR CONTROL | C22030300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-03 | 1246 | keep | 0 | Mar | 2022 | 0.00084864 | 0.00084864 | Momentary | FALSE | FALSE | Not_TMED_Event | 1246
BARRANQUITAS | 2022-03-03 07:08 | 2022-03-03 12:16 | 50 | 005:08 | P | DESGANCHE | CONDUCTORES EN EL SUELO POR ARBOL | C22030300078 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-03-03 | 15400 | keep | 0 | Mar | 2022 | 0.010489 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-03 07:32 | 2022-03-03 12:35 | 60 | 005:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22030300014 | New_Event | Cutout Failure | Include | Include | Equipment | 303 | 2022-03-03 | 18180 | keep | 0 | Mar | 2022 | 0.012382 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-03-03 07:43 | 2022-03-03 10:00 | 50 | 002:17 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L SE RETIRO PARARRAYO | R22030300044 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 137 | 2022-03-03 | 6850 | keep | 0 | Mar | 2022 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-03 07:52 | 2022-03-03 17:54 | 25 | 010:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA Y UNO DE 75KVA POR 2 DE 50KVA ESTABAN LIQUEANDO ACEITE | S22030300043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 602 | 2022-03-03 | 15050 | keep | 0 | Mar | 2022 | 0.01025 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-03-03 07:57 | 2022-03-03 07:58 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 732 | keep | 0 | Mar | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-03-03 07:59 | 2022-03-03 08:00 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE CERRO POR SCADA LLEVA PARTE 1336-08 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-03-03 07:59 | 2022-03-03 08:00 | 1001 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE CERRO POR SCADA LLEVA 80% DEL 1348-06 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 1001 | keep | 0 | Mar | 2022 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2022-03-03 07:59 | 2022-03-03 08:00 | 278 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE CERRO POR SCADA LLEVA 100% 1348-07, | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 278 | keep | 0 | Mar | 2022 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-03-03 07:59 | 2022-03-03 08:00 | 9 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE CERRO POR SCADA LLEVA 100% 1348-07, 80% DEL 1348-06 Y PARTE 1336-08 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 9 | keep | 0 | Mar | 2022 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-03-03 08:14 | 2022-03-03 11:17 | 250 | 003:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE CON AVE | C22030300054 | New_Event |  |  | Include | Wildlife | 183 | 2022-03-03 | 45750 | keep | 0 | Mar | 2022 | 0.03116 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2022-03-03 08:53 | 2022-03-03 16:51 | 10 | 007:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS | C22030300060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 478 | 2022-03-03 | 4780 | keep | 0 | Mar | 2022 | 0.0032556 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-03 08:58 | 2022-03-03 12:06 | 250 | 003:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L & 1 X 80 EN RISER SE RETIRO PALOMA | R22030300052 | New_Event |  |  | Include | Wildlife | 188 | 2022-03-03 | 47000 | keep | 0 | Mar | 2022 | 0.032011 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2022-03-03 09:03 | 2022-03-03 14:37 | 180 | 005:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22030300062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2022-03-03 | 60120 | keep | 0 | Mar | 2022 | 0.040947 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2022-03-03 09:05 | 2022-03-03 10:45 | 6 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE | S22030300054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-03-03 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-03 09:08 | 2022-03-03 13:17 | 3 | 004:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | R22030300053 | New_Event | Wire Down | Include | Include | Equipment | 249 | 2022-03-03 | 747 | keep | 0 | Mar | 2022 | 0.00050878 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-03-03 09:22 | 2022-03-03 13:27 | 1 | 004:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE QUEMADO | C22030300065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 245 | 2022-03-03 | 245 | keep | 0 | Mar | 2022 | 0.00016687 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-03 09:29 | 2022-03-03 10:24 | 4 | 000:55 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL SECUNDARIO | C22030300066 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 55 | 2022-03-03 | 220 | keep | 0 | Mar | 2022 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-03-03 09:32 | 2022-03-03 09:33 | 400 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE 1206-03 LLEVA PARTE DEL 1204-05 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-03-03 09:32 | 2022-03-03 09:33 | 3500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE 1206-03 LLEVA PARTE DEL 1204-05 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 3500 | keep | 0 | Mar | 2022 | 0.0023838 | 0.0023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 3500
ARECIBO | 2022-03-03 09:34 | 2022-03-03 12:53 | 15 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA POR PALOMA | A22030300026 | New_Event |  |  | Include | Wildlife | 199 | 2022-03-03 | 2985 | keep | 0 | Mar | 2022 | 0.0020331 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-03 09:35 | 2022-03-03 15:43 | 3 | 006:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C22030300067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 368 | 2022-03-03 | 1104 | keep | 0 | Mar | 2022 | 0.00075193 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-03-03 09:38 | 2022-03-03 20:30 | 50 | 010:52 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | A22030300009 | Partial_restoration | Defective Pole | Include | Include | Equipment | 652 | 2022-03-03 | 32600 | keep | 0 | Mar | 2022 | 0.022204 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-03 09:56 | 2022-03-03 13:11 | 1 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA BOMBAS AAA | A22030300029 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2022-03-03 | 195 | keep | 0 | Mar | 2022 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-03 10:20 | 2022-03-03 15:20 | 200 | 005:00 | P | HERRAJE ROTO O PODRIDO | 1 X 50 EN CORTE E LINEA SE REEMPLAZO CRUCETA PARTIDA | C22030300071 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 300 | 2022-03-03 | 60000 | keep | 0 | Mar | 2022 | 0.040866 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-03-03 10:21 | 2022-03-03 18:22 | 1 | 008:01 | P | DESGANCHE | 2 X 40 EN RISER, 3 X 50 EN C/L Y 1 X 65 EN C/L PRINCIPAL | R22030300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 481 | 2022-03-03 | 481 | keep | 0 | Mar | 2022 | 0.00032761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-03 10:27 | 2022-03-03 11:01 | 42 | 000:34 | P | NO SE REPORTO CAUSA | 1X65 EN CORTE DE LINEA | B22030300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2022-03-03 | 1428 | keep | 0 | Mar | 2022 | 0.0009726 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
ARECIBO | 2022-03-03 10:30 | 2022-03-03 14:11 | 40 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA INFORMA FOREMAN QUE NO IDENTIFICO CAUSA | A22030300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-03-03 | 8840 | keep | 0 | Mar | 2022 | 0.0060209 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-03 10:59 | 2022-03-03 13:18 | 18 | 002:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | B22030300036 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2022-03-03 | 2502 | keep | 0 | Mar | 2022 | 0.0017041 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-03-03 11:20 | 2022-03-03 12:41 | 6 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22030300065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2022-03-03 | 486 | keep | 0 | Mar | 2022 | 0.00033101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-03 11:41 | 2022-03-03 13:41 | 30 | 002:00 | P | DESGANCHE | 1 X 40 EN C/L SE RETEZO LINEA CRUZADA | S22030300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-03-03 | 3600 | keep | 0 | Mar | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-03 11:57 | 2022-03-03 12:01 | 2000 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SPARE 1619-02 LLEVANDO APROX. 2,000 CLIENTES DEL 1336-06 Y SE CERRO POR SCADA | R22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-03 | 8000 | keep | 0 | Mar | 2022 | 0.0054488 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
BARRANQUITAS | 2022-03-03 12:16 | 2022-03-03 13:43 | 229 | 001:27 | T | DESGANCHE | SE ABRIO INTERRUPTOR ARBOL SOBRE LINEAS DERRIBARON AL SUELO CONDUCTORES | C22030300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-03-03 | 19923 | keep | 0 | Mar | 2022 | 0.013569 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
BARRANQUITAS | 2022-03-03 12:16 | 2022-03-03 13:43 | 1246 | 001:27 | T | DESGANCHE | AVERIA DEL 9901-01 SE ABRIO INTERRUPTOR ARBOL SOBRE LINEAS DERRIBARON AL SUELO CONDUCTORES | C22030300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-03-03 | 108402 | keep | 0 | Mar | 2022 | 0.073832 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
CAGUAS | 2022-03-03 12:28 | 2022-03-04 10:28 | 5 | 022:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA | C22030300082 | New_Event | Cutout Failure | Include | Include | Equipment | 1320 | 2022-03-03 | 6600 | keep | 0 | Mar | 2022 | 0.0044952 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-03-03 12:31 | 2022-03-03 13:36 | 10 | 001:05 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE SECUNDARIO | R22030300061 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 65 | 2022-03-03 | 650 | keep | 0 | Mar | 2022 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-03 12:41 | 2022-03-03 20:35 | 2 | 007:54 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE REPARO NEUTRAL | M22030300047 | New_Event | Defective Pole | Include | Include | Equipment | 474 | 2022-03-03 | 948 | keep | 0 | Mar | 2022 | 0.00064568 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-03 13:13 | 2022-03-03 19:45 | 30 | 006:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22030300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-03-03 | 11760 | keep | 0 | Mar | 2022 | 0.0080097 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-03 13:41 | 2022-03-03 17:42 | 50 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L AVE CRUZO LINEAS | P22030300055 | New_Event |  |  | Include | Wildlife | 241 | 2022-03-03 | 12050 | keep | 0 | Mar | 2022 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-03-03 13:43 | 2022-03-04 11:54 | 70 | 022:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR EN EL SUELO | C22030300078 | New_Event | Wire Down | Include | Include | Equipment | 1331 | 2022-03-03 | 93170 | keep | 0 | Mar | 2022 | 0.063458 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-03-03 14:07 | 2022-03-03 15:36 | 1 | 001:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | A22030300044 | New_Event | Wire Down | Include | Include | Equipment | 89 | 2022-03-03 | 89 | keep | 0 | Mar | 2022 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-03 14:15 | 2022-03-03 14:41 | 6 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22030300042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-03-03 | 156 | keep | 0 | Mar | 2022 | 0.00010625 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-03 14:21 | 2022-03-03 16:34 | 7 | 002:13 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CONVERTIDOR POSTE PRIMARIO PARTIDO | M22030300057 | New_Event | Defective Pole | Include | Include | Equipment | 133 | 2022-03-03 | 931 | keep | 0 | Mar | 2022 | 0.0006341 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-03-03 14:30 | 2022-03-03 14:48 | 6 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO SECUNDARIA | R22030300068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2022-03-03 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-03 14:30 | 2022-03-03 18:38 | 10 | 004:08 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C22030300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-03-03 | 2480 | keep | 0 | Mar | 2022 | 0.0016891 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-03 14:32 | 2022-03-03 16:04 | 20 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22030300040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-03-03 | 1840 | keep | 0 | Mar | 2022 | 0.0012532 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-03 14:33 | 2022-03-03 14:34 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 2147 | keep | 0 | Mar | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
AGUADILLA | 2022-03-03 14:34 | 2022-03-03 15:19 | 18 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO | M22030300062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-03-03 | 810 | keep | 0 | Mar | 2022 | 0.00055169 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-03-03 14:38 | 2022-03-04 08:20 | 130 | 017:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 65 EN CORTE DE LINEA LLUVIAS | C22030300109 | New_Event | Bad Weather | Include | Include | Weather | 1062 | 2022-03-03 | 138060 | keep | 0 | Mar | 2022 | 0.094032 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
FAJARDO | 2022-03-03 14:40 | 2022-03-03 15:14 | 7 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R22030300070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2022-03-03 | 238 | keep | 0 | Mar | 2022 | 0.0001621 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-03 14:41 | 2022-03-03 17:50 | 40 | 003:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA Y 1 X 80 EN CORTE DE LINEA | M22030300064 | New_Event | Wire Down | Include | Include | Equipment | 189 | 2022-03-03 | 7560 | keep | 0 | Mar | 2022 | 0.0051491 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-03 14:42 | 2022-03-03 16:05 | 2067 | 001:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR LINEA PRIMARIA ROTA SE SECCIONALIZO DEJANDO 99% EN SERVICIO | M22030300066 | New_Event | Wire Down | Include | Include | Equipment | 83 | 2022-03-03 | 171561 | keep | 0 | Mar | 2022 | 0.11685 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-03-03 14:47 | 2022-03-03 14:48 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22030300074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 1352 | keep | 0 | Mar | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-03-03 15:02 | 2022-03-03 16:15 | 1 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR | M22030300083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-03-03 | 73 | keep | 0 | Mar | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-03 15:14 | 2022-03-03 18:41 | 400 | 003:27 | P | DESGANCHE | 2 X 100 Y 2 X 80 EN CORTES DE DE LINEA | C22030300115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-03-03 | 82800 | keep | 0 | Mar | 2022 | 0.056395 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-03-03 15:30 | 2022-03-03 16:10 | 2 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A22030300047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-03 | 80 | keep | 0 | Mar | 2022 | 5.4488e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-03 16:05 | 2022-03-03 18:59 | 2045 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22030300121 | Partial_restoration | Wire Down | Include | Include | Equipment | 174 | 2022-03-03 | 355830 | keep | 0 | Mar | 2022 | 0.24235 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-03 16:07 | 2022-03-03 17:11 | 35 | 001:04 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | S22030300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-03-03 | 2240 | keep | 0 | Mar | 2022 | 0.0015257 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-03-03 16:13 | 2022-03-03 19:34 | 225 | 003:21 | T | AISLADOR ROTO, PARTIDO O SAFADO | EN DISPARO DE 1303-05 QUE LLEVA 1303-04 SE SECCIONALIZO EN CAMINO LOS ROMEROS CON BIGIOS Y SE CERRO EN CAMINO LOS ROMEROS CON BAEZ, ENTRO 100% 1303-04 | S22030300085 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2022-03-03 | 45225 | keep | 0 | Mar | 2022 | 0.030803 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-03 16:13 | 2022-03-03 18:50 | 870 | 002:37 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1303-05 SE SECCIONALIZO EN CAMINO LUCIANO VAZQUEZ Y SE CERRO POR SCADA, LLEVA 1303-04 | S22030300085 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 157 | 2022-03-03 | 136590 | keep | 0 | Mar | 2022 | 0.093031 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
GUAYAMA | 2022-03-03 16:13 | 2022-03-03 18:02 | 15 | 001:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22030300065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 109 | 2022-03-03 | 1635 | keep | 0 | Mar | 2022 | 0.0011136 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-03-03 16:23 | 2022-03-03 19:20 | 30 | 002:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L Y 1 X 10 EN XMR FUSIBLE PODRIDO | R22030300076 | New_Event | Cutout Failure | Include | Include | Equipment | 177 | 2022-03-03 | 5310 | keep | 0 | Mar | 2022 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-03-03 16:27 | 2022-03-03 16:28 | 3902 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22030300128 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-03 | 3902 | keep | 0 | Mar | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
BAYAMON | 2022-03-03 16:28 | 2022-03-03 17:45 | 15 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22030300005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-03-03 | 1155 | keep | 0 | Mar | 2022 | 0.00078667 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-03 16:28 | 2022-03-03 19:48 | 100 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22030300131 | 1st_after_momentary |  |  | Include | Wildlife | 200 | 2022-03-03 | 20000 | keep | 0 | Mar | 2022 | 0.013622 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-03-03 16:32 | 2022-03-03 18:31 | 10 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22030300067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2022-03-03 | 1190 | keep | 0 | Mar | 2022 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-03 16:34 | 2022-03-03 23:06 | 85 | 006:32 | P | ESTRUCTURA AVERIADA | 3 X 80 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO | M22030300141 | Additional_clients | Defective Pole | Include | Include | Equipment | 392 | 2022-03-03 | 33320 | keep | 0 | Mar | 2022 | 0.022694 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-03 17:06 | 2022-03-03 17:09 | 922 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-03 | 2766 | keep | 0 | Mar | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-03 17:06 | 2022-03-03 17:09 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-03 | 405 | keep | 0 | Mar | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2022-03-03 17:06 | 2022-03-03 17:20 | 25 | 000:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030300131 | New_Event | Bad Weather | Include | Include | Weather | 14 | 2022-03-03 | 350 | keep | 0 | Mar | 2022 | 0.00023838 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-03-03 17:12 | 2022-03-03 19:56 | 2 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN S/W MAL TIEMPO | P22030300071 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2022-03-03 | 328 | keep | 0 | Mar | 2022 | 0.0002234 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-03 17:50 | 2022-03-03 19:10 | 20 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030300143 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2022-03-03 | 1600 | keep | 0 | Mar | 2022 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-03 17:56 | 2022-03-03 19:30 | 12 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P22030300075 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2022-03-03 | 1128 | keep | 0 | Mar | 2022 | 0.00076828 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-03 18:01 | 2022-03-03 18:02 | 176 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR | M22030300145 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-03 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-03-03 18:02 | 2022-03-03 21:33 | 50 | 003:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030300148 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 211 | 2022-03-03 | 10550 | keep | 0 | Mar | 2022 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-03-03 18:12 | 2022-03-03 21:51 | 200 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22030300138 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2022-03-03 | 43800 | keep | 0 | Mar | 2022 | 0.029832 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-03-03 18:27 | 2022-03-03 23:33 | 70 | 005:06 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030300151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-03-03 | 21420 | keep | 0 | Mar | 2022 | 0.014589 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-03-03 18:31 | 2022-03-04 00:07 | 8 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22030300154 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2022-03-03 | 2688 | keep | 0 | Mar | 2022 | 0.0018308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-03-03 18:37 | 2022-03-04 09:47 | 1 | 015:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | R22030300083 | New_Event | Cutout Failure | Include | Include | Equipment | 910 | 2022-03-03 | 910 | keep | 0 | Mar | 2022 | 0.0006198 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-03 18:42 | 2022-03-03 18:43 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22030300085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 2179 | keep | 0 | Mar | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
HUMACAO | 2022-03-03 18:47 | 2022-03-03 22:47 | 130 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22030300152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2022-03-03 | 31200 | keep | 0 | Mar | 2022 | 0.02125 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2022-03-03 18:48 | 2022-03-03 18:49 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 1310 | keep | 0 | Mar | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-03-03 18:50 | 2022-03-03 19:04 | 435 | 000:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EN CAMINO LUCIANO VAZQUEZ Y SE CERRO EN EL PRIMER PUNTO DEL CAMINO LUCIONO VAZQUEZ ENTRO 50% DEL 1303-05 | S22030300085 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 14 | 2022-03-03 | 6090 | keep | 0 | Mar | 2022 | 0.0041479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-03 19:04 | 2022-03-03 20:17 | 350 | 001:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EN CAMINO PEDRO VIERA Y SE CERRO EN CAMINO LOS ROMERO CON BIGIOS | S22030300085 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2022-03-03 | 25550 | keep | 0 | Mar | 2022 | 0.017402 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-03 19:20 | 2022-03-03 20:33 | 2 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A22030300058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2022-03-03 | 146 | keep | 0 | Mar | 2022 | 9.944e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-03-03 20:03 | 2022-03-03 20:04 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22030300161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 2900 | keep | 0 | Mar | 2022 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
MAYAGÃœEZ | 2022-03-03 20:11 | 2022-03-03 22:26 | 8 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22030300167 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2022-03-03 | 1080 | keep | 0 | Mar | 2022 | 0.00073558 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-03 20:17 | 2022-03-03 21:08 | 200 | 000:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DISCOS Y SE CERRO EN CAMINO PEDRO VIERA | S22030300085 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 51 | 2022-03-03 | 10200 | keep | 0 | Mar | 2022 | 0.0069472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-03 20:22 | 2022-03-03 20:23 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22030300165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-03 | 3005 | keep | 0 | Mar | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
PONCE | 2022-03-03 20:49 | 2022-03-04 07:36 | 5 | 010:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR AVE CRUZO FASE | P22030300093 | New_Event |  |  | Include | Wildlife | 647 | 2022-03-03 | 3235 | keep | 0 | Mar | 2022 | 0.0022033 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-03 20:50 | 2022-03-04 03:45 | 120 | 006:55 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S22030300267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 415 | 2022-03-03 | 49800 | keep | 0 | Mar | 2022 | 0.033919 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-03-03 21:09 | 2022-03-03 22:10 | 80 | 001:01 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTE DE LINEAS | R22030300090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-03-03 | 4880 | keep | 0 | Mar | 2022 | 0.0033237 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-03-03 22:21 | 2022-03-04 00:01 | 10 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22030300063 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-03-03 | 1000 | keep | 0 | Mar | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-03 22:24 | 2022-03-04 02:42 | 20 | 004:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN XMR Y SE REPARO SECUNDARIA | S22030300307 | New_Event | Secondary Wire Down | Include | Include | Equipment | 258 | 2022-03-03 | 5160 | keep | 0 | Mar | 2022 | 0.0035145 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-03 22:59 | 2022-03-04 02:08 | 200 | 003:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030300176 | New_Event | Bad Weather | Include | Include | Weather | 189 | 2022-03-03 | 37800 | keep | 0 | Mar | 2022 | 0.025745 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-03 22:59 | 2022-03-04 01:14 | 15 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22030300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-03-03 | 2025 | keep | 0 | Mar | 2022 | 0.0013792 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-03 23:04 | 2022-03-04 16:10 | 1 | 017:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22030300177 | New_Event | Wire Down | Include | Include | Equipment | 1026 | 2022-03-03 | 1026 | keep | 0 | Mar | 2022 | 0.0006988 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-03 23:58 | 2022-03-04 | 3957 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22030300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-03 | 7914 | keep | 0 | Mar | 2022 | 0.0053902 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2022-03-04 01:00 | 2022-03-04 01:01 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 58 | keep | 0 | Mar | 2022 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-03-04 02:48 | 2022-03-04 09:44 | 67 | 006:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8200 | S22030400019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 416 | 2022-03-04 | 27872 | keep | 0 | Mar | 2022 | 0.018983 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-03-04 02:48 | 2022-03-04 09:44 | 1587 | 006:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8200 | S22030400019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 416 | 2022-03-04 | 660192 | keep | 0 | Mar | 2022 | 0.44965 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
BAYAMON | 2022-03-04 02:48 | 2022-03-04 09:44 | 521 | 006:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8200 | S22030400019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 416 | 2022-03-04 | 216736 | keep | 0 | Mar | 2022 | 0.14762 | 0.00035485 | Sustained | FALSE | FALSE | Not_TMED_Event | 521
BAYAMON | 2022-03-04 02:48 | 2022-03-04 09:44 | 1307 | 006:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8200 | S22030400019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 416 | 2022-03-04 | 543712 | keep | 0 | Mar | 2022 | 0.37032 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
MAYAGÃœEZ | 2022-03-04 03:19 | 2022-03-04 19:30 | 100 | 016:11 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | M22030400007 | New_Event | Defective Pole | Include | Include | Equipment | 971 | 2022-03-04 | 97100 | keep | 0 | Mar | 2022 | 0.066134 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-04 03:28 | 2022-03-04 09:22 | 595 | 005:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 SE SECCIONALIZO Y SE ENERGIZO SUBESTACION | M22030400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 354 | 2022-03-04 | 210630 | keep | 0 | Mar | 2022 | 0.14346 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-03-04 03:28 | 2022-03-04 09:22 | 51 | 005:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 SE SECCIONALIZO Y SE ENERGIZO SUBESTACION | M22030400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 354 | 2022-03-04 | 18054 | keep | 0 | Mar | 2022 | 0.012296 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-04 03:28 | 2022-03-04 09:22 | 721 | 005:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 SE SECCIONALIZO Y SE ENERGIZO SUBESTACION | M22030400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 354 | 2022-03-04 | 255234 | keep | 0 | Mar | 2022 | 0.17384 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-03-04 03:28 | 2022-03-04 07:58 | 1382 | 004:30 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 8100 Y SE ENERGIZO LA SUBESTACION | A22030400004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 270 | 2022-03-04 | 373140 | keep | 0 | Mar | 2022 | 0.25414 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-03-04 03:28 | 2022-03-04 07:58 | 654 | 004:30 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 8100 Y SE ENERGIZO LA SUBESTACION | A22030400004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 270 | 2022-03-04 | 176580 | keep | 0 | Mar | 2022 | 0.12027 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
HUMACAO | 2022-03-04 04:14 | 2022-03-04 07:01 | 200 | 002:47 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22030400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-03-04 | 33400 | keep | 0 | Mar | 2022 | 0.022749 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-03-04 04:16 | 2022-03-04 18:19 | 100 | 014:03 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22030400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 843 | 2022-03-04 | 84300 | keep | 0 | Mar | 2022 | 0.057416 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-04 04:17 | 2022-03-04 10:46 | 18 | 006:29 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | B22030400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 389 | 2022-03-04 | 7002 | keep | 0 | Mar | 2022 | 0.004769 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-03-04 07:18 | 2022-03-04 07:19 | 5191 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 40% DEL 1718-03 | B22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 5191 | keep | 0 | Mar | 2022 | 0.0035356 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
BAYAMON | 2022-03-04 07:19 | 2022-03-04 17:21 | 30 | 010:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B22030400037 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 602 | 2022-03-04 | 18060 | keep | 0 | Mar | 2022 | 0.012301 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-04 07:23 | 2022-03-04 07:24 | 1042 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1710-05 LLEVA TRANSFERIDA 40% DE LA CARGA DEL 1718-03 | B22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 1042 | keep | 0 | Mar | 2022 | 0.0007097 | 0.0007097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1042
SAN JUAN | 2022-03-04 07:31 | 2022-03-04 13:09 | 60 | 005:38 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/L SE REALIZO DESGANCHE | S22030400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2022-03-04 | 20280 | keep | 0 | Mar | 2022 | 0.013813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-04 07:33 | 2022-03-04 10:59 | 1 | 003:26 | P | DESGANCHE | 2X65 EN CORTE DE LINEA | B22030400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-03-04 | 206 | keep | 0 | Mar | 2022 | 0.00014031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-04 07:34 | 2022-03-04 07:35 | 2107 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | A22030400021 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-04 | 2107 | keep | 0 | Mar | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2022-03-04 07:35 | 2022-03-04 09:48 | 15 | 002:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22030400028 | 1st_after_momentary |  |  | Include | Wildlife | 133 | 2022-03-04 | 1995 | keep | 0 | Mar | 2022 | 0.0013588 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-03-04 07:36 | 2022-03-04 09:52 | 1 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22030400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-03-04 | 136 | keep | 0 | Mar | 2022 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-04 07:49 | 2022-03-04 14:47 | 1 | 006:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER 1 X 25 NX | S22030400069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 418 | 2022-03-04 | 418 | keep | 0 | Mar | 2022 | 0.0002847 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-04 07:56 | 2022-03-04 10:41 | 1 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN MONTURA TRIFASICA NO SE REPORTO CAUSA | P22030400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-03-04 | 165 | keep | 0 | Mar | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-04 08:09 | 2022-03-04 09:51 | 1 | 001:42 | P | OTRAS CAUSAS | 3X100 DEL SU-1A @ TRANSCLOSURE PRIVADO | B22030400019 | New_Event | Other Causes | Include | Include | Other | 102 | 2022-03-04 | 102 | keep | 0 | Mar | 2022 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-04 08:11 | 2022-03-04 17:24 | 30 | 009:13 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZARON BAJANTES SECUNDARIOS QUEMADOS Y TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C22030400013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 553 | 2022-03-04 | 16590 | keep | 0 | Mar | 2022 | 0.011299 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-04 08:15 | 2022-03-04 09:27 | 80 | 001:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-5 NO SE REPORTO CAUSA | P22030400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2022-03-04 | 5760 | keep | 0 | Mar | 2022 | 0.0039231 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-03-04 08:18 | 2022-03-04 09:33 | 1 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | R22030400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-03-04 | 75 | keep | 0 | Mar | 2022 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-04 08:23 | 2022-03-04 10:22 | 8 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA INFORMO EL FOREMAN QUE NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22030400026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-03-04 | 952 | keep | 0 | Mar | 2022 | 0.0006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-04 08:25 | 2022-03-04 22:08 | 20 | 013:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | M22030400037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 823 | 2022-03-04 | 16460 | keep | 0 | Mar | 2022 | 0.011211 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-04 08:29 | 2022-03-04 11:05 | 30 | 002:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REEMPLAZO CAJA | M22030400038 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2022-03-04 | 4680 | keep | 0 | Mar | 2022 | 0.0031875 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-03-04 08:34 | 2022-03-04 22:40 | 15 | 014:06 | P | DESGANCHE | 1 X 15 EN XMR Y SE REALIZO DESGANCHE | B22030400076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 846 | 2022-03-04 | 12690 | keep | 0 | Mar | 2022 | 0.0086431 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-04 08:42 | 2022-03-04 11:23 | 50 | 002:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22030400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-03-04 | 8050 | keep | 0 | Mar | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-04 08:45 | 2022-03-04 13:08 | 42 | 004:23 | P | DESGANCHE | 1X30 EN CORTE DE LINEA | B22030400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2022-03-04 | 11046 | keep | 0 | Mar | 2022 | 0.0075234 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
AGUADILLA | 2022-03-04 08:52 | 2022-03-04 08:53 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22030400045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 1047 | keep | 0 | Mar | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
MAYAGÃœEZ | 2022-03-04 08:56 | 2022-03-04 12:59 | 8 | 004:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-03-04 | 1944 | keep | 0 | Mar | 2022 | 0.001324 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-03-04 09:10 | 2022-03-04 09:11 | 5630 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C22030400016 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-04 | 5630 | keep | 0 | Mar | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
MAYAGÃœEZ | 2022-03-04 09:10 | 2022-03-04 12:54 | 4 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22030400050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2022-03-04 | 896 | keep | 0 | Mar | 2022 | 0.00061026 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-03-04 09:11 | 2022-03-04 14:24 | 8 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZARON BAJANTES PRIMARIOS QUEMADOS HACIA TRANSFORMADOR | C22030400024 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 313 | 2022-03-04 | 2504 | keep | 0 | Mar | 2022 | 0.0017055 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-04 09:26 | 2022-03-04 09:27 | 3433 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1204-02 20% POR 1303-02 | S22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 3433 | keep | 0 | Mar | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
PONCE | 2022-03-04 09:29 | 2022-03-04 09:30 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030400039 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 2113 | keep | 0 | Mar | 2022 | 0.0014392 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-04 09:35 | 2022-03-04 15:00 | 75 | 005:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 2 X 65 EN CORTE DE LINEA | B22030400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2022-03-04 | 24375 | keep | 0 | Mar | 2022 | 0.016602 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-03-04 09:55 | 2022-03-04 12:35 | 100 | 002:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO UNA CAJA PRIMARIA AVERIADA | A22030400033 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2022-03-04 | 16000 | keep | 0 | Mar | 2022 | 0.010898 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-04 09:57 | 2022-03-04 17:52 | 1 | 007:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER INFORMA UT2 TRAINED QUE NO SE DETERMINO CAUSA | A22030400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 475 | 2022-03-04 | 475 | keep | 0 | Mar | 2022 | 0.00032352 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-04 10:06 | 2022-03-04 13:53 | 10 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22030400095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-03-04 | 2270 | keep | 0 | Mar | 2022 | 0.0015461 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-04 10:30 | 2022-03-04 12:37 | 6 | 002:07 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR POR SOBRECARGA | M22030400064 | New_Event | Trip Due To Overload | Include | Include | Other | 127 | 2022-03-04 | 762 | keep | 0 | Mar | 2022 | 0.00051899 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-03-04 10:41 | 2022-03-04 10:56 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22030400025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2022-03-04 | 15 | keep | 0 | Mar | 2022 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-04 10:42 | 2022-03-04 21:12 | 100 | 010:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA POR ENCIMA DE PRIMARIA | S22030400101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 630 | 2022-03-04 | 63000 | keep | 0 | Mar | 2022 | 0.042909 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-03-04 10:52 | 2022-03-04 14:14 | 8 | 003:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETESAR LINEA PRIMARIA Y NEUTRAL CRUZADAS | A22030400040 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-03-04 | 1616 | keep | 0 | Mar | 2022 | 0.0011007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-04 10:53 | 2022-03-04 12:25 | 52 | 001:32 | P | DESGANCHE | 1X65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE DE BAMBU | B22030400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-03-04 | 4784 | keep | 0 | Mar | 2022 | 0.0032584 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-03-04 11:03 | 2022-03-04 11:12 | 67 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | PERSONAL DE SUBESTACIONES DISPARO LA BARRA DE 38KV | S22030400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-03-04 | 603 | keep | 0 | Mar | 2022 | 0.0004107 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-03-04 11:03 | 2022-03-04 11:12 | 1587 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | PERSONAL DE SUBESTACIONES DISPARO LA BARRA DE 38KV | S22030400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-03-04 | 14283 | keep | 0 | Mar | 2022 | 0.0097281 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
BAYAMON | 2022-03-04 11:03 | 2022-03-04 11:12 | 521 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | PERSONAL DE SUBESTACIONES DISPARO LA BARRA DE 38KV | S22030400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-03-04 | 4689 | keep | 0 | Mar | 2022 | 0.0031937 | 0.00035485 | Sustained | FALSE | FALSE | Not_TMED_Event | 521
BAYAMON | 2022-03-04 11:03 | 2022-03-04 11:12 | 1307 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | PERSONAL DE SUBESTACIONES DISPARO LA BARRA DE 38KV | S22030400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2022-03-04 | 11763 | keep | 0 | Mar | 2022 | 0.0080117 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
ARECIBO | 2022-03-04 11:25 | 2022-03-04 12:51 | 7 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22030400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2022-03-04 | 602 | keep | 0 | Mar | 2022 | 0.00041002 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-03-04 11:27 | 2022-03-04 15:44 | 70 | 004:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22030400043 | New_Event | Cutout Failure | Include | Include | Equipment | 257 | 2022-03-04 | 17990 | keep | 0 | Mar | 2022 | 0.012253 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-03-04 11:37 | 2022-03-04 15:43 | 104 | 004:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA | C22030400037 | New_Event | Wire Down | Include | Include | Equipment | 246 | 2022-03-04 | 25584 | keep | 0 | Mar | 2022 | 0.017425 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
BARRANQUITAS | 2022-03-04 11:54 | 2022-03-04 12:57 | 229 | 001:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTES ABIERTOS EN TRONCAL | C22030400038 | Additional_clients | Wire Down | Include | Include | Equipment | 63 | 2022-03-04 | 14427 | keep | 0 | Mar | 2022 | 0.0098262 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-04 11:54 | 2022-03-04 12:57 | 1246 | 001:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTES ABIERTOS EN TRONCAL CARGA POR EL 9901-01 | C22030400038 | New_Event | Wire Down | Include | Include | Equipment | 63 | 2022-03-04 | 78498 | keep | 0 | Mar | 2022 | 0.053465 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
SAN JUAN | 2022-03-04 12:04 | 2022-03-04 19:39 | 1 | 007:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22030400044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 455 | 2022-03-04 | 455 | keep | 0 | Mar | 2022 | 0.0003099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-04 12:11 | 2022-03-04 20:00 | 15 | 007:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22030400024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 469 | 2022-03-04 | 7035 | keep | 0 | Mar | 2022 | 0.0047915 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-04 12:20 | 2022-03-04 16:13 | 15 | 003:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA AVERIADO | B22030400050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 233 | 2022-03-04 | 3495 | keep | 0 | Mar | 2022 | 0.0023804 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-04 12:34 | 2022-03-04 12:35 | 2956 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE LLEVA LA CARGA DEL 1907-05 | S22030400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-04 | 2956 | keep | 0 | Mar | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-03-04 12:35 | 2022-03-04 17:04 | 100 | 004:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22030400133 | New_Event | Cutout Failure | Include | Include | Equipment | 269 | 2022-03-04 | 26900 | keep | 0 | Mar | 2022 | 0.018321 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-04 13:02 | 2022-03-04 14:41 | 128 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030400046 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2022-03-04 | 12672 | keep | 0 | Mar | 2022 | 0.0086308 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
MAYAGÃœEZ | 2022-03-04 13:31 | 2022-03-04 15:09 | 80 | 001:38 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030400085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-03-04 | 7840 | keep | 0 | Mar | 2022 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-04 13:48 | 2022-03-04 14:22 | 1 | 000:34 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER INFORMA UT2 TRAINED QUE NO SE DETERMINO CAUSA | A22030400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2022-03-04 | 34 | keep | 0 | Mar | 2022 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-04 13:50 | 2022-03-04 16:00 | 33 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | A22030400049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2022-03-04 | 4290 | keep | 0 | Mar | 2022 | 0.0029219 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-03-04 13:59 | 2022-03-04 16:12 | 6 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22030400144 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2022-03-04 | 798 | keep | 0 | Mar | 2022 | 0.00054351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-04 14:05 | 2022-03-04 14:50 | 50 | 000:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-03-04 | 2250 | keep | 0 | Mar | 2022 | 0.0015325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-04 14:11 | 2022-03-04 14:12 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 9501-03 DISPARO INTERRUPTOR Y SE CERRO POR SCADA | B22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 3070 | keep | 0 | Mar | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-03-04 14:11 | 2022-03-04 14:12 | 1070 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA 9501-01 | B22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 1070 | keep | 0 | Mar | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
MAYAGÃœEZ | 2022-03-04 14:15 | 2022-03-04 14:35 | 1 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22030400005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-03-04 | 20 | keep | 0 | Mar | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-04 14:21 | 2022-03-04 15:27 | 4 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C22030400061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2022-03-04 | 264 | keep | 0 | Mar | 2022 | 0.00017981 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-04 14:46 | 2022-03-04 16:15 | 30 | 001:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-03-04 | 2670 | keep | 0 | Mar | 2022 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-04 14:46 | 2022-03-04 15:39 | 10 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22030400064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-03-04 | 530 | keep | 0 | Mar | 2022 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-04 14:53 | 2022-03-04 16:21 | 60 | 001:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22030400066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-03-04 | 5280 | keep | 0 | Mar | 2022 | 0.0035962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-04 15:04 | 2022-03-04 18:48 | 48 | 003:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-03-04 | 10752 | keep | 0 | Mar | 2022 | 0.0073231 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2022-03-04 15:09 | 2022-03-04 18:26 | 9 | 003:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22030400099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 197 | 2022-03-04 | 1773 | keep | 0 | Mar | 2022 | 0.0012076 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-03-04 15:11 | 2022-03-04 18:34 | 922 | 003:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO A LA SALIDA DEL 1401-08 QUE LLEVA 1346-05 | S22030400160 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2022-03-04 | 187166 | keep | 0 | Mar | 2022 | 0.12748 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-04 15:11 | 2022-03-04 18:34 | 135 | 003:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO A LA SALIDA DEL 1401-08 QUE LLEVA 1346-05 | S22030400160 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2022-03-04 | 27405 | keep | 0 | Mar | 2022 | 0.018665 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
AGUADILLA | 2022-03-04 15:11 | 2022-03-04 16:41 | 10 | 001:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR AVERIADA | M22030400101 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2022-03-04 | 900 | keep | 0 | Mar | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-03-04 15:12 | 2022-03-04 16:49 | 20 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22030400036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-03-04 | 1940 | keep | 0 | Mar | 2022 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-04 15:23 | 2022-03-04 23:40 | 382 | 008:17 | S | NO SE REPORTO CAUSA | DISPARO DE MLB 0010 SE HIZO PRUEBAS A TRANSFORMADOR Y SE CERRO INTERRUPTORES | M22030400103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2022-03-04 | 189854 | keep | 0 | Mar | 2022 | 0.12931 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2022-03-04 15:23 | 2022-03-04 23:40 | 39 | 008:17 | S | NO SE REPORTO CAUSA | DISPARO DE MLB 0010 SE HIZO PRUEBAS A TRANSFORMADOR Y SE CERRO INTERRUPTORES | M22030400103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2022-03-04 | 19383 | keep | 0 | Mar | 2022 | 0.013202 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2022-03-04 15:27 | 2022-03-04 16:15 | 15 | 000:48 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | R22030400055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 48 | 2022-03-04 | 720 | keep | 0 | Mar | 2022 | 0.00049039 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-03-04 15:34 | 2022-03-04 19:23 | 9 | 003:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO LINEA SECUNDARIA ROTA A CAUSA DE UN CAMION QUE LA PARTIO | A22030400060 | New_Event |  |  | Include | Wildlife | 229 | 2022-03-04 | 2061 | keep | 0 | Mar | 2022 | 0.0014037 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-03-04 16:27 | 2022-03-04 17:05 | 1 | 000:38 | P | DESGANCHE | 1 X 30 EN C/L | R22030400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-03-04 | 38 | keep | 0 | Mar | 2022 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-04 17:02 | 2022-03-04 19:19 | 12 | 002:17 | P | DESGANCHE | 1 X 20 EN RISER CRUCE DE FASE PRIMARIA POR RAMA | P22030400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-03-04 | 1644 | keep | 0 | Mar | 2022 | 0.0011197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-04 17:08 | 2022-03-04 17:09 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 6014-02 | M22030400145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 1444 | keep | 0 | Mar | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-03-04 17:08 | 2022-03-04 17:09 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-01 | M22030400145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 3630 | keep | 0 | Mar | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
CAGUAS | 2022-03-04 17:09 | 2022-03-05 10:04 | 1 | 016:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22030400070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1015 | 2022-03-04 | 1015 | keep | 0 | Mar | 2022 | 0.00069131 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-04 17:10 | 2022-03-05 07:30 | 4 | 014:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P22030400060 | New_Event | Bad Weather | Include | Include | Weather | 860 | 2022-03-04 | 3440 | keep | 0 | Mar | 2022 | 0.002343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-03-04 17:17 | 2022-03-04 17:40 | 1 | 000:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE MONTURA DE TRANSFORMADORES | B22030400075 | New_Event | Wire Down | Include | Include | Equipment | 23 | 2022-03-04 | 23 | keep | 0 | Mar | 2022 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-04 17:33 | 2022-03-05 12:52 | 20 | 019:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030400141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1159 | 2022-03-04 | 23180 | keep | 0 | Mar | 2022 | 0.015788 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-03-04 17:48 | 2022-03-04 20:35 | 8 | 002:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA. INFORMO MANUEL BONET FOREMAN QUE SE ENCONTRABA DERRETIDA EN UN LADO POR SER DE BAJA CALIDAD | A22030400076 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2022-03-04 | 1336 | keep | 0 | Mar | 2022 | 0.00090994 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-04 17:51 | 2022-03-04 17:54 | 68 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1102-01 LLEVA 1105-04 Y 1105-05 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 204 | keep | 0 | Mar | 2022 | 0.00013894 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-03-04 17:51 | 2022-03-04 17:54 | 171 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1102-02 LLEVANDO LA CARGA DEL 1110-02 Y 1110-05 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 513 | keep | 0 | Mar | 2022 | 0.0003494 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-03-04 17:51 | 2022-03-04 17:54 | 1837 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 5511 | keep | 0 | Mar | 2022 | 0.0037535 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
BAYAMON | 2022-03-04 17:51 | 2022-03-04 17:54 | 536 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-01 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 1608 | keep | 0 | Mar | 2022 | 0.0010952 | 0.00036507 | Momentary | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2022-03-04 17:51 | 2022-03-04 17:54 | 348 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-01 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 1044 | keep | 0 | Mar | 2022 | 0.00071106 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2022-03-04 17:51 | 2022-03-04 17:54 | 559 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1102-01 LLEVA 1105-04 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 1677 | keep | 0 | Mar | 2022 | 0.0011422 | 0.00038073 | Momentary | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2022-03-04 17:51 | 2022-03-04 17:54 | 370 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1102-01 LLEVA 1105-05 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 1110 | keep | 0 | Mar | 2022 | 0.00075602 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2022-03-04 17:51 | 2022-03-04 17:54 | 455 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1102-02 LLEVANDO LA CARGA DEL 1110-02 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 1365 | keep | 0 | Mar | 2022 | 0.0009297 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2022-03-04 17:51 | 2022-03-04 17:54 | 283 | 000:03 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1102-02 LLEVANDO LA CARGA DEL 1110-05 | S22030400224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-04 | 849 | keep | 0 | Mar | 2022 | 0.00057825 | 0.00019275 | Momentary | FALSE | FALSE | Not_TMED_Event | 283
HUMACAO | 2022-03-04 17:56 | 2022-03-04 20:35 | 2354 | 002:39 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO | C22030400078 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 159 | 2022-03-04 | 374286 | keep | 0 | Mar | 2022 | 0.25492 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
ARECIBO | 2022-03-04 17:58 | 2022-03-04 17:59 | 128 | 000:01 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030400074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-04 | 128 | keep | 0 | Mar | 2022 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
MAYAGÃœEZ | 2022-03-04 18:10 | 2022-03-04 18:11 | 4641 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030400149 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-04 | 4641 | keep | 0 | Mar | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-03-04 18:15 | 2022-03-04 18:16 | 4641 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030400150 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-04 | 4641 | keep | 0 | Mar | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-03-04 18:16 | 2022-03-05 15:24 | 10 | 021:08 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN PM SE ALAMBRO TRAMO DE 125 PIES DE ALAMBRE #2 CON TERMINACIONES EN LOS EXTREMOS | M22030400151 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1268 | 2022-03-04 | 12680 | keep | 0 | Mar | 2022 | 0.0086363 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-04 18:51 | 2022-03-04 18:52 | 450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR SCADA | B22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 450 | keep | 0 | Mar | 2022 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
MAYAGÃœEZ | 2022-03-04 19:07 | 2022-03-05 15:15 | 16 | 020:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22030400166 | New_Event | Cutout Failure | Include | Include | Equipment | 1208 | 2022-03-04 | 19328 | keep | 0 | Mar | 2022 | 0.013164 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-03-04 20:07 | 2022-03-04 22:21 | 10 | 002:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22030400256 | New_Event | Secondary Wire Down | Include | Include | Equipment | 134 | 2022-03-04 | 1340 | keep | 0 | Mar | 2022 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-04 20:28 | 2022-03-04 22:44 | 500 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA TOTAL PARA CERRAR PUENTE PRIMARIO | B22030400083 | New_Event | Wire Down | Include | Include | Equipment | 136 | 2022-03-04 | 68000 | keep | 0 | Mar | 2022 | 0.046314 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2022-03-04 20:35 | 2022-03-04 21:28 | 2000 | 000:53 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIERON PB2 Y PB3 BYPASS | C22030400078 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 53 | 2022-03-04 | 106000 | keep | 0 | Mar | 2022 | 0.072196 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-04 21:05 | 2022-03-04 21:07 | 86 | 000:02 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 20% POR EL 1658-14 | R22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-04 | 172 | keep | 0 | Mar | 2022 | 0.00011715 | 5.8574e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 86
SAN JUAN | 2022-03-04 21:05 | 2022-03-04 21:07 | 1 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 20% DEL 1657-02 | R22030400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-04 | 2 | keep | 0 | Mar | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-04 21:21 | 2022-03-04 23:14 | 2067 | 001:53 | T | MAL TIEMPO/RAYOS/WET ASH | LLUVIA Y FUERTES VIENTOS EN EL AREA | M22030400193 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-03-04 | 233571 | keep | 0 | Mar | 2022 | 0.15908 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
HUMACAO | 2022-03-04 21:28 | 2022-03-04 21:39 | 2354 | 000:11 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO | C22030400078 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 11 | 2022-03-04 | 25894 | keep | 0 | Mar | 2022 | 0.017636 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-04 21:29 | 2022-03-05 18:11 | 25 | 020:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 65 ENJ CORTE DE LINEA SECUNDARIA PEGANDO CAJA PRIMARIO | S22030400271 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1242 | 2022-03-04 | 31050 | keep | 0 | Mar | 2022 | 0.021148 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-04 21:39 | 2022-03-04 22:01 | 2000 | 000:22 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIERON PB2 Y PB3 BYPASS | C22030400078 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 22 | 2022-03-04 | 44000 | keep | 0 | Mar | 2022 | 0.029968 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-03-04 21:49 | 2022-03-05 00:25 | 190 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN RISER CRUCE POR IGUANA Y PARARRAYO AVERIADO | R22030400050 | New_Event |  |  | Include | Wildlife | 156 | 2022-03-04 | 29640 | keep | 0 | Mar | 2022 | 0.020188 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
HUMACAO | 2022-03-04 22:01 | 2022-03-04 22:08 | 2354 | 000:07 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO OPERACIONES Y SECCIONALIZANDO LAZO SOTERRADO DE PB-2 PROBANDO MALO. | C22030400076 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 7 | 2022-03-04 | 16478 | keep | 0 | Mar | 2022 | 0.011223 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-04 22:08 | 2022-03-04 23:02 | 774 | 000:54 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO OPERACIONES Y SECCIONALIZANDO LAZO SOTERRADO DE PB-2 PROBANDO MALO. | C22030400076 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 54 | 2022-03-04 | 41796 | keep | 0 | Mar | 2022 | 0.028467 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-04 22:41 | 2022-03-04 22:42 | 1000 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF PARTE POR 1620-2 | S22030500043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 1000 | keep | 0 | Mar | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-04 22:41 | 2022-03-04 22:42 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22030400273 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-04 | 3718 | keep | 0 | Mar | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-03-04 22:44 | 2022-03-06 09:59 | 2 | 035:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO PORTAFUSIBLE | S22030400274 | New_Event | Cutout Failure | Include | Include | Equipment | 2115 | 2022-03-04 | 4230 | keep | 0 | Mar | 2022 | 0.002881 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-03-04 23:22 | 2022-03-04 23:55 | 2354 | 000:33 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO OPERACIONES Y SECCIONALIZANDO LAZO SOTERRADO DE PB-2 PROBANDO MALO. | C22030400076 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 33 | 2022-03-04 | 77682 | keep | 0 | Mar | 2022 | 0.052909 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2022-03-04 23:35 | 2022-03-05 10:18 | 60 | 010:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030400241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 643 | 2022-03-04 | 38580 | keep | 0 | Mar | 2022 | 0.026277 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-03-04 23:40 | 2022-03-05 01:13 | 80 | 001:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22030400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-03-04 | 7440 | keep | 0 | Mar | 2022 | 0.0050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-03-05 00:25 | 2022-03-05 01:13 | 1074 | 000:48 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTELLIRUPTER 2604-3G EN OPERACIONES PARA TRANSFERIR CARGA AFECTADA DEL PB-2 @ 2604-3 POR EL INTELLIRUPTER 2604-3F N/O | C22030400076 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 48 | 2022-03-05 | 51552 | keep | 0 | Mar | 2022 | 0.035112 | 0.0007315 | Sustained | FALSE | FALSE | Not_TMED_Event | 1074
BAYAMON | 2022-03-05 00:50 | 2022-03-05 09:06 | 30 | 008:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22030500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 496 | 2022-03-05 | 14880 | keep | 0 | Mar | 2022 | 0.010135 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-05 00:54 | 2022-03-05 09:53 | 40 | 008:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22030500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 539 | 2022-03-05 | 21560 | keep | 0 | Mar | 2022 | 0.014684 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-05 01:04 | 2022-03-05 01:05 | 989 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C22030500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 989 | keep | 0 | Mar | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-03-05 01:05 | 2022-03-05 06:19 | 150 | 005:14 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | C22030500016 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 314 | 2022-03-05 | 47100 | keep | 0 | Mar | 2022 | 0.03208 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-03-05 01:13 | 2022-03-05 10:32 | 774 | 009:19 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO DEL SU-11 AL PB-2 SE DEJO SECCIONALIZADO EL SU-G13 | C22030400078 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 559 | 2022-03-05 | 432666 | keep | 0 | Mar | 2022 | 0.29469 | 0.00052717 | Sustained | FALSE | FALSE | Not_TMED_Event | 774
CANOVANAS | 2022-03-05 01:28 | 2022-03-05 08:10 | 20 | 006:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE LLEVO CONDUCTOR A AISLADOR | R22030500008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 402 | 2022-03-05 | 8040 | keep | 0 | Mar | 2022 | 0.005476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-05 01:28 | 2022-03-05 12:00 | 5 | 010:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 10 EN TRANSFORMADOR SE REPARO BAJANTE PARTIDO Y PARARRAYOS | M22030500007 | New_Event | Wire Down | Include | Include | Equipment | 632 | 2022-03-05 | 3160 | keep | 0 | Mar | 2022 | 0.0021523 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-05 01:31 | 2022-03-05 01:32 | 3432 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 20% DE LA CARGA POR EL 1303-02 | S22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 3432 | keep | 0 | Mar | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-03-05 02:22 | 2022-03-05 02:23 | 770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22030500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 770 | keep | 0 | Mar | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-03-05 02:24 | 2022-03-05 02:25 | 770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22030500016 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 770 | keep | 0 | Mar | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
BAYAMON | 2022-03-05 02:59 | 2022-03-05 04:06 | 200 | 001:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y 2X200 EN CORTES DE LINEAS | B22030500010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2022-03-05 | 13400 | keep | 0 | Mar | 2022 | 0.0091267 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-05 03:13 | 2022-03-05 03:15 | 520 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 20% DE SU CARGA POR EL 1717-04 | B22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-05 | 1040 | keep | 0 | Mar | 2022 | 0.00070834 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
VEGA BAJA | 2022-03-05 03:14 | 2022-03-05 07:34 | 10 | 004:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR | B22030500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2022-03-05 | 2600 | keep | 0 | Mar | 2022 | 0.0017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-05 03:18 | 2022-03-05 15:32 | 70 | 012:14 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-9 | S22030500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 734 | 2022-03-05 | 51380 | keep | 0 | Mar | 2022 | 0.034995 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-03-05 03:44 | 2022-03-05 12:33 | 40 | 008:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L LEVANTO CONDUCTOR | C22030500019 | New_Event | Wire Down | Include | Include | Equipment | 529 | 2022-03-05 | 21160 | keep | 0 | Mar | 2022 | 0.014412 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-05 04:15 | 2022-03-05 04:16 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 308 | keep | 0 | Mar | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2022-03-05 04:59 | 2022-03-05 13:40 | 80 | 008:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500003 | New_Event | Bad Weather | Include | Include | Weather | 521 | 2022-03-05 | 41680 | keep | 0 | Mar | 2022 | 0.028388 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-03-05 05:00 | 2022-03-05 05:01 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 9207-09 | B22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 1859 | keep | 0 | Mar | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-03-05 05:00 | 2022-03-05 05:01 | 7 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 9207-08 | B22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 7 | keep | 0 | Mar | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-03-05 05:46 | 2022-03-05 05:47 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 2039 | keep | 0 | Mar | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
SAN JUAN | 2022-03-05 06:04 | 2022-03-05 06:06 | 1000 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF PARTE POR 1620-2 | S22030500043 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-05 06:04 | 2022-03-05 06:06 | 3718 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF LLEVA PARTE DEL 1206-3 | S22030500043 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 7436 | keep | 0 | Mar | 2022 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-03-05 06:07 | 2022-03-05 06:09 | 1447 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA 1419-12 Y 9 | S22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-05 | 2894 | keep | 0 | Mar | 2022 | 0.0019711 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-03-05 06:07 | 2022-03-05 06:09 | 266 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SU CARGA POR 1112-4 MAL TIEMPO | S22030500000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 532 | keep | 0 | Mar | 2022 | 0.00036234 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-03-05 06:07 | 2022-03-05 06:09 | 73 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SU CARGA POR 1112-4 MAL TIEMPO | S22030500000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 146 | keep | 0 | Mar | 2022 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2022-03-05 06:08 | 2022-03-05 06:12 | 1000 | 000:04 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1620-2 MAL TIEMPO | S22030500043 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 4 | 2022-03-05 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-05 06:08 | 2022-03-05 06:12 | 3718 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE DEL 1206-3 MAL TIEMPO | S22030500043 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 4 | 2022-03-05 | 14872 | keep | 0 | Mar | 2022 | 0.010129 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-03-05 06:27 | 2022-03-05 17:44 | 15 | 011:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR SE RETIRO 2 GALLINAS DE PALO Y SE HIZO DESGANCHE | S22030500048 | New_Event |  |  | Include | Wildlife | 677 | 2022-03-05 | 10155 | keep | 0 | Mar | 2022 | 0.0069165 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-05 06:31 | 2022-03-05 06:33 | 3005 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22030500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-05 | 6010 | keep | 0 | Mar | 2022 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
SAN JUAN | 2022-03-05 06:51 | 2022-03-05 06:52 | 3046 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | R22030500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-05 | 3046 | keep | 0 | Mar | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-03-05 06:52 | 2022-03-05 11:03 | 20 | 004:11 | P | DESGANCHE | 1 X 40 EN AEREO PROVISIONAL SE REALIZO DESGANCHE | R22030500034 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-03-05 | 5020 | keep | 0 | Mar | 2022 | 0.0034191 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-03-05 06:55 | 2022-03-05 12:54 | 10 | 005:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22030500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 359 | 2022-03-05 | 3590 | keep | 0 | Mar | 2022 | 0.0024451 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-05 07:18 | 2022-03-05 08:36 | 20 | 001:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | R22030500026 | New_Event |  |  | Include | Wildlife | 78 | 2022-03-05 | 1560 | keep | 0 | Mar | 2022 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-05 07:33 | 2022-03-05 15:32 | 120 | 007:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | S22030500054 | New_Event | Bad Weather | Include | Include | Weather | 479 | 2022-03-05 | 57480 | keep | 0 | Mar | 2022 | 0.039149 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-03-05 07:39 | 2022-03-05 09:15 | 30 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | R22030500032 | New_Event |  |  | Include | Wildlife | 96 | 2022-03-05 | 2880 | keep | 0 | Mar | 2022 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-05 07:41 | 2022-03-05 17:20 | 40 | 009:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR PALOMA | C22030500034 | New_Event |  |  | Include | Wildlife | 579 | 2022-03-05 | 23160 | keep | 0 | Mar | 2022 | 0.015774 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-05 07:46 | 2022-03-05 10:04 | 10 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22030500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-03-05 | 1380 | keep | 0 | Mar | 2022 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-05 07:47 | 2022-03-05 07:49 | 1000 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1620-2 MAL TIEMPO | S22030500055 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-05 07:47 | 2022-03-05 07:49 | 3718 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE DEL 1206-3 MAL TIEMPO | S22030500055 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 7436 | keep | 0 | Mar | 2022 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2022-03-05 08:03 | 2022-03-05 10:15 | 30 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA FUERTE | R22030500037 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2022-03-05 | 3960 | keep | 0 | Mar | 2022 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-05 08:09 | 2022-03-05 10:50 | 200 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 200 EN C/L Y 1 X 100 EN RISER | B22030500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-03-05 | 32200 | keep | 0 | Mar | 2022 | 0.021931 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-05 08:15 | 2022-03-05 11:18 | 10 | 003:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR CON DERRAME DE ACEITE DE 25 X 25 KVA | B22030500006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 183 | 2022-03-05 | 1830 | keep | 0 | Mar | 2022 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-05 08:39 | 2022-03-05 08:40 | 725 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22030500052 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-05 | 725 | keep | 0 | Mar | 2022 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2022-03-05 08:40 | 2022-03-05 19:11 | 60 | 010:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO | C22030500054 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 631 | 2022-03-05 | 37860 | keep | 0 | Mar | 2022 | 0.025786 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-05 08:52 | 2022-03-05 14:49 | 12 | 005:57 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO AVERIADO Y SE ENERGIZO DE T-1 @ T-3 | B22030500009 | New_Event | UG Cable Fault | Include | Include | Equipment | 357 | 2022-03-05 | 4284 | keep | 0 | Mar | 2022 | 0.0029178 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-05 08:56 | 2022-03-05 13:44 | 134 | 004:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C22030500055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-03-05 | 38592 | keep | 0 | Mar | 2022 | 0.026285 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2022-03-05 09:07 | 2022-03-05 19:02 | 18 | 009:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA POR 50KVA | B22030500011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 595 | 2022-03-05 | 10710 | keep | 0 | Mar | 2022 | 0.0072945 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-03-05 09:13 | 2022-03-05 09:14 | 27 | 000:01 | T | OTRAS CAUSAS | RECERRO | B22030500000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-03-05 | 27 | keep | 0 | Mar | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-03-05 09:14 | 2022-03-05 14:33 | 10 | 005:19 | P | OTRAS CAUSAS | 2 X 80 EN SU-6 1 X 65 EN SU-B Y SE DEJO ABIERTO DE SU @ FACCIO NO HUBO ACCESO A VERIFICAR | B22030500016 | 1st_after_momentary | Other Causes | Include | Include | Other | 319 | 2022-03-05 | 3190 | keep | 0 | Mar | 2022 | 0.0021727 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-05 09:15 | 2022-03-05 09:19 | 1000 | 000:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE INTERRUPTOR PARA ABRIR MACHETE PUENTE SAFADO COLGANDO SOBRE AISLADOR PARTIDO PARTE POR 1206-3 | S22030500067 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-03-05 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-05 09:15 | 2022-03-05 09:19 | 3133 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA ABRIR MACHETE PUENTE SAFADO COLGANDO SOBRE AISLADOR PARTIDO LLEVA PARTE 1204-5 | S22030500067 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-03-05 | 12532 | keep | 0 | Mar | 2022 | 0.0085355 | 0.0021339 | Momentary | FALSE | FALSE | Not_TMED_Event | 3133
SAN JUAN | 2022-03-05 09:19 | 2022-03-05 11:07 | 700 | 001:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIR MACHETE PARA REPARAR PUENTE SOBRE AISLADOR PARTIDO PARTE POR EL 1206-3 | S22030500067 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 108 | 2022-03-05 | 75600 | keep | 0 | Mar | 2022 | 0.051491 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
FAJARDO | 2022-03-05 09:37 | 2022-03-05 14:32 | 3 | 004:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22030500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 295 | 2022-03-05 | 885 | keep | 0 | Mar | 2022 | 0.00060277 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-05 09:54 | 2022-03-05 15:47 | 100 | 005:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22030500018 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2022-03-05 | 35300 | keep | 0 | Mar | 2022 | 0.024043 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-05 10:04 | 2022-03-05 12:32 | 60 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE DE LINEA A CAJA | S22030500076 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2022-03-05 | 8880 | keep | 0 | Mar | 2022 | 0.0060481 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-03-05 10:04 | 2022-03-05 14:32 | 60 | 004:28 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22030500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2022-03-05 | 16080 | keep | 0 | Mar | 2022 | 0.010952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-03-05 10:04 | 2022-03-05 18:00 | 30 | 007:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22030500073 | New_Event | Bad Weather | Include | Include | Weather | 476 | 2022-03-05 | 14280 | keep | 0 | Mar | 2022 | 0.009726 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-05 10:10 | 2022-03-05 14:08 | 10 | 003:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A22030500029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 238 | 2022-03-05 | 2380 | keep | 0 | Mar | 2022 | 0.001621 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-05 10:14 | 2022-03-05 10:16 | 1076 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE LE DIO PRUEBA POR SCADA Y QUEDO EN SERVICIO | P22030500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-05 | 2152 | keep | 0 | Mar | 2022 | 0.0014657 | 0.00073286 | Momentary | FALSE | FALSE | Not_TMED_Event | 1076
FAJARDO | 2022-03-05 10:15 | 2022-03-05 12:01 | 10 | 001:46 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR SE REALIZO DESGANCHE | R22030500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-03-05 | 1060 | keep | 0 | Mar | 2022 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-05 10:21 | 2022-03-05 11:46 | 100 | 001:25 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-03-05 | 8500 | keep | 0 | Mar | 2022 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-05 10:32 | 2022-03-05 17:28 | 751 | 006:56 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO N/O DEL SU-4.1 AL SU-2.1.1 SE DEJO SU-13 SECCIONALIZADO | C22030400076 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 416 | 2022-03-05 | 312416 | keep | 0 | Mar | 2022 | 0.21279 | 0.0005115 | Sustained | FALSE | FALSE | Not_TMED_Event | 751
SAN JUAN | 2022-03-05 10:46 | 2022-03-05 12:10 | 1 | 001:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE TRANSFORMADORES | R22030500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-03-05 | 84 | keep | 0 | Mar | 2022 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-03-05 10:49 | 2022-03-05 13:27 | 10 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R22030500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-03-05 | 1580 | keep | 0 | Mar | 2022 | 0.0010761 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-05 10:50 | 2022-03-05 13:17 | 8 | 002:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE Y TOMA | S22030500083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 147 | 2022-03-05 | 1176 | keep | 0 | Mar | 2022 | 0.00080097 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-05 10:50 | 2022-03-06 12:11 | 9 | 025:21 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE T-490 @ T-489 MEDIANTE GOI BY-220305-02 | B22030500019 | New_Event | UG Cable Fault | Include | Include | Equipment | 1521 | 2022-03-05 | 13689 | keep | 0 | Mar | 2022 | 0.0093235 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-03-05 11:12 | 2022-03-05 11:13 | 393 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR 6007-05 EL CUAL ESTA LLEVANDO LA CARGA DEL 6007-04 | M22030500029 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-05 | 393 | keep | 0 | Mar | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-03-05 11:12 | 2022-03-05 11:13 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-04 | M22030500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 4 | keep | 0 | Mar | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-05 11:13 | 2022-03-05 17:29 | 300 | 006:16 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030500031 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 376 | 2022-03-05 | 112800 | keep | 0 | Mar | 2022 | 0.076828 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-03-05 11:28 | 2022-03-05 11:41 | 10 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22030500065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-03-05 | 130 | keep | 0 | Mar | 2022 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-05 11:33 | 2022-03-05 11:50 | 1 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22030500012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2022-03-05 | 17 | keep | 0 | Mar | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-05 12:22 | 2022-03-05 14:36 | 36 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22030500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-03-05 | 4824 | keep | 0 | Mar | 2022 | 0.0032856 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-03-05 12:31 | 2022-03-05 14:58 | 37 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22030500097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-03-05 | 5439 | keep | 0 | Mar | 2022 | 0.0037045 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
ARECIBO | 2022-03-05 12:51 | 2022-03-05 14:10 | 10 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR INFORMA UL2 TRAINED NO IDENTIFICO CAUSA | A22030500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-03-05 | 790 | keep | 0 | Mar | 2022 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-05 12:57 | 2022-03-05 12:58 | 828 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 60% POR 1206-04 | S22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 828 | keep | 0 | Mar | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-03-05 12:57 | 2022-03-05 12:58 | 3995 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 80% POR 1206-04 | S22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 3995 | keep | 0 | Mar | 2022 | 0.002721 | 0.002721 | Momentary | FALSE | FALSE | Not_TMED_Event | 3995
SAN JUAN | 2022-03-05 12:57 | 2022-03-05 12:58 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 20% 1303-02 80% DEL 1204-4 Y 60% 1204-3 | S22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 1799 | keep | 0 | Mar | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-03-05 12:57 | 2022-03-05 12:58 | 487 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 20% POR 1206-04 | S22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 487 | keep | 0 | Mar | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
ARECIBO | 2022-03-05 13:09 | 2022-03-05 15:09 | 20 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500042 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2022-03-05 | 2400 | keep | 0 | Mar | 2022 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-03-05 13:21 | 2022-03-05 15:43 | 15 | 002:22 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PARARRAYO | C22030500100 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 142 | 2022-03-05 | 2130 | keep | 0 | Mar | 2022 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-05 13:30 | 2022-03-05 22:45 | 60 | 009:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030500292 | New_Event | Bad Weather | Include | Include | Weather | 555 | 2022-03-05 | 33300 | keep | 0 | Mar | 2022 | 0.02268 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-05 13:39 | 2022-03-05 20:38 | 60 | 006:59 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN CORTE DE LINEA AVERIA DE RISER TEMPORERO A PM 241 | R22030500070 | New_Event | UG Cable Fault | Include | Include | Equipment | 419 | 2022-03-05 | 25140 | keep | 0 | Mar | 2022 | 0.017123 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-05 13:57 | 2022-03-05 15:53 | 80 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22030500101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-03-05 | 9280 | keep | 0 | Mar | 2022 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-03-05 14:02 | 2022-03-05 15:35 | 6 | 001:33 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | R22030500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-03-05 | 558 | keep | 0 | Mar | 2022 | 0.00038005 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-05 14:06 | 2022-03-05 16:30 | 263 | 002:24 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA | S22030500104 | New_Event | Bad Weather | Include | Include | Weather | 144 | 2022-03-05 | 37872 | keep | 0 | Mar | 2022 | 0.025794 | 0.00017913 | Sustained | FALSE | FALSE | Not_TMED_Event | 263
MAYAGÃœEZ | 2022-03-05 14:08 | 2022-03-05 14:09 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 2067 | keep | 0 | Mar | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
CAGUAS | 2022-03-05 14:10 | 2022-03-05 16:42 | 800 | 002:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22030500112 | New_Event | Bad Weather | Include | Include | Weather | 152 | 2022-03-05 | 121600 | keep | 0 | Mar | 2022 | 0.082821 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
MAYAGÃœEZ | 2022-03-05 14:15 | 2022-03-06 09:10 | 19 | 018:55 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PARARRAYO QUEMADO | M22030500054 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1135 | 2022-03-05 | 21565 | keep | 0 | Mar | 2022 | 0.014688 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2022-03-05 14:16 | 2022-03-05 19:54 | 30 | 005:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22030500055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 338 | 2022-03-05 | 10140 | keep | 0 | Mar | 2022 | 0.0069063 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-05 14:30 | 2022-03-05 17:01 | 20 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500056 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2022-03-05 | 3020 | keep | 0 | Mar | 2022 | 0.0020569 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-03-05 14:31 | 2022-03-05 17:00 | 40 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500068 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2022-03-05 | 5960 | keep | 0 | Mar | 2022 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-05 14:33 | 2022-03-05 14:47 | 27 | 000:14 | T | OTRAS CAUSAS | HACIENDO PRUEBA HACIA FACCIO DISPARO INTERRUPTOR | B22030500028 | New_Event | Other Causes | Include | Include | Other | 14 | 2022-03-05 | 378 | keep | 0 | Mar | 2022 | 0.00025745 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-03-05 14:37 | 2022-03-05 19:13 | 299 | 004:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA Y PARARRAYO | B22030500029 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2022-03-05 | 82524 | keep | 0 | Mar | 2022 | 0.056207 | 0.00020365 | Sustained | FALSE | FALSE | Not_TMED_Event | 299
BAYAMON | 2022-03-05 14:40 | 2022-03-05 16:31 | 80 | 001:51 | P | DESGANCHE | 3 X 80 EN C/L SE REALIZO DESGANCHE | B22030500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-03-05 | 8880 | keep | 0 | Mar | 2022 | 0.0060481 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-05 14:41 | 2022-03-05 15:33 | 1017 | 000:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR SE PATRULLO Y SE ENCONTRO LINEA PRIMERIA ROTA SE SECCIONALIZO | M22030500084 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2022-03-05 | 52884 | keep | 0 | Mar | 2022 | 0.036019 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-03-05 14:44 | 2022-03-05 14:45 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 3041 | keep | 0 | Mar | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-03-05 14:45 | 2022-03-05 14:46 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030500061 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 3041 | keep | 0 | Mar | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-03-05 14:47 | 2022-03-05 14:48 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030500064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 3041 | keep | 0 | Mar | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
VEGA BAJA | 2022-03-05 14:47 | 2022-03-05 15:34 | 10 | 000:47 | P | OTRAS CAUSAS | 2 X 80 EN SU-6 1 X 65 EN SU-B Y SE DEJO ABIERTO DE SU @ FACCIO NO HUBO ACCESO A VERIFICAR | B22030500016 | Partial_restoration | Other Causes | Include | Include | Other | 47 | 2022-03-05 | 470 | keep | 0 | Mar | 2022 | 0.00032011 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-05 14:50 | 2022-03-05 16:36 | 800 | 001:46 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22030500124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-03-05 | 84800 | keep | 0 | Mar | 2022 | 0.057757 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BARRANQUITAS | 2022-03-05 14:53 | 2022-03-05 14:54 | 3296 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22030500127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 3296 | keep | 0 | Mar | 2022 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
MAYAGÃœEZ | 2022-03-05 14:54 | 2022-03-06 10:20 | 5 | 019:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22030500067 | New_Event | Bad Weather | Include | Include | Weather | 1166 | 2022-03-05 | 5830 | keep | 0 | Mar | 2022 | 0.0039708 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-03-05 14:56 | 2022-03-05 16:24 | 70 | 001:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 25 EN CORTES DE LINEA SE REEMPLAZO PIN POLE TOP | R22030500076 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 88 | 2022-03-05 | 6160 | keep | 0 | Mar | 2022 | 0.0041955 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-03-05 14:59 | 2022-03-05 17:50 | 50 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P22030500029 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2022-03-05 | 8550 | keep | 0 | Mar | 2022 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-05 15:00 | 2022-03-05 15:01 | 1109 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | P22030500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 1109 | keep | 0 | Mar | 2022 | 0.00075533 | 0.00075533 | Momentary | FALSE | FALSE | Not_TMED_Event | 1109
SAN JUAN | 2022-03-05 15:16 | 2022-03-05 15:18 | 1000 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF PARTE POR 1620-2 SE VERIFICO CON PERSONAL EN EL AREA | S22030500000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-05 15:16 | 2022-03-05 15:18 | 3718 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF LLEVA PARTE DEL 1206-3 SE VERIFICO CON PERSONAL EN EL AREA | S22030500000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 7436 | keep | 0 | Mar | 2022 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-03-05 15:19 | 2022-03-05 15:54 | 1000 | 000:35 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PATRULLO MAL TIEMPO EN EL AREA SE PROBO QUEDO EN SERVICIO PARTE POR 1620-2 | S22030500114 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 35 | 2022-03-05 | 35000 | keep | 0 | Mar | 2022 | 0.023838 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-05 15:19 | 2022-03-05 15:54 | 3718 | 000:35 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO SE PATRULLO MAL TIEMPO EN EL AREA SE PROBO QUEDO EN SERVICIO LLEVA PARTE DEL 1206-3 | S22030500114 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 35 | 2022-03-05 | 130130 | keep | 0 | Mar | 2022 | 0.088631 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2022-03-05 15:21 | 2022-03-05 15:22 | 3896 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR MAL TIEMPO EN SERVICIO | C22030500133 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-05 | 3896 | keep | 0 | Mar | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-03-05 15:22 | 2022-03-05 17:55 | 70 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22030500089 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 153 | 2022-03-05 | 10710 | keep | 0 | Mar | 2022 | 0.0072945 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-03-05 15:28 | 2022-03-05 15:29 | 1001 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22030500146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 1001 | keep | 0 | Mar | 2022 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
MAYAGÃœEZ | 2022-03-05 15:33 | 2022-03-05 22:45 | 800 | 007:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M22030500084 | Partial_restoration | Wire Down | Include | Include | Equipment | 432 | 2022-03-05 | 345600 | keep | 0 | Mar | 2022 | 0.23539 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-05 15:37 | 2022-03-05 15:38 | 2999 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030500086 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-05 | 2999 | keep | 0 | Mar | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2022-03-05 15:38 | 2022-03-05 17:22 | 1500 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR SE PATRULLO Y SE SECCIONALIZO DEJANDO 50% EN SERVICIO SE ENCONTRO LINEA PRIMARIA ROTA | M22030500095 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 104 | 2022-03-05 | 156000 | keep | 0 | Mar | 2022 | 0.10625 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
CAGUAS | 2022-03-05 15:40 | 2022-03-05 19:50 | 200 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C22030500140 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2022-03-05 | 50000 | keep | 0 | Mar | 2022 | 0.034055 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-05 15:44 | 2022-03-05 18:28 | 69 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L SE REPARO CONDUCTOR Y SE SUBIO LINEA | B22030500059 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2022-03-05 | 11316 | keep | 0 | Mar | 2022 | 0.0077073 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
SAN JUAN | 2022-03-05 15:54 | 2022-03-05 17:37 | 154 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | S22030500126 | Partial_restoration | Bad Weather | Include | Include | Weather | 103 | 2022-03-05 | 15862 | keep | 0 | Mar | 2022 | 0.010804 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-05 15:58 | 2022-03-06 09:31 | 10 | 017:33 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE PRIMARIO | P22030500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1053 | 2022-03-05 | 10530 | keep | 0 | Mar | 2022 | 0.0071719 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-05 15:59 | 2022-03-05 19:33 | 115 | 003:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030500094 | New_Event | Bad Weather | Include | Include | Weather | 214 | 2022-03-05 | 24610 | keep | 0 | Mar | 2022 | 0.016762 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CANOVANAS | 2022-03-05 16:07 | 2022-03-05 18:01 | 6 | 001:54 | P | OTRAS CAUSAS | 1 X 20 Y 2 X 10 EN TRANSFORMADORES PROBLEMA DEL CLIENTE | R22030500082 | New_Event | Other Causes | Include | Include | Other | 114 | 2022-03-05 | 684 | keep | 0 | Mar | 2022 | 0.00046587 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-05 16:07 | 2022-03-05 16:46 | 12 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA PARA REPARAR LINEA SECUNDARIA | C22030500104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-03-05 | 468 | keep | 0 | Mar | 2022 | 0.00031875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-03-05 16:23 | 2022-03-05 18:14 | 90 | 001:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | C22030500156 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2022-03-05 | 9990 | keep | 0 | Mar | 2022 | 0.0068041 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-03-05 16:40 | 2022-03-05 18:48 | 14 | 002:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030500133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-05 | 1792 | keep | 0 | Mar | 2022 | 0.0012205 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-03-05 17:10 | 2022-03-05 18:50 | 20 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA | B22030500071 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2022-03-05 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-03-05 17:12 | 2022-03-05 21:07 | 80 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500074 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2022-03-05 | 18800 | keep | 0 | Mar | 2022 | 0.012805 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-05 17:16 | 2022-03-06 08:57 | 15 | 015:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500075 | New_Event | Bad Weather | Include | Include | Weather | 941 | 2022-03-05 | 14115 | keep | 0 | Mar | 2022 | 0.0096137 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-05 17:22 | 2022-03-05 18:18 | 25 | 000:56 | P | DESGANCHE | 2 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030500166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-03-05 | 1400 | keep | 0 | Mar | 2022 | 0.00095353 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-05 17:28 | 2022-03-05 17:31 | 721 | 000:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO N/O DEL SU-5A5A AL SU-5A5A1 SE DEJO SU-13 SECCIONALIZADO | C22030400076 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 3 | 2022-03-05 | 2163 | keep | 0 | Mar | 2022 | 0.0014732 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-03-05 17:29 | 2022-03-05 17:31 | 2524 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22030500084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-05 | 5048 | keep | 0 | Mar | 2022 | 0.0034382 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
AGUADILLA | 2022-03-05 17:29 | 2022-03-05 17:30 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 1261 | keep | 0 | Mar | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
HUMACAO | 2022-03-05 17:31 | 2022-03-05 17:33 | 654 | 000:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO N/O DEL PB-F AL SU-MV2 SE DEJO SU-13 SECCIONALIZADO | C22030400076 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2022-03-05 | 1308 | keep | 0 | Mar | 2022 | 0.00089087 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
HUMACAO | 2022-03-05 17:33 | 2022-03-05 17:44 | 550 | 000:11 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO N/O DEL SU-4B AL SU-4B6 SE DEJO SU-13 SECCIONALIZADO | C22030400076 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 11 | 2022-03-05 | 6050 | keep | 0 | Mar | 2022 | 0.0041206 | 0.0003746 | Sustained | FALSE | FALSE | Not_TMED_Event | 550
PONCE | 2022-03-05 17:34 | 2022-03-05 17:35 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22030500067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 1606 | keep | 0 | Mar | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
SAN JUAN | 2022-03-05 17:37 | 2022-03-05 17:39 | 1000 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO PARTE POR 1620-2 | S22030500141 | Partial_restoration | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-05 17:37 | 2022-03-05 17:39 | 3718 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA PARTE DEL 1206-3 MAL TIEMPO | S22030500141 | Additional_clients | Bad Weather | Include | Include | Weather | 2 | 2022-03-05 | 7436 | keep | 0 | Mar | 2022 | 0.0050646 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-05 17:38 | 2022-03-06 12:18 | 15 | 018:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030500180 | New_Event | Bad Weather | Include | Include | Weather | 1120 | 2022-03-05 | 16800 | keep | 0 | Mar | 2022 | 0.011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-05 17:39 | 2022-03-05 18:59 | 154 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | S22030500126 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 80 | 2022-03-05 | 12320 | keep | 0 | Mar | 2022 | 0.0083911 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-03-05 17:43 | 2022-03-05 19:48 | 50 | 002:05 | P | DESGANCHE | 1 X 50 RN RISER RAMA CRUZANDO BAJANTE A CAJA | S22030500143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-03-05 | 6250 | keep | 0 | Mar | 2022 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-05 17:43 | 2022-03-05 23:57 | 46 | 006:14 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN C/L AVERIA SOTERRADA DE T-48 @ T-47 | R22030500087 | New_Event | UG Cable Fault | Include | Include | Equipment | 374 | 2022-03-05 | 17204 | keep | 0 | Mar | 2022 | 0.011718 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
CANOVANAS | 2022-03-05 17:43 | 2022-03-06 19:19 | 15 | 025:36 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DEL T-48 AL T-47 | R22030500087 | New_Event | UG Cable Fault | Include | Include | Equipment | 1536 | 2022-03-05 | 23040 | keep | 0 | Mar | 2022 | 0.015692 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-05 17:48 | 2022-03-05 19:34 | 100 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22030500079 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2022-03-05 | 10600 | keep | 0 | Mar | 2022 | 0.0072196 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-03-05 18:00 | 2022-03-05 18:34 | 100 | 000:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22030500088 | New_Event | Cutout Failure | Include | Include | Equipment | 34 | 2022-03-05 | 3400 | keep | 0 | Mar | 2022 | 0.0023157 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-03-05 18:13 | 2022-03-06 19:08 | 25 | 024:55 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22030500088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1495 | 2022-03-05 | 37375 | keep | 0 | Mar | 2022 | 0.025456 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-03-05 18:18 | 2022-03-05 21:26 | 2999 | 003:08 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22030500095 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-03-05 | 563812 | keep | 0 | Mar | 2022 | 0.38401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-05 18:21 | 2022-03-06 09:20 | 100 | 014:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22030500211 | New_Event | Cutout Failure | Include | Include | Equipment | 899 | 2022-03-05 | 89900 | keep | 0 | Mar | 2022 | 0.06123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-05 18:28 | 2022-03-05 18:29 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 8007-04 | A22030500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-05 18:28 | 2022-03-05 18:29 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22030500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-03-05 18:33 | 2022-03-05 20:44 | 2201 | 002:11 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR SE CERRO INTERRUPTOR | A22030500092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2022-03-05 | 288331 | keep | 0 | Mar | 2022 | 0.19638 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-03-05 18:55 | 2022-03-05 19:33 | 3 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22030500104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-03-05 | 114 | keep | 0 | Mar | 2022 | 7.7645e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-05 19:03 | 2022-03-05 19:05 | 1860 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22030500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-03-05 | 3720 | keep | 0 | Mar | 2022 | 0.0025337 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-03-05 19:05 | 2022-03-05 22:02 | 100 | 002:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y SE REEMPLAZO CAJA PRIMARIA | S22030500161 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 177 | 2022-03-05 | 17700 | keep | 0 | Mar | 2022 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-05 19:13 | 2022-03-05 19:15 | 3597 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR POR EMERGENCIA CAJA EN FUEGO A PETICION DE ELVIN MORALES | B22030500000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2022-03-05 | 7194 | keep | 0 | Mar | 2022 | 0.0048998 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-05 19:13 | 2022-03-05 21:04 | 6 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030500241 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2022-03-05 | 666 | keep | 0 | Mar | 2022 | 0.00045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-05 19:15 | 2022-03-05 20:05 | 299 | 000:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA Y PARARRAYO | B22030500029 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 50 | 2022-03-05 | 14950 | keep | 0 | Mar | 2022 | 0.010182 | 0.00020365 | Sustained | FALSE | FALSE | Not_TMED_Event | 299
BARRANQUITAS | 2022-03-05 19:34 | 2022-03-05 19:35 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE CAYEY A SANTA ISABEL | C22030500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-05 | 2725 | keep | 0 | Mar | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-05 19:34 | 2022-03-05 19:35 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE CAYEY A SANTA ISABEL | C22030500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-05 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-05 19:34 | 2022-03-05 19:35 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE CAYEY A SANTA ISABEL | C22030500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-05 | 1437 | keep | 0 | Mar | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-03-05 19:34 | 2022-03-05 19:35 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE CAYEY A SANTA ISABEL | C22030500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-05 | 2565 | keep | 0 | Mar | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-03-05 19:34 | 2022-03-05 19:35 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE CAYEY A SANTA ISABEL | C22030500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-05 | 3565 | keep | 0 | Mar | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BAYAMON | 2022-03-05 19:38 | 2022-03-06 01:00 | 100 | 005:22 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTES DE LINEA | B22030500086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2022-03-05 | 32200 | keep | 0 | Mar | 2022 | 0.021931 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-05 19:51 | 2022-03-05 22:30 | 200 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 100 EN CORTES DE LINEA | S22030500164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-03-05 | 31800 | keep | 0 | Mar | 2022 | 0.021659 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-03-05 20:32 | 2022-03-05 21:14 | 4 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22030500056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-03-05 | 168 | keep | 0 | Mar | 2022 | 0.00011442 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-03-05 20:38 | 2022-03-06 11:04 | 40 | 014:26 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN C/L REEMPLAZO PISTOLA Y REPARO EL ALAMBRE | R22030500070 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 866 | 2022-03-05 | 34640 | keep | 0 | Mar | 2022 | 0.023593 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-05 20:44 | 2022-03-05 20:54 | 59 | 000:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | AISLADOR PARTIDO | A22030500135 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 10 | 2022-03-05 | 590 | keep | 0 | Mar | 2022 | 0.00040185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-05 20:54 | 2022-03-05 20:56 | 2201 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | PERSONAL LOCALIZANDO AVERIA DISPARO INTERRUPTOR SE CERRO INTERRUPTOR | A22030500131 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-03-05 | 4402 | keep | 0 | Mar | 2022 | 0.0029982 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-05 20:56 | 2022-03-05 22:15 | 59 | 001:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE CERRO CORTE DE LINEA | A22030500135 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 79 | 2022-03-05 | 4661 | keep | 0 | Mar | 2022 | 0.0031746 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
ARECIBO | 2022-03-05 21:00 | 2022-03-06 01:00 | 6 | 004:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMDAOR PARA SECCIONALIZAR POSTE PARTIDO | A22030500137 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 240 | 2022-03-05 | 1440 | keep | 0 | Mar | 2022 | 0.00098078 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-03-05 21:02 | 2022-03-05 23:10 | 149 | 002:08 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22030500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-05 | 19072 | keep | 0 | Mar | 2022 | 0.01299 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
BAYAMON | 2022-03-05 21:33 | 2022-03-05 23:58 | 100 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22030500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-03-05 | 14500 | keep | 0 | Mar | 2022 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-05 21:35 | 2022-03-07 14:00 | 12 | 040:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA Y PIN | C22030500214 | New_Event | Cutout Failure | Include | Include | Equipment | 2425 | 2022-03-05 | 29100 | keep | 0 | Mar | 2022 | 0.01982 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-05 21:35 | 2022-03-06 08:48 | 23 | 011:13 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO BAMBUAS | C22030500215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2022-03-05 | 15479 | keep | 0 | Mar | 2022 | 0.010543 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2022-03-05 21:59 | 2022-03-06 18:36 | 15 | 020:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030500291 | New_Event | Bad Weather | Include | Include | Weather | 1237 | 2022-03-05 | 18555 | keep | 0 | Mar | 2022 | 0.012638 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-05 22:03 | 2022-03-06 11:15 | 56 | 013:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO ABRIENDO EN CONVERTIDOR Y SE CERRO N/O CONTRA 3405-03 | C22030500216 | New_Event | Wire Down | Include | Include | Equipment | 792 | 2022-03-05 | 44352 | keep | 0 | Mar | 2022 | 0.030208 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
ARECIBO | 2022-03-05 22:05 | 2022-03-06 07:48 | 7 | 009:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22030500141 | New_Event | Cutout Failure | Include | Include | Equipment | 583 | 2022-03-05 | 4081 | keep | 0 | Mar | 2022 | 0.0027796 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-03-05 22:26 | 2022-03-06 13:31 | 30 | 015:05 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO Y RETEZO LINEA | C22030500221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 905 | 2022-03-05 | 27150 | keep | 0 | Mar | 2022 | 0.018492 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-03-05 22:34 | 2022-03-06 10:11 | 1 | 011:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN BANCO DE XMR POR IGUANA | C22030500222 | New_Event |  |  | Include | Wildlife | 697 | 2022-03-05 | 697 | keep | 0 | Mar | 2022 | 0.00047472 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-05 22:44 | 2022-03-05 22:45 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-05 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2022-03-05 23:32 | 2022-03-06 15:55 | 40 | 016:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030500145 | New_Event | Bad Weather | Include | Include | Weather | 983 | 2022-03-05 | 39320 | keep | 0 | Mar | 2022 | 0.026781 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-03-05 23:59 | 2022-03-06 11:46 | 40 | 011:47 | P | DESGANCHE | 1 X 50 EN C/L | R22030500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 707 | 2022-03-05 | 28280 | keep | 0 | Mar | 2022 | 0.019261 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-06 00:33 | 2022-03-06 00:34 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 308 | keep | 0 | Mar | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-03-06 01:22 | 2022-03-06 10:39 | 2 | 009:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REEMPLAZO CAJA AVERIADA | B22030600002 | New_Event | Cutout Failure | Include | Include | Equipment | 557 | 2022-03-06 | 1114 | keep | 0 | Mar | 2022 | 0.00075874 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-03-06 01:28 | 2022-03-06 07:48 | 75 | 006:20 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2022-03-06 | 28500 | keep | 0 | Mar | 2022 | 0.019411 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-03-06 01:44 | 2022-03-06 17:22 | 3 | 015:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C22030600015 | New_Event | Bad Weather | Include | Include | Weather | 938 | 2022-03-06 | 2814 | keep | 0 | Mar | 2022 | 0.0019166 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-06 03:18 | 2022-03-06 12:09 | 100 | 008:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600008 | New_Event | Bad Weather | Include | Include | Weather | 531 | 2022-03-06 | 53100 | keep | 0 | Mar | 2022 | 0.036166 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-06 04:18 | 2022-03-07 10:42 | 25 | 030:24 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22030600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1824 | 2022-03-06 | 45600 | keep | 0 | Mar | 2022 | 0.031058 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-03-06 04:31 | 2022-03-06 09:44 | 350 | 005:13 | P | DESCONECTIVO DEFECTUOSO | AUXILIAR DE LINEA DE LA FASE A AVERIADO SE TRANSFIERE LA CARGA AL 4201-04 | P22030600002 | New_Event | Switch Failure | Include | Include | Equipment | 313 | 2022-03-06 | 109550 | keep | 0 | Mar | 2022 | 0.074614 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2022-03-06 05:17 | 2022-03-06 05:18 | 1 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 99% DE LA CARGA POR EL 1657-04 UNICA CARGA BOMBAS DE AAA | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-06 05:45 | 2022-03-06 10:11 | 1 | 004:26 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | B22030600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2022-03-06 | 266 | keep | 0 | Mar | 2022 | 0.00018117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-06 06:00 | 2022-03-06 06:01 | 2245 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1658-14 CERRADO POR CONTROL | R22030600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2245 | keep | 0 | Mar | 2022 | 0.0015291 | 0.0015291 | Momentary | FALSE | FALSE | Not_TMED_Event | 2245
SAN JUAN | 2022-03-06 06:00 | 2022-03-06 06:01 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1658-13 | R22030600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-06 06:33 | 2022-03-06 10:40 | 200 | 004:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22030600010 | New_Event | Cutout Failure | Include | Include | Equipment | 247 | 2022-03-06 | 49400 | keep | 0 | Mar | 2022 | 0.033646 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-03-06 06:34 | 2022-03-06 06:35 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1619-02 | R22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-03-06 06:34 | 2022-03-06 13:22 | 141 | 006:48 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22030600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2022-03-06 | 57528 | keep | 0 | Mar | 2022 | 0.039182 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
BAYAMON | 2022-03-06 06:52 | 2022-03-06 09:15 | 40 | 002:23 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B22030600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-03-06 | 5720 | keep | 0 | Mar | 2022 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-06 06:56 | 2022-03-06 06:57 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2113 | keep | 0 | Mar | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2022-03-06 07:17 | 2022-03-06 10:18 | 100 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600018 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2022-03-06 | 18100 | keep | 0 | Mar | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-06 07:26 | 2022-03-06 11:58 | 400 | 004:32 | P | HERRAJE ROTO O PODRIDO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | A22030600019 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 272 | 2022-03-06 | 108800 | keep | 0 | Mar | 2022 | 0.074103 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2022-03-06 07:29 | 2022-03-06 10:33 | 120 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600022 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2022-03-06 | 22080 | keep | 0 | Mar | 2022 | 0.015039 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2022-03-06 07:34 | 2022-03-06 17:15 | 75 | 009:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600022 | New_Event | Bad Weather | Include | Include | Weather | 581 | 2022-03-06 | 43575 | keep | 0 | Mar | 2022 | 0.029679 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-03-06 07:35 | 2022-03-06 07:36 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1709-02 LLEVANDO LA CARGA DEL 1720-08 Y SE CERRO POR SCADA | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2402 | keep | 0 | Mar | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-03-06 07:35 | 2022-03-06 07:36 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1709-02 LLEVANDO LA CARGA DEL 1720-08 Y SE CERRO POR SCADA | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-06 07:36 | 2022-03-06 19:17 | 80 | 011:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22030600025 | New_Event | Bad Weather | Include | Include | Weather | 701 | 2022-03-06 | 56080 | keep | 0 | Mar | 2022 | 0.038196 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-06 07:39 | 2022-03-06 07:40 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22030600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2201 | keep | 0 | Mar | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
MAYAGÃœEZ | 2022-03-06 07:42 | 2022-03-06 10:44 | 40 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600026 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2022-03-06 | 7280 | keep | 0 | Mar | 2022 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-06 07:44 | 2022-03-07 06:05 | 150 | 022:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22030600164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1341 | 2022-03-06 | 201150 | keep | 0 | Mar | 2022 | 0.137 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-06 07:45 | 2022-03-06 12:30 | 40 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | R22030600007 | New_Event |  |  | Include | Wildlife | 285 | 2022-03-06 | 11400 | keep | 0 | Mar | 2022 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-06 07:48 | 2022-03-06 07:49 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-06 07:48 | 2022-03-06 07:49 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22030600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
AGUADILLA | 2022-03-06 07:51 | 2022-03-06 07:52 | 1192 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M22030600028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-06 | 1192 | keep | 0 | Mar | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-03-06 07:52 | 2022-03-06 12:34 | 300 | 004:42 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030600021 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-03-06 | 84600 | keep | 0 | Mar | 2022 | 0.057621 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-03-06 07:52 | 2022-03-06 07:53 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600031 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-06 07:52 | 2022-03-06 07:53 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22030600031 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-03-06 08:02 | 2022-03-06 08:03 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600041 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-06 08:02 | 2022-03-06 08:03 | 438 | 000:01 | T | NO SE REPORTO CAUSA | LLEVA LA CARGA DEL 8007-03 | A22030600041 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-03-06 08:04 | 2022-03-06 08:05 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-06 08:04 | 2022-03-06 08:05 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22030600049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-03-06 08:07 | 2022-03-06 08:08 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600053 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-06 08:07 | 2022-03-06 08:08 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22030600053 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-03-06 08:08 | 2022-03-06 09:25 | 2228 | 001:17 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600055 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-03-06 | 171556 | keep | 0 | Mar | 2022 | 0.11685 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-06 08:08 | 2022-03-06 09:25 | 438 | 001:17 | T | NO SE REPORTO CAUSA | SE ABRIO EL INTERRUPTOR YA QUE RECERRABA CONTINUAMENTE SE PATRULLO POR MANUEL BONET Y NO SE IDENTIFICO CAUSA SE CERRO POR SCADA LLEVA LA CARGA DEL 8007-03 | A22030600055 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-03-06 | 33726 | keep | 0 | Mar | 2022 | 0.022971 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
MAYAGÃœEZ | 2022-03-06 08:21 | 2022-03-06 12:12 | 150 | 003:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600046 | New_Event | Bad Weather | Include | Include | Weather | 231 | 2022-03-06 | 34650 | keep | 0 | Mar | 2022 | 0.0236 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-06 08:26 | 2022-03-06 11:01 | 1 | 002:35 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO PERSONAL AJENO A LUMA REALIZANDO EXCAVACION AVERIO CABLE SE PASO CARGA CERRANDO N/O CONTRA 1114-01 TORRE NORTE MINILLAS | S22030600006 | New_Event |  |  | Include | Wildlife | 155 | 2022-03-06 | 155 | keep | 0 | Mar | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-06 08:31 | 2022-03-07 17:42 | 11 | 033:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22030600010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1991 | 2022-03-06 | 21901 | keep | 0 | Mar | 2022 | 0.014917 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-03-06 08:33 | 2022-03-06 08:35 | 723 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 LLEVANDO LA CARGA DEL 1711-05 Y SE CERRO POR SCADA | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-06 | 1446 | keep | 0 | Mar | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-03-06 08:33 | 2022-03-06 08:35 | 1976 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 LLEVANDO LA CARGA DEL 1711-05 Y SE CERRO POR SCADA | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-06 | 3952 | keep | 0 | Mar | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
YAUCO | 2022-03-06 08:35 | 2022-03-06 11:30 | 3973 | 002:55 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE ABREN MACHETES PARA SECCIONALIZAR ALIMENTADOR | P22030600013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 175 | 2022-03-06 | 695275 | keep | 0 | Mar | 2022 | 0.47355 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
ARECIBO | 2022-03-06 08:37 | 2022-03-06 13:50 | 100 | 005:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22030600069 | New_Event |  |  | Include | Wildlife | 313 | 2022-03-06 | 31300 | keep | 0 | Mar | 2022 | 0.021318 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-06 08:40 | 2022-03-06 13:44 | 58 | 005:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22030600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2022-03-06 | 17632 | keep | 0 | Mar | 2022 | 0.012009 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
HUMACAO | 2022-03-06 08:51 | 2022-03-06 11:04 | 16 | 002:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN C/L SE RETIRO CHANGO | C22030600011 | New_Event |  |  | Include | Wildlife | 133 | 2022-03-06 | 2128 | keep | 0 | Mar | 2022 | 0.0014494 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2022-03-06 09:05 | 2022-03-06 11:30 | 10 | 002:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P22030600020 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2022-03-06 | 1450 | keep | 0 | Mar | 2022 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-06 09:09 | 2022-03-06 14:42 | 40 | 005:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR PORTAFUSIBLE QUEMADO | S22030600009 | New_Event | Cutout Failure | Include | Include | Equipment | 333 | 2022-03-06 | 13320 | keep | 0 | Mar | 2022 | 0.0090722 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-03-06 09:31 | 2022-03-06 10:37 | 15 | 001:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22030600088 | New_Event | Wire Down | Include | Include | Equipment | 66 | 2022-03-06 | 990 | keep | 0 | Mar | 2022 | 0.00067428 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-06 09:36 | 2022-03-06 11:25 | 6 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22030600090 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2022-03-06 | 654 | keep | 0 | Mar | 2022 | 0.00044544 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-06 09:42 | 2022-03-06 10:48 | 30 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600095 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2022-03-06 | 1980 | keep | 0 | Mar | 2022 | 0.0013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-03-06 09:43 | 2022-03-06 12:00 | 50 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22030600017 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2022-03-06 | 6850 | keep | 0 | Mar | 2022 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-06 09:47 | 2022-03-06 12:41 | 36 | 002:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZARON AISLADORES | C22030600019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2022-03-06 | 6264 | keep | 0 | Mar | 2022 | 0.0042664 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-03-06 09:50 | 2022-03-06 09:51 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22030600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 3046 | keep | 0 | Mar | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
ARECIBO | 2022-03-06 09:56 | 2022-03-06 09:57 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | SU CARGA POR EL 8007-04 | A22030600116 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-06 09:56 | 2022-03-06 09:57 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 8007-03 | A22030600041 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-06 09:58 | 2022-03-06 09:59 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO 95% DE LA CARGA DEL 1717-02 | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 5961 | keep | 0 | Mar | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-03-06 09:58 | 2022-03-06 09:59 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO 95% DE LA CARGA DEL 1717-02 | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 865 | keep | 0 | Mar | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
SAN JUAN | 2022-03-06 09:59 | 2022-03-06 10:01 | 553 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1529-15 | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-06 | 1106 | keep | 0 | Mar | 2022 | 0.00075329 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-03-06 09:59 | 2022-03-06 10:01 | 1802 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 30% DEL 1346-2 | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-06 | 3604 | keep | 0 | Mar | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-03-06 10:04 | 2022-03-06 10:07 | 1310 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-06 | 3930 | keep | 0 | Mar | 2022 | 0.0026767 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2022-03-06 10:05 | 2022-03-06 18:02 | 10 | 007:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600120 | New_Event | Bad Weather | Include | Include | Weather | 477 | 2022-03-06 | 4770 | keep | 0 | Mar | 2022 | 0.0032488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-06 10:15 | 2022-03-06 11:45 | 99 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE DESPEJO FASE | S22030600030 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2022-03-06 | 8910 | keep | 0 | Mar | 2022 | 0.0060686 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2022-03-06 10:18 | 2022-03-06 11:01 | 478 | 000:43 | T | DESGANCHE | DISPARO 1705-01 LLEVANDO 90% DEL 1705-03. SE ENVIO A PATRULLAR E INFORMO ELVIN MORALES QUE DESGANCHO PENCA ENCIMA DE ALIMENTADOR. SE CERRO POR SCADA. BY-220306-01 | B22030600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-03-06 | 20554 | keep | 0 | Mar | 2022 | 0.013999 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-03-06 10:18 | 2022-03-06 11:01 | 854 | 000:43 | P | DESGANCHE | DISPARO 1705-01 LLEVANDO 90% DEL 1705-03. SE ENVIO A PATRULLAR E INFORMO ELVIN MORALES QUE DESGANCHO PENCA ENCIMA DE ALIMENTADOR. SE CERRO POR SCADA. BY-220306-01 | B22030600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-03-06 | 36722 | keep | 0 | Mar | 2022 | 0.025011 | 0.00058166 | Sustained | FALSE | FALSE | Not_TMED_Event | 854
MAYAGÃœEZ | 2022-03-06 10:20 | 2022-03-06 12:57 | 21 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600111 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2022-03-06 | 3297 | keep | 0 | Mar | 2022 | 0.0022456 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-03-06 10:22 | 2022-03-06 15:38 | 10 | 005:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | S22030600034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 316 | 2022-03-06 | 3160 | keep | 0 | Mar | 2022 | 0.0021523 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-06 10:22 | 2022-03-06 15:03 | 100 | 004:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C22030600024 | New_Event | Bad Weather | Include | Include | Weather | 281 | 2022-03-06 | 28100 | keep | 0 | Mar | 2022 | 0.019139 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-06 10:25 | 2022-03-06 12:25 | 239 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22030600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-03-06 | 28680 | keep | 0 | Mar | 2022 | 0.019534 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
BAYAMON | 2022-03-06 10:28 | 2022-03-06 10:29 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2147 | keep | 0 | Mar | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
ARECIBO | 2022-03-06 10:30 | 2022-03-06 12:21 | 50 | 001:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22030600130 | New_Event | Wire Down | Include | Include | Equipment | 111 | 2022-03-06 | 5550 | keep | 0 | Mar | 2022 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-06 10:47 | 2022-03-06 11:01 | 3708 | 000:14 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR POR CONTROL PARA CERRAR N/O CONTRA 1114-3 OPERADOR NO FUNCIONA | S22030600048 | New_Event |  |  | Include | Wildlife | 14 | 2022-03-06 | 51912 | keep | 0 | Mar | 2022 | 0.035357 | 0.0025255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3708
PONCE | 2022-03-06 10:47 | 2022-03-06 13:15 | 70 | 002:28 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22030600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-03-06 | 10360 | keep | 0 | Mar | 2022 | 0.0070561 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-03-06 10:49 | 2022-03-06 20:56 | 200 | 010:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600135 | New_Event | Bad Weather | Include | Include | Weather | 607 | 2022-03-06 | 121400 | keep | 0 | Mar | 2022 | 0.082685 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-03-06 10:50 | 2022-03-06 14:53 | 80 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030600123 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2022-03-06 | 19440 | keep | 0 | Mar | 2022 | 0.01324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-06 10:56 | 2022-03-07 12:42 | 30 | 025:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C22030600170 | New_Event | Bad Weather | Include | Include | Weather | 1546 | 2022-03-06 | 46380 | keep | 0 | Mar | 2022 | 0.031589 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-03-06 11:00 | 2022-03-06 12:00 | 14 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR BARRAS EN PEDESTAL | P22030500082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-06 | 840 | keep | 0 | Mar | 2022 | 0.00057212 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2022-03-06 11:05 | 2022-03-06 14:35 | 40 | 003:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEAS PRIMARIAS ARRIADAS | P22030600051 | New_Event | Wire Down | Include | Include | Equipment | 210 | 2022-03-06 | 8400 | keep | 0 | Mar | 2022 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-06 11:14 | 2022-03-07 10:39 | 2 | 023:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22030600139 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1405 | 2022-03-06 | 2810 | keep | 0 | Mar | 2022 | 0.0019139 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2022-03-06 11:30 | 2022-03-06 12:28 | 1984 | 000:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRARON MACHETES QUE FUERON ABIERTOS PARA SECCIONALIZAR ALIMENTADOR | P22030600025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 58 | 2022-03-06 | 115072 | keep | 0 | Mar | 2022 | 0.078375 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
VEGA BAJA | 2022-03-06 11:31 | 2022-03-06 11:41 | 20 | 000:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA FUERTE | B22030600060 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2022-03-06 | 200 | keep | 0 | Mar | 2022 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-06 11:33 | 2022-03-06 12:21 | 150 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22030600062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-03-06 | 7200 | keep | 0 | Mar | 2022 | 0.0049039 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-06 11:41 | 2022-03-06 11:42 | 844 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 844 | keep | 0 | Mar | 2022 | 0.00057484 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
VEGA BAJA | 2022-03-06 11:41 | 2022-03-06 11:42 | 2216 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO | B22030600000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2022-03-06 | 2216 | keep | 0 | Mar | 2022 | 0.0015093 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-06 11:42 | 2022-03-06 21:09 | 20 | 009:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA FUERTE | B22030600060 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 567 | 2022-03-06 | 11340 | keep | 0 | Mar | 2022 | 0.0077236 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-03-06 11:43 | 2022-03-06 14:53 | 654 | 003:10 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-03-06 | 124260 | keep | 0 | Mar | 2022 | 0.084633 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
CAGUAS | 2022-03-06 11:47 | 2022-03-07 09:31 | 200 | 021:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22030600041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1304 | 2022-03-06 | 260800 | keep | 0 | Mar | 2022 | 0.17763 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-06 11:47 | 2022-03-06 15:52 | 300 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA LLUVIAS | C22030600042 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2022-03-06 | 73500 | keep | 0 | Mar | 2022 | 0.050061 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-03-06 11:51 | 2022-03-07 10:00 | 200 | 022:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUIVAS | C22030600044 | New_Event | Bad Weather | Include | Include | Weather | 1329 | 2022-03-06 | 265800 | keep | 0 | Mar | 2022 | 0.18104 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-03-06 11:53 | 2022-03-06 14:14 | 178 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030600140 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2022-03-06 | 25098 | keep | 0 | Mar | 2022 | 0.017094 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
CANOVANAS | 2022-03-06 12:01 | 2022-03-06 13:02 | 50 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | R22030600022 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2022-03-06 | 3050 | keep | 0 | Mar | 2022 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-03-06 12:02 | 2022-03-06 13:23 | 109 | 001:21 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P22030600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-03-06 | 8829 | keep | 0 | Mar | 2022 | 0.0060134 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
SAN JUAN | 2022-03-06 12:05 | 2022-03-06 14:49 | 100 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L CERRO PUENTE DE CAJA A LINEA | S22030600060 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2022-03-06 | 16400 | keep | 0 | Mar | 2022 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-06 12:23 | 2022-03-06 16:28 | 478 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600156 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2022-03-06 | 117110 | keep | 0 | Mar | 2022 | 0.079763 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
SAN JUAN | 2022-03-06 12:25 | 2022-03-06 14:35 | 1 | 002:10 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN BANCO DE TRANSFORMADORES SE RETIRO ENREDADERA | R22030600023 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 130 | 2022-03-06 | 130 | keep | 0 | Mar | 2022 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-06 12:28 | 2022-03-06 14:05 | 1479 | 001:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO RISER QUE FUERON ABIERTOS PARA SECCIONALIZAR ALIMENTADOR | P22030600067 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 97 | 2022-03-06 | 143463 | keep | 0 | Mar | 2022 | 0.097712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-06 12:37 | 2022-03-07 20:24 | 400 | 031:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A22030600155 | New_Event | Wire Down | Include | Include | Equipment | 1907 | 2022-03-06 | 762800 | keep | 0 | Mar | 2022 | 0.51954 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-03-06 12:38 | 2022-03-06 12:39 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22030600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-06 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-06 12:38 | 2022-03-06 12:39 | 2266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22030600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-06 | 2266 | keep | 0 | Mar | 2022 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2022-03-06 12:38 | 2022-03-06 12:39 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22030600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-06 | 1399 | keep | 0 | Mar | 2022 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
PONCE | 2022-03-06 12:40 | 2022-03-06 17:25 | 45 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22030600073 | New_Event |  |  | Include | Wildlife | 285 | 2022-03-06 | 12825 | keep | 0 | Mar | 2022 | 0.008735 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-03-06 12:40 | 2022-03-06 15:54 | 70 | 003:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600166 | New_Event | Bad Weather | Include | Include | Weather | 194 | 2022-03-06 | 13580 | keep | 0 | Mar | 2022 | 0.0092493 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-03-06 12:42 | 2022-03-08 14:31 | 10 | 049:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR T-11 AVERIADO MEDIANTE G.O.I. BY-220308-01 | B22030600074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2989 | 2022-03-06 | 29890 | keep | 0 | Mar | 2022 | 0.020358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-06 12:46 | 2022-03-06 14:36 | 150 | 001:50 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22030600159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-03-06 | 16500 | keep | 0 | Mar | 2022 | 0.011238 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-03-06 12:48 | 2022-03-06 17:30 | 100 | 004:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-03-06 | 28200 | keep | 0 | Mar | 2022 | 0.019207 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-03-06 12:55 | 2022-03-06 15:00 | 106 | 002:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22030600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-03-06 | 13250 | keep | 0 | Mar | 2022 | 0.0090245 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
ARECIBO | 2022-03-06 12:57 | 2022-03-06 18:50 | 40 | 005:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-03-06 | 14120 | keep | 0 | Mar | 2022 | 0.0096171 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-06 12:59 | 2022-03-06 13:00 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030600076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 969 | keep | 0 | Mar | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
PONCE | 2022-03-06 13:03 | 2022-03-06 18:30 | 100 | 005:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22030600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-03-06 | 32700 | keep | 0 | Mar | 2022 | 0.022272 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-06 13:04 | 2022-03-06 14:55 | 50 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600174 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2022-03-06 | 5550 | keep | 0 | Mar | 2022 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-06 13:09 | 2022-03-07 12:59 | 48 | 023:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030600175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1430 | 2022-03-06 | 68640 | keep | 0 | Mar | 2022 | 0.04675 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
AGUADILLA | 2022-03-06 13:09 | 2022-03-06 16:33 | 6 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22030600176 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2022-03-06 | 1224 | keep | 0 | Mar | 2022 | 0.00083366 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-06 13:10 | 2022-03-06 17:27 | 150 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600177 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2022-03-06 | 38550 | keep | 0 | Mar | 2022 | 0.026256 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-03-06 13:11 | 2022-03-06 13:12 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 3025 | keep | 0 | Mar | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
AGUADILLA | 2022-03-06 13:11 | 2022-03-07 00:35 | 40 | 011:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030600177 | New_Event | Bad Weather | Include | Include | Weather | 684 | 2022-03-06 | 27360 | keep | 0 | Mar | 2022 | 0.018635 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-06 13:11 | 2022-03-07 00:26 | 100 | 011:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030600178 | New_Event | Bad Weather | Include | Include | Weather | 675 | 2022-03-06 | 67500 | keep | 0 | Mar | 2022 | 0.045974 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-06 13:14 | 2022-03-06 13:15 | 1648 | 000:01 | T | DESGANCHE | RECIERRE LLEVA EL 70% DE LA CARGA DEL 2402-02 | R22030600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-06 | 1648 | keep | 0 | Mar | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-03-06 13:14 | 2022-03-06 13:15 | 2391 | 000:01 | P | DESGANCHE | RECERRO INTERRUPTOR 70% DE LA CARGA POR EL 2302-03 | R22030600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-06 | 2391 | keep | 0 | Mar | 2022 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CANOVANAS | 2022-03-06 13:15 | 2022-03-06 17:00 | 36 | 003:45 | P | DESGANCHE | 1 X 30 Y 1 X 65 EN CORTES DE LINEA SE REALIZO DESGANCHE | R22030600034 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-03-06 | 8100 | keep | 0 | Mar | 2022 | 0.0055169 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
AGUADILLA | 2022-03-06 13:16 | 2022-03-06 13:17 | 1827 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22030600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-06 | 1827 | keep | 0 | Mar | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2022-03-06 13:16 | 2022-03-06 21:46 | 45 | 008:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600181 | New_Event | Bad Weather | Include | Include | Weather | 510 | 2022-03-06 | 22950 | keep | 0 | Mar | 2022 | 0.015631 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-03-06 13:17 | 2022-03-06 22:45 | 50 | 009:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22030600194 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 568 | 2022-03-06 | 28400 | keep | 0 | Mar | 2022 | 0.019343 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-06 13:21 | 2022-03-06 17:08 | 83 | 003:47 | P | DESGANCHE | 1 X 30 Y 1 X 65 EN CORTES DE LINEA SE REALIZO DESGANCHE | R22030600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-03-06 | 18841 | keep | 0 | Mar | 2022 | 0.012833 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
AGUADILLA | 2022-03-06 13:22 | 2022-03-06 15:02 | 356 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030600183 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-03-06 | 35600 | keep | 0 | Mar | 2022 | 0.024247 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
CAGUAS | 2022-03-06 13:27 | 2022-03-06 13:28 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1307 | keep | 0 | Mar | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-03-06 13:27 | 2022-03-06 13:28 | 2281 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2281 | keep | 0 | Mar | 2022 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
UTUADO | 2022-03-06 13:27 | 2022-03-06 18:55 | 40 | 005:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600185 | New_Event | Bad Weather | Include | Include | Weather | 328 | 2022-03-06 | 13120 | keep | 0 | Mar | 2022 | 0.008936 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-06 13:28 | 2022-03-06 20:16 | 130 | 006:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C22030600057 | New_Event | Bad Weather | Include | Include | Weather | 408 | 2022-03-06 | 53040 | keep | 0 | Mar | 2022 | 0.036125 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2022-03-06 13:30 | 2022-03-06 13:31 | 131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 131 | keep | 0 | Mar | 2022 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
MAYAGÃœEZ | 2022-03-06 13:31 | 2022-03-07 10:42 | 80 | 021:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030600189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1271 | 2022-03-06 | 101680 | keep | 0 | Mar | 2022 | 0.069254 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-06 13:32 | 2022-03-06 13:33 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S22030600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1310 | keep | 0 | Mar | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
AGUADILLA | 2022-03-06 13:32 | 2022-03-06 17:15 | 60 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030600190 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-03-06 | 13380 | keep | 0 | Mar | 2022 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-06 13:35 | 2022-03-06 17:25 | 7 | 003:50 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO Y REPARO BAJANTE SECUNDARIO | S22030600071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 230 | 2022-03-06 | 1610 | keep | 0 | Mar | 2022 | 0.0010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-06 13:36 | 2022-03-06 13:44 | 427 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-03-06 | 3416 | keep | 0 | Mar | 2022 | 0.0023266 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
CANOVANAS | 2022-03-06 13:37 | 2022-03-06 16:30 | 364 | 002:53 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA SE REALIZO DESGANCHE | R22030600050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-03-06 | 62972 | keep | 0 | Mar | 2022 | 0.04289 | 0.00024792 | Sustained | FALSE | FALSE | Not_TMED_Event | 364
ARECIBO | 2022-03-06 13:39 | 2022-03-06 20:04 | 25 | 006:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22030600188 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 385 | 2022-03-06 | 9625 | keep | 0 | Mar | 2022 | 0.0065555 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-06 13:42 | 2022-03-06 15:38 | 100 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C22030600068 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2022-03-06 | 11600 | keep | 0 | Mar | 2022 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-06 13:45 | 2022-03-06 17:27 | 100 | 003:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L REMPLAZO CAJA QUEMADA | S22030600076 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2022-03-06 | 22200 | keep | 0 | Mar | 2022 | 0.01512 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-06 13:48 | 2022-03-06 13:49 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 3597 | keep | 0 | Mar | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-03-06 13:51 | 2022-03-07 10:34 | 30 | 020:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22030600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1243 | 2022-03-06 | 37290 | keep | 0 | Mar | 2022 | 0.025398 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-06 13:52 | 2022-03-06 18:43 | 20 | 004:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22030600192 | New_Event | Bad Weather | Include | Include | Weather | 291 | 2022-03-06 | 5820 | keep | 0 | Mar | 2022 | 0.003964 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-06 13:58 | 2022-03-06 15:52 | 100 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA | S22030600091 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2022-03-06 | 11400 | keep | 0 | Mar | 2022 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-03-06 13:59 | 2022-03-07 14:40 | 12 | 024:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR TIPO PAD MOUNTED DE 50 KVA A 7.62 KV AVERIADO | P22030600095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1481 | 2022-03-06 | 17772 | keep | 0 | Mar | 2022 | 0.012104 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-03-06 13:59 | 2022-03-06 15:26 | 50 | 001:27 | P | TRANSFORMADOR AVERIADO | AVERIA EN T-12 SE ABRIO DE T-12 HACIA T-11 Y DEL T-12 HACIA EL T-13 SE CERRO N/O EN T-15 HACIA T-16 | P22030600113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 87 | 2022-03-06 | 4350 | keep | 0 | Mar | 2022 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-06 14:04 | 2022-03-06 18:46 | 200 | 004:42 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTES DE LINEA | C22030600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-03-06 | 56400 | keep | 0 | Mar | 2022 | 0.038414 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-03-06 14:05 | 2022-03-06 15:22 | 991 | 001:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR AVERIADO Y SE CERRARON MACHETES | P22030600090 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 77 | 2022-03-06 | 76307 | keep | 0 | Mar | 2022 | 0.051972 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-06 14:06 | 2022-03-06 15:52 | 1604 | 001:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C22030600097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-03-06 | 170024 | keep | 0 | Mar | 2022 | 0.1158 | 0.0010925 | Sustained | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-03-06 14:06 | 2022-03-06 15:52 | 1131 | 001:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C22030600097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-03-06 | 119886 | keep | 0 | Mar | 2022 | 0.081654 | 0.00077032 | Sustained | FALSE | FALSE | Not_TMED_Event | 1131
BARRANQUITAS | 2022-03-06 14:06 | 2022-03-06 15:52 | 2362 | 001:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C22030600097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-03-06 | 250372 | keep | 0 | Mar | 2022 | 0.17053 | 0.0016087 | Sustained | FALSE | FALSE | Not_TMED_Event | 2362
ARECIBO | 2022-03-06 14:10 | 2022-03-07 07:42 | 10 | 017:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600199 | New_Event | Bad Weather | Include | Include | Weather | 1052 | 2022-03-06 | 10520 | keep | 0 | Mar | 2022 | 0.0071651 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-06 14:11 | 2022-03-06 16:38 | 300 | 002:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 Y 1 X 65 EN CORTES DE LINEA LLUVIAS | C22030600096 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2022-03-06 | 44100 | keep | 0 | Mar | 2022 | 0.030036 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2022-03-06 14:12 | 2022-03-06 16:31 | 30 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | P22030600098 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2022-03-06 | 4170 | keep | 0 | Mar | 2022 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-03-06 14:16 | 2022-03-07 10:57 | 50 | 020:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22030600160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1241 | 2022-03-06 | 62050 | keep | 0 | Mar | 2022 | 0.042262 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-06 14:21 | 2022-03-07 00:48 | 50 | 010:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22030600094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 627 | 2022-03-06 | 31350 | keep | 0 | Mar | 2022 | 0.021352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-06 14:24 | 2022-03-07 09:48 | 40 | 019:24 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22030600095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1164 | 2022-03-06 | 46560 | keep | 0 | Mar | 2022 | 0.031712 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-06 14:25 | 2022-03-06 18:30 | 76 | 004:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA CONTAMINACION EN CAJA PRIMARIA | R22030600064 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2022-03-06 | 18620 | keep | 0 | Mar | 2022 | 0.012682 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
ARECIBO | 2022-03-06 14:28 | 2022-03-06 17:51 | 40 | 003:23 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-03-06 | 8120 | keep | 0 | Mar | 2022 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-06 14:28 | 2022-03-06 20:49 | 60 | 006:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600215 | New_Event | Bad Weather | Include | Include | Weather | 381 | 2022-03-06 | 22860 | keep | 0 | Mar | 2022 | 0.01557 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-03-06 14:33 | 2022-03-06 19:55 | 33 | 005:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C22030600132 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2022-03-06 | 10626 | keep | 0 | Mar | 2022 | 0.0072373 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
PONCE | 2022-03-06 14:34 | 2022-03-06 15:29 | 1293 | 000:55 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR NO REALIZO CICLO DE RECIERRE NI TAMPOCO OPERO POR SCADA SE CERRO MANUAL ELECTRICAMENTE | P22030600104 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 55 | 2022-03-06 | 71115 | keep | 0 | Mar | 2022 | 0.048436 | 0.00088066 | Sustained | FALSE | FALSE | Not_TMED_Event | 1293
HUMACAO | 2022-03-06 14:42 | 2022-03-07 14:56 | 4 | 024:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22030600139 | New_Event | Bad Weather | Include | Include | Weather | 1454 | 2022-03-06 | 5816 | keep | 0 | Mar | 2022 | 0.0039613 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-03-06 14:45 | 2022-03-06 16:14 | 50 | 001:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-03-06 | 4450 | keep | 0 | Mar | 2022 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-03-06 14:46 | 2022-03-07 12:04 | 50 | 021:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C22030600145 | New_Event | Bad Weather | Include | Include | Weather | 1278 | 2022-03-06 | 63900 | keep | 0 | Mar | 2022 | 0.043522 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-06 14:50 | 2022-03-07 11:10 | 70 | 020:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22030600216 | New_Event | Cutout Failure | Include | Include | Equipment | 1220 | 2022-03-06 | 85400 | keep | 0 | Mar | 2022 | 0.058166 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-03-06 14:51 | 2022-03-06 14:52 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7003-02 | M22030600211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 470 | keep | 0 | Mar | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
AGUADILLA | 2022-03-06 14:51 | 2022-03-06 14:52 | 1345 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 7003-01 | M22030600211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1345 | keep | 0 | Mar | 2022 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2022-03-06 14:52 | 2022-03-07 14:42 | 12 | 023:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO | A22030600217 | New_Event | Wire Down | Include | Include | Equipment | 1430 | 2022-03-06 | 17160 | keep | 0 | Mar | 2022 | 0.011688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-03-06 14:58 | 2022-03-06 19:18 | 35 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | P22030600111 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2022-03-06 | 9100 | keep | 0 | Mar | 2022 | 0.006198 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-03-06 15:00 | 2022-03-06 16:47 | 60 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE DE FASES POR CARPA NO ANCLADA | P22030600112 | New_Event |  |  | Include | Wildlife | 107 | 2022-03-06 | 6420 | keep | 0 | Mar | 2022 | 0.0043726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-06 15:00 | 2022-03-06 22:00 | 40 | 007:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22030600221 | New_Event | Bad Weather | Include | Include | Weather | 420 | 2022-03-06 | 16800 | keep | 0 | Mar | 2022 | 0.011442 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-06 15:04 | 2022-03-06 16:39 | 969 | 001:35 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMA DEL TRONCAL PRIMARIO Y SE COLOCO EN SERVICIO | P22030600117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-03-06 | 92055 | keep | 0 | Mar | 2022 | 0.062698 | 0.00065998 | Sustained | FALSE | FALSE | Not_TMED_Event | 969
HUMACAO | 2022-03-06 15:07 | 2022-03-06 18:52 | 70 | 003:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | CV2203060016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-03-06 | 15750 | keep | 0 | Mar | 2022 | 0.010727 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-03-06 15:11 | 2022-03-06 15:12 | 2041 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR PUENTE ABIERTO EN SERVICIO | R22030600071 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-06 | 2041 | keep | 0 | Mar | 2022 | 0.0013901 | 0.0013901 | Momentary | FALSE | FALSE | Not_TMED_Event | 2041
FAJARDO | 2022-03-06 15:12 | 2022-03-06 18:12 | 48 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A LINEA CON GOI-SJ-220306-51 | R22030600094 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 180 | 2022-03-06 | 8640 | keep | 0 | Mar | 2022 | 0.0058847 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
HUMACAO | 2022-03-06 15:14 | 2022-03-06 18:04 | 90 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C22030600172 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2022-03-06 | 15300 | keep | 0 | Mar | 2022 | 0.010421 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-03-06 15:14 | 2022-03-06 16:41 | 3026 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CONVERTIDOR POR EL 3102-01 APROX 1,608 CLIENTES | C22030600174 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2022-03-06 | 263262 | keep | 0 | Mar | 2022 | 0.17931 | 0.002061 | Sustained | FALSE | FALSE | Not_TMED_Event | 3026
ARECIBO | 2022-03-06 15:14 | 2022-03-06 15:15 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22030600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-06 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-06 15:14 | 2022-03-06 15:15 | 2266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22030600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-06 | 2266 | keep | 0 | Mar | 2022 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2022-03-06 15:14 | 2022-03-06 15:15 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 | A22030600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-06 | 1399 | keep | 0 | Mar | 2022 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
HUMACAO | 2022-03-06 15:16 | 2022-03-06 17:41 | 100 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C22030600178 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2022-03-06 | 14500 | keep | 0 | Mar | 2022 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-06 15:16 | 2022-03-07 16:09 | 10 | 024:53 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL CAIDO SOBRE LAS LINEAS | M22030600214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1493 | 2022-03-06 | 14930 | keep | 0 | Mar | 2022 | 0.010169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-06 15:17 | 2022-03-06 18:07 | 400 | 002:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 5 CAJAS PRIMARIAS QUEMADAS 3 X 100 EN CORTES DE LINEAS | C22030600180 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2022-03-06 | 68000 | keep | 0 | Mar | 2022 | 0.046314 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2022-03-06 15:21 | 2022-03-06 17:19 | 69 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C22030600184 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2022-03-06 | 8142 | keep | 0 | Mar | 2022 | 0.0055455 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
ARECIBO | 2022-03-06 15:23 | 2022-03-06 22:04 | 50 | 006:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22030600233 | New_Event | Bad Weather | Include | Include | Weather | 401 | 2022-03-06 | 20050 | keep | 0 | Mar | 2022 | 0.013656 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-06 15:24 | 2022-03-06 15:25 | 1337 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030600218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1337 | keep | 0 | Mar | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
PONCE | 2022-03-06 15:27 | 2022-03-06 16:41 | 30 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | P22030600124 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2022-03-06 | 2220 | keep | 0 | Mar | 2022 | 0.001512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-03-06 15:27 | 2022-03-06 20:09 | 25 | 004:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600239 | New_Event | Bad Weather | Include | Include | Weather | 282 | 2022-03-06 | 7050 | keep | 0 | Mar | 2022 | 0.0048017 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-06 15:33 | 2022-03-06 15:35 | 1310 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | S22030600108 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-06 | 2620 | keep | 0 | Mar | 2022 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-03-06 15:38 | 2022-03-06 15:39 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO CARGA 1720-08 | B22030600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2402 | keep | 0 | Mar | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-03-06 15:38 | 2022-03-06 15:39 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1709-02 LLEVANDO LA CARGA DEL 1720-08 | S22030600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-06 15:48 | 2022-03-06 15:54 | 2060 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-06 | 12360 | keep | 0 | Mar | 2022 | 0.0084183 | 0.0014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 2060
BAYAMON | 2022-03-06 15:48 | 2022-03-06 15:54 | 2605 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1718-03 LLEVANDO 40% 1710-05 | B22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-06 | 15630 | keep | 0 | Mar | 2022 | 0.010646 | 0.0017743 | Sustained | FALSE | FALSE | Not_TMED_Event | 2605
BARRANQUITAS | 2022-03-06 15:48 | 2022-03-07 09:26 | 60 | 017:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE ZAFADO HACIA CORTE DE LINEA | C20030600221 | New_Event | Wire Down | Include | Include | Equipment | 1058 | 2022-03-06 | 63480 | keep | 0 | Mar | 2022 | 0.043236 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-03-06 15:49 | 2022-03-07 16:05 | 25 | 024:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22030600224 | New_Event |  |  | Include | Wildlife | 1456 | 2022-03-06 | 36400 | keep | 0 | Mar | 2022 | 0.024792 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-06 15:50 | 2022-03-07 07:34 | 80 | 015:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISCO ROTO 1 X 50 EN CORTE DE LINEA | C22030600230 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 944 | 2022-03-06 | 75520 | keep | 0 | Mar | 2022 | 0.051436 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-03-06 15:51 | 2022-03-07 10:55 | 60 | 019:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22030600232 | New_Event | Bad Weather | Include | Include | Weather | 1144 | 2022-03-06 | 68640 | keep | 0 | Mar | 2022 | 0.04675 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-03-06 15:58 | 2022-03-06 16:59 | 50 | 001:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C22030600235 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2022-03-06 | 3050 | keep | 0 | Mar | 2022 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-06 15:58 | 2022-03-06 23:19 | 200 | 007:21 | P | DESGANCHE | SE RETIRO RAMA DE ARBOL Y SE LEVANTO CONDUCTOR 1X 50 EN C/L | B22030600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2022-03-06 | 88200 | keep | 0 | Mar | 2022 | 0.060073 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-03-06 15:59 | 2022-03-06 20:52 | 50 | 004:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22030600239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-03-06 | 14650 | keep | 0 | Mar | 2022 | 0.009978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-06 16:00 | 2022-03-06 21:10 | 260 | 005:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C22030600241 | New_Event | Bad Weather | Include | Include | Weather | 310 | 2022-03-06 | 80600 | keep | 0 | Mar | 2022 | 0.054896 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
AGUADILLA | 2022-03-06 16:11 | 2022-03-06 17:51 | 40 | 001:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | M22030600231 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2022-03-06 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-06 16:15 | 2022-03-06 16:16 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22030600122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2446 | keep | 0 | Mar | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
UTUADO | 2022-03-06 16:20 | 2022-03-06 19:40 | 45 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600251 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2022-03-06 | 9000 | keep | 0 | Mar | 2022 | 0.0061299 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-03-06 16:22 | 2022-03-06 17:43 | 1293 | 001:21 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR BAJANTE DE PARARRAYO CRUZANDO FASE PRIMARIA SE RETIRO PARARRAYOS Y SE COLOCO INTERRUPTOR EN SERVICIO | P22030600139 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 81 | 2022-03-06 | 104733 | keep | 0 | Mar | 2022 | 0.071333 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-06 16:25 | 2022-03-06 17:14 | 427 | 000:49 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO EL BKR MECANICAMENTE | S22030600117 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-03-06 | 20923 | keep | 0 | Mar | 2022 | 0.014251 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-06 16:29 | 2022-03-07 19:43 | 5 | 027:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR PRIMARIO Y SECUNDARIO | C22030600262 | New_Event | Wire Down | Include | Include | Equipment | 1634 | 2022-03-06 | 8170 | keep | 0 | Mar | 2022 | 0.0055645 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-06 16:40 | 2022-03-07 14:00 | 89 | 021:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C22030600214 | New_Event | Wire Down | Include | Include | Equipment | 1280 | 2022-03-06 | 113920 | keep | 0 | Mar | 2022 | 0.07759 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
CAGUAS | 2022-03-06 16:41 | 2022-03-06 17:48 | 67 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTORES CRUZADOS | C22030600174 | Partial_restoration | Wire Down | Include | Include | Equipment | 67 | 2022-03-06 | 4489 | keep | 0 | Mar | 2022 | 0.0030574 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-06 16:42 | 2022-03-06 18:46 | 45 | 002:04 | P | DESGANCHE | 1 X 65 EN C/L | S22030600122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-03-06 | 5580 | keep | 0 | Mar | 2022 | 0.0038005 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-03-06 16:42 | 2022-03-07 12:52 | 70 | 020:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO COINDUCTOR EN EL SUELO | C22030600277 | New_Event | Wire Down | Include | Include | Equipment | 1210 | 2022-03-06 | 84700 | keep | 0 | Mar | 2022 | 0.057689 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-03-06 16:42 | 2022-03-06 20:17 | 30 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600257 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2022-03-06 | 6450 | keep | 0 | Mar | 2022 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-06 17:02 | 2022-03-07 00:40 | 200 | 007:38 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | B22030600145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2022-03-06 | 91600 | keep | 0 | Mar | 2022 | 0.062388 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-03-06 17:05 | 2022-03-06 17:06 | 200 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22030600152 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-06 | 200 | keep | 0 | Mar | 2022 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-03-06 17:06 | 2022-03-07 07:24 | 57 | 014:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA CABLES CRUZADOS | P22030600153 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 858 | 2022-03-06 | 48906 | keep | 0 | Mar | 2022 | 0.03331 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
ARECIBO | 2022-03-06 17:09 | 2022-03-07 10:19 | 15 | 017:10 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22030600265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1030 | 2022-03-06 | 15450 | keep | 0 | Mar | 2022 | 0.010523 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-06 17:15 | 2022-03-06 18:07 | 100 | 000:52 | P | DESGANCHE | 1 X 100 EN SALIDA DE CONVERTIDOR CRUCE DE FASE PRIMARIA POR RAMA | P22030600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-03-06 | 5200 | keep | 0 | Mar | 2022 | 0.0035417 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-03-06 17:15 | 2022-03-06 20:21 | 624 | 003:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22030600246 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2022-03-06 | 116064 | keep | 0 | Mar | 2022 | 0.079051 | 0.000425 | Sustained | FALSE | FALSE | Not_TMED_Event | 624
MAYAGÃœEZ | 2022-03-06 17:23 | 2022-03-07 03:55 | 120 | 010:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030600053 | New_Event | Bad Weather | Include | Include | Weather | 632 | 2022-03-06 | 75840 | keep | 0 | Mar | 2022 | 0.051654 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-03-06 17:26 | 2022-03-06 21:06 | 10 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030600256 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2022-03-06 | 2200 | keep | 0 | Mar | 2022 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-06 17:42 | 2022-03-06 19:16 | 30 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | P22030600163 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-03-06 | 2820 | keep | 0 | Mar | 2022 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-03-06 17:42 | 2022-03-06 18:57 | 30 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA FUERTE | B22030600098 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-03-06 | 2250 | keep | 0 | Mar | 2022 | 0.0015325 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-06 17:43 | 2022-03-06 19:59 | 20 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTARON 2 CONDUCTORES PRIMARIOS PARTIDOS. | S22030600144 | New_Event | Wire Down | Include | Include | Equipment | 136 | 2022-03-06 | 2720 | keep | 0 | Mar | 2022 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-06 17:44 | 2022-03-06 19:52 | 40 | 002:08 | P | DESGANCHE | 1 X 40 EN C/L Y 1 X 20 XMR | S22030600145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-06 | 5120 | keep | 0 | Mar | 2022 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-06 17:48 | 2022-03-06 17:51 | 3026 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA CONVERTIDOR POR EL 3102-01 APROX 1,608 CLIENTES | C22030600174 | Additional_clients | Wire Down | Include | Include | Equipment | 3 | 2022-03-06 | 9078 | keep | 0 | Mar | 2022 | 0.006183 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-06 17:51 | 2022-03-06 18:25 | 67 | 000:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESCUZARON VARIOS PUNTOS DEL ALIMENTADOR | C22030600174 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 34 | 2022-03-06 | 2278 | keep | 0 | Mar | 2022 | 0.0015515 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2022-03-06 17:55 | 2022-03-06 17:56 | 3230 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M22030600262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-06 | 3230 | keep | 0 | Mar | 2022 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
MAYAGÃœEZ | 2022-03-06 17:56 | 2022-03-06 18:56 | 25 | 001:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030600196 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-03-06 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-06 17:59 | 2022-03-06 21:11 | 44 | 003:12 | P | DESGANCHE | 1 X 65 EN C/L | S22030600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-03-06 | 8448 | keep | 0 | Mar | 2022 | 0.0057539 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
UTUADO | 2022-03-06 18:02 | 2022-03-07 11:05 | 6 | 017:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22030600278 | New_Event | Wire Down | Include | Include | Equipment | 1023 | 2022-03-06 | 6138 | keep | 0 | Mar | 2022 | 0.0041806 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-03-06 18:03 | 2022-03-07 09:54 | 25 | 015:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P22030600170 | New_Event | Bad Weather | Include | Include | Weather | 951 | 2022-03-06 | 23775 | keep | 0 | Mar | 2022 | 0.016193 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-06 18:07 | 2022-03-06 18:08 | 1569 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C22030600363 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-06 | 1569 | keep | 0 | Mar | 2022 | 0.0010686 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-06 18:08 | 2022-03-06 21:50 | 400 | 003:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 5 CAJAS PRIMARIAS QUEMADAS 3 X 100 EN CORTES DE LINEAS | C22030600180 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 222 | 2022-03-06 | 88800 | keep | 0 | Mar | 2022 | 0.060481 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2022-03-06 18:24 | 2022-03-06 21:42 | 687 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22030600272 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2022-03-06 | 136026 | keep | 0 | Mar | 2022 | 0.092647 | 0.00046791 | Sustained | FALSE | FALSE | Not_TMED_Event | 687
SAN JUAN | 2022-03-06 18:30 | 2022-03-07 11:41 | 40 | 017:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R22030600120 | New_Event | Wire Down | Include | Include | Equipment | 1031 | 2022-03-06 | 41240 | keep | 0 | Mar | 2022 | 0.028088 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-06 18:31 | 2022-03-06 19:34 | 35 | 001:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22030600121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-03-06 | 2205 | keep | 0 | Mar | 2022 | 0.0015018 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-03-06 18:38 | 2022-03-07 06:32 | 40 | 011:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22030600182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 714 | 2022-03-06 | 28560 | keep | 0 | Mar | 2022 | 0.019452 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-06 18:44 | 2022-03-07 11:23 | 79 | 016:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C22030600386 | New_Event | Bad Weather | Include | Include | Weather | 999 | 2022-03-06 | 78921 | keep | 0 | Mar | 2022 | 0.053753 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
PONCE | 2022-03-06 18:44 | 2022-03-07 08:20 | 112 | 013:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA PAJARO CRUZO FASE | P22030600017 | New_Event |  |  | Include | Wildlife | 816 | 2022-03-06 | 91392 | keep | 0 | Mar | 2022 | 0.062247 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
CAGUAS | 2022-03-06 18:49 | 2022-03-07 17:58 | 95 | 023:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA, REEMPLAZO 2 PIN POLE TOP Y 2 AISLADORES | C22030600392 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1389 | 2022-03-06 | 131955 | keep | 0 | Mar | 2022 | 0.089874 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-06 18:50 | 2022-03-07 05:10 | 40 | 010:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030600279 | New_Event | Bad Weather | Include | Include | Weather | 620 | 2022-03-06 | 24800 | keep | 0 | Mar | 2022 | 0.016891 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-06 19:05 | 2022-03-07 10:17 | 1 | 015:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600297 | New_Event | Bad Weather | Include | Include | Weather | 912 | 2022-03-06 | 912 | keep | 0 | Mar | 2022 | 0.00062116 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-06 19:14 | 2022-03-06 19:15 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22030600284 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
FAJARDO | 2022-03-06 19:27 | 2022-03-06 21:26 | 1 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R22030600128 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2022-03-06 | 119 | keep | 0 | Mar | 2022 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-06 19:32 | 2022-03-08 13:46 | 10 | 042:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE XMR | B22030600184 | New_Event | Wire Down | Include | Include | Equipment | 2534 | 2022-03-06 | 25340 | keep | 0 | Mar | 2022 | 0.017259 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-06 19:32 | 2022-03-07 18:45 | 12 | 023:13 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | B22030600183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1393 | 2022-03-06 | 16716 | keep | 0 | Mar | 2022 | 0.011385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-06 19:40 | 2022-03-06 20:49 | 50 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600303 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-03-06 | 3450 | keep | 0 | Mar | 2022 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-06 19:45 | 2022-03-07 08:57 | 100 | 013:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 100 AMP CRUCE X RATA | R22030600131 | New_Event |  |  | Include | Wildlife | 792 | 2022-03-06 | 79200 | keep | 0 | Mar | 2022 | 0.053943 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-06 20:00 | 2022-03-06 22:35 | 1 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22030600200 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2022-03-06 | 155 | keep | 0 | Mar | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-06 20:01 | 2022-03-07 13:25 | 50 | 017:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22030600424 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1044 | 2022-03-06 | 52200 | keep | 0 | Mar | 2022 | 0.035553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-06 20:06 | 2022-03-07 09:38 | 26 | 013:32 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION QUEMADA EN RISER | S22030600165 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 812 | 2022-03-06 | 21112 | keep | 0 | Mar | 2022 | 0.014379 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2022-03-06 20:10 | 2022-03-06 21:42 | 10 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA LEVANTAR LINEA SECUNDARIA | S22030600166 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-03-06 | 920 | keep | 0 | Mar | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-06 20:11 | 2022-03-07 06:39 | 75 | 010:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU#4 NO SE ENCONTRO CAUSA | P22030600205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 628 | 2022-03-06 | 47100 | keep | 0 | Mar | 2022 | 0.03208 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2022-03-06 20:11 | 2022-03-06 20:50 | 20 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600322 | Partial_restoration | Bad Weather | Include | Include | Weather | 39 | 2022-03-06 | 780 | keep | 0 | Mar | 2022 | 0.00053125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-06 20:37 | 2022-03-07 11:21 | 60 | 014:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22030600446 | New_Event | Vegetation Contact | Include | Include | Vegetation | 884 | 2022-03-06 | 53040 | keep | 0 | Mar | 2022 | 0.036125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-06 20:45 | 2022-03-07 14:53 | 117 | 018:08 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22030600174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1088 | 2022-03-06 | 127296 | keep | 0 | Mar | 2022 | 0.086701 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
UTUADO | 2022-03-06 21:24 | 2022-03-07 10:08 | 8 | 012:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030600219 | New_Event | Bad Weather | Include | Include | Weather | 764 | 2022-03-06 | 6112 | keep | 0 | Mar | 2022 | 0.0041629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-06 21:34 | 2022-03-07 05:42 | 70 | 008:08 | P | DESGANCHE | 1 X 65 Y SE REALIZO DESGANCHE | B22030600205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2022-03-06 | 34160 | keep | 0 | Mar | 2022 | 0.023266 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-03-06 21:45 | 2022-03-07 13:10 | 20 | 015:25 | P | NO SE REPORTO CAUSA | SE CERRO PUENTE ABIERTO Y SE CERRO C/L (NO FUNDIO) | B22030600206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 925 | 2022-03-06 | 18500 | keep | 0 | Mar | 2022 | 0.0126 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-06 21:50 | 2022-03-06 21:52 | 1569 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL | C22030600475 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2022-03-06 | 3138 | keep | 0 | Mar | 2022 | 0.0021373 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-06 21:52 | 2022-03-07 10:23 | 400 | 012:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 5 CAJAS PRIMARIAS QUEMADAS 3 X 100 EN CORTES DE LINEAS | C22030600180 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 751 | 2022-03-06 | 300400 | keep | 0 | Mar | 2022 | 0.2046 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2022-03-06 21:56 | 2022-03-07 10:35 | 54 | 012:39 | P | DESGANCHE | 1 X 65 EN C/L | R22030600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 759 | 2022-03-06 | 40986 | keep | 0 | Mar | 2022 | 0.027915 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2022-03-06 22:05 | 2022-03-07 20:05 | 7 | 022:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5KVA Y SE REMPLAZO 3 CAJAS DE 100 AMP Y 3 X 15 EN TRANSFORMADOR | S22030600178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1320 | 2022-03-06 | 9240 | keep | 0 | Mar | 2022 | 0.0062933 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-03-06 22:05 | 2022-03-07 12:00 | 5 | 013:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22030600227 | New_Event | Secondary Wire Down | Include | Include | Equipment | 835 | 2022-03-06 | 4175 | keep | 0 | Mar | 2022 | 0.0028436 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-03-06 22:21 | 2022-03-07 19:32 | 10 | 021:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO TRAMO SECUNDARIO APROXIMADO DE 20' | B22030600212 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1271 | 2022-03-06 | 12710 | keep | 0 | Mar | 2022 | 0.0086567 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-06 22:52 | 2022-03-07 14:56 | 1 | 016:04 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 NX DE 18 EN TRANSCLOSURE POR CONTAMINACION | C22030600500 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 964 | 2022-03-06 | 964 | keep | 0 | Mar | 2022 | 0.00065658 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-06 23:04 | 2022-03-06 23:06 | 2192 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-06 | 4384 | keep | 0 | Mar | 2022 | 0.0029859 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
MAYAGÃœEZ | 2022-03-06 23:12 | 2022-03-06 23:13 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
CANOVANAS | 2022-03-06 23:45 | 2022-03-06 23:46 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22030600149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-06 | 2708 | keep | 0 | Mar | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BAYAMON | 2022-03-06 23:54 | 2022-03-07 13:21 | 25 | 013:27 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S22030600183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2022-03-06 | 20175 | keep | 0 | Mar | 2022 | 0.013741 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-03-07 00:19 | 2022-03-07 09:05 | 30 | 008:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030700002 | New_Event | Bad Weather | Include | Include | Weather | 526 | 2022-03-07 | 15780 | keep | 0 | Mar | 2022 | 0.010748 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-07 00:48 | 2022-03-07 00:49 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22030700000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 2735 | keep | 0 | Mar | 2022 | 0.0018628 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-07 00:49 | 2022-03-07 01:45 | 50 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22030600094 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 56 | 2022-03-07 | 2800 | keep | 0 | Mar | 2022 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-03-07 01:22 | 2022-03-07 12:20 | 7 | 010:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | P22030700003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 658 | 2022-03-07 | 4606 | keep | 0 | Mar | 2022 | 0.0031371 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-03-07 01:30 | 2022-03-07 02:15 | 15 | 000:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA QUE CAYO SOBRE POSTE | A22030600228 | New_Event | Wire Down | Include | Include | Equipment | 45 | 2022-03-07 | 675 | keep | 0 | Mar | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-07 01:36 | 2022-03-07 12:40 | 45 | 011:04 | P | DESGANCHE | 3 X 65 EN C/L SE REALIZO DESGANCHE DE ARBOL Y SE LEVANTO DOS FASES | B22030700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 664 | 2022-03-07 | 29880 | keep | 0 | Mar | 2022 | 0.020351 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-07 01:48 | 2022-03-08 06:28 | 20 | 028:40 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S22030700246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1720 | 2022-03-07 | 34400 | keep | 0 | Mar | 2022 | 0.02343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-07 01:56 | 2022-03-07 10:57 | 30 | 009:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO Y SE REALIZO DESGANCHE | S22030700004 | New_Event | Wire Down | Include | Include | Equipment | 541 | 2022-03-07 | 16230 | keep | 0 | Mar | 2022 | 0.011054 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-07 03:30 | 2022-03-07 03:31 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 2697 | keep | 0 | Mar | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
AGUADILLA | 2022-03-07 04:11 | 2022-03-07 04:12 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 1827 | keep | 0 | Mar | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2022-03-07 04:50 | 2022-03-07 05:56 | 2203 | 001:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA NO CARGA EN EL CAMPO | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-03-07 | 145398 | keep | 0 | Mar | 2022 | 0.09903 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-03-07 05:16 | 2022-03-07 05:17 | 641 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1133-04 | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 641 | keep | 0 | Mar | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2022-03-07 05:16 | 2022-03-07 05:17 | 308 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1133-04 | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 308 | keep | 0 | Mar | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-03-07 05:16 | 2022-03-07 05:17 | 333 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1105-02 Y 1105-01 | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 333 | keep | 0 | Mar | 2022 | 0.0002268 | 0.0002268 | Momentary | FALSE | FALSE | Not_TMED_Event | 333
CAGUAS | 2022-03-07 05:17 | 2022-03-07 07:47 | 1709 | 002:30 | T | DESGANCHE | DISPARO SE RETIRARON BAMBUAS SOBRE LINEA | C22030700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-03-07 | 256350 | keep | 0 | Mar | 2022 | 0.1746 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
BARRANQUITAS | 2022-03-07 05:24 | 2022-03-07 05:25 | 2635 | 000:01 | T | DESGANCHE | RECIERRE | C22030700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-07 | 2635 | keep | 0 | Mar | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-03-07 05:25 | 2022-03-07 12:33 | 200 | 007:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22030700019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 428 | 2022-03-07 | 85600 | keep | 0 | Mar | 2022 | 0.058302 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-03-07 05:33 | 2022-03-07 05:34 | 1825 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | S22030700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-07 | 1825 | keep | 0 | Mar | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-03-07 05:34 | 2022-03-07 11:57 | 100 | 006:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO DOS FASES EN EL SUELO Y SE PROCEDIO A SECCIONALIZAR MEDIANTE GOI BY-220307-01 | S22030700069 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 383 | 2022-03-07 | 38300 | keep | 0 | Mar | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-07 05:48 | 2022-03-07 07:30 | 45 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22030700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-03-07 | 4590 | keep | 0 | Mar | 2022 | 0.0031262 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-03-07 05:59 | 2022-03-07 11:10 | 12 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030700007 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2022-03-07 | 3732 | keep | 0 | Mar | 2022 | 0.0025418 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-07 06:00 | 2022-03-07 09:30 | 150 | 003:30 | P | DESGANCHE | 1 X 40, 1X 50 Y 1 X 100 EN CORTES DE LINEA | R22030700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-03-07 | 31500 | keep | 0 | Mar | 2022 | 0.021455 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-03-07 06:03 | 2022-03-07 06:13 | 377 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22030700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-03-07 | 3770 | keep | 0 | Mar | 2022 | 0.0025677 | 0.00025677 | Sustained | FALSE | FALSE | Not_TMED_Event | 377
PONCE | 2022-03-07 06:40 | 2022-03-07 06:43 | 1712 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR NO RECERRO | P22030700016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-07 | 5136 | keep | 0 | Mar | 2022 | 0.0034981 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-03-07 06:40 | 2022-03-07 06:43 | 7 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE 5005-03 QUE LLEVA CARGA DE 5010-04 | P22030700016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-07 | 21 | keep | 0 | Mar | 2022 | 1.4303e-05 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-07 06:43 | 2022-03-07 08:33 | 800 | 001:50 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO 20% 1206-03. SE CERRO MACHETES N/O CON 1620-02 Y SE ABRIO MACHETES EN CARR 848 FRENTE A ALMACENES KOPER POR BAMBUA EN LA LINEA 50 % EN SERVICIO 1206-03 | S22030700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-03-07 | 88000 | keep | 0 | Mar | 2022 | 0.059936 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
SAN JUAN | 2022-03-07 06:43 | 2022-03-07 07:50 | 3718 | 001:07 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1620-02 LLEVANDO 20% 1206-03. SE CERRO POR CONTROL ABRIENDO MACHETES N/O CON 1206-03. BAMBUA CRUZANDO LINEAS | S22030700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-03-07 | 249106 | keep | 0 | Mar | 2022 | 0.16966 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2022-03-07 06:57 | 2022-03-07 15:54 | 17 | 008:57 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22030700038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 537 | 2022-03-07 | 9129 | keep | 0 | Mar | 2022 | 0.0062177 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-03-07 07:06 | 2022-03-07 13:00 | 200 | 005:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22030700008 | New_Event | Wire Down | Include | Include | Equipment | 354 | 2022-03-07 | 70800 | keep | 0 | Mar | 2022 | 0.048222 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-07 07:11 | 2022-03-07 13:55 | 167 | 006:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22030700042 | New_Event | Bad Weather | Include | Include | Weather | 404 | 2022-03-07 | 67468 | keep | 0 | Mar | 2022 | 0.045952 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
ARECIBO | 2022-03-07 07:15 | 2022-03-07 18:06 | 15 | 010:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | A22030700010 | New_Event | Bad Weather | Include | Include | Weather | 651 | 2022-03-07 | 9765 | keep | 0 | Mar | 2022 | 0.0066509 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-07 07:19 | 2022-03-07 09:40 | 2 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030700030 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2022-03-07 | 282 | keep | 0 | Mar | 2022 | 0.00019207 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-07 07:29 | 2022-03-07 17:43 | 8 | 010:14 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y SE DESGANCHO Y TOMA | S22030700065 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 614 | 2022-03-07 | 4912 | keep | 0 | Mar | 2022 | 0.0033455 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-07 07:40 | 2022-03-07 07:41 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1530-07 LLEVANDO CARGA 1526-02 Y 1530-06 | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 1420 | keep | 0 | Mar | 2022 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-03-07 07:40 | 2022-03-07 07:41 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1530-07 LLEVANDO CARGA 1526-02 Y 1530-06 | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 437 | keep | 0 | Mar | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-03-07 07:40 | 2022-03-07 07:41 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1530-07 LLEVANDO CARGA 1526-02 Y 1530-06 | S22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 643 | keep | 0 | Mar | 2022 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
HUMACAO | 2022-03-07 07:57 | 2022-03-07 16:17 | 48 | 008:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE DESGANCHO Y REEMPLAZARON CAJA PRIMARIA | C22030700061 | New_Event | Cutout Failure | Include | Include | Equipment | 500 | 2022-03-07 | 24000 | keep | 0 | Mar | 2022 | 0.016346 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2022-03-07 08:07 | 2022-03-07 12:05 | 18 | 003:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030700015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-03-07 | 4284 | keep | 0 | Mar | 2022 | 0.0029178 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-03-07 08:22 | 2022-03-07 13:05 | 1 | 004:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030700017 | New_Event | Bad Weather | Include | Include | Weather | 283 | 2022-03-07 | 283 | keep | 0 | Mar | 2022 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-07 08:27 | 2022-03-07 12:52 | 1 | 004:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION QUEMADA EN RISER | S22030700093 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 265 | 2022-03-07 | 265 | keep | 0 | Mar | 2022 | 0.00018049 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-07 08:33 | 2022-03-07 09:13 | 400 | 000:40 | P | DESGANCHE | SE REALIZO DESGANCHE CON VARETA Y SE CERRO MACHETES CARGA POR 1620-02 | S22030700040 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-03-07 | 16000 | keep | 0 | Mar | 2022 | 0.010898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-03-07 08:39 | 2022-03-07 09:56 | 6 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO CABLE SECUNDARIO Y SE REGULO VOLTAJE EN TRANSFORMADOR | P22030700031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-03-07 | 462 | keep | 0 | Mar | 2022 | 0.00031467 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-03-07 08:43 | 2022-03-07 09:36 | 1 | 000:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR FUSIBLE PODRIDO | R22030700061 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2022-03-07 | 53 | keep | 0 | Mar | 2022 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-07 08:43 | 2022-03-07 11:24 | 1 | 002:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M22030700023 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 161 | 2022-03-07 | 161 | keep | 0 | Mar | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-07 08:50 | 2022-03-08 10:20 | 1 | 025:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE PRIMARIO Y SECUNDARIO | C22030700081 | New_Event | Wire Down | Include | Include | Equipment | 1530 | 2022-03-07 | 1530 | keep | 0 | Mar | 2022 | 0.0010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-07 08:54 | 2022-03-07 17:26 | 20 | 008:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C22030700110 | New_Event | Service Transformer Failure | Include | Include | Equipment | 512 | 2022-03-07 | 10240 | keep | 0 | Mar | 2022 | 0.0069744 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-03-07 08:55 | 2022-03-07 12:23 | 16 | 003:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | C22030700111 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2022-03-07 | 3328 | keep | 0 | Mar | 2022 | 0.0022667 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-03-07 09:00 | 2022-03-07 17:36 | 50 | 008:36 | P | DESGANCHE | 1 X 50 EN C/L | C22030700112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2022-03-07 | 25800 | keep | 0 | Mar | 2022 | 0.017572 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-07 09:13 | 2022-03-07 09:42 | 30 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A XMR NO FUNDIO | R22030700066 | New_Event | Wire Down | Include | Include | Equipment | 29 | 2022-03-07 | 870 | keep | 0 | Mar | 2022 | 0.00059255 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-07 09:18 | 2022-03-07 13:39 | 30 | 004:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030700027 | New_Event | Bad Weather | Include | Include | Weather | 261 | 2022-03-07 | 7830 | keep | 0 | Mar | 2022 | 0.005333 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-07 09:19 | 2022-03-07 10:29 | 57 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P22030700037 | New_Event |  |  | Include | Wildlife | 70 | 2022-03-07 | 3990 | keep | 0 | Mar | 2022 | 0.0027176 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2022-03-07 09:25 | 2022-03-07 21:43 | 1 | 012:18 | P | DESGANCHE | 1X100 EN CORTE DE LINEA DESGANCHE | S22030700113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 738 | 2022-03-07 | 738 | keep | 0 | Mar | 2022 | 0.00050265 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-07 09:30 | 2022-03-07 18:06 | 600 | 008:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA PRIMARIA PARTIDA SE ABRIO BRECHA CON COMPANIA EXPERT SE SEGUIRA MANANA | M22030700117 | New_Event | Wire Down | Include | Include | Equipment | 516 | 2022-03-07 | 309600 | keep | 0 | Mar | 2022 | 0.21087 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-03-07 09:40 | 2022-03-07 12:54 | 63 | 003:14 | P | OTRAS CAUSAS | 1 X 100 EN CORTE DE LINEA PRINCIPAL 1 X 80 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS QUEMADAS EN C/L Y SE DEJO RISER PRIVADO ABIERTO Y TAG POR AVERIA EN RISER | S22030700116 | New_Event | Other Causes | Include | Include | Other | 194 | 2022-03-07 | 12222 | keep | 0 | Mar | 2022 | 0.0083243 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
MAYAGÃœEZ | 2022-03-07 09:42 | 2022-03-07 15:45 | 150 | 006:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO Y NEUTRAL PRIMARIO ROTO | M22030700031 | New_Event | Wire Down | Include | Include | Equipment | 363 | 2022-03-07 | 54450 | keep | 0 | Mar | 2022 | 0.037086 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-03-07 09:43 | 2022-03-07 19:10 | 20 | 009:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A22030700030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 567 | 2022-03-07 | 11340 | keep | 0 | Mar | 2022 | 0.0077236 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-07 09:54 | 2022-03-07 11:04 | 7 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRAS SULFATADAS | C22030700140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-03-07 | 490 | keep | 0 | Mar | 2022 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-03-07 10:05 | 2022-03-07 12:43 | 7 | 002:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZO DE LINEA SECUNDARIA | P22030700042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 158 | 2022-03-07 | 1106 | keep | 0 | Mar | 2022 | 0.00075329 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-07 10:09 | 2022-03-07 12:13 | 10 | 002:04 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR PARA DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | S22030700088 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 124 | 2022-03-07 | 1240 | keep | 0 | Mar | 2022 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-07 10:16 | 2022-03-08 10:40 | 1 | 024:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030700127 | New_Event | Bad Weather | Include | Include | Weather | 1464 | 2022-03-07 | 1464 | keep | 0 | Mar | 2022 | 0.00099712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-07 10:17 | 2022-03-07 10:19 | 5809 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1716-03 LLEVANDO LA CARGA DEL 1710-01 | B22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-07 | 11618 | keep | 0 | Mar | 2022 | 0.007913 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-03-07 10:17 | 2022-03-07 21:49 | 1812 | 011:32 | T | NO SE REPORTO CAUSA | DISPARO 1716-03 LLEVANDO LA CARGA DEL 1710-01 | B22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 692 | 2022-03-07 | 1253904 | keep | 0 | Mar | 2022 | 0.85403 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
HUMACAO | 2022-03-07 10:18 | 2022-03-07 17:28 | 30 | 007:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22030700155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2022-03-07 | 12900 | keep | 0 | Mar | 2022 | 0.0087861 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-07 10:19 | 2022-03-08 09:53 | 1 | 023:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22030700019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1414 | 2022-03-07 | 1414 | keep | 0 | Mar | 2022 | 0.00096307 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-07 10:23 | 2022-03-07 10:28 | 1569 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE VERIFICO PERSONAL FUERA | C22030700159 | Additional_clients | Cutout Failure | Include | Include | Equipment | 5 | 2022-03-07 | 7845 | keep | 0 | Mar | 2022 | 0.0053432 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-07 10:28 | 2022-03-07 11:38 | 400 | 001:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 5 CAJAS PRIMARIAS QUEMADAS 3 X 100 EN CORTES DE LINEAS | C22030600180 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 70 | 2022-03-07 | 28000 | keep | 0 | Mar | 2022 | 0.019071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-07 10:31 | 2022-03-07 16:02 | 1 | 005:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22030700041 | New_Event | Bad Weather | Include | Include | Weather | 331 | 2022-03-07 | 331 | keep | 0 | Mar | 2022 | 0.00022544 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-07 10:35 | 2022-03-07 12:06 | 165 | 001:31 | P | DESGANCHE | 2 X 40 Y 2 X 50 EN C/LS | R22030700081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-03-07 | 15015 | keep | 0 | Mar | 2022 | 0.010227 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
PONCE | 2022-03-07 10:48 | 2022-03-07 10:49 | 2689 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030700050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 2689 | keep | 0 | Mar | 2022 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | Not_TMED_Event | 2689
UTUADO | 2022-03-07 10:51 | 2022-03-07 13:08 | 1 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22030700042 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2022-03-07 | 137 | keep | 0 | Mar | 2022 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-07 10:52 | 2022-03-07 14:24 | 30 | 003:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22030700085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-03-07 | 6360 | keep | 0 | Mar | 2022 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-03-07 10:55 | 2022-03-07 10:56 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 12600 | C22030700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-07 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-07 10:55 | 2022-03-07 10:56 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 12600 | C22030700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-07 | 640 | keep | 0 | Mar | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
HUMACAO | 2022-03-07 10:56 | 2022-03-07 18:41 | 60 | 007:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22030600232 | Partial_restoration | Bad Weather | Include | Include | Weather | 465 | 2022-03-07 | 27900 | keep | 0 | Mar | 2022 | 0.019003 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-07 11:00 | 2022-03-07 15:14 | 14 | 004:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B22030700082 | New_Event | Wire Down | Include | Include | Equipment | 254 | 2022-03-07 | 3556 | keep | 0 | Mar | 2022 | 0.002422 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-03-07 11:14 | 2022-03-07 11:15 | 2735 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B22030700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-07 | 2735 | keep | 0 | Mar | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-03-07 11:15 | 2022-03-07 18:05 | 76 | 006:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | B22030700091 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 410 | 2022-03-07 | 31160 | keep | 0 | Mar | 2022 | 0.021223 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
VEGA BAJA | 2022-03-07 11:21 | 2022-03-07 11:22 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 1284 | keep | 0 | Mar | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
CANOVANAS | 2022-03-07 11:31 | 2022-03-07 14:22 | 10 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 12 EN TRANSFORMADOR | R22030700089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-03-07 | 1710 | keep | 0 | Mar | 2022 | 0.0011647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-07 11:32 | 2022-03-07 19:04 | 200 | 007:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A22030700051 | New_Event | Bad Weather | Include | Include | Weather | 452 | 2022-03-07 | 90400 | keep | 0 | Mar | 2022 | 0.061571 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-03-07 11:33 | 2022-03-07 13:44 | 20 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN RISER MAL TIEMPO | M22030700031 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2022-03-07 | 2620 | keep | 0 | Mar | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-07 11:35 | 2022-03-07 16:08 | 1 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22030700185 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2022-03-07 | 273 | keep | 0 | Mar | 2022 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-07 11:36 | 2022-03-07 15:28 | 30 | 003:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C20030600039 | New_Event | Bad Weather | Include | Include | Weather | 232 | 2022-03-07 | 6960 | keep | 0 | Mar | 2022 | 0.0047404 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-03-07 11:43 | 2022-03-09 13:28 | 11 | 049:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES EN BAJANTES DEL XMR | C22030700169 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2985 | 2022-03-07 | 32835 | keep | 0 | Mar | 2022 | 0.022364 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-03-07 12:18 | 2022-03-07 16:04 | 50 | 003:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE | R22030700094 | New_Event |  |  | Include | Wildlife | 226 | 2022-03-07 | 11300 | keep | 0 | Mar | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-03-07 12:21 | 2022-03-07 15:10 | 30 | 002:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 CORTE DE LINEA SE SEPARO LINEAS PRIMARIAS CRUZADAS | M22030700062 | New_Event | Wire Down | Include | Include | Equipment | 169 | 2022-03-07 | 5070 | keep | 0 | Mar | 2022 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-07 12:34 | 2022-03-07 17:18 | 79 | 004:44 | P | NO SE REPORTO CAUSA | 2X80 DE RISER @ SU-4 | B22030700102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2022-03-07 | 22436 | keep | 0 | Mar | 2022 | 0.015281 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
CAGUAS | 2022-03-07 12:46 | 2022-03-07 15:40 | 25 | 002:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22030700210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-03-07 | 4350 | keep | 0 | Mar | 2022 | 0.0029628 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-07 12:52 | 2022-03-08 16:46 | 15 | 027:54 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE EN LINEA PRIMARIA Y REPARAR SECUNDARIA AVERIADA | C22030600277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1674 | 2022-03-07 | 25110 | keep | 0 | Mar | 2022 | 0.017102 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-07 13:01 | 2022-03-07 14:27 | 278 | 001:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22030700175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-03-07 | 23908 | keep | 0 | Mar | 2022 | 0.016284 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
MAYAGÃœEZ | 2022-03-07 13:05 | 2022-03-09 15:30 | 15 | 050:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M22030700068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3025 | 2022-03-07 | 45375 | keep | 0 | Mar | 2022 | 0.030905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-07 13:10 | 2022-03-07 15:49 | 58 | 002:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22030700065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-03-07 | 9222 | keep | 0 | Mar | 2022 | 0.0062811 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
MAYAGÃœEZ | 2022-03-07 13:32 | 2022-03-07 16:56 | 100 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER Y 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | M22030700073 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2022-03-07 | 20400 | keep | 0 | Mar | 2022 | 0.013894 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-07 13:38 | 2022-03-07 22:15 | 26 | 008:37 | P | DESGANCHE | 1X40 EN C/L | B22030700114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2022-03-07 | 13442 | keep | 0 | Mar | 2022 | 0.0091553 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-03-07 13:40 | 2022-03-07 14:45 | 7 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22030700186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-03-07 | 455 | keep | 0 | Mar | 2022 | 0.0003099 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-07 13:47 | 2022-03-07 15:12 | 10 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER PORTAFUSIBLE | S22030700187 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2022-03-07 | 850 | keep | 0 | Mar | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-07 13:50 | 2022-03-07 14:35 | 2 | 000:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22030700188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-03-07 | 90 | keep | 0 | Mar | 2022 | 6.1299e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-07 14:07 | 2022-03-07 19:38 | 28 | 005:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22030700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-03-07 | 9268 | keep | 0 | Mar | 2022 | 0.0063124 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2022-03-07 14:10 | 2022-03-07 15:24 | 42 | 001:14 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22030700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-03-07 | 3108 | keep | 0 | Mar | 2022 | 0.0021168 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
ARECIBO | 2022-03-07 14:23 | 2022-03-07 18:35 | 6 | 004:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 50 EN RISER Y 3 X 65 EN CORTE DE LINEA AUTO IMPACTO SWITCH UNIT | A22030700079 | New_Event |  |  | Include | Wildlife | 252 | 2022-03-07 | 1512 | keep | 0 | Mar | 2022 | 0.0010298 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-07 14:26 | 2022-03-07 18:11 | 15 | 003:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A22030700081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 225 | 2022-03-07 | 3375 | keep | 0 | Mar | 2022 | 0.0022987 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-03-07 14:33 | 2022-03-07 17:32 | 25 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR TENSOR | P22030700076 | New_Event |  |  | Include | Wildlife | 179 | 2022-03-07 | 4475 | keep | 0 | Mar | 2022 | 0.0030479 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-07 14:34 | 2022-03-07 17:54 | 137 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR GLOBO | C22030700241 | New_Event |  |  | Include | Wildlife | 200 | 2022-03-07 | 27400 | keep | 0 | Mar | 2022 | 0.018662 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
MAYAGÃœEZ | 2022-03-07 14:34 | 2022-03-07 15:55 | 1 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA AVE CRUZO FASES A TIERRA | M22030700082 | New_Event |  |  | Include | Wildlife | 81 | 2022-03-07 | 81 | keep | 0 | Mar | 2022 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-07 14:35 | 2022-03-08 14:00 | 50 | 023:25 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 30 EN CORTE DE LINEA PARARRAYO CRUZADO | M22030700083 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1405 | 2022-03-07 | 70250 | keep | 0 | Mar | 2022 | 0.047847 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-03-07 14:44 | 2022-03-07 17:02 | 72 | 002:18 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR RAMA | C22030700247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-03-07 | 9936 | keep | 0 | Mar | 2022 | 0.0067674 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
MAYAGÃœEZ | 2022-03-07 14:46 | 2022-03-08 15:38 | 8 | 024:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | M22030700087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1492 | 2022-03-07 | 11936 | keep | 0 | Mar | 2022 | 0.0081296 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-03-07 14:56 | 2022-03-07 15:00 | 15 | 000:04 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22030700101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-03-07 | 60 | keep | 0 | Mar | 2022 | 4.0866e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-07 15:02 | 2022-03-07 18:49 | 20 | 003:47 | P | NO SE REPORTO CAUSA | 1X40 EN CORTE DE LINEA | B22030700138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-03-07 | 4540 | keep | 0 | Mar | 2022 | 0.0030922 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-07 15:05 | 2022-03-07 15:56 | 68 | 000:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE RETIRO PALMA Y BEJUCO DE TRANSFORMADOR | C22030700254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-03-07 | 3468 | keep | 0 | Mar | 2022 | 0.002362 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
VEGA BAJA | 2022-03-07 15:09 | 2022-03-07 15:24 | 652 | 000:15 | S | LINEA DE TRANSMISION 38KV | LINEA 7800 | B22030700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-03-07 | 9780 | keep | 0 | Mar | 2022 | 0.0066611 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-03-07 15:09 | 2022-03-07 15:24 | 2704 | 000:15 | S | LINEA DE TRANSMISION 38KV | LINEA 7800 | B22030700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-03-07 | 40560 | keep | 0 | Mar | 2022 | 0.027625 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2022-03-07 15:11 | 2022-03-07 19:34 | 18 | 004:23 | P | NO SE REPORTO CAUSA | 1X25 EN C/L | B22030700143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-03-07 | 4734 | keep | 0 | Mar | 2022 | 0.0032243 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-03-07 15:13 | 2022-03-07 19:08 | 50 | 003:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS | A22030700087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-03-07 | 11750 | keep | 0 | Mar | 2022 | 0.0080029 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-07 15:14 | 2022-03-07 15:15 | 6136 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR 1709-01 LLEVA TRANSFERIDA LA CARGA DEL 1720-01 | B22030700000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-03-07 | 6136 | keep | 0 | Mar | 2022 | 0.0041792 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-07 15:15 | 2022-03-07 15:40 | 14 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B22030700082 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 25 | 2022-03-07 | 350 | keep | 0 | Mar | 2022 | 0.00023838 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-03-07 15:26 | 2022-03-07 18:56 | 17 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22030500130 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2022-03-07 | 3570 | keep | 0 | Mar | 2022 | 0.0024315 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2022-03-07 15:37 | 2022-03-07 15:38 | 1 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3X40 EN C/L & 3X30 EN C/L & SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B22030700056 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-07 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-07 15:40 | 2022-03-07 18:01 | 6136 | 002:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ELIMINO NEUTRAL DE POSTE DESDE EL SUELO A VARETA | B22030700193 | Additional_clients | Wire Down | Include | Include | Equipment | 141 | 2022-03-07 | 865176 | keep | 0 | Mar | 2022 | 0.58927 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-07 15:51 | 2022-03-07 18:38 | 25 | 002:47 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22030700092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-03-07 | 4175 | keep | 0 | Mar | 2022 | 0.0028436 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-07 16:03 | 2022-03-07 17:02 | 100 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA E INSTALARON 2 RIGIDOS | C22030600246 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2022-03-07 | 5900 | keep | 0 | Mar | 2022 | 0.0040185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-07 16:08 | 2022-03-07 18:51 | 79 | 002:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 30 EN CORTES DE LINEA CRUCE POR AVE | C22030700280 | New_Event |  |  | Include | Wildlife | 163 | 2022-03-07 | 12877 | keep | 0 | Mar | 2022 | 0.0087705 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
CAGUAS | 2022-03-07 16:21 | 2022-03-07 16:22 | 1307 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22030700283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-07 | 1307 | keep | 0 | Mar | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-03-07 16:22 | 2022-03-07 21:19 | 109 | 004:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE DE BAMBUA | C22030700299 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-03-07 | 32373 | keep | 0 | Mar | 2022 | 0.022049 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
CAGUAS | 2022-03-07 16:30 | 2022-03-07 17:50 | 7 | 001:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE ELIMINO RAMA DE LA LINEA | C22030700287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-03-07 | 560 | keep | 0 | Mar | 2022 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-07 16:39 | 2022-03-08 16:33 | 80 | 023:54 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEAS REALIZO DESGANCHE Y REPARO LINEA PRIMARIA ROTA | C22030700287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1434 | 2022-03-07 | 114720 | keep | 0 | Mar | 2022 | 0.078135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-03-07 16:42 | 2022-03-07 17:30 | 40 | 000:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO AVE | R22030700113 | New_Event |  |  | Include | Wildlife | 48 | 2022-03-07 | 1920 | keep | 0 | Mar | 2022 | 0.0013077 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-07 17:26 | 2022-03-07 17:27 | 40 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X80 EN C/L SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S22030700145 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-07 | 40 | keep | 0 | Mar | 2022 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-07 17:27 | 2022-03-07 17:50 | 30 | 000:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22030700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-03-07 | 690 | keep | 0 | Mar | 2022 | 0.00046996 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-07 17:33 | 2022-03-07 20:09 | 125 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR PALOMA | C22030700311 | New_Event |  |  | Include | Wildlife | 156 | 2022-03-07 | 19500 | keep | 0 | Mar | 2022 | 0.013281 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-03-07 18:01 | 2022-03-07 20:40 | 14 | 002:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B22030700082 | Partial_restoration | Wire Down | Include | Include | Equipment | 159 | 2022-03-07 | 2226 | keep | 0 | Mar | 2022 | 0.0015161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-07 18:06 | 2022-03-08 20:54 | 400 | 026:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO BRECHA CON COMPANIA EXPERT SE CONTINUA MANANA | M22030700117 | New_Event | Wire Down | Include | Include | Equipment | 1608 | 2022-03-07 | 643200 | keep | 0 | Mar | 2022 | 0.43808 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-03-07 18:24 | 2022-03-07 21:14 | 5 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A22030700104 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2022-03-07 | 850 | keep | 0 | Mar | 2022 | 0.00057893 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-07 18:37 | 2022-03-07 20:36 | 6 | 001:59 | P | SECUNDARIA/DESGANCHE | 1 X 80 EN TRANSFORMADOR REQUIERE DESGANCHE | A22030700106 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 119 | 2022-03-07 | 714 | keep | 0 | Mar | 2022 | 0.0004863 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-03-07 18:56 | 2022-03-07 19:26 | 1 | 000:30 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | C22030700338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-03-07 | 30 | keep | 0 | Mar | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-07 19:06 | 2022-03-08 11:07 | 80 | 016:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22030700270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 961 | 2022-03-07 | 76880 | keep | 0 | Mar | 2022 | 0.052363 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-07 19:10 | 2022-03-08 12:30 | 5 | 017:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22030700124 | New_Event | Bad Weather | Include | Include | Weather | 1040 | 2022-03-07 | 5200 | keep | 0 | Mar | 2022 | 0.0035417 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-03-07 19:21 | 2022-03-07 20:41 | 50 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE CRUZO LINEAS | R22030700120 | New_Event |  |  | Include | Wildlife | 80 | 2022-03-07 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-03-07 19:22 | 2022-03-08 16:03 | 5 | 020:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A22030800125 | New_Event | Wire Down | Include | Include | Equipment | 1241 | 2022-03-07 | 6205 | keep | 0 | Mar | 2022 | 0.0042262 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-07 19:34 | 2022-03-07 21:40 | 97 | 002:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 40 EN CORTES DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C22030700342 | New_Event | Cutout Failure | Include | Include | Equipment | 126 | 2022-03-07 | 12222 | keep | 0 | Mar | 2022 | 0.0083243 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
VEGA BAJA | 2022-03-07 19:40 | 2022-03-07 23:23 | 652 | 003:43 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 7800 | B22030700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2022-03-07 | 145396 | keep | 0 | Mar | 2022 | 0.099029 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-03-07 19:40 | 2022-03-07 23:23 | 2704 | 003:43 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 7800 | B22030700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 223 | 2022-03-07 | 602992 | keep | 0 | Mar | 2022 | 0.4107 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
CANOVANAS | 2022-03-07 20:02 | 2022-03-07 20:03 | 4154 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 4154 | keep | 0 | Mar | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
HUMACAO | 2022-03-07 20:12 | 2022-03-08 07:35 | 16 | 011:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER REMPLAZO PORTAFUSIBLE QUEMADO | C22030700345 | New_Event | Cutout Failure | Include | Include | Equipment | 683 | 2022-03-07 | 10928 | keep | 0 | Mar | 2022 | 0.007443 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-03-07 20:16 | 2022-03-07 21:53 | 15 | 001:37 | P | NO SE REPORTO CAUSA | 2 X 140 EN CORTE DE LINEA NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M22030700130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-03-07 | 1455 | keep | 0 | Mar | 2022 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-07 20:18 | 2022-03-07 21:30 | 40 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A22030700117 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2022-03-07 | 2880 | keep | 0 | Mar | 2022 | 0.0019616 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-07 20:18 | 2022-03-07 20:42 | 12 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | A22030700064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-03-07 | 288 | keep | 0 | Mar | 2022 | 0.00019616 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-07 20:20 | 2022-03-08 07:32 | 50 | 011:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA AVERIADA | C22030700347 | New_Event | Cutout Failure | Include | Include | Equipment | 672 | 2022-03-07 | 33600 | keep | 0 | Mar | 2022 | 0.022885 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-07 20:21 | 2022-03-07 21:44 | 12 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFROMADOR NO SE ENCONTRO CAUSA | A22030700118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-03-07 | 996 | keep | 0 | Mar | 2022 | 0.00067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-07 20:24 | 2022-03-07 23:29 | 60 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030700132 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2022-03-07 | 11100 | keep | 0 | Mar | 2022 | 0.0075602 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-03-07 20:42 | 2022-03-08 10:38 | 6 | 013:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C22030700353 | New_Event | Wire Down | Include | Include | Equipment | 836 | 2022-03-07 | 5016 | keep | 0 | Mar | 2022 | 0.0034164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-03-07 21:02 | 2022-03-08 01:32 | 100 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22030700117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2022-03-07 | 27000 | keep | 0 | Mar | 2022 | 0.01839 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-07 21:18 | 2022-03-07 22:04 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | R22030700125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-03-07 | 460 | keep | 0 | Mar | 2022 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-07 21:19 | 2022-03-07 21:20 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
AGUADILLA | 2022-03-07 21:30 | 2022-03-07 21:31 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030700130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 1192 | keep | 0 | Mar | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2022-03-07 21:31 | 2022-03-07 21:32 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE BREAKER SE CERRO POR CONTROL LLEVA LA CARGA DEL 1720-07 | B22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-07 | 6136 | keep | 0 | Mar | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
ARECIBO | 2022-03-07 21:34 | 2022-03-08 10:08 | 40 | 012:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A22030700121 | New_Event | Bad Weather | Include | Include | Weather | 754 | 2022-03-07 | 30160 | keep | 0 | Mar | 2022 | 0.020542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-07 21:42 | 2022-03-07 21:43 | 2696 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22030700121 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-07 | 2696 | keep | 0 | Mar | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-03-07 21:43 | 2022-03-08 06:38 | 368 | 008:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO | P22030700124 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 535 | 2022-03-07 | 196880 | keep | 0 | Mar | 2022 | 0.13409 | 0.00025064 | Sustained | FALSE | FALSE | Not_TMED_Event | 368
VEGA BAJA | 2022-03-07 21:52 | 2022-03-08 07:00 | 60 | 009:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22030700521 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 548 | 2022-03-07 | 32880 | keep | 0 | Mar | 2022 | 0.022394 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-07 22:03 | 2022-03-08 08:36 | 30 | 010:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR | A22030700125 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 633 | 2022-03-07 | 18990 | keep | 0 | Mar | 2022 | 0.012934 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-07 22:56 | 2022-03-07 23:00 | 450 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22030700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-07 | 1800 | keep | 0 | Mar | 2022 | 0.001226 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
VEGA BAJA | 2022-03-07 23:23 | 2022-03-08 09:11 | 1622 | 009:48 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE MEDIANTE SWITCH FORM BY-220307-03 | B22030700195 | New_Event | Switch Failure | Include | Include | Equipment | 588 | 2022-03-07 | 953736 | keep | 0 | Mar | 2022 | 0.64959 | 0.0011047 | Sustained | FALSE | FALSE | Not_TMED_Event | 1622
BAYAMON | 2022-03-07 23:25 | 2022-03-08 00:09 | 6136 | 000:44 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA CARGA POR EL 1709-01 | B22030700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-03-07 | 269984 | keep | 0 | Mar | 2022 | 0.18388 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-03-07 23:33 | 2022-03-08 03:12 | 10 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22030700217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-03-07 | 2190 | keep | 0 | Mar | 2022 | 0.0014916 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-08 00:11 | 2022-03-08 01:38 | 100 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030800002 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-03-08 | 8700 | keep | 0 | Mar | 2022 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-08 00:47 | 2022-03-08 00:48 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 3046 | keep | 0 | Mar | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-03-08 00:54 | 2022-03-08 11:10 | 31 | 010:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN SU 1 X 1 X 65 EN AEREO PROVISIONAL SE REPARO TERMINACION EN PROVISIONAL AEREO | R22030800001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 616 | 2022-03-08 | 19096 | keep | 0 | Mar | 2022 | 0.013006 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2022-03-08 01:04 | 2022-03-08 11:03 | 10 | 009:59 | P | SECUNDARIA/DESGANCHE | 1 X 30 EN XMR SE REALIZO DESGANCHE | S22030800003 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 599 | 2022-03-08 | 5990 | keep | 0 | Mar | 2022 | 0.0040798 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-08 01:46 | 2022-03-08 01:48 | 737 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA LLEVA 5% DEL 1346-03 Y 60% POR EL 1529-15 | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-08 | 1474 | keep | 0 | Mar | 2022 | 0.0010039 | 0.00050197 | Momentary | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2022-03-08 01:46 | 2022-03-08 01:48 | 121 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERUPTOR SE CERRO POR SCADA 5% POR EL 1346-02 | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-08 | 242 | keep | 0 | Mar | 2022 | 0.00016483 | 8.2413e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 121
SAN JUAN | 2022-03-08 03:58 | 2022-03-08 15:19 | 40 | 011:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 50 EN CORTE DE LINEA | S22030800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 681 | 2022-03-08 | 27240 | keep | 0 | Mar | 2022 | 0.018553 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-08 04:02 | 2022-03-08 11:00 | 30 | 006:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE LEVANTO SECUNDARIA | S22030700298 | New_Event | Secondary Wire Down | Include | Include | Equipment | 418 | 2022-03-08 | 12540 | keep | 0 | Mar | 2022 | 0.0085409 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-08 04:46 | 2022-03-08 11:09 | 40 | 006:23 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22030800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-03-08 | 15320 | keep | 0 | Mar | 2022 | 0.010434 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-08 05:10 | 2022-03-08 05:14 | 31 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-08 | 124 | keep | 0 | Mar | 2022 | 8.4456e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2022-03-08 05:30 | 2022-03-08 06:35 | 15 | 001:05 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA SECCIONALIZAR POSTE RECOSTADO SOBRE BALCON | S22030800015 | New_Event | Defective Pole | Include | Include | Equipment | 65 | 2022-03-08 | 975 | keep | 0 | Mar | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-08 06:00 | 2022-03-08 10:10 | 30 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030800002 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2022-03-08 | 7500 | keep | 0 | Mar | 2022 | 0.0051082 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-08 06:26 | 2022-03-08 06:27 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030800017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
HUMACAO | 2022-03-08 06:34 | 2022-03-08 06:36 | 3420 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-08 | 6840 | keep | 0 | Mar | 2022 | 0.0046587 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
SAN JUAN | 2022-03-08 06:35 | 2022-03-08 16:44 | 36 | 010:09 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE Y SE CERRO CORTE DE LINEA | S22030800033 | Additional_clients | Defective Pole | Include | Include | Equipment | 609 | 2022-03-08 | 21924 | keep | 0 | Mar | 2022 | 0.014932 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-08 06:51 | 2022-03-08 06:52 | 2064 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030800021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 2064 | keep | 0 | Mar | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
HUMACAO | 2022-03-08 07:13 | 2022-03-08 11:29 | 50 | 004:16 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU - 5A3 AVERIA DEL T - 3 @ T - 4 | C22030800004 | New_Event | UG Cable Fault | Include | Include | Equipment | 256 | 2022-03-08 | 12800 | keep | 0 | Mar | 2022 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-08 07:25 | 2022-03-08 12:50 | 200 | 005:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS | A22030800011 | New_Event | Cutout Failure | Include | Include | Equipment | 325 | 2022-03-08 | 65000 | keep | 0 | Mar | 2022 | 0.044271 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-03-08 07:56 | 2022-03-08 13:04 | 2523 | 005:08 | S | DESCONECTIVO DEFECTUOSO | SUBESTACION FUERA DE SERVICIO CON DOS FUSIBLES FUNDIDOS EN EL TRANSFORMADOR, SE REMOVIO AUXILIAR DE BARRA DEL INTERRUPTOR 8011-03(SPARE) | A22030800094 | New_Event | Switch Failure | Include | Include | Equipment | 308 | 2022-03-08 | 777084 | keep | 0 | Mar | 2022 | 0.52927 | 0.0017184 | Sustained | FALSE | FALSE | Not_TMED_Event | 2523
ARECIBO | 2022-03-08 07:56 | 2022-03-08 13:04 | 1607 | 005:08 | S | DESCONECTIVO DEFECTUOSO | SUBESTACION FUERA DE SERVICIO CON DOS FUSIBLES FUNDIDOS EN EL TRANSFORMADOR, SE REMOVIO AUXILIAR DE BARRA DEL INTERRUPTOR 8011-03(SPARE) | A22030800094 | New_Event | Switch Failure | Include | Include | Equipment | 308 | 2022-03-08 | 494956 | keep | 0 | Mar | 2022 | 0.33711 | 0.0010945 | Sustained | FALSE | FALSE | Not_TMED_Event | 1607
ARECIBO | 2022-03-08 07:56 | 2022-03-08 13:04 | 1722 | 005:08 | S | DESCONECTIVO DEFECTUOSO | SUBESTACION FUERA DE SERVICIO CON DOS FUSIBLES FUNDIDOS EN EL TRANSFORMADOR, SE REMOVIO AUXILIAR DE BARRA DEL INTERRUPTOR 8011-03(SPARE) | A22030800094 | New_Event | Switch Failure | Include | Include | Equipment | 308 | 2022-03-08 | 530376 | keep | 0 | Mar | 2022 | 0.36124 | 0.0011728 | Sustained | FALSE | FALSE | Not_TMED_Event | 1722
HUMACAO | 2022-03-08 08:00 | 2022-03-08 08:36 | 1 | 000:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 20 EN SU - PS - 2 REQUIERE MANTENIMIENTO | C22030800012 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 36 | 2022-03-08 | 36 | keep | 0 | Mar | 2022 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-08 08:09 | 2022-03-09 08:53 | 1 | 024:44 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER | C22030800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1484 | 2022-03-08 | 1484 | keep | 0 | Mar | 2022 | 0.0010107 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-08 08:11 | 2022-03-08 11:55 | 2 | 003:44 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | P22030800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-03-08 | 448 | keep | 0 | Mar | 2022 | 0.00030513 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-03-08 08:15 | 2022-03-08 10:29 | 15 | 002:14 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE SECUNDARIO | B22030800029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 134 | 2022-03-08 | 2010 | keep | 0 | Mar | 2022 | 0.001369 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-03-08 08:16 | 2022-03-08 10:20 | 125 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030800047 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2022-03-08 | 15500 | keep | 0 | Mar | 2022 | 0.010557 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-03-08 08:29 | 2022-03-08 15:49 | 1 | 007:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN RISER CRUCE POR AVE | C22030800016 | New_Event |  |  | Include | Wildlife | 440 | 2022-03-08 | 440 | keep | 0 | Mar | 2022 | 0.00029968 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-08 08:43 | 2022-03-08 11:00 | 8 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LLEVO CONDUCTOR A AISLADOR | S22030800031 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2022-03-08 | 1096 | keep | 0 | Mar | 2022 | 0.00074648 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-08 08:48 | 2022-03-08 18:14 | 10 | 009:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22030800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 566 | 2022-03-08 | 5660 | keep | 0 | Mar | 2022 | 0.003855 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-08 08:50 | 2022-03-08 12:03 | 1 | 003:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22030800044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2022-03-08 | 193 | keep | 0 | Mar | 2022 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-08 08:52 | 2022-03-08 19:32 | 5 | 010:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA EN MONTURA DE TRANSFORMADOR | M22030800040 | New_Event | Cutout Failure | Include | Include | Equipment | 640 | 2022-03-08 | 3200 | keep | 0 | Mar | 2022 | 0.0021795 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-08 09:02 | 2022-03-08 14:45 | 2 | 005:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | A22030800099 | New_Event | Cutout Failure | Include | Include | Equipment | 343 | 2022-03-08 | 686 | keep | 0 | Mar | 2022 | 0.00046723 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-08 09:04 | 2022-03-08 15:35 | 10 | 006:31 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | M22030800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2022-03-08 | 3910 | keep | 0 | Mar | 2022 | 0.0026631 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-08 09:08 | 2022-03-08 15:46 | 60 | 006:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22030800019 | New_Event |  |  | Include | Wildlife | 398 | 2022-03-08 | 23880 | keep | 0 | Mar | 2022 | 0.016265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-08 09:16 | 2022-03-08 09:50 | 1 | 000:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22030800048 | New_Event | Bad Weather | Include | Include | Weather | 34 | 2022-03-08 | 34 | keep | 0 | Mar | 2022 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-08 09:18 | 2022-03-08 16:40 | 51 | 007:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X100 EN CORTE DE LINEA POR CRUCE DE AVE EN EL 13KV | B22030800046 | New_Event |  |  | Include | Wildlife | 442 | 2022-03-08 | 22542 | keep | 0 | Mar | 2022 | 0.015353 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2022-03-08 09:25 | 2022-03-08 18:00 | 8 | 008:35 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22030800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 515 | 2022-03-08 | 4120 | keep | 0 | Mar | 2022 | 0.0028061 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-08 09:31 | 2022-03-08 14:11 | 33 | 004:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA CON GOI SJ-220308-01A | R22030800021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 280 | 2022-03-08 | 9240 | keep | 0 | Mar | 2022 | 0.0062933 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
FAJARDO | 2022-03-08 09:50 | 2022-03-08 11:26 | 9 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRAS SECUNDARIAS Y REPARAR TOMAS SOTERRADAS | R22030800019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2022-03-08 | 864 | keep | 0 | Mar | 2022 | 0.00058847 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-03-08 09:50 | 2022-03-08 16:13 | 1 | 006:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN MONTURA DE TRANSFORMADORES Y LOS BAJANTES PRIMARIOS | A22030800106 | New_Event | Cutout Failure | Include | Include | Equipment | 383 | 2022-03-08 | 383 | keep | 0 | Mar | 2022 | 0.00026086 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-08 09:55 | 2022-03-08 10:07 | 10 | 000:12 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | P22030800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2022-03-08 | 120 | keep | 0 | Mar | 2022 | 8.1731e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-08 10:01 | 2022-03-08 15:49 | 1 | 005:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22030800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2022-03-08 | 348 | keep | 0 | Mar | 2022 | 0.00023702 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-08 10:08 | 2022-03-08 10:09 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 271 | keep | 0 | Mar | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CAGUAS | 2022-03-08 10:30 | 2022-03-08 16:55 | 100 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 RISER, 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER. MAL TIEMPO | C22030800025 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2022-03-08 | 38500 | keep | 0 | Mar | 2022 | 0.026222 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-03-08 10:39 | 2022-03-08 12:17 | 1 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22030800114 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2022-03-08 | 98 | keep | 0 | Mar | 2022 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-08 10:55 | 2022-03-08 16:25 | 30 | 005:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | M22030800013 | New_Event | Wire Down | Include | Include | Equipment | 330 | 2022-03-08 | 9900 | keep | 0 | Mar | 2022 | 0.0067428 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-08 10:58 | 2022-03-08 15:56 | 1 | 004:58 | P | NO SE REPORTO CAUSA | 1X100 DE RISER @ SUBESTACION PRIVADA | B22030800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2022-03-08 | 298 | keep | 0 | Mar | 2022 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-08 11:00 | 2022-03-08 13:54 | 15 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BARRAS EN PEDESTAL | B22030800053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2022-03-08 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-08 11:00 | 2022-03-08 14:29 | 40 | 003:29 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C22030800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-03-08 | 8360 | keep | 0 | Mar | 2022 | 0.005694 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-08 11:00 | 2022-03-08 12:55 | 15 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN XMR | B22030800058 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2022-03-08 | 1725 | keep | 0 | Mar | 2022 | 0.0011749 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-08 11:03 | 2022-03-08 11:04 | 1089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 1089 | keep | 0 | Mar | 2022 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
SAN JUAN | 2022-03-08 11:22 | 2022-03-08 16:01 | 1 | 004:39 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER 1 X 80 EN SU 15 SE REEMPLAZO 5 PIES DE CONDUCTOR Y SE REALIZO TERMINACION | R22030800029 | New_Event | UG Cable Fault | Include | Include | Equipment | 279 | 2022-03-08 | 279 | keep | 0 | Mar | 2022 | 0.00019003 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-08 11:25 | 2022-03-08 16:05 | 10 | 004:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B22030800049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 280 | 2022-03-08 | 2800 | keep | 0 | Mar | 2022 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-08 11:29 | 2022-03-08 20:38 | 30 | 009:09 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DEL SU-2A3 @ T-3 Y REPARO CABLE AVERIADO DEL T-3 @ T-4 | C22030800004 | New_Event | UG Cable Fault | Include | Include | Equipment | 549 | 2022-03-08 | 16470 | keep | 0 | Mar | 2022 | 0.011218 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-03-08 11:40 | 2022-03-09 09:48 | 1 | 022:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | B22030800061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1328 | 2022-03-08 | 1328 | keep | 0 | Mar | 2022 | 0.00090449 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-08 11:45 | 2022-03-09 11:09 | 15 | 023:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22030800062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1404 | 2022-03-08 | 21060 | keep | 0 | Mar | 2022 | 0.014344 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-08 11:53 | 2022-03-08 13:49 | 12 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22030800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-03-08 | 1392 | keep | 0 | Mar | 2022 | 0.00094808 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-08 12:00 | 2022-03-09 12:56 | 1 | 024:56 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | P22030800016 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1496 | 2022-03-08 | 1496 | keep | 0 | Mar | 2022 | 0.0010189 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-08 12:10 | 2022-03-08 15:05 | 1500 | 002:55 | T | LINEA DE TRANSMISION 115KV | SE ABRIO INTERRUPTOR A PETICION DEL JOURNEYMAN JOSIAH SULLIVAN PARA REPARAR LINEA 36100 QUE CAYO SOBRE EL TRONCAL DEL ALIMENTADOR | A22030800132 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 175 | 2022-03-08 | 262500 | keep | 0 | Mar | 2022 | 0.17879 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-03-08 12:25 | 2022-03-08 15:25 | 8 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO Y CONECTORES | S22030800067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-03-08 | 1440 | keep | 0 | Mar | 2022 | 0.00098078 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-08 12:29 | 2022-03-08 14:49 | 6 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE REPARO JUMPER EN LA MONTURA | S22030800069 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2022-03-08 | 840 | keep | 0 | Mar | 2022 | 0.00057212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-08 12:31 | 2022-03-08 14:30 | 12 | 001:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO PORTAFUSIBLE | A22030800139 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2022-03-08 | 1428 | keep | 0 | Mar | 2022 | 0.0009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-03-08 12:43 | 2022-03-08 14:10 | 55 | 001:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | P22030800034 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2022-03-08 | 4785 | keep | 0 | Mar | 2022 | 0.003259 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
FAJARDO | 2022-03-08 12:50 | 2022-03-08 13:08 | 1 | 000:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN BANCO DE TRANSFORMADORES SE REMPLAZO PORTAFUSIBLE Y SE REALIZO DESGANCHE | R22030800033 | New_Event | Cutout Failure | Include | Include | Equipment | 18 | 2022-03-08 | 18 | keep | 0 | Mar | 2022 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-08 12:55 | 2022-03-08 12:56 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
CAGUAS | 2022-03-08 12:57 | 2022-03-08 19:41 | 90 | 006:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA RETIRO GLOBO SOBRE LINEA | C22030800052 | New_Event |  |  | Include | Wildlife | 404 | 2022-03-08 | 36360 | keep | 0 | Mar | 2022 | 0.024765 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-03-08 13:00 | 2022-03-08 14:40 | 10 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR 300 PIES SECUNDARIA AVERIADA | C22030600317 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-03-08 | 1000 | keep | 0 | Mar | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-08 13:00 | 2022-03-08 15:36 | 1 | 002:36 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE ABRIO PUENTES PRIMARIO HACIA BOMBA DE RIEGO EN DESUSO DEBIDO A POSTE PRIMARIO EN EL SUELO | P22030800041 | New_Event | Defective Pole | Include | Include | Equipment | 156 | 2022-03-08 | 156 | keep | 0 | Mar | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-08 13:01 | 2022-03-08 15:26 | 23 | 002:25 | P | NO SE REPORTO CAUSA | 1X20 EN TRANSFORMADOR | B22030800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-03-08 | 3335 | keep | 0 | Mar | 2022 | 0.0022715 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
HUMACAO | 2022-03-08 13:09 | 2022-03-08 13:10 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22030800056 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-08 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-08 13:10 | 2022-03-08 18:17 | 60 | 005:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22030800058 | 1st_after_momentary |  |  | Include | Wildlife | 307 | 2022-03-08 | 18420 | keep | 0 | Mar | 2022 | 0.012546 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-03-08 13:10 | 2022-03-08 13:30 | 1 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22030800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-03-08 | 20 | keep | 0 | Mar | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-08 13:19 | 2022-03-08 15:41 | 15 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P22030800043 | New_Event | Wire Down | Include | Include | Equipment | 142 | 2022-03-08 | 2130 | keep | 0 | Mar | 2022 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-08 13:20 | 2022-03-08 14:17 | 3 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN LA LINEA SECUNDARIA | A22030800101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-03-08 | 171 | keep | 0 | Mar | 2022 | 0.00011647 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-03-08 13:37 | 2022-03-08 16:26 | 40 | 002:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO DE AISLADOR ROTO | A22030800153 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 169 | 2022-03-08 | 6760 | keep | 0 | Mar | 2022 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-08 13:42 | 2022-03-08 18:48 | 80 | 005:06 | P | DESGANCHE | 1X50 EN C/L SE RETIRO ARBOL DE PINO QUE CAYO SOBRE LA LINEA Y SE REMPLAZO CRUCETA | B22030800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-03-08 | 24480 | keep | 0 | Mar | 2022 | 0.016673 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-08 13:56 | 2022-03-08 19:20 | 20 | 005:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22030800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-03-08 | 6480 | keep | 0 | Mar | 2022 | 0.0044135 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-08 14:20 | 2022-03-08 16:49 | 110 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | S22030800129 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2022-03-08 | 16390 | keep | 0 | Mar | 2022 | 0.011163 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BAYAMON | 2022-03-08 14:27 | 2022-03-08 14:28 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 3X15 EN BANCO DE TRANSFORMADORES | S22030800084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-08 14:33 | 2022-03-08 14:34 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22030800159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-08 14:36 | 2022-03-08 15:23 | 1 | 000:47 | P | PROTECCION DEFECTUOSA | 1 X 30 EN RISER Y SE REALIZO COORDINACION DE FUSIBLES | R22030800038 | New_Event | Protection Miscoordination | Include | Include | Other | 47 | 2022-03-08 | 47 | keep | 0 | Mar | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-08 14:38 | 2022-03-08 18:25 | 150 | 003:47 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22030800160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-03-08 | 34050 | keep | 0 | Mar | 2022 | 0.023191 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-03-08 14:50 | 2022-03-08 14:51 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 470 | keep | 0 | Mar | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-03-08 14:55 | 2022-03-08 18:22 | 100 | 003:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22030800119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-03-08 | 20700 | keep | 0 | Mar | 2022 | 0.014099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-08 15:09 | 2022-03-08 15:10 | 1420 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO SU CARGA POR 1530-7 | S2203080000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-08 | 1420 | keep | 0 | Mar | 2022 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-03-08 15:09 | 2022-03-08 15:10 | 437 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO SU CARGA POR 1530-7 | S2203080000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-08 | 437 | keep | 0 | Mar | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-03-08 15:09 | 2022-03-08 15:10 | 643 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA CARGA 1526-2 Y 1530-6 | S22030800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-08 | 643 | keep | 0 | Mar | 2022 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2022-03-08 15:10 | 2022-03-08 17:02 | 420 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO | S2203080000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 112 | 2022-03-08 | 47040 | keep | 0 | Mar | 2022 | 0.032039 | 0.00028606 | Sustained | FALSE | FALSE | Not_TMED_Event | 420
BAYAMON | 2022-03-08 15:10 | 2022-03-08 17:02 | 150 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO | S2203080000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 112 | 2022-03-08 | 16800 | keep | 0 | Mar | 2022 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-08 15:10 | 2022-03-08 17:02 | 150 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO | S22030800000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 112 | 2022-03-08 | 16800 | keep | 0 | Mar | 2022 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-08 15:12 | 2022-03-08 16:32 | 4 | 001:20 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO TRAMO SECUNDARIO PARTIDO (NO FUNDIO) | B22030600204 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 80 | 2022-03-08 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-03-08 15:16 | 2022-03-09 11:22 | 3 | 020:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22030800073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1206 | 2022-03-08 | 3618 | keep | 0 | Mar | 2022 | 0.0024642 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-03-08 15:19 | 2022-03-08 19:18 | 8 | 003:59 | P | DESGANCHE | 1 X 10 EN XMR RETIRO RAMA SOBRE LINEA | C22030800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-03-08 | 1912 | keep | 0 | Mar | 2022 | 0.0013023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-03-08 15:47 | 2022-03-08 15:50 | 591 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1400 | P22030800060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-08 | 1773 | keep | 0 | Mar | 2022 | 0.0012076 | 0.00040253 | Momentary | FALSE | FALSE | Not_TMED_Event | 591
HUMACAO | 2022-03-08 15:49 | 2022-03-08 15:51 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C22030800087 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-08 | 4252 | keep | 0 | Mar | 2022 | 0.002896 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-08 15:49 | 2022-03-08 18:00 | 15 | 002:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M22030800128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-08 | 1965 | keep | 0 | Mar | 2022 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-08 15:50 | 2022-03-08 18:34 | 80 | 002:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22030800169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-03-08 | 13120 | keep | 0 | Mar | 2022 | 0.008936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-03-08 15:51 | 2022-03-08 18:40 | 1 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22030800024 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-03-08 | 169 | keep | 0 | Mar | 2022 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-08 15:51 | 2022-03-08 16:50 | 1 | 000:59 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L | C22030800031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-03-08 | 59 | keep | 0 | Mar | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-08 16:00 | 2022-03-08 20:50 | 303 | 004:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22030800495 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2022-03-08 | 87870 | keep | 0 | Mar | 2022 | 0.059848 | 0.00020637 | Sustained | FALSE | FALSE | Not_TMED_Event | 303
MAYAGÃœEZ | 2022-03-08 16:05 | 2022-03-08 22:25 | 150 | 006:20 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA | M22030800133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2022-03-08 | 57000 | keep | 0 | Mar | 2022 | 0.038822 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-08 16:16 | 2022-03-08 17:38 | 3 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | R22030800036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2022-03-08 | 246 | keep | 0 | Mar | 2022 | 0.00016755 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-03-08 16:17 | 2022-03-08 18:20 | 15 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22030800172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-03-08 | 1845 | keep | 0 | Mar | 2022 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-08 16:32 | 2022-03-08 21:08 | 8 | 004:36 | P | DESGANCHE | 1X40 EN C/L SE REMPLAZO PARARRAYO Y SE DESGANCHO | B22030800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-03-08 | 2208 | keep | 0 | Mar | 2022 | 0.0015039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-03-08 16:52 | 2022-03-08 20:07 | 60 | 003:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22030800178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-03-08 | 11700 | keep | 0 | Mar | 2022 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-08 16:54 | 2022-03-09 00:59 | 30 | 008:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22030800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 485 | 2022-03-08 | 14550 | keep | 0 | Mar | 2022 | 0.0099099 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-08 16:54 | 2022-03-08 18:15 | 150 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22030800179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-03-08 | 12150 | keep | 0 | Mar | 2022 | 0.0082753 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-08 16:56 | 2022-03-08 18:23 | 2203 | 001:27 | T | NO SE REPORTO CAUSA | DISPARO SE NORMALIZO CARGA | S22030800234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-03-08 | 191661 | keep | 0 | Mar | 2022 | 0.13054 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-03-08 16:56 | 2022-03-08 18:18 | 246 | 001:22 | T | NO SE REPORTO CAUSA | DISPARO CON CARGA 1424-6 SE NORMALIZARON CARGA EN SERVICIO | S22030800234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-03-08 | 20172 | keep | 0 | Mar | 2022 | 0.013739 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
ARECIBO | 2022-03-08 16:59 | 2022-03-08 21:48 | 60 | 004:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A22030800183 | New_Event | Wire Down | Include | Include | Equipment | 289 | 2022-03-08 | 17340 | keep | 0 | Mar | 2022 | 0.01181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-08 17:02 | 2022-03-08 21:15 | 1420 | 004:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO PUENTE EN SALIDA RISER SU CARGA POR 1530-7 | S22030800175 | Additional_clients | Wire Down | Include | Include | Equipment | 253 | 2022-03-08 | 359260 | keep | 0 | Mar | 2022 | 0.24469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-08 17:02 | 2022-03-08 21:15 | 437 | 004:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO PUENTE EN SALIDA RISER SU CARGA POR 1530-7 | S22030800175 | Additional_clients | Wire Down | Include | Include | Equipment | 253 | 2022-03-08 | 110561 | keep | 0 | Mar | 2022 | 0.075303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-08 17:02 | 2022-03-08 21:15 | 643 | 004:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO PUENTE EN SALIDA RISER LLAVA CARGA 1530-6 Y 1526-2 | S22030800175 | Additional_clients | Wire Down | Include | Include | Equipment | 253 | 2022-03-08 | 162679 | keep | 0 | Mar | 2022 | 0.1108 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-03-08 17:11 | 2022-03-08 17:48 | 19 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y TOMA | R22030800042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-03-08 | 703 | keep | 0 | Mar | 2022 | 0.00047881 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-03-08 17:13 | 2022-03-08 18:31 | 2 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA EN VARIOS PUNTOS | B22030800091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2022-03-08 | 156 | keep | 0 | Mar | 2022 | 0.00010625 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-03-08 17:28 | 2022-03-08 17:29 | 3463 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030800106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 3463 | keep | 0 | Mar | 2022 | 0.0023586 | 0.0023586 | Momentary | FALSE | FALSE | Not_TMED_Event | 3463
GUAYAMA | 2022-03-08 18:00 | 2022-03-08 18:08 | 2 | 000:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN MONTURA TRIFASICA PARA REMPLAZAR CONECTOR EN BAJANTE SECUNDARIO | P22030800070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 8 | 2022-03-08 | 16 | keep | 0 | Mar | 2022 | 1.0898e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-03-08 18:00 | 2022-03-08 19:06 | 2 | 001:06 | P | OTRAS CAUSAS | 1X25 EN CORTE DE LINEA (POR AVERIA DE CLIENTE) | B22030800093 | New_Event | Other Causes | Include | Include | Other | 66 | 2022-03-08 | 132 | keep | 0 | Mar | 2022 | 8.9905e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-08 18:06 | 2022-03-09 13:15 | 2 | 019:09 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22030800151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1149 | 2022-03-08 | 2298 | keep | 0 | Mar | 2022 | 0.0015652 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-03-08 18:22 | 2022-03-08 21:20 | 70 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M22030800155 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2022-03-08 | 12460 | keep | 0 | Mar | 2022 | 0.0084864 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-03-08 18:27 | 2022-03-08 19:42 | 1 | 001:15 | P | DESGANCHE | SE REMPLAZO TOMA DE SERVICIO & SE DESGANCHO | B22030800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-03-08 | 75 | keep | 0 | Mar | 2022 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-08 18:32 | 2022-03-08 18:38 | 1483 | 000:06 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO 30% POR 1336-8 | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-08 | 8898 | keep | 0 | Mar | 2022 | 0.0060604 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-08 18:32 | 2022-03-08 18:38 | 1500 | 000:06 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO PARTE POR 1336-8 | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-08 | 9000 | keep | 0 | Mar | 2022 | 0.0061299 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-08 18:32 | 2022-03-08 18:38 | 5290 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1336-9, 30% DEL 1204-4 Y PARTE DEL 1204-5 | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-08 | 31740 | keep | 0 | Mar | 2022 | 0.021618 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-08 18:32 | 2022-03-08 18:38 | 207 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1336-08 | S22030800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-08 | 1242 | keep | 0 | Mar | 2022 | 0.00084592 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-03-08 18:37 | 2022-03-08 18:38 | 601 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO L-7300 | S22030800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-08 | 601 | keep | 0 | Mar | 2022 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-03-08 18:37 | 2022-03-08 18:38 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO L-7300 | S22030800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-08 | 640 | keep | 0 | Mar | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-03-08 18:37 | 2022-03-08 18:38 | 1699 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO L-7300 | S22030800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-08 | 1699 | keep | 0 | Mar | 2022 | 0.0011572 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-03-08 18:37 | 2022-03-08 18:38 | 892 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO L-7300 | S22030800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-08 | 892 | keep | 0 | Mar | 2022 | 0.00060754 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-03-08 18:37 | 2022-03-08 18:38 | 1066 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO L-7300 | S22030800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-08 | 1066 | keep | 0 | Mar | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2022-03-08 18:52 | 2022-03-08 21:24 | 50 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA (NO FUNDIO) | B22030800099 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2022-03-08 | 7600 | keep | 0 | Mar | 2022 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-08 19:02 | 2022-03-08 21:38 | 601 | 002:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE EN EL PISO FUSIBLE FUNDIDO 38KV CAMPANA Y PARARRAYO SE PASO CARGA AL 1418-5 | S22030800377 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2022-03-08 | 93756 | keep | 0 | Mar | 2022 | 0.063857 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-03-08 19:02 | 2022-03-08 21:38 | 640 | 002:36 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE EN EL PISO FUSIBLE FUNDIDO 38KV CAMPANA Y PARARRAYO SE PASO CARGA AL 1418-5 | S22030800377 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2022-03-08 | 99840 | keep | 0 | Mar | 2022 | 0.068001 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-03-08 19:02 | 2022-03-08 22:23 | 1699 | 003:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA AL 1423-01 | S22030800377 | New_Event | Wire Down | Include | Include | Equipment | 201 | 2022-03-08 | 341499 | keep | 0 | Mar | 2022 | 0.23259 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-03-08 19:02 | 2022-03-08 23:25 | 892 | 004:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA AL 1335-05 | S22030800377 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-03-08 | 234596 | keep | 0 | Mar | 2022 | 0.15978 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-03-08 19:02 | 2022-03-08 21:13 | 1066 | 002:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO ALAMBRE EN EL PISO 1437-4 FUNDIO FUSIBLE 38KV CAMPANA Y PARARRAYO SE PASO CARGA AL 1423-2 | S22030800377 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2022-03-08 | 139646 | keep | 0 | Mar | 2022 | 0.095112 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
MAYAGÃœEZ | 2022-03-08 19:23 | 2022-03-09 13:10 | 200 | 017:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA PRIMARIA | M22030800167 | New_Event | Cutout Failure | Include | Include | Equipment | 1067 | 2022-03-08 | 213400 | keep | 0 | Mar | 2022 | 0.14535 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-03-08 19:41 | 2022-03-09 07:27 | 9 | 011:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE NEUTRAL PRIMARIO SAFADO EN TRANSFORMADOR | P22030800087 | New_Event | Wire Down | Include | Include | Equipment | 706 | 2022-03-08 | 6354 | keep | 0 | Mar | 2022 | 0.0043277 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2022-03-08 20:28 | 2022-03-09 15:03 | 25 | 018:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22030800132 | New_Event |  |  | Include | Wildlife | 1115 | 2022-03-08 | 27875 | keep | 0 | Mar | 2022 | 0.018986 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-03-08 20:29 | 2022-03-09 12:45 | 1 | 016:16 | P | PARARRAYOS DEFECTUOSO | 3 X 10 EN BANCO DE XMR SE REMPLAZO PARARAYO | B22030800104 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 976 | 2022-03-08 | 976 | keep | 0 | Mar | 2022 | 0.00066475 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-08 20:44 | 2022-03-09 04:04 | 300 | 007:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA | A22030800217 | New_Event | Wire Down | Include | Include | Equipment | 440 | 2022-03-08 | 132000 | keep | 0 | Mar | 2022 | 0.089905 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-03-08 20:54 | 2022-03-09 07:21 | 400 | 010:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE ABRIRA CORTE DE LINEA PARA REPARAR | M22030700117 | New_Event | Wire Down | Include | Include | Equipment | 627 | 2022-03-08 | 250800 | keep | 0 | Mar | 2022 | 0.17082 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-03-08 21:14 | 2022-03-09 11:40 | 2 | 014:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REEMPLAZO BAJANTE SECUNDARIO | R22030800052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 866 | 2022-03-08 | 1732 | keep | 0 | Mar | 2022 | 0.0011797 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-08 21:43 | 2022-03-08 23:23 | 30 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S22030800564 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2022-03-08 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-03-08 22:07 | 2022-03-08 23:00 | 1 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO XMR PARA REPARAR BAJANTE SECUNDARIO | C22030800119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-03-08 | 53 | keep | 0 | Mar | 2022 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-08 22:30 | 2022-03-09 07:39 | 45 | 009:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22030800138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 549 | 2022-03-08 | 24705 | keep | 0 | Mar | 2022 | 0.016826 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-03-08 22:55 | 2022-03-08 22:56 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030800192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-08 | 1827 | keep | 0 | Mar | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-03-08 23:15 | 2022-03-09 01:35 | 100 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22030800196 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2022-03-08 | 14000 | keep | 0 | Mar | 2022 | 0.0095353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-08 23:24 | 2022-03-09 14:33 | 20 | 015:09 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN RISER POR TRANSFORMADOR 50 KVA AVERIADO | A22030800227 | New_Event | Service Transformer Failure | Include | Include | Equipment | 909 | 2022-03-08 | 18180 | keep | 0 | Mar | 2022 | 0.012382 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-08 23:25 | 2022-03-09 03:57 | 89 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES | S22030800377 | Partial_restoration | Wire Down | Include | Include | Equipment | 272 | 2022-03-08 | 24208 | keep | 0 | Mar | 2022 | 0.016488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-08 23:25 | 2022-03-09 08:50 | 8 | 009:25 | P | ESTRUCTURA AVERIADA | SE ABRIERON PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO | A22030800228 | New_Event | Defective Pole | Include | Include | Equipment | 565 | 2022-03-08 | 4520 | keep | 0 | Mar | 2022 | 0.0030786 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-08 23:36 | 2022-03-09 09:23 | 40 | 009:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 SMU 20 EN SU - 1B CRUCE X RATA | R22030800053 | New_Event |  |  | Include | Wildlife | 587 | 2022-03-08 | 23480 | keep | 0 | Mar | 2022 | 0.015992 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-08 23:53 | 2022-03-09 12:18 | 34 | 012:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S22030800585 | New_Event | Cutout Failure | Include | Include | Equipment | 745 | 2022-03-08 | 25330 | keep | 0 | Mar | 2022 | 0.017252 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
ARECIBO | 2022-03-09 00:01 | 2022-03-10 18:43 | 30 | 042:42 | P | ESTRUCTURA AVERIADA | SE REMPLAZO DOS POSTES PRIMARIOS PARTIDOS Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22030900118 | New_Event | Defective Pole | Include | Include | Equipment | 2562 | 2022-03-09 | 76860 | keep | 0 | Mar | 2022 | 0.052349 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-03-09 00:32 | 2022-03-09 07:08 | 36 | 006:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO GLOBO DE HELIO DE LINEA PRIMARIA | P22030900004 | New_Event |  |  | Include | Wildlife | 396 | 2022-03-09 | 14256 | keep | 0 | Mar | 2022 | 0.0097097 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2022-03-09 00:54 | 2022-03-09 06:51 | 27 | 005:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22030900002 | New_Event | Bad Weather | Include | Include | Weather | 357 | 2022-03-09 | 9639 | keep | 0 | Mar | 2022 | 0.0065651 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2022-03-09 02:13 | 2022-03-09 02:14 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 1859 | keep | 0 | Mar | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
YAUCO | 2022-03-09 02:16 | 2022-03-09 08:25 | 67 | 006:09 | P | DESGANCHE | 3 X 80 2 X 100 EN CORTE DE LINEA SE RETIRO ARBOL DE LINEA | P22030900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-03-09 | 24723 | keep | 0 | Mar | 2022 | 0.016839 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-03-09 03:57 | 2022-03-09 06:03 | 40 | 002:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B22030900001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 126 | 2022-03-09 | 5040 | keep | 0 | Mar | 2022 | 0.0034327 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-09 04:01 | 2022-03-09 04:02 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 2113 | keep | 0 | Mar | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2022-03-09 04:03 | 2022-03-09 07:47 | 159 | 003:44 | P | ESTRUCTURA AVERIADA | 1 X 40 EN C/L SECCIONALIZO POSTE PARTIDO | R22030900001 | New_Event | Defective Pole | Include | Include | Equipment | 224 | 2022-03-09 | 35616 | keep | 0 | Mar | 2022 | 0.024258 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
ARECIBO | 2022-03-09 04:04 | 2022-03-09 04:05 | 1916 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR LINEA PRIMARIA PARTIDA | A22030900012 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-03-09 | 1916 | keep | 0 | Mar | 2022 | 0.001305 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-09 04:05 | 2022-03-09 12:03 | 300 | 007:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22030800217 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 478 | 2022-03-09 | 143400 | keep | 0 | Mar | 2022 | 0.097669 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-03-09 04:10 | 2022-03-09 16:21 | 60 | 012:11 | P | DESGANCHE | 1X65 EN CORTE DE LINEA | B22030900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 731 | 2022-03-09 | 43860 | keep | 0 | Mar | 2022 | 0.029873 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-09 04:32 | 2022-03-09 08:48 | 35 | 004:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CULEBRA CRUZO CAJA PRIMARIA | A22030900015 | New_Event |  |  | Include | Wildlife | 256 | 2022-03-09 | 8960 | keep | 0 | Mar | 2022 | 0.0061026 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-03-09 04:55 | 2022-03-09 04:56 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22031000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 3046 | keep | 0 | Mar | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-03-09 05:03 | 2022-03-09 05:06 | 2245 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1658-15 CERRADO POR CONTROL | R22030900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-09 | 6735 | keep | 0 | Mar | 2022 | 0.0045872 | 0.0015291 | Momentary | FALSE | FALSE | Not_TMED_Event | 2245
SAN JUAN | 2022-03-09 05:03 | 2022-03-09 05:06 | 1 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1658-13 CERRADO POR CONTROL | R22030900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-09 | 3 | keep | 0 | Mar | 2022 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-09 05:26 | 2022-03-09 05:33 | 36 | 000:07 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1620-03 | S22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-09 | 252 | keep | 0 | Mar | 2022 | 0.00017164 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-03-09 05:26 | 2022-03-09 05:33 | 1073 | 000:07 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1620-01 | S22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-09 | 7511 | keep | 0 | Mar | 2022 | 0.0051157 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
PONCE | 2022-03-09 06:00 | 2022-03-09 06:01 | 1730 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 1730 | keep | 0 | Mar | 2022 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
MAYAGÃœEZ | 2022-03-09 06:07 | 2022-03-09 12:47 | 10 | 006:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2022-03-09 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-09 06:17 | 2022-03-09 09:00 | 80 | 002:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-03-09 | 13040 | keep | 0 | Mar | 2022 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-09 06:33 | 2022-03-09 17:30 | 14 | 010:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO TRAMO SECUNDARIO (TRASPATIO) | B22030900004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 657 | 2022-03-09 | 9198 | keep | 0 | Mar | 2022 | 0.0062647 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-03-09 06:47 | 2022-03-09 15:00 | 10 | 008:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR SE RETIRO CRUCETA PODRIDA Y SE REMPLAZO PARARRAYOS AVERIADO | M22030900009 | New_Event | Wire Down | Include | Include | Equipment | 493 | 2022-03-09 | 4930 | keep | 0 | Mar | 2022 | 0.0033578 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-09 07:00 | 2022-03-09 15:47 | 1 | 008:47 | P | DESGANCHE | 1 X 65 EN RISER | R22030900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 527 | 2022-03-09 | 527 | keep | 0 | Mar | 2022 | 0.00035894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-09 07:12 | 2022-03-09 07:13 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030900018 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 2113 | keep | 0 | Mar | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2022-03-09 07:21 | 2022-03-09 14:22 | 600 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO Y REPARAR LINEA Y NEUTRAL PRIMARIOS | M22030700117 | Additional_clients | Wire Down | Include | Include | Equipment | 421 | 2022-03-09 | 252600 | keep | 0 | Mar | 2022 | 0.17204 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-09 07:22 | 2022-03-09 09:06 | 40 | 001:44 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22030900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-03-09 | 4160 | keep | 0 | Mar | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-09 07:28 | 2022-03-09 17:17 | 1 | 009:49 | P | NO SE REPORTO CAUSA | 1 X 65 1 X 30 EN C/LÂ´S Y 1 X 20 EN BANCO DE XMRS NO CAUSA | R22030900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 589 | 2022-03-09 | 589 | keep | 0 | Mar | 2022 | 0.00040117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-09 07:29 | 2022-03-09 16:55 | 35 | 009:26 | P | OTRAS CAUSAS | 1 X 100 EN CORTE DE LINEA SE DEJO FUERA 1 CLIENTE CON AVERIA INTERNA | S22030900055 | New_Event | Other Causes | Include | Include | Other | 566 | 2022-03-09 | 19810 | keep | 0 | Mar | 2022 | 0.013493 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-03-09 07:36 | 2022-03-09 10:35 | 55 | 002:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REEMPLAZO AISLADOR | R22030900011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 179 | 2022-03-09 | 9845 | keep | 0 | Mar | 2022 | 0.0067054 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-03-09 07:40 | 2022-03-09 07:45 | 922 | 000:05 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1401-8 | S22030900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-03-09 | 4610 | keep | 0 | Mar | 2022 | 0.0031399 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-09 07:40 | 2022-03-09 07:45 | 837 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1401-07 | S22030900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-03-09 | 4185 | keep | 0 | Mar | 2022 | 0.0028504 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-03-09 07:40 | 2022-03-09 07:45 | 908 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA CARGA 1401-6 | S22030900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-03-09 | 4540 | keep | 0 | Mar | 2022 | 0.0030922 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-03-09 07:40 | 2022-03-09 07:45 | 135 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA CARGA 1346-5 | S22030900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-03-09 | 675 | keep | 0 | Mar | 2022 | 0.00045974 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-03-09 07:40 | 2022-03-09 07:45 | 1 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S22030900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-03-09 | 5 | keep | 0 | Mar | 2022 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-09 07:40 | 2022-03-09 07:45 | 1295 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S22030900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-03-09 | 6475 | keep | 0 | Mar | 2022 | 0.0044101 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
CANOVANAS | 2022-03-09 07:47 | 2022-03-09 13:10 | 2 | 005:23 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | R22030900001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 323 | 2022-03-09 | 646 | keep | 0 | Mar | 2022 | 0.00043999 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-09 07:48 | 2022-03-09 17:43 | 20 | 009:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22030900068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2022-03-09 | 11900 | keep | 0 | Mar | 2022 | 0.008105 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-09 07:56 | 2022-03-09 11:10 | 1 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 18 FUSIBLE TIPO NX EN TRANSCLOSURE | C22030900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-03-09 | 194 | keep | 0 | Mar | 2022 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-09 08:05 | 2022-03-09 08:08 | 327 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 2603-06 (SPARE) LLEVANDO 2603-07 SE CERRO POR SCADA | C22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-09 | 981 | keep | 0 | Mar | 2022 | 0.00066815 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2022-03-09 08:06 | 2022-03-09 08:07 | 5252 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B22030900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-09 | 5252 | keep | 0 | Mar | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2022-03-09 08:07 | 2022-03-09 11:21 | 10 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO NEUTRAL PRIMARIO | B22030900007 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 194 | 2022-03-09 | 1940 | keep | 0 | Mar | 2022 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-09 08:17 | 2022-03-09 15:21 | 20 | 007:04 | P | OTRAS CAUSAS | 2 X 10 EN TRANSFORMADOR. SE DEJO FUERA UN RISER SECUNDARIO PRIVADO HACIA EDIFICIO 926 POR AVERIA | S22030900078 | New_Event | Other Causes | Include | Include | Other | 424 | 2022-03-09 | 8480 | keep | 0 | Mar | 2022 | 0.0057757 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-03-09 08:21 | 2022-03-09 09:42 | 1352 | 001:21 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL #12 SE ENCONTRO BANDERA CON INDICACION DE FASE A Y B DE TIEMPO EN 5602-02SUBESTACION LO REFIERE A PROTECCION | P22030900035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-03-09 | 109512 | keep | 0 | Mar | 2022 | 0.074588 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2022-03-09 08:21 | 2022-03-09 10:10 | 3973 | 001:49 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL #12 SE ENCONTRO BANDERA CON INDICACION DE FASE A Y B DE TIEMPO EN 5602-02 SUBESTACION LO REFIERE A PROTECCION | P22030900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-03-09 | 433057 | keep | 0 | Mar | 2022 | 0.29495 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-03-09 08:21 | 2022-03-09 09:42 | 2484 | 001:21 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION PORTATIL #12 SE ENCONTRO BANDERA CON INDICACION DE FASE A Y B DE TIEMPO EN 5602-02 SUBESTACION LO REFIERE A PROTECCION | P22030900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-03-09 | 201204 | keep | 0 | Mar | 2022 | 0.13704 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
CAGUAS | 2022-03-09 08:24 | 2022-03-09 12:37 | 20 | 004:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22030900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2022-03-09 | 5060 | keep | 0 | Mar | 2022 | 0.0034463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-09 08:28 | 2022-03-09 08:29 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22030900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 1261 | keep | 0 | Mar | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
ARECIBO | 2022-03-09 08:50 | 2022-03-09 18:30 | 4 | 009:40 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTES PRIMARIOS | A22030900080 | Partial_restoration | Defective Pole | Include | Include | Equipment | 580 | 2022-03-09 | 2320 | keep | 0 | Mar | 2022 | 0.0015801 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-09 08:57 | 2022-03-09 09:42 | 9 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL DE BAJANTE SECUNDARIO | C22030800125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2022-03-09 | 405 | keep | 0 | Mar | 2022 | 0.00027584 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-03-09 08:59 | 2022-03-09 15:29 | 2 | 006:30 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO Y REEMPLAZO CAJA AVERIADA | R22030900022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 390 | 2022-03-09 | 780 | keep | 0 | Mar | 2022 | 0.00053125 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-03-09 09:02 | 2022-03-09 13:01 | 1 | 003:59 | P | DESGANCHE | 1 X 25 EN C/L | R22030900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-03-09 | 239 | keep | 0 | Mar | 2022 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-09 09:07 | 2022-03-09 12:18 | 2 | 003:11 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRANSFORMADOR | S22030900105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-03-09 | 382 | keep | 0 | Mar | 2022 | 0.00026018 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-03-09 09:11 | 2022-03-09 14:38 | 7 | 005:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN XMR SE REPARO SECUNDARIA CRUZADA CON MENSAJERO. | C22030900027 | New_Event |  |  | Include | Wildlife | 327 | 2022-03-09 | 2289 | keep | 0 | Mar | 2022 | 0.001559 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-09 09:31 | 2022-03-09 19:10 | 40 | 009:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL DE LAS LINEAS | M22030900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 579 | 2022-03-09 | 23160 | keep | 0 | Mar | 2022 | 0.015774 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-03-09 09:42 | 2022-03-09 11:24 | 1 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN MONTURA TRIFASICA DESCARGA ELECTRICA | P22030900051 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2022-03-09 | 102 | keep | 0 | Mar | 2022 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-03-09 09:55 | 2022-03-09 11:08 | 20 | 001:13 | P | DESGANCHE | 1 X 40 EN C/L | R22030900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-03-09 | 1460 | keep | 0 | Mar | 2022 | 0.0009944 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-09 09:56 | 2022-03-09 15:35 | 50 | 005:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22030900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2022-03-09 | 16950 | keep | 0 | Mar | 2022 | 0.011545 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-09 09:59 | 2022-03-09 16:47 | 100 | 006:48 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2022-03-09 | 40800 | keep | 0 | Mar | 2022 | 0.027789 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-09 10:00 | 2022-03-09 13:15 | 9 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M22030900023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2022-03-09 | 1755 | keep | 0 | Mar | 2022 | 0.0011953 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-03-09 10:01 | 2022-03-09 13:20 | 100 | 003:19 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN SU-11 CONTAMINACION | S22030900124 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 199 | 2022-03-09 | 19900 | keep | 0 | Mar | 2022 | 0.013554 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-03-09 10:10 | 2022-03-09 11:23 | 991 | 001:13 | P | OTRAS CAUSAS | MACHETES ABIERTOS SECCIONALIZANDO LINEA | P22030900058 | New_Event | Other Causes | Include | Include | Other | 73 | 2022-03-09 | 72343 | keep | 0 | Mar | 2022 | 0.049272 | 0.00067497 | Sustained | FALSE | FALSE | Not_TMED_Event | 991
MAYAGÃœEZ | 2022-03-09 10:20 | 2022-03-09 18:45 | 1 | 008:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | M22030900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 505 | 2022-03-09 | 505 | keep | 0 | Mar | 2022 | 0.00034395 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-09 10:23 | 2022-03-09 11:49 | 8 | 001:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR PEDESTAL | C22030900033 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 86 | 2022-03-09 | 688 | keep | 0 | Mar | 2022 | 0.00046859 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-09 10:26 | 2022-03-09 10:27 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LA CARGA POR 6404-02 | M22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 1117 | keep | 0 | Mar | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-03-09 10:26 | 2022-03-09 10:27 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LLEVA LA CARGA DEL 6404-01 | M22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 1671 | keep | 0 | Mar | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
CAGUAS | 2022-03-09 10:35 | 2022-03-09 11:01 | 817 | 000:26 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA. HABIA PERSONAL DE SUBESTACIONES TRABAJANDO CON RTU E INDICARON NO TUVIERON QUE VER CON DISPARO | C22030900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-03-09 | 21242 | keep | 0 | Mar | 2022 | 0.014468 | 0.00055645 | Sustained | FALSE | FALSE | Not_TMED_Event | 817
HUMACAO | 2022-03-09 10:37 | 2022-03-09 14:27 | 65 | 003:50 | P | DESGANCHE | 1 X 50 Y 1 X 25 EN CORTES DE LINEAS | C22030900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-03-09 | 14950 | keep | 0 | Mar | 2022 | 0.010182 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-03-09 10:56 | 2022-03-09 11:33 | 12 | 000:37 | P | OTRAS CAUSAS | SE ABRE TRANSFORMADOR PARA QUE SECCION DE LOW VOLTAGE REMPLAZE MAIN BREAKER | P22030900061 | New_Event | Other Causes | Include | Include | Other | 37 | 2022-03-09 | 444 | keep | 0 | Mar | 2022 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-09 10:57 | 2022-03-09 16:51 | 12 | 005:54 | P | NO SE REPORTO CAUSA | 1X10 EN EL T-6 | B22030900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 354 | 2022-03-09 | 4248 | keep | 0 | Mar | 2022 | 0.0028933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-09 10:57 | 2022-03-09 14:32 | 1 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22030900068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2022-03-09 | 215 | keep | 0 | Mar | 2022 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-03-09 11:00 | 2022-03-09 12:19 | 1 | 001:19 | P | DESGANCHE | 2 X 30 EN C/L | R22030900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-03-09 | 79 | keep | 0 | Mar | 2022 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-09 11:00 | 2022-03-09 16:23 | 55 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L REEMPLAZO BAJANTE PRIMARIO | R22030900031 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2022-03-09 | 17765 | keep | 0 | Mar | 2022 | 0.0121 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2022-03-09 11:00 | 2022-03-09 11:11 | 11 | 000:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22030800054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 11 | 2022-03-09 | 121 | keep | 0 | Mar | 2022 | 8.2413e-05 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-03-09 11:04 | 2022-03-09 19:05 | 45 | 008:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22030900051 | New_Event | Bad Weather | Include | Include | Weather | 481 | 2022-03-09 | 21645 | keep | 0 | Mar | 2022 | 0.014742 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-03-09 11:10 | 2022-03-09 11:25 | 1 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P22030900017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-03-09 | 15 | keep | 0 | Mar | 2022 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-09 11:25 | 2022-03-09 14:21 | 1 | 002:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22030900063 | New_Event |  |  | Include | Wildlife | 176 | 2022-03-09 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-09 11:37 | 2022-03-09 12:01 | 7 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y CONEXIONES | C22030900025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2022-03-09 | 168 | keep | 0 | Mar | 2022 | 0.00011442 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-09 11:44 | 2022-03-09 12:31 | 21 | 000:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22030900058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-03-09 | 987 | keep | 0 | Mar | 2022 | 0.00067224 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-03-09 12:09 | 2022-03-09 13:19 | 2 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO QUEMADO POR CALIBRE # 1/0 - CU | B22030900022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-03-09 | 140 | keep | 0 | Mar | 2022 | 9.5353e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-03-09 12:10 | 2022-03-09 13:35 | 20 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | R22030900040 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2022-03-09 | 1700 | keep | 0 | Mar | 2022 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-09 12:16 | 2022-03-09 16:11 | 50 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R22030900041 | New_Event |  |  | Include | Wildlife | 235 | 2022-03-09 | 11750 | keep | 0 | Mar | 2022 | 0.0080029 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-09 12:16 | 2022-03-09 14:10 | 100 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN REGULADPRES POR MAL TIEMPO | P22030900067 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2022-03-09 | 11400 | keep | 0 | Mar | 2022 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-09 12:16 | 2022-03-09 14:56 | 2 | 002:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A22030900086 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2022-03-09 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-09 12:26 | 2022-03-09 12:33 | 3432 | 000:07 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA 80% DE SU CARGA | S22030900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-09 | 24024 | keep | 0 | Mar | 2022 | 0.016363 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
MAYAGÃœEZ | 2022-03-09 12:50 | 2022-03-10 16:46 | 40 | 027:56 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | M22030900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1676 | 2022-03-09 | 67040 | keep | 0 | Mar | 2022 | 0.045661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-09 12:52 | 2022-03-09 14:25 | 3701 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV POR CRUCE DE GUINEA EN FASE C EN LA ALTA DEL XMR 2702 | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2022-03-09 | 344193 | keep | 0 | Mar | 2022 | 0.23443 | 0.0025207 | Sustained | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-03-09 12:52 | 2022-03-09 14:25 | 989 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV POR CRUCE DE GUINEA EN FASE C EN LA ALTA DEL XMR 2702 | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2022-03-09 | 91977 | keep | 0 | Mar | 2022 | 0.062645 | 0.0006736 | Sustained | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-03-09 12:52 | 2022-03-09 14:25 | 1467 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV POR CRUCE DE GUINEA EN FASE C EN LA ALTA DEL XMR 2702 | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2022-03-09 | 136431 | keep | 0 | Mar | 2022 | 0.092923 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-03-09 12:52 | 2022-03-09 14:25 | 1835 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV POR CRUCE DE GUINEA EN FASE C EN LA ALTA DEL XMR 2702 | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2022-03-09 | 170655 | keep | 0 | Mar | 2022 | 0.11623 | 0.0012498 | Sustained | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-03-09 12:52 | 2022-03-09 14:25 | 71 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV POR CRUCE DE GUINEA EN FASE C EN LA ALTA DEL XMR 2702 | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2022-03-09 | 6603 | keep | 0 | Mar | 2022 | 0.0044973 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
CAGUAS | 2022-03-09 12:58 | 2022-03-09 15:22 | 12 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR 200 PIES DE SECUNDARIA AVERIADA | C22030900038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2022-03-09 | 1728 | keep | 0 | Mar | 2022 | 0.0011769 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-09 12:59 | 2022-03-09 14:19 | 150 | 001:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO PORTA FUSIBLE | A22030900092 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2022-03-09 | 12000 | keep | 0 | Mar | 2022 | 0.0081731 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-03-09 13:00 | 2022-03-09 13:51 | 1 | 000:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE TESO TENSOR | P22030900076 | New_Event |  |  | Include | Wildlife | 51 | 2022-03-09 | 51 | keep | 0 | Mar | 2022 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-09 13:40 | 2022-03-09 15:12 | 10 | 001:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO CON DERRAME DE ACEITE DE 37.5KV A 4.16KV POR UNO DE 50KVA A 4.16KV | P22030900078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 92 | 2022-03-09 | 920 | keep | 0 | Mar | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-09 13:43 | 2022-03-09 15:38 | 10 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22030900108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2022-03-09 | 1150 | keep | 0 | Mar | 2022 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-09 13:52 | 2022-03-09 21:29 | 80 | 007:37 | P | DESGANCHE | 3X200 EN CORTE DE LINEA SE DESGANCHO | B22030900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2022-03-09 | 36560 | keep | 0 | Mar | 2022 | 0.024901 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-09 13:54 | 2022-03-09 17:35 | 32 | 003:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X40 EN C/L Y SE REMPLAZO AISLADOR | B22030900030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 221 | 2022-03-09 | 7072 | keep | 0 | Mar | 2022 | 0.0048167 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2022-03-09 13:55 | 2022-03-09 17:13 | 11 | 003:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR SE REPARO CABLE EN BARRA DE PEDESTAL | S22030700283 | New_Event | Secondary Wire Down | Include | Include | Equipment | 198 | 2022-03-09 | 2178 | keep | 0 | Mar | 2022 | 0.0014834 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-03-09 13:57 | 2022-03-09 16:04 | 90 | 002:07 | P | DESGANCHE | 2 X 100 Y 1 X 80 EN CORTES DE LINEA REQUIERE DESGANCHE | M22030900096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-03-09 | 11430 | keep | 0 | Mar | 2022 | 0.0077849 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-03-09 13:59 | 2022-03-09 16:09 | 150 | 002:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-03-09 | 19500 | keep | 0 | Mar | 2022 | 0.013281 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-03-09 14:03 | 2022-03-09 14:40 | 30 | 000:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y REPARO PUENTE ABIERTO | C22030700144 | New_Event | Wire Down | Include | Include | Equipment | 37 | 2022-03-09 | 1110 | keep | 0 | Mar | 2022 | 0.00075602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-03-09 14:12 | 2022-03-09 14:13 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22030900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 470 | keep | 0 | Mar | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
AGUADILLA | 2022-03-09 14:12 | 2022-03-09 14:13 | 1345 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 7003-01 QUE ESTA LLEVANDO LA CARGA DEL 7003-02 | M22030900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 1345 | keep | 0 | Mar | 2022 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
MAYAGÃœEZ | 2022-03-09 14:19 | 2022-03-09 18:43 | 600 | 004:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 1 X 100 Y 1 X 80 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M22030900102 | New_Event | Bad Weather | Include | Include | Weather | 264 | 2022-03-09 | 158400 | keep | 0 | Mar | 2022 | 0.10789 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
HUMACAO | 2022-03-09 14:28 | 2022-03-09 15:34 | 70 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 25 EN CORTES DE LINEAS | C22030900169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-03-09 | 4620 | keep | 0 | Mar | 2022 | 0.0031467 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-03-09 14:33 | 2022-03-09 19:19 | 10 | 004:46 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR PM DE 50KVA X 50KVA | A22030800227 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 286 | 2022-03-09 | 2860 | keep | 0 | Mar | 2022 | 0.0019479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-09 14:49 | 2022-03-09 17:30 | 108 | 002:41 | P | NO SE REPORTO CAUSA | 1X100 DE RISER @ SU-3 | B22030900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-03-09 | 17388 | keep | 0 | Mar | 2022 | 0.011843 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-03-09 14:55 | 2022-03-09 17:00 | 9 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S22030900233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-03-09 | 1125 | keep | 0 | Mar | 2022 | 0.00076623 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-03-09 15:06 | 2022-03-09 16:20 | 9 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO EN XMR Y CONECTORES EN LINEA SECUNDARIA | C22030900171 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2022-03-09 | 666 | keep | 0 | Mar | 2022 | 0.00045361 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-03-09 15:27 | 2022-03-09 18:45 | 10 | 003:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO CAJA AVERIADA | R22030900064 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-03-09 | 1980 | keep | 0 | Mar | 2022 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-09 15:28 | 2022-03-09 15:41 | 222 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LA LINEA SE CERRO POR CONTROL LLEVA LA CARGA DEL 1909-09 | B22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-03-09 | 2886 | keep | 0 | Mar | 2022 | 0.0019656 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-03-09 15:28 | 2022-03-09 15:41 | 4456 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1907-03 SE VERIFICO PERSONAL FUERA DE LA LINEA SE CERRO POR CONTROL LLEVA TRANSFERIDA LA CARGA DEL 1909-09 | B22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-03-09 | 57928 | keep | 0 | Mar | 2022 | 0.039454 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
FAJARDO | 2022-03-09 15:46 | 2022-03-09 18:46 | 7 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R22030900067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-03-09 | 1260 | keep | 0 | Mar | 2022 | 0.00085818 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-09 15:52 | 2022-03-09 15:53 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 2302 | keep | 0 | Mar | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
PONCE | 2022-03-09 16:10 | 2022-03-09 16:54 | 50 | 000:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO EN NUETRAL COMUN | P22030900102 | New_Event | Wire Down | Include | Include | Equipment | 44 | 2022-03-09 | 2200 | keep | 0 | Mar | 2022 | 0.0014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-09 16:12 | 2022-03-09 19:24 | 15 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN XMR CRUCE X AVE | R22030900069 | New_Event |  |  | Include | Wildlife | 192 | 2022-03-09 | 2880 | keep | 0 | Mar | 2022 | 0.0019616 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-09 16:37 | 2022-03-09 20:11 | 110 | 003:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C22030900183 | New_Event | Cutout Failure | Include | Include | Equipment | 214 | 2022-03-09 | 23540 | keep | 0 | Mar | 2022 | 0.016033 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2022-03-09 16:39 | 2022-03-09 16:44 | 676 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-03-09 | 3380 | keep | 0 | Mar | 2022 | 0.0023021 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-03-09 16:39 | 2022-03-09 16:44 | 2873 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-03-09 | 14365 | keep | 0 | Mar | 2022 | 0.0097839 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2022-03-09 16:39 | 2022-03-09 16:44 | 3902 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C22030900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2022-03-09 | 19510 | keep | 0 | Mar | 2022 | 0.013288 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
CAGUAS | 2022-03-09 16:49 | 2022-03-10 11:43 | 6 | 018:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C22030900194 | New_Event |  |  | Include | Wildlife | 1134 | 2022-03-09 | 6804 | keep | 0 | Mar | 2022 | 0.0046342 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-09 16:58 | 2022-03-09 18:25 | 80 | 001:27 | P | DESGANCHE | 1 X 25 Y 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22030900113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-03-09 | 6960 | keep | 0 | Mar | 2022 | 0.0047404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-09 17:00 | 2022-03-09 21:35 | 150 | 004:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA PUENTE ABIERTO | C22030900196 | New_Event | Wire Down | Include | Include | Equipment | 275 | 2022-03-09 | 41250 | keep | 0 | Mar | 2022 | 0.028095 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-03-09 17:22 | 2022-03-09 18:08 | 90 | 000:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A RISER EN PROVICIONAL AEREO | P22030900106 | New_Event | Wire Down | Include | Include | Equipment | 46 | 2022-03-09 | 4140 | keep | 0 | Mar | 2022 | 0.0028197 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-03-09 17:43 | 2022-03-09 17:44 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030900109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 969 | keep | 0 | Mar | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2022-03-09 17:47 | 2022-03-10 17:19 | 1 | 023:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO Y SE REALIZO DESGANCHE | A22030900114 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1412 | 2022-03-09 | 1412 | keep | 0 | Mar | 2022 | 0.00096171 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-09 17:54 | 2022-03-09 17:55 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C22030900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 3420 | keep | 0 | Mar | 2022 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
MAYAGÃœEZ | 2022-03-09 17:55 | 2022-03-09 19:45 | 8 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22030900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2022-03-09 | 880 | keep | 0 | Mar | 2022 | 0.00059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-03-09 18:03 | 2022-03-09 18:04 | 676 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C22030900000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-03-09 | 676 | keep | 0 | Mar | 2022 | 0.00046042 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-09 18:03 | 2022-03-09 18:04 | 2873 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C22030900000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-03-09 | 2873 | keep | 0 | Mar | 2022 | 0.0019568 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-09 18:03 | 2022-03-09 18:04 | 3902 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C22030900000 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-03-09 | 3902 | keep | 0 | Mar | 2022 | 0.0026576 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-09 18:04 | 2022-03-09 23:59 | 158 | 005:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN C/L SE LEVANTO CONDUCTOR Y SE REEMPLAZO HERRAJES Y PIN POLE TOP | C22030900209 | New_Event | Wire Down | Include | Include | Equipment | 355 | 2022-03-09 | 56090 | keep | 0 | Mar | 2022 | 0.038203 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
CAGUAS | 2022-03-09 18:10 | 2022-03-09 19:24 | 870 | 001:14 | T | DESGANCHE | SE ABRIO MACHETES EN CARR 172 KM 16.9 CERTENEJAS 40% EN SERVICIO | C22030900213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-03-09 | 64380 | keep | 0 | Mar | 2022 | 0.043849 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-03-09 18:11 | 2022-03-09 20:47 | 10 | 002:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO PEDESTAL | B22030900049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 156 | 2022-03-09 | 1560 | keep | 0 | Mar | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-09 18:13 | 2022-03-09 23:32 | 30 | 005:19 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE ARBOL | B22030900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2022-03-09 | 9570 | keep | 0 | Mar | 2022 | 0.0065181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-03-09 18:20 | 2022-03-09 20:04 | 8 | 001:44 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR PARA REALIZAR DESGANCHE Y REPARAR LINEA SECUNDARIA | P22030900103 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 104 | 2022-03-09 | 832 | keep | 0 | Mar | 2022 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-03-09 18:43 | 2022-03-09 21:31 | 80 | 002:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22030900147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-03-09 | 13440 | keep | 0 | Mar | 2022 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-03-09 18:52 | 2022-03-09 20:48 | 15 | 001:56 | P | DESGANCHE | 1 X 30 EN C/L | R22030900074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-03-09 | 1740 | keep | 0 | Mar | 2022 | 0.0011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-03-09 18:58 | 2022-03-10 12:01 | 180 | 017:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M22030900149 | New_Event | Wire Down | Include | Include | Equipment | 1023 | 2022-03-09 | 184140 | keep | 0 | Mar | 2022 | 0.12542 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
GUAYAMA | 2022-03-09 19:11 | 2022-03-09 20:49 | 20 | 001:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22030900116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-03-09 | 1960 | keep | 0 | Mar | 2022 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-09 19:24 | 2022-03-09 20:20 | 522 | 000:56 | P | DESGANCHE | INTERRUPTOR SECCIONALIZADO SE ABRIO MACHETES EN CARR 172 KM 15.5 CERTENEJAS, CIDRA 60% EN SERVICIO | C22030900213 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-03-09 | 29232 | keep | 0 | Mar | 2022 | 0.01991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-09 19:32 | 2022-03-10 08:27 | 8 | 012:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | A22030900116 | New_Event | Cutout Failure | Include | Include | Equipment | 775 | 2022-03-09 | 6200 | keep | 0 | Mar | 2022 | 0.0042228 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-03-09 20:06 | 2022-03-10 09:45 | 80 | 013:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22030900273 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 819 | 2022-03-09 | 65520 | keep | 0 | Mar | 2022 | 0.044625 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-09 20:07 | 2022-03-10 00:01 | 80 | 003:54 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE DEJO PUENTES PRIMARIOS ABIERTOS POR POSTE PRIMARIO PARTIDO | A22030900118 | New_Event | Defective Pole | Include | Include | Equipment | 234 | 2022-03-09 | 18720 | keep | 0 | Mar | 2022 | 0.01275 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-09 20:20 | 2022-03-09 21:13 | 348 | 000:53 | P | DESGANCHE | SE ABRIO MACHETES EN CARR 787 FTE HOSPITAL PANAMERICANO PARA SECCIONALIZAR BAMBUAS SOBRE LINEAS Y REPARAR PUENTE ABIERTO 80% EN SERVICIO | C22030900213 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-03-09 | 18444 | keep | 0 | Mar | 2022 | 0.012562 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-09 20:23 | 2022-03-10 12:34 | 50 | 016:11 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22030900167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 971 | 2022-03-09 | 48550 | keep | 0 | Mar | 2022 | 0.033067 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-09 20:23 | 2022-03-10 01:59 | 300 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO CONDUCTOR EN EL SUELO | B22030900055 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2022-03-09 | 100800 | keep | 0 | Mar | 2022 | 0.068654 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-03-09 20:34 | 2022-03-09 22:19 | 50 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO PORTAFUSIBLE | S22030900286 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2022-03-09 | 5250 | keep | 0 | Mar | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-09 20:42 | 2022-03-09 20:43 | 5668 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22030900079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 5668 | keep | 0 | Mar | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
PONCE | 2022-03-09 21:05 | 2022-03-09 21:06 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22030900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-09 | 2379 | keep | 0 | Mar | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CAGUAS | 2022-03-09 21:13 | 2022-03-09 23:10 | 174 | 001:57 | P | DESGANCHE | SE CERRARON MACHETES EN CARR 787 FTE HOSPITAL PANAMERICANO 100% EN SERVICIO | C22030900213 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-03-09 | 20358 | keep | 0 | Mar | 2022 | 0.013866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-09 21:39 | 2022-03-10 11:40 | 300 | 014:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN C/L SE REPARO LIGADURA EN AISLADOR Y SE DESGANCHO | B22030900068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 841 | 2022-03-09 | 252300 | keep | 0 | Mar | 2022 | 0.17184 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-03-09 23:32 | 2022-03-10 09:42 | 60 | 010:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | R22030900082 | New_Event | Cutout Failure | Include | Include | Equipment | 610 | 2022-03-09 | 36600 | keep | 0 | Mar | 2022 | 0.024928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-09 23:38 | 2022-03-10 20:51 | 2174 | 021:13 | T | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO DE POSTE A CAUSA DE ACCIDENTE VEHICULAR | M22030900181 | New_Event |  |  | Include | Wildlife | 1273 | 2022-03-09 | 2767502 | keep | 0 | Mar | 2022 | 1.8849 | 0.0014807 | Sustained | FALSE | FALSE | Not_TMED_Event | 2174
SAN JUAN | 2022-03-10 00:50 | 2022-03-11 09:00 | 20 | 032:10 | P | NO SE REPORTO CAUSA | SE REEMPLAZO 1 X 20 EN RISER | S22031000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1930 | 2022-03-10 | 38600 | keep | 0 | Mar | 2022 | 0.02629 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-10 01:15 | 2022-03-10 03:10 | 514 | 001:55 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1520-05 | S22031000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-03-10 | 59110 | keep | 0 | Mar | 2022 | 0.04026 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-03-10 01:15 | 2022-03-10 03:41 | 752 | 002:26 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO Y SE CERRARON MACHETES DE AMARRE CONTRA EL 1520-5 | S22031000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-03-10 | 109792 | keep | 0 | Mar | 2022 | 0.074779 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-03-10 01:15 | 2022-03-10 03:10 | 68 | 001:55 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE ABRIERON MACHETES DE AMARRE CONTRA 1520-04 Y SE CERRO POR SCADA LLEVA 1520-01 | S22031000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-03-10 | 7820 | keep | 0 | Mar | 2022 | 0.0053262 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CAGUAS | 2022-03-10 01:56 | 2022-03-10 10:16 | 200 | 008:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22031000003 | New_Event | Cutout Failure | Include | Include | Equipment | 500 | 2022-03-10 | 100000 | keep | 0 | Mar | 2022 | 0.06811 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-10 01:59 | 2022-03-10 02:04 | 3295 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR PERSONAL REALIZANDO PRUEBAS A C/L SE VERIFICIO PERSONAL FUERA Y SE CERRO POR SCADA | B22031000000 | New_Event | Wire Down | Include | Include | Equipment | 5 | 2022-03-10 | 16475 | keep | 0 | Mar | 2022 | 0.011221 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-03-10 02:04 | 2022-03-10 05:08 | 300 | 003:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO CONDUCTOR EN EL SUELO | B22030900055 | Partial_restoration | Wire Down | Include | Include | Equipment | 184 | 2022-03-10 | 55200 | keep | 0 | Mar | 2022 | 0.037596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-10 02:40 | 2022-03-10 07:11 | 200 | 004:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22031000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-03-10 | 54200 | keep | 0 | Mar | 2022 | 0.036915 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-03-10 03:12 | 2022-03-10 12:40 | 20 | 009:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22031000001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 568 | 2022-03-10 | 11360 | keep | 0 | Mar | 2022 | 0.0077372 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-10 03:25 | 2022-03-10 11:15 | 50 | 007:50 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER. AVERIA NUEVA DE T-517 @ T-518 Y AVERIA VIEJA DE T-519 @ T-520. SE QUEDO FUERA T-518 & T-519. REFERIDO A CONSTRUCCION | B22031000016 | New_Event | UG Cable Fault | Include | Include | Equipment | 470 | 2022-03-10 | 23500 | keep | 0 | Mar | 2022 | 0.016006 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-10 03:41 | 2022-03-10 04:12 | 300 | 000:31 | P | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CONDICION Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S22031000003 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-03-10 | 9300 | keep | 0 | Mar | 2022 | 0.0063342 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-10 03:59 | 2022-03-10 06:30 | 100 | 002:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22031000021 | New_Event |  |  | Include | Wildlife | 151 | 2022-03-10 | 15100 | keep | 0 | Mar | 2022 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-10 04:22 | 2022-03-10 04:23 | 528 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22031000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 528 | keep | 0 | Mar | 2022 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
BAYAMON | 2022-03-10 05:08 | 2022-03-10 07:14 | 1676 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES MEDIANTE GOI BY-220310-01 PARA LEVANTAR DOS FASES EN EL SUELO | B22030900055 | Additional_clients | Wire Down | Include | Include | Equipment | 126 | 2022-03-10 | 211176 | keep | 0 | Mar | 2022 | 0.14383 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-10 05:11 | 2022-03-10 09:39 | 100 | 004:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22031000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-03-10 | 26800 | keep | 0 | Mar | 2022 | 0.018253 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-10 06:53 | 2022-03-10 10:22 | 120 | 003:29 | P | NO SE REPORTO CAUSA | 2 X 100 SMU-20 EN SU-DVC5 | R22031000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2022-03-10 | 25080 | keep | 0 | Mar | 2022 | 0.017082 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-03-10 06:57 | 2022-03-10 10:12 | 44 | 003:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LAS LINEAS | M22031000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-03-10 | 8580 | keep | 0 | Mar | 2022 | 0.0058438 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
ARECIBO | 2022-03-10 07:02 | 2022-03-10 12:49 | 15 | 005:47 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR 25 KVA | A22031000004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 347 | 2022-03-10 | 5205 | keep | 0 | Mar | 2022 | 0.0035451 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-10 07:11 | 2022-03-10 09:45 | 60 | 002:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22031000006 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-03-10 | 9240 | keep | 0 | Mar | 2022 | 0.0062933 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-10 07:32 | 2022-03-10 17:06 | 60 | 009:34 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN SALIDA DE CONVERTIDOR | M22031000007 | New_Event | Switch Failure | Include | Include | Equipment | 574 | 2022-03-10 | 34440 | keep | 0 | Mar | 2022 | 0.023457 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-10 07:34 | 2022-03-10 09:25 | 16 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A22031000005 | New_Event |  |  | Include | Wildlife | 111 | 2022-03-10 | 1776 | keep | 0 | Mar | 2022 | 0.0012096 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-03-10 07:43 | 2022-03-10 13:54 | 60 | 006:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | R22031000014 | New_Event |  |  | Include | Wildlife | 371 | 2022-03-10 | 22260 | keep | 0 | Mar | 2022 | 0.015161 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-03-10 07:51 | 2022-03-10 07:52 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031000056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 2859 | keep | 0 | Mar | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
VEGA BAJA | 2022-03-10 08:02 | 2022-03-10 14:09 | 20 | 006:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22031000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2022-03-10 | 7340 | keep | 0 | Mar | 2022 | 0.0049992 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-10 08:16 | 2022-03-10 11:06 | 50 | 002:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L SE ENCONTRO PALOMA | R22031000018 | New_Event |  |  | Include | Wildlife | 170 | 2022-03-10 | 8500 | keep | 0 | Mar | 2022 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-10 08:23 | 2022-03-10 11:34 | 50 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO SE CERRO CORTE DE LINEA | A22031000008 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2022-03-10 | 9550 | keep | 0 | Mar | 2022 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-10 08:25 | 2022-03-10 14:56 | 15 | 006:31 | P | DESGANCHE | 1X10 EN TRANSFORMADOR | S22031000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2022-03-10 | 5865 | keep | 0 | Mar | 2022 | 0.0039946 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-03-10 08:36 | 2022-03-10 08:37 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 1894 | keep | 0 | Mar | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
GUAYAMA | 2022-03-10 08:40 | 2022-03-10 08:50 | 25 | 000:10 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO DE MACHETES QUEMADOS | P22031000010 | New_Event | Switch Failure | Include | Include | Equipment | 10 | 2022-03-10 | 250 | keep | 0 | Mar | 2022 | 0.00017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-03-10 08:48 | 2022-03-10 17:20 | 10 | 008:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | M22031000030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 512 | 2022-03-10 | 5120 | keep | 0 | Mar | 2022 | 0.0034872 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-10 09:00 | 2022-03-10 10:30 | 250 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO TRAMO PARA CERRAR PUENTE ABIERTO SJ-220210-01 | S22031000120 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2022-03-10 | 22500 | keep | 0 | Mar | 2022 | 0.015325 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-03-10 09:00 | 2022-03-10 14:23 | 1 | 005:23 | P | NO SE REPORTO CAUSA | 1X25 EN TRANSFORMADOR | S22031000077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 323 | 2022-03-10 | 323 | keep | 0 | Mar | 2022 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-10 09:01 | 2022-03-10 09:02 | 10211 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR CARGA POR 1206-3 | S22031000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-03-10 | 10211 | keep | 0 | Mar | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-03-10 09:01 | 2022-03-10 09:02 | 4133 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | S22031000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-03-10 | 4133 | keep | 0 | Mar | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-03-10 09:02 | 2022-03-10 17:10 | 65 | 008:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X100 EN CORTE DE LINEA Y SE INSTALARON SEPARADORES | S22031000140 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 488 | 2022-03-10 | 31720 | keep | 0 | Mar | 2022 | 0.021604 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-03-10 10:10 | 2022-03-10 16:46 | 1 | 006:36 | P | NO SE REPORTO CAUSA | 1X80 EN EL SU-11 | S22031000105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 396 | 2022-03-10 | 396 | keep | 0 | Mar | 2022 | 0.00026971 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-10 10:20 | 2022-03-10 15:24 | 60 | 005:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA. MENSAJERO DE FIBRA OPTICA CRUZADO CON LINEA PRIMARIA | C22031000079 | New_Event |  |  | Include | Wildlife | 304 | 2022-03-10 | 18240 | keep | 0 | Mar | 2022 | 0.012423 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-03-10 10:26 | 2022-03-10 15:06 | 60 | 004:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE REMPLAZO BAJANTE EN PROVISIONAL HACIA T-240 | R22031000046 | New_Event | Wire Down | Include | Include | Equipment | 280 | 2022-03-10 | 16800 | keep | 0 | Mar | 2022 | 0.011442 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-10 10:45 | 2022-03-10 14:38 | 1 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22031000039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2022-03-10 | 233 | keep | 0 | Mar | 2022 | 0.0001587 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-10 10:56 | 2022-03-10 13:30 | 40 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22031000059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-03-10 | 6160 | keep | 0 | Mar | 2022 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-10 11:12 | 2022-03-10 11:13 | 2694 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR | A22031000046 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-03-10 | 2694 | keep | 0 | Mar | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2022-03-10 11:13 | 2022-03-10 15:23 | 100 | 004:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA Y SE REMPLAZO AISLADOR ROTO | A22031000052 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 250 | 2022-03-10 | 25000 | keep | 0 | Mar | 2022 | 0.017027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-10 11:14 | 2022-03-10 11:15 | 2076 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1718-03 LLEVANDO 40% DEL 1710-05 | B22031000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 2076 | keep | 0 | Mar | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-03-10 11:14 | 2022-03-10 11:15 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1718-03 LLEVANDO 40% DEL 1710-05 | B22031000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 2605 | keep | 0 | Mar | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-03-10 11:15 | 2022-03-11 14:54 | 20 | 027:39 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA ENTRE T-517 Y T519 | B22031000016 | New_Event | UG Cable Fault | Include | Include | Equipment | 1659 | 2022-03-10 | 33180 | keep | 0 | Mar | 2022 | 0.022599 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-03-10 11:17 | 2022-03-10 12:34 | 100 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031000049 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2022-03-10 | 7700 | keep | 0 | Mar | 2022 | 0.0052444 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-10 11:26 | 2022-03-10 13:39 | 100 | 002:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA AVERIADA | C22031000086 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2022-03-10 | 13300 | keep | 0 | Mar | 2022 | 0.0090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-03-10 11:27 | 2022-03-10 13:10 | 14 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 30 1 X 15 EN RISER NO SE ENCONTRO NADA | P22031000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-03-10 | 1442 | keep | 0 | Mar | 2022 | 0.00098214 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-03-10 11:46 | 2022-03-11 13:40 | 100 | 025:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22031000122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1554 | 2022-03-10 | 155400 | keep | 0 | Mar | 2022 | 0.10584 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-10 11:51 | 2022-03-10 19:45 | 40 | 007:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REEMPLAZO CAJA QUEMADA | M22031000055 | New_Event | Cutout Failure | Include | Include | Equipment | 474 | 2022-03-10 | 18960 | keep | 0 | Mar | 2022 | 0.012914 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-10 11:58 | 2022-03-10 13:15 | 80 | 001:17 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X80 EN C/L | S22031000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-03-10 | 6160 | keep | 0 | Mar | 2022 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-10 12:00 | 2022-03-10 12:40 | 1 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22031000123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-03-10 | 40 | keep | 0 | Mar | 2022 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-10 12:10 | 2022-03-10 12:57 | 1 | 000:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE PRIMARIO EN MONTURA TRIFASICA | P22031000013 | New_Event | Wire Down | Include | Include | Equipment | 47 | 2022-03-10 | 47 | keep | 0 | Mar | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-10 12:26 | 2022-03-10 16:50 | 10 | 004:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | A22031000058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 264 | 2022-03-10 | 2640 | keep | 0 | Mar | 2022 | 0.0017981 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-10 12:55 | 2022-03-10 17:39 | 40 | 004:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | C22031000092 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2022-03-10 | 11360 | keep | 0 | Mar | 2022 | 0.0077372 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-10 13:03 | 2022-03-10 15:03 | 40 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L PERSONAL DE CABLE TV DESGANCHANDO TUMBARON RAMA | R22031000064 | New_Event |  |  | Include | Wildlife | 120 | 2022-03-10 | 4800 | keep | 0 | Mar | 2022 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-10 13:10 | 2022-03-10 15:53 | 15 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22031000069 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2022-03-10 | 2445 | keep | 0 | Mar | 2022 | 0.0016653 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-10 13:24 | 2022-03-10 20:50 | 80 | 007:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | A22031000063 | New_Event | Cutout Failure | Include | Include | Equipment | 446 | 2022-03-10 | 35680 | keep | 0 | Mar | 2022 | 0.024301 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-10 13:29 | 2022-03-10 17:57 | 40 | 004:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22031000097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-03-10 | 10720 | keep | 0 | Mar | 2022 | 0.0073013 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-10 13:40 | 2022-03-10 16:21 | 50 | 002:41 | P | DESGANCHE | 1X80 EN CORTE DE LINEA | S22031000138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-03-10 | 8050 | keep | 0 | Mar | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-10 13:56 | 2022-03-10 16:01 | 29 | 002:05 | P | NO SE REPORTO CAUSA | 1X20 EN TRANSFORMADOR | S22031000139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-03-10 | 3625 | keep | 0 | Mar | 2022 | 0.002469 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
YAUCO | 2022-03-10 14:05 | 2022-03-10 15:00 | 8 | 000:55 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR REALIZAR DESGANCHE SECUNDARIO Y LEVANTAR SECUNDARIA DEL PISO | P22031000018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 55 | 2022-03-10 | 440 | keep | 0 | Mar | 2022 | 0.00029968 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-03-10 14:07 | 2022-03-10 19:29 | 12 | 005:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | A22031000067 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2022-03-10 | 3864 | keep | 0 | Mar | 2022 | 0.0026318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-03-10 14:11 | 2022-03-10 15:03 | 969 | 000:52 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. NO SE REPORTO LA CAUSA | P22031000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-03-10 | 50388 | keep | 0 | Mar | 2022 | 0.034319 | 0.00065998 | Sustained | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2022-03-10 14:24 | 2022-03-10 18:57 | 20 | 004:33 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22031000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2022-03-10 | 5460 | keep | 0 | Mar | 2022 | 0.0037188 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-10 14:25 | 2022-03-10 17:06 | 50 | 002:41 | P | DESGANCHE | 1 X 65 EN C/L | R22031000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-03-10 | 8050 | keep | 0 | Mar | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-10 14:25 | 2022-03-10 14:26 | 426 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031000026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 426 | keep | 0 | Mar | 2022 | 0.00029015 | 0.00029015 | Momentary | FALSE | FALSE | Not_TMED_Event | 426
PONCE | 2022-03-10 14:26 | 2022-03-10 18:18 | 213 | 003:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE EN TRONCAL DEL ALIMENTADOR Y FIJAR LINEA A AISLADOR SE CERRO N/O CON EL 4501-01 PARA TRANSFERIR EL 50% DE LA CARGA | P22031000050 | New_Event | Wire Down | Include | Include | Equipment | 232 | 2022-03-10 | 49416 | keep | 0 | Mar | 2022 | 0.033657 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
CAGUAS | 2022-03-10 14:35 | 2022-03-10 14:44 | 1 | 000:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE XMR | C22031000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-03-10 | 9 | keep | 0 | Mar | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-10 14:56 | 2022-03-10 20:29 | 50 | 005:33 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22031000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2022-03-10 | 16650 | keep | 0 | Mar | 2022 | 0.01134 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-10 14:57 | 2022-03-10 23:05 | 30 | 008:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22031000086 | New_Event | Bad Weather | Include | Include | Weather | 488 | 2022-03-10 | 14640 | keep | 0 | Mar | 2022 | 0.0099712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-10 15:04 | 2022-03-10 17:43 | 100 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M22031000091 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2022-03-10 | 15900 | keep | 0 | Mar | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-10 15:23 | 2022-03-10 17:27 | 2694 | 002:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE ABRIO MACHETES PARA SECCIONALIZAR AVERIA DE AISLADORES ROTOS Y SE CERRO EL INTERRUPTOR | A22031000078 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 124 | 2022-03-10 | 334056 | keep | 0 | Mar | 2022 | 0.22752 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-03-10 15:36 | 2022-03-10 16:47 | 1 | 001:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22031000079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-03-10 | 71 | keep | 0 | Mar | 2022 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-10 15:38 | 2022-03-10 16:47 | 100 | 001:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22031000112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-03-10 | 6900 | keep | 0 | Mar | 2022 | 0.0046996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-03-10 15:46 | 2022-03-10 15:47 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031000032 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 969 | keep | 0 | Mar | 2022 | 0.00065998 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-10 15:56 | 2022-03-11 00:11 | 40 | 008:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22031000104 | New_Event | Bad Weather | Include | Include | Weather | 495 | 2022-03-10 | 19800 | keep | 0 | Mar | 2022 | 0.013486 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-10 16:07 | 2022-03-10 17:36 | 137 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO ENCONTRARON CAUSA PARA EL FUSIBLE FUNDIDO | A22031000088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-03-10 | 12193 | keep | 0 | Mar | 2022 | 0.0083046 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-03-10 16:26 | 2022-03-10 18:34 | 42 | 002:08 | P | DESGANCHE | 1X100 EN CORTE DE LINEA | S22031000154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-10 | 5376 | keep | 0 | Mar | 2022 | 0.0036616 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
VEGA BAJA | 2022-03-10 16:29 | 2022-03-10 19:15 | 30 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22031000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-03-10 | 4980 | keep | 0 | Mar | 2022 | 0.0033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-10 16:31 | 2022-03-10 18:42 | 20 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | M22031000112 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2022-03-10 | 2620 | keep | 0 | Mar | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-10 16:50 | 2022-03-11 13:43 | 30 | 020:53 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE COLOCO BOLSA POR DERRAME DE ACEITE. SE REFIRIO A CONSTRUCCION PARA SU REEMPLAZO | B22031000079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1253 | 2022-03-10 | 37590 | keep | 0 | Mar | 2022 | 0.025602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-10 17:01 | 2022-03-10 17:04 | 234 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22031000057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-10 | 702 | keep | 0 | Mar | 2022 | 0.00047813 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2022-03-10 17:01 | 2022-03-10 17:04 | 2468 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 200 | P22031000057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-10 | 7404 | keep | 0 | Mar | 2022 | 0.0050428 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
BAYAMON | 2022-03-10 17:11 | 2022-03-10 17:13 | 959 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO ALIMENTADOR 1904-07 LLEVANDO LAS CARGAS DEL 1901-01 Y 1901-04 A PETICION DE HECTOR DIAZ POR SEGURIDAD PARA PODER ABRIR LAS CAJAS SIN VOLTAJE POR FUERTES LLUVIAS | S22031000166 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-03-10 | 1918 | keep | 0 | Mar | 2022 | 0.0013063 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-03-10 17:11 | 2022-03-10 17:13 | 1264 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO ALIMENTADOR 1904-07 LLEVANDO LAS CARGAS DEL 1901-01 Y 1901-04 A PETICION DE HECTOR DIAZ POR SEGURIDAD PARA PODER ABRIR LAS CAJAS SIN VOLTAJE POR FUERTES LLUVIAS | S22031000166 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-03-10 | 2528 | keep | 0 | Mar | 2022 | 0.0017218 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2022-03-10 17:12 | 2022-03-10 21:37 | 10 | 004:25 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN XMR SE DESGANCHO ENREDADERA | S22031000165 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 265 | 2022-03-10 | 2650 | keep | 0 | Mar | 2022 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-10 17:13 | 2022-03-10 18:00 | 300 | 000:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA AVERIADA | S22031000152 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 47 | 2022-03-10 | 14100 | keep | 0 | Mar | 2022 | 0.0096034 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-03-10 17:15 | 2022-03-10 17:54 | 7 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22031000096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-03-10 | 273 | keep | 0 | Mar | 2022 | 0.00018594 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-03-10 17:27 | 2022-03-10 18:20 | 1347 | 000:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22031000078 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 53 | 2022-03-10 | 71391 | keep | 0 | Mar | 2022 | 0.048624 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-10 17:29 | 2022-03-10 20:10 | 3 | 002:41 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN RISER Y 1 X 80 SU SE ELIMINO PARARRAYO | R22031000085 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 161 | 2022-03-10 | 483 | keep | 0 | Mar | 2022 | 0.00032897 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-10 17:29 | 2022-03-10 19:01 | 65 | 001:32 | P | PARARRAYOS DEFECTUOSO | 3 X 100 EN C/L Y 2X 40 EN OTRO C/L SE ELIMINO PARARRAYOS | B22031000084 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 92 | 2022-03-10 | 5980 | keep | 0 | Mar | 2022 | 0.004073 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-03-10 17:31 | 2022-03-10 19:40 | 50 | 002:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO DISCOS | R22031000084 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2022-03-10 | 6450 | keep | 0 | Mar | 2022 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-10 17:34 | 2022-03-10 18:12 | 1 | 000:38 | P | DESGANCHE | 1X50 EN CORTE DE LINEA | S22031000169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-03-10 | 38 | keep | 0 | Mar | 2022 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-10 17:42 | 2022-03-11 15:50 | 100 | 022:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22031000125 | New_Event | Wire Down | Include | Include | Equipment | 1328 | 2022-03-10 | 132800 | keep | 0 | Mar | 2022 | 0.090449 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-03-10 17:51 | 2022-03-10 19:30 | 25 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P22031000061 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2022-03-10 | 2475 | keep | 0 | Mar | 2022 | 0.0016857 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-10 17:54 | 2022-03-10 19:21 | 28 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22031000123 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-03-10 | 2436 | keep | 0 | Mar | 2022 | 0.0016591 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2022-03-10 18:02 | 2022-03-10 18:43 | 10 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE SUBIERON TAPS 1 @ 3 Y SE REPARARRON CONEXIONES SECUNDARIAS | B22031000097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2022-03-10 | 410 | keep | 0 | Mar | 2022 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-10 18:06 | 2022-03-10 18:07 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 2113 | keep | 0 | Mar | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-03-10 18:18 | 2022-03-10 18:49 | 213 | 000:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO LINEA A AISLADOR, SE CERRO PUENTE EN TRONCAL Y SE CERRO INTERRUPTOR | P22031000050 | Partial_restoration | Wire Down | Include | Include | Equipment | 31 | 2022-03-10 | 6603 | keep | 0 | Mar | 2022 | 0.0044973 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-10 18:20 | 2022-03-10 21:34 | 10 | 003:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS | M22031000131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-03-10 | 1940 | keep | 0 | Mar | 2022 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-10 18:35 | 2022-03-10 18:39 | 1117 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6404-02 LLEVA CARGA DEL 6404-01 | M22031000136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-10 | 4468 | keep | 0 | Mar | 2022 | 0.0030431 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-03-10 18:35 | 2022-03-10 18:39 | 1671 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22031000136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-10 | 6684 | keep | 0 | Mar | 2022 | 0.0045524 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
BAYAMON | 2022-03-10 18:40 | 2022-03-10 19:22 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22031000106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-03-10 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-10 18:45 | 2022-03-10 20:30 | 6 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN XMR CRICE DE AVE | R22031000086 | New_Event |  |  | Include | Wildlife | 105 | 2022-03-10 | 630 | keep | 0 | Mar | 2022 | 0.00042909 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-10 18:51 | 2022-03-10 18:52 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22031000121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-10 | 5042 | keep | 0 | Mar | 2022 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BAYAMON | 2022-03-10 19:01 | 2022-03-10 19:25 | 5809 | 000:24 | T | PARARRAYOS DEFECTUOSO | DISPARO 1716-03 LLEVANDO EL 1710-01 AL CERRAR FUSIBLES EN ORDEN 7032. SE ABRIO CORTE DE LINEA NUEVAMENTE Y SE CERRO INTERRUPTOR POR SCADA PARA TRABAJAR AVERIA RADIAL | B22031000110 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 24 | 2022-03-10 | 139416 | keep | 0 | Mar | 2022 | 0.094956 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-10 19:01 | 2022-03-10 19:25 | 1812 | 000:24 | T | PARARRAYOS DEFECTUOSO | DISPARO 1716-03 LLEVANDO EL 1710-01 AL CERRAR FUSIBLES EN ORDEN 7032. SE ABRIO CORTE DE LINEA NUEVAMENTE Y SE CERRO INTERRUPTOR POR SCADA PARA TRABAJAR AVERIA RADIAL | B22031000110 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 24 | 2022-03-10 | 43488 | keep | 0 | Mar | 2022 | 0.029619 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2022-03-10 19:03 | 2022-03-10 20:51 | 1 | 001:48 | P | SECUNDARIA/DESGANCHE | 1 X 20 Y 1 X 25 EN SUBESTACION PRIVADA SE REALIZO DESGANCHE DE ARBOL EN SECUNDARIA | B22031000000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 108 | 2022-03-10 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-10 19:07 | 2022-03-11 06:15 | 20 | 011:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE | P22031000065 | New_Event |  |  | Include | Wildlife | 668 | 2022-03-10 | 13360 | keep | 0 | Mar | 2022 | 0.0090994 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-10 19:25 | 2022-03-10 23:19 | 65 | 003:54 | P | PARARRAYOS DEFECTUOSO | 3 X 100 EN C/L, 2 X 40 EN OTRO C/L SE ELIMINO PARARRAYO | B22031000084 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 234 | 2022-03-10 | 15210 | keep | 0 | Mar | 2022 | 0.010359 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-10 19:31 | 2022-03-11 07:29 | 10 | 011:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BARRA EN PEDESTAL | C22031000128 | New_Event | Secondary Wire Down | Include | Include | Equipment | 718 | 2022-03-10 | 7180 | keep | 0 | Mar | 2022 | 0.0048903 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-10 20:36 | 2022-03-10 23:10 | 15 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22031000150 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2022-03-10 | 2310 | keep | 0 | Mar | 2022 | 0.0015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-10 20:53 | 2022-03-11 06:24 | 15 | 009:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REEMPLAZO CAJA DE XMR | C22031000132 | New_Event | Cutout Failure | Include | Include | Equipment | 571 | 2022-03-10 | 8565 | keep | 0 | Mar | 2022 | 0.0058336 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-10 20:53 | 2022-03-11 09:17 | 10 | 012:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | C22031000131 | New_Event | Secondary Wire Down | Include | Include | Equipment | 744 | 2022-03-10 | 7440 | keep | 0 | Mar | 2022 | 0.0050674 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-10 21:33 | 2022-03-10 23:16 | 742 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO PUENTE ABIERTO CARGA POR EL 1335-05 | S22031000000 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-03-10 | 76426 | keep | 0 | Mar | 2022 | 0.052053 | 0.00050537 | Sustained | FALSE | FALSE | Not_TMED_Event | 742
SAN JUAN | 2022-03-10 21:33 | 2022-03-10 23:16 | 314 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPOR SE CERRO PUENTE ABIERTO LLEVANDO 1437-04 Y 1301-02 | S22031000000 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-03-10 | 32342 | keep | 0 | Mar | 2022 | 0.022028 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2022-03-10 21:33 | 2022-03-10 23:16 | 892 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO PUENTE ABIERTO CARGA POR EL 1335-05 | S22031000000 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-03-10 | 91876 | keep | 0 | Mar | 2022 | 0.062576 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
MAYAGÃœEZ | 2022-03-10 22:24 | 2022-03-11 03:00 | 20 | 004:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | M22031000158 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2022-03-10 | 5520 | keep | 0 | Mar | 2022 | 0.0037596 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-10 22:56 | 2022-03-11 16:10 | 15 | 017:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22031000159 | New_Event |  |  | Include | Wildlife | 1034 | 2022-03-10 | 15510 | keep | 0 | Mar | 2022 | 0.010564 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-11 00:10 | 2022-03-12 09:00 | 150 | 032:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22031100052 | New_Event | Wire Down | Include | Include | Equipment | 1970 | 2022-03-11 | 295500 | keep | 0 | Mar | 2022 | 0.20126 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-03-11 00:59 | 2022-03-11 09:18 | 58 | 008:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA | R22031100002 | New_Event | Cutout Failure | Include | Include | Equipment | 499 | 2022-03-11 | 28942 | keep | 0 | Mar | 2022 | 0.019712 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-03-11 02:26 | 2022-03-11 08:55 | 35 | 006:29 | P | DESGANCHE | 1 X 25 EN AEREO PROVISIONAL SE RETIRO PENCA | S22031100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 389 | 2022-03-11 | 13615 | keep | 0 | Mar | 2022 | 0.0092731 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-03-11 03:50 | 2022-03-11 05:37 | 314 | 001:47 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRARON MACHETES PREVIAMENTE ABIERTOS 75% POR EL 1014-16 | S22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-03-11 | 33598 | keep | 0 | Mar | 2022 | 0.022883 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
BAYAMON | 2022-03-11 03:50 | 2022-03-11 05:27 | 295 | 001:37 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE CERRO POR SCADA | S22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-03-11 | 28615 | keep | 0 | Mar | 2022 | 0.01949 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
BAYAMON | 2022-03-11 04:48 | 2022-03-11 06:27 | 40 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L SE RETIRO PAJARO | B22031100004 | New_Event |  |  | Include | Wildlife | 99 | 2022-03-11 | 3960 | keep | 0 | Mar | 2022 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-11 05:31 | 2022-03-11 09:32 | 63 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y EN SU'S 1 X 50 Y 1 X 20 | R22031100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-03-11 | 15183 | keep | 0 | Mar | 2022 | 0.010341 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
FAJARDO | 2022-03-11 05:44 | 2022-03-11 08:38 | 70 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | R22031100006 | New_Event | Wire Down | Include | Include | Equipment | 174 | 2022-03-11 | 12180 | keep | 0 | Mar | 2022 | 0.0082957 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-03-11 05:51 | 2022-03-11 09:15 | 70 | 003:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R22031100008 | New_Event | Bad Weather | Include | Include | Weather | 204 | 2022-03-11 | 14280 | keep | 0 | Mar | 2022 | 0.009726 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-03-11 05:53 | 2022-03-11 11:15 | 30 | 005:22 | P | DESGANCHE | 1 X 40 E C/L. SE REALIZO DESGANCHE | B22031100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-03-11 | 9660 | keep | 0 | Mar | 2022 | 0.0065794 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-11 06:28 | 2022-03-11 10:20 | 10 | 003:52 | P | DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE | B22031100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-03-11 | 2320 | keep | 0 | Mar | 2022 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-03-11 06:38 | 2022-03-11 09:15 | 60 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031100004 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2022-03-11 | 9420 | keep | 0 | Mar | 2022 | 0.0064159 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-03-11 06:43 | 2022-03-11 06:44 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22031100004 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-11 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-11 06:44 | 2022-03-11 08:44 | 200 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C22031100005 | 1st_after_momentary |  |  | Include | Wildlife | 120 | 2022-03-11 | 24000 | keep | 0 | Mar | 2022 | 0.016346 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-03-11 06:58 | 2022-03-11 06:59 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22031100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 2999 | keep | 0 | Mar | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
HUMACAO | 2022-03-11 07:00 | 2022-03-11 07:01 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 4 | keep | 0 | Mar | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-03-11 08:13 | 2022-03-11 09:55 | 25 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | P22031100002 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-03-11 | 2550 | keep | 0 | Mar | 2022 | 0.0017368 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-11 08:29 | 2022-03-11 08:30 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 551 | keep | 0 | Mar | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2022-03-11 08:42 | 2022-03-11 10:56 | 40 | 002:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUERMADO DE 100 X 100KVA | R22031100024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2022-03-11 | 5360 | keep | 0 | Mar | 2022 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-11 08:58 | 2022-03-11 14:25 | 1 | 005:27 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS AVERIADO | M22031100010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 327 | 2022-03-11 | 327 | keep | 0 | Mar | 2022 | 0.00022272 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-11 09:05 | 2022-03-11 12:10 | 8 | 003:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M22031100012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 185 | 2022-03-11 | 1480 | keep | 0 | Mar | 2022 | 0.001008 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-03-11 09:16 | 2022-03-11 16:22 | 80 | 007:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M22031100016 | New_Event | Cutout Failure | Include | Include | Equipment | 426 | 2022-03-11 | 34080 | keep | 0 | Mar | 2022 | 0.023212 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-11 09:18 | 2022-03-11 09:19 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 5062 | keep | 0 | Mar | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
VEGA BAJA | 2022-03-11 09:27 | 2022-03-11 09:28 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 1310 | keep | 0 | Mar | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-03-11 09:27 | 2022-03-11 13:36 | 10 | 004:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CAUSA: PITIRRE | B22031100012 | New_Event |  |  | Include | Wildlife | 249 | 2022-03-11 | 2490 | keep | 0 | Mar | 2022 | 0.0016959 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-03-11 09:38 | 2022-03-11 10:38 | 3 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | C22031100025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-11 | 180 | keep | 0 | Mar | 2022 | 0.0001226 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-03-11 09:40 | 2022-03-11 12:04 | 20 | 002:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA X 50KVA | S22031100010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 144 | 2022-03-11 | 2880 | keep | 0 | Mar | 2022 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-11 09:45 | 2022-03-11 10:45 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22031100009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-11 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-11 09:49 | 2022-03-11 10:49 | 50 | 001:00 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | S22031100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-03-11 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-03-11 09:50 | 2022-03-11 14:00 | 4 | 004:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | P22031100008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 250 | 2022-03-11 | 1000 | keep | 0 | Mar | 2022 | 0.0006811 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-11 09:56 | 2022-03-11 14:45 | 1117 | 004:49 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR 6404-02 PARA REMPLAZAR POSTE PRIMARIO PARTIDO EN EL TRONCAL DEL ALIMENTADOR ESTE ESTA LLEVANDO LA CARGA DEL 6404-01 | M22031100025 | New_Event | Defective Pole | Include | Include | Equipment | 289 | 2022-03-11 | 322813 | keep | 0 | Mar | 2022 | 0.21987 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-03-11 09:56 | 2022-03-11 14:45 | 1671 | 004:49 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA REMPLAZAR POSTE PRIMARIO PARTIDO EN EL TRONCAL DEL ALIMENTADOR | M22031100025 | New_Event | Defective Pole | Include | Include | Equipment | 289 | 2022-03-11 | 482919 | keep | 0 | Mar | 2022 | 0.32891 | 0.0011381 | Sustained | FALSE | FALSE | Not_TMED_Event | 1671
GUAYAMA | 2022-03-11 10:00 | 2022-03-11 11:12 | 2 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR BARRAS EN PEDESTAL | P22031100003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2022-03-11 | 144 | keep | 0 | Mar | 2022 | 9.8078e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-03-11 10:09 | 2022-03-11 12:50 | 6 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO LINEA SECUNDARIA DERRIBADA POR VEHICULO PRIVADO | C22031100028 | New_Event |  |  | Include | Wildlife | 161 | 2022-03-11 | 966 | keep | 0 | Mar | 2022 | 0.00065794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-11 10:21 | 2022-03-11 17:25 | 20 | 007:04 | P | NO SE REPORTO CAUSA | 1X20 C/L 1X10 EN T-6 1X10 EN T-7 | B22031100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2022-03-11 | 8480 | keep | 0 | Mar | 2022 | 0.0057757 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-11 10:31 | 2022-03-11 10:32 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-02 LLEVANDO LA CARGA DEL 1720-08 | S22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 2402 | keep | 0 | Mar | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-03-11 10:31 | 2022-03-11 10:32 | 1 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1709-02 LLEVANDO LA CARGA DEL 1720-08 | B22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-11 10:32 | 2022-03-11 10:33 | 4664 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRRE INTERRUPTOR | M22031100029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-03-11 | 4664 | keep | 0 | Mar | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2022-03-11 10:33 | 2022-03-11 19:28 | 8 | 008:55 | P | PARARRAYOS DEFECTUOSO | 3 X 80 Y 1 X 50 EN RISER SE REMPLAZO PARARRAYOS AVERIADO | M22031100076 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 535 | 2022-03-11 | 4280 | keep | 0 | Mar | 2022 | 0.0029151 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-11 10:40 | 2022-03-11 11:28 | 11 | 000:48 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA SECCIONALIZAR POSTE SECUNDARIO PARTIDO | M22031100015 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 48 | 2022-03-11 | 528 | keep | 0 | Mar | 2022 | 0.00035962 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-03-11 11:25 | 2022-03-11 14:14 | 12 | 002:49 | P | SECUNDARIA/DESGANCHE | SE DESGANCHO SE SUBIO/RETEZO SECUNDARIA (NO FUNDIO) | B22031100025 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 169 | 2022-03-11 | 2028 | keep | 0 | Mar | 2022 | 0.0013813 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-11 11:37 | 2022-03-11 15:16 | 12 | 003:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO QUEMADO | B22031100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 219 | 2022-03-11 | 2628 | keep | 0 | Mar | 2022 | 0.0017899 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-11 11:43 | 2022-03-11 12:00 | 100 | 000:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU | R20031100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-03-11 | 1700 | keep | 0 | Mar | 2022 | 0.0011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-11 11:51 | 2022-03-11 14:55 | 40 | 003:04 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN CORTE DE LINEA SE INSTALO AEREO PROVISIONAL DEL PM-52 AL PM-53 | M22031000055 | New_Event | UG Cable Fault | Include | Include | Equipment | 184 | 2022-03-11 | 7360 | keep | 0 | Mar | 2022 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-03-11 12:00 | 2022-03-11 12:49 | 5 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | P22031100016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2022-03-11 | 245 | keep | 0 | Mar | 2022 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-11 12:02 | 2022-03-11 12:03 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 4085 | keep | 0 | Mar | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
PONCE | 2022-03-11 13:04 | 2022-03-11 13:05 | 1730 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 1730 | keep | 0 | Mar | 2022 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
PONCE | 2022-03-11 13:15 | 2022-03-11 13:51 | 969 | 000:36 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. NO CERRO POR SCADA SE CERRO DE FORMA MANUAL | P22031100023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2022-03-11 | 34884 | keep | 0 | Mar | 2022 | 0.023759 | 0.00065998 | Sustained | FALSE | FALSE | Not_TMED_Event | 969
BARRANQUITAS | 2022-03-11 13:31 | 2022-03-11 18:46 | 20 | 005:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 10 XMR , SE REEMPLAZO PIN POLE TOP Y SUBIO LINEA PRIMARIA SAFADA, NO FUNDIO EN PRIMARIA. | C22031100037 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 315 | 2022-03-11 | 6300 | keep | 0 | Mar | 2022 | 0.0042909 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-11 13:32 | 2022-03-11 17:04 | 20 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22031100049 | New_Event |  |  | Include | Wildlife | 212 | 2022-03-11 | 4240 | keep | 0 | Mar | 2022 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-03-11 13:38 | 2022-03-11 14:19 | 1 | 000:41 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA INSTALAR 30 PIES DE TOMA WR6077862 PERSONAL DE LOW VOLTAJE | A22031100028 | New_Event | Other Causes | Include | Include | Other | 41 | 2022-03-11 | 41 | keep | 0 | Mar | 2022 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-11 14:04 | 2022-03-11 19:00 | 10 | 004:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22031100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-03-11 | 2960 | keep | 0 | Mar | 2022 | 0.002016 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-03-11 14:19 | 2022-03-11 15:20 | 30 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO CONECTORES QUEMADOS EN EL BAJANTE SECUNDARIO Y EN LA LINEA SECUNDARIA | R22031100041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-03-11 | 1830 | keep | 0 | Mar | 2022 | 0.0012464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-11 14:28 | 2022-03-12 09:20 | 75 | 018:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22031100059 | New_Event | Bad Weather | Include | Include | Weather | 1132 | 2022-03-11 | 84900 | keep | 0 | Mar | 2022 | 0.057825 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-03-11 14:38 | 2022-03-11 17:23 | 32 | 002:45 | P | DESGANCHE | 1 X 50 Y 1 X 15 EN C/L'S DESGANCHO Y REMPLAZO AISLADOR ROTO | R22031100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-03-11 | 5280 | keep | 0 | Mar | 2022 | 0.0035962 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2022-03-11 14:54 | 2022-03-11 14:55 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 4085 | keep | 0 | Mar | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
PONCE | 2022-03-11 14:58 | 2022-03-11 14:59 | 607 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE AMMARADO CON EL 5007-04 LLEVA LA CARGA POR 5007-04 | P22031100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 607 | keep | 0 | Mar | 2022 | 0.00041342 | 0.00041342 | Momentary | FALSE | FALSE | Not_TMED_Event | 607
PONCE | 2022-03-11 14:58 | 2022-03-11 14:59 | 462 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE AMMARADO CON EL 5007-02 LLEVA LA CARGA DEL 5007-02 | P22031100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 462 | keep | 0 | Mar | 2022 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
MAYAGÃœEZ | 2022-03-11 15:05 | 2022-03-11 17:45 | 15 | 002:40 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | M22031100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-03-11 | 2400 | keep | 0 | Mar | 2022 | 0.0016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-03-11 15:28 | 2022-03-11 17:39 | 42 | 002:11 | P | DESGANCHE | 1X100 EN C/L (SE RETIRO RAMA DEL TENDIDO ELECTRICO) | B22031100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-11 | 5502 | keep | 0 | Mar | 2022 | 0.0037474 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2022-03-11 15:36 | 2022-03-11 15:37 | 721 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1423-01 QUE LLEVA 1437-03 | S22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 721 | keep | 0 | Mar | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-03-11 15:36 | 2022-03-11 15:37 | 1699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1423-01 QUE LLEVA 1437-03 | S22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 1699 | keep | 0 | Mar | 2022 | 0.0011572 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-03-11 15:45 | 2022-03-11 18:07 | 1 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 20 SMU 20 EN SU - 2 NO CAUSA | R22031100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-03-11 | 142 | keep | 0 | Mar | 2022 | 9.6716e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-11 15:54 | 2022-03-11 18:48 | 120 | 002:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22031100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-03-11 | 20880 | keep | 0 | Mar | 2022 | 0.014221 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-03-11 15:56 | 2022-03-11 20:42 | 180 | 004:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22031100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2022-03-11 | 51480 | keep | 0 | Mar | 2022 | 0.035063 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CAGUAS | 2022-03-11 15:57 | 2022-03-12 15:46 | 50 | 023:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22031100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1429 | 2022-03-11 | 71450 | keep | 0 | Mar | 2022 | 0.048664 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-11 16:05 | 2022-03-11 17:00 | 5 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO BARRAS EN PEDESTAL SOTERRADO | A22031100038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-03-11 | 275 | keep | 0 | Mar | 2022 | 0.0001873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-03-11 16:34 | 2022-03-11 20:50 | 50 | 004:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22031100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-03-11 | 12800 | keep | 0 | Mar | 2022 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-11 17:20 | 2022-03-11 17:47 | 1 | 000:27 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA | C22031100049 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 27 | 2022-03-11 | 27 | keep | 0 | Mar | 2022 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-11 17:37 | 2022-03-11 19:44 | 20 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN TRANSFORMADOR. SE REEMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P22031100028 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2022-03-11 | 2540 | keep | 0 | Mar | 2022 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-11 18:00 | 2022-03-11 21:55 | 56 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22031100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-03-11 | 13160 | keep | 0 | Mar | 2022 | 0.0089632 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-03-11 18:02 | 2022-03-11 21:18 | 80 | 003:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X100 EN SU-4 1X80 EN C/L & SE REMPLAZO CAJA PRIMARIA | B22031100048 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2022-03-11 | 15680 | keep | 0 | Mar | 2022 | 0.01068 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-11 18:16 | 2022-03-11 18:18 | 1825 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 3650 | keep | 0 | Mar | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-03-11 18:16 | 2022-03-11 18:18 | 47 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 94 | keep | 0 | Mar | 2022 | 6.4023e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-03-11 18:16 | 2022-03-11 18:18 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 1343-03 LLEVA PARTE DEL 1908-03 POR CONVERTIDOR | S22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 630 | keep | 0 | Mar | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-03-11 18:16 | 2022-03-11 18:18 | 2 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 4 | keep | 0 | Mar | 2022 | 2.7244e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-11 18:16 | 2022-03-11 18:18 | 2391 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 4782 | keep | 0 | Mar | 2022 | 0.003257 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2022-03-11 18:16 | 2022-03-11 18:18 | 400 | 000:02 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 1343-03 LLEVA PARTE DEL 1908-03 POR CONVERTIDOR | S22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 800 | keep | 0 | Mar | 2022 | 0.00054488 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2022-03-11 18:16 | 2022-03-11 18:18 | 2276 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 4552 | keep | 0 | Mar | 2022 | 0.0031003 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-03-11 18:16 | 2022-03-11 18:18 | 777 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 1554 | keep | 0 | Mar | 2022 | 0.0010584 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-03-11 18:16 | 2022-03-11 18:18 | 12 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 24 | keep | 0 | Mar | 2022 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-11 18:16 | 2022-03-11 18:18 | 1290 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22031100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-11 | 2580 | keep | 0 | Mar | 2022 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
PONCE | 2022-03-11 18:31 | 2022-03-12 09:48 | 60 | 015:17 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEA DIFERENTES POR DESGANCHE | P22031100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 917 | 2022-03-11 | 55020 | keep | 0 | Mar | 2022 | 0.037474 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-11 18:31 | 2022-03-12 07:58 | 1 | 013:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A22031100039 | New_Event | Bad Weather | Include | Include | Weather | 807 | 2022-03-11 | 807 | keep | 0 | Mar | 2022 | 0.00054964 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-11 18:40 | 2022-03-11 19:51 | 10 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BAJANTES DE XMR & CONEXIONES SECUNDARIAS (NO FUNDIO) | B22030600034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-03-11 | 710 | keep | 0 | Mar | 2022 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-11 18:44 | 2022-03-11 20:48 | 500 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA Y VIENTO | M22031100075 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2022-03-11 | 62000 | keep | 0 | Mar | 2022 | 0.042228 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-03-11 19:05 | 2022-03-11 21:05 | 445 | 002:00 | P | DESCONECTIVO DEFECTUOSO | DISPARO 1437-04 SE SECCIONALIZO EN CALLE LINARES Y SE CERRO AMARRE CONTRA 1335-05 EN CALLE RIAZA 80% EN SERVICIO. LA CARGA DEL 1301-02 60% ENTRO COMPLETA QUE ESTABA POR 1437-04 AHORA POR 1335-05 | S22031100065 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2022-03-11 | 53400 | keep | 0 | Mar | 2022 | 0.03637 | 0.00030309 | Sustained | FALSE | FALSE | Not_TMED_Event | 445
SAN JUAN | 2022-03-11 19:05 | 2022-03-11 21:05 | 892 | 002:00 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE SECCIONALIZO EN CALLE LINARES Y SE CERRO AMARRE CONTRA 1335-05 EN CALLE RIAZA 80% EN SERVICIO Y LA CARGA DEL 1301-02 60% ENTRO COMPLETA | S22031100065 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2022-03-11 | 107040 | keep | 0 | Mar | 2022 | 0.072904 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
BAYAMON | 2022-03-11 21:00 | 2022-03-11 23:57 | 30 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S22031100086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2022-03-11 | 5310 | keep | 0 | Mar | 2022 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-11 21:05 | 2022-03-12 00:32 | 172 | 003:27 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETE QUEMADO EN LA CALLE LINARES, SE CERRO RISER DE SALIDA Y SE CERRO POR SCADA | S22031100065 | Partial_restoration | Switch Failure | Include | Include | Equipment | 207 | 2022-03-11 | 35604 | keep | 0 | Mar | 2022 | 0.02425 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-11 21:05 | 2022-03-11 22:15 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIRA TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22031100091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-03-11 | 700 | keep | 0 | Mar | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-11 21:12 | 2022-03-11 21:13 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6404-02 QUE ESTA LLEVANDO LA CARGA DEL 6404-01 | M22031100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 1117 | keep | 0 | Mar | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2022-03-11 21:12 | 2022-03-11 21:13 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-11 | 1671 | keep | 0 | Mar | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
ARECIBO | 2022-03-11 21:50 | 2022-03-12 11:37 | 5 | 013:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARARON CONEXIONES SECUNDARIAS | A22031100041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 827 | 2022-03-11 | 4135 | keep | 0 | Mar | 2022 | 0.0028163 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-11 21:52 | 2022-03-12 16:22 | 40 | 018:30 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22031100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1110 | 2022-03-11 | 44400 | keep | 0 | Mar | 2022 | 0.030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-11 22:10 | 2022-03-12 15:49 | 15 | 017:39 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR DE 50KVA X 50KVA | C22031100056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1059 | 2022-03-11 | 15885 | keep | 0 | Mar | 2022 | 0.010819 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-11 22:33 | 2022-03-12 05:39 | 100 | 007:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22031100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 426 | 2022-03-11 | 42600 | keep | 0 | Mar | 2022 | 0.029015 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-11 23:12 | 2022-03-12 12:26 | 8 | 013:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22031100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 794 | 2022-03-11 | 6352 | keep | 0 | Mar | 2022 | 0.0043263 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-11 23:16 | 2022-03-11 23:26 | 30 | 000:10 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22031100058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-03-11 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-11 23:16 | 2022-03-11 23:18 | 1124 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | R22031100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-11 | 2248 | keep | 0 | Mar | 2022 | 0.0015311 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
SAN JUAN | 2022-03-11 23:59 | 2022-03-12 21:40 | 20 | 021:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22031100103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1301 | 2022-03-11 | 26020 | keep | 0 | Mar | 2022 | 0.017722 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-12 00:10 | 2022-03-12 08:08 | 120 | 007:58 | P | DESGANCHE | 1 X 65 Y 1X 50 SE REALIZO DESGANCHE | S22031200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 478 | 2022-03-12 | 57360 | keep | 0 | Mar | 2022 | 0.039068 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-03-12 00:12 | 2022-03-12 12:03 | 10 | 011:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PARTIDA | C22031200001 | New_Event | Cutout Failure | Include | Include | Equipment | 711 | 2022-03-12 | 7110 | keep | 0 | Mar | 2022 | 0.0048426 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-12 00:18 | 2022-03-12 00:19 | 3046 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECERRO | R22031200000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2022-03-12 | 3046 | keep | 0 | Mar | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-03-12 00:19 | 2022-03-12 11:51 | 31 | 011:32 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN AEREO PROVISIONAL SE REPARO TERMINACION | R22031200007 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 692 | 2022-03-12 | 21452 | keep | 0 | Mar | 2022 | 0.014611 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2022-03-12 00:47 | 2022-03-12 11:50 | 141 | 011:03 | P | CABLE SOTERRADO AVERIADO | 1 X 65 1 X 50 EN C/L Y 1 X 40 EN PROVISIONAL HACIA T-18. AVERIA NUEVA DE T-14 @ T-13 Y AVERIA VIEJA DE T-10 @ SU-C. FUERA DE SERVICIO T-13, T-12, T-11 Y T-10 | B22031200009 | New_Event | UG Cable Fault | Include | Include | Equipment | 663 | 2022-03-12 | 93483 | keep | 0 | Mar | 2022 | 0.063671 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
YAUCO | 2022-03-12 01:43 | 2022-03-12 08:50 | 1000 | 007:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE 200A EN ENTRADA DE CONVERTIDOR 13KV A 4KV | P22031200001 | New_Event | Cutout Failure | Include | Include | Equipment | 427 | 2022-03-12 | 427000 | keep | 0 | Mar | 2022 | 0.29083 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
CAGUAS | 2022-03-12 02:09 | 2022-03-12 07:39 | 100 | 005:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22031200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2022-03-12 | 33000 | keep | 0 | Mar | 2022 | 0.022476 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-12 02:18 | 2022-03-12 10:32 | 23 | 008:14 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN SU 4E SE REPARO TERMINACION EN AEREO PROVISIONAL | R22031200006 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 494 | 2022-03-12 | 11362 | keep | 0 | Mar | 2022 | 0.0077386 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-03-12 03:58 | 2022-03-12 04:11 | 1 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO CON PERSONAL DE LA REPRESA LA PLATA Y SE CERRO POR SCADA | B2203120000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-03-12 | 13 | keep | 0 | Mar | 2022 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-12 05:11 | 2022-03-12 10:46 | 36 | 005:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22031200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2022-03-12 | 12060 | keep | 0 | Mar | 2022 | 0.008214 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-03-12 05:26 | 2022-03-12 05:27 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 2608 | keep | 0 | Mar | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
SAN JUAN | 2022-03-12 06:45 | 2022-03-12 06:46 | 3718 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22031200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-12 | 3718 | keep | 0 | Mar | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-03-12 06:46 | 2022-03-12 12:30 | 100 | 005:44 | P | DESGANCHE | SE REEMPLAZO CAJA PRIMARIA 1 X 100 | S22031200017 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-03-12 | 34400 | keep | 0 | Mar | 2022 | 0.02343 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-12 07:43 | 2022-03-12 07:44 | 1565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 1565 | keep | 0 | Mar | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
ARECIBO | 2022-03-12 08:05 | 2022-03-12 10:05 | 60 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA FOREMAN NO ENCONTRO CAUSA | A22031200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-03-12 | 7200 | keep | 0 | Mar | 2022 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-12 08:06 | 2022-03-12 09:57 | 27 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | R22031200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-03-12 | 2997 | keep | 0 | Mar | 2022 | 0.0020412 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-03-12 08:12 | 2022-03-12 15:14 | 25 | 007:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE SE DESGANCHO Y SE CERRO C/L | B22031200036 | New_Event | Wire Down | Include | Include | Equipment | 422 | 2022-03-12 | 10550 | keep | 0 | Mar | 2022 | 0.0071856 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-03-12 08:12 | 2022-03-12 12:30 | 100 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B22031200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2022-03-12 | 25800 | keep | 0 | Mar | 2022 | 0.017572 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-12 08:13 | 2022-03-12 09:40 | 60 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22031200008 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-03-12 | 5220 | keep | 0 | Mar | 2022 | 0.0035553 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-12 08:15 | 2022-03-12 12:24 | 25 | 004:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | M22031200009 | New_Event | Cutout Failure | Include | Include | Equipment | 249 | 2022-03-12 | 6225 | keep | 0 | Mar | 2022 | 0.0042398 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-12 08:17 | 2022-03-12 12:05 | 100 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22031200013 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2022-03-12 | 22800 | keep | 0 | Mar | 2022 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-03-12 08:17 | 2022-03-12 09:29 | 25 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P22031200008 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2022-03-12 | 1800 | keep | 0 | Mar | 2022 | 0.001226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-03-12 08:18 | 2022-03-12 16:39 | 70 | 008:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | C22031200003 | New_Event | Wire Down | Include | Include | Equipment | 501 | 2022-03-12 | 35070 | keep | 0 | Mar | 2022 | 0.023886 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-03-12 08:19 | 2022-03-12 15:05 | 45 | 006:46 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON 2 MACHETES QUEMADOS | R22031200020 | New_Event | Switch Failure | Include | Include | Equipment | 406 | 2022-03-12 | 18270 | keep | 0 | Mar | 2022 | 0.012444 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-12 08:19 | 2022-03-12 10:19 | 30 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22031200040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-03-12 | 3600 | keep | 0 | Mar | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-12 08:20 | 2022-03-12 13:26 | 50 | 005:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-1 | S22031200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2022-03-12 | 15300 | keep | 0 | Mar | 2022 | 0.010421 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-12 08:22 | 2022-03-12 15:13 | 6 | 006:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22031200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2022-03-12 | 2466 | keep | 0 | Mar | 2022 | 0.0016796 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-03-12 08:22 | 2022-03-12 13:34 | 6 | 005:12 | P | DESGANCHE | 2 X 20 EN TRANSFORMADOR POR DESGANCHE | P22031200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-03-12 | 1872 | keep | 0 | Mar | 2022 | 0.001275 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-12 08:26 | 2022-03-12 12:09 | 130 | 003:43 | P | DESGANCHE | SE REALIZO DESGANCHE 2 X 65 EN CORTE DE LINEA | S22031200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-03-12 | 28990 | keep | 0 | Mar | 2022 | 0.019745 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-03-12 08:29 | 2022-03-12 12:57 | 15 | 004:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZARON AISLADORES | R22031200025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 268 | 2022-03-12 | 4020 | keep | 0 | Mar | 2022 | 0.002738 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-12 08:52 | 2022-03-12 13:37 | 150 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22031200020 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2022-03-12 | 42750 | keep | 0 | Mar | 2022 | 0.029117 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-12 08:59 | 2022-03-12 16:24 | 8 | 007:25 | P | TRANSFORMADOR AVERIADO | SE IDENTIFICO PM-21 AVERIADO | S22031200078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 445 | 2022-03-12 | 3560 | keep | 0 | Mar | 2022 | 0.0024247 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-12 09:10 | 2022-03-12 12:05 | 100 | 002:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 ENTRADA DE RISER 1 X 50 Y 1 X 40 EN DIFERENTES CORTES DE LINEA POR AVE | P22031200020 | New_Event |  |  | Include | Wildlife | 175 | 2022-03-12 | 17500 | keep | 0 | Mar | 2022 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-12 09:20 | 2022-03-12 11:20 | 1588 | 002:00 | S | PROTECCION DEFECTUOSA | SE SECCIONALIZO 1711-02 POR PROTECCION DEFECTUOSA Y SE ENERGIZO EL RESTO | B22031200178 | New_Event | Protection Miscoordination | Include | Include | Other | 120 | 2022-03-12 | 190560 | keep | 0 | Mar | 2022 | 0.12979 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2022-03-12 09:20 | 2022-03-12 11:20 | 723 | 002:00 | S | PROTECCION DEFECTUOSA | SE SECCIONALIZO 1711-02 POR PROTECCION DEFECTUOSA Y SE ENERGIZO EL RESTO LLEVA 1711-05 | B22031200178 | New_Event | Protection Miscoordination | Include | Include | Other | 120 | 2022-03-12 | 86760 | keep | 0 | Mar | 2022 | 0.059092 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-03-12 09:20 | 2022-03-12 11:20 | 13 | 002:00 | S | PROTECCION DEFECTUOSA | SE SECCIONALIZO 1711-02 POR PROTECCION DEFECTUOSA Y SE ENERGIZO EL RESTO. 1711-03 LLEVA 400 CLIENTES DEL 1716-03 | B22031200178 | New_Event | Protection Miscoordination | Include | Include | Other | 120 | 2022-03-12 | 1560 | keep | 0 | Mar | 2022 | 0.0010625 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-03-12 09:20 | 2022-03-12 16:26 | 1976 | 007:06 | S | PROTECCION DEFECTUOSA | SE SECCIONALIZO 1711-02 POR PROTECCION DEFECTUOSA Y SE ENERGIZO EL RESTO CARGA DEL 1711-05 POR 1711-02 | B22031200178 | New_Event | Protection Miscoordination | Include | Include | Other | 426 | 2022-03-12 | 841776 | keep | 0 | Mar | 2022 | 0.57333 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-03-12 09:20 | 2022-03-12 11:20 | 400 | 002:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO 1711-02 POR PROTECCION DEFECTUOSA Y SE ENERGIZO EL RESTO. 1711-03 LLEVA 400 CLIENTES DEL 1716-03 | B22031200178 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2022-03-12 | 48000 | keep | 0 | Mar | 2022 | 0.032693 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
PONCE | 2022-03-12 09:31 | 2022-03-12 09:32 | 75 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 75 | keep | 0 | Mar | 2022 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-03-12 09:31 | 2022-03-12 09:32 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 449 | keep | 0 | Mar | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2022-03-12 09:42 | 2022-03-12 09:43 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTRRUPCION | S22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 2203 | keep | 0 | Mar | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
MAYAGÃœEZ | 2022-03-12 09:47 | 2022-03-12 10:01 | 35 | 000:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO LINEAS | M22031200016 | New_Event |  |  | Include | Wildlife | 14 | 2022-03-12 | 490 | keep | 0 | Mar | 2022 | 0.00033374 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-03-12 09:48 | 2022-03-12 13:57 | 3 | 004:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO SECUNDARIA DEL SUELO | C22031200031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 249 | 2022-03-12 | 747 | keep | 0 | Mar | 2022 | 0.00050878 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-12 10:13 | 2022-03-12 10:14 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1530-07 | S22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 1420 | keep | 0 | Mar | 2022 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-03-12 10:13 | 2022-03-12 10:14 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1530-07 | S22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 437 | keep | 0 | Mar | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-03-12 10:13 | 2022-03-12 10:14 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1526-02 Y 1530-06 | S22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 643 | keep | 0 | Mar | 2022 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
HUMACAO | 2022-03-12 10:14 | 2022-03-12 19:47 | 7 | 009:33 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XRM RETIRO ENREDADERA | C22031200033 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 573 | 2022-03-12 | 4011 | keep | 0 | Mar | 2022 | 0.0027319 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-12 10:27 | 2022-03-12 10:28 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 2179 | keep | 0 | Mar | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2022-03-12 10:32 | 2022-03-12 10:33 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 4381 | keep | 0 | Mar | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2022-03-12 10:33 | 2022-03-12 10:34 | 1261 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22031200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-12 | 1261 | keep | 0 | Mar | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
BAYAMON | 2022-03-12 10:34 | 2022-03-12 11:14 | 8 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22031200134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-12 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-12 10:40 | 2022-03-12 11:49 | 426 | 001:09 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABREN CAJAS DE CORTE DE LINEA PARA CERRAR INTERRUPTOR Y SECCIONALIZAR AVERIA CAUSADA POR ACCIDENTE DE AUTO Y POSTE PARTIDO. ENTRA EL 80% DEL ALIMENTADOR | P22031200029 | New_Event |  |  | Include | Wildlife | 69 | 2022-03-12 | 29394 | keep | 0 | Mar | 2022 | 0.02002 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
CAGUAS | 2022-03-12 10:52 | 2022-03-12 14:10 | 50 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22031200036 | New_Event |  |  | Include | Wildlife | 198 | 2022-03-12 | 9900 | keep | 0 | Mar | 2022 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-03-12 11:07 | 2022-03-12 15:31 | 60 | 004:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22031200046 | New_Event | Bad Weather | Include | Include | Weather | 264 | 2022-03-12 | 15840 | keep | 0 | Mar | 2022 | 0.010789 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-12 11:10 | 2022-03-12 19:05 | 3 | 007:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | R22031200059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 475 | 2022-03-12 | 1425 | keep | 0 | Mar | 2022 | 0.00097056 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-12 11:20 | 2022-03-12 18:05 | 500 | 006:45 | P | PROTECCION DEFECTUOSA | SE SECCIONALIZO 1711-02 EN AVE PERIFERICA Y SE CERRO MACHETES EN BTC ANTES DEL RIO | B22031200178 | New_Event | Protection Miscoordination | Include | Include | Other | 405 | 2022-03-12 | 202500 | keep | 0 | Mar | 2022 | 0.13792 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-03-12 11:27 | 2022-03-12 13:49 | 2617 | 002:22 | T | DESGANCHE | SE SECCIONALIZO EN URB AVENTURA Y SE CERRO POR SCADA | B22031200283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-03-12 | 371614 | keep | 0 | Mar | 2022 | 0.2531 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
SAN JUAN | 2022-03-12 11:28 | 2022-03-12 11:29 | 737 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 60% POR EL 1529-15 Y LLEVANDO 5% DEL 1346-03 | S22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 737 | keep | 0 | Mar | 2022 | 0.00050197 | 0.00050197 | Momentary | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2022-03-12 11:28 | 2022-03-12 11:29 | 121 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 5% DE LA CARGA POR EL 1346-02 | S22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 121 | keep | 0 | Mar | 2022 | 8.2413e-05 | 8.2413e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 121
MAYAGÃœEZ | 2022-03-12 11:28 | 2022-03-12 12:50 | 8 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR SE ENCONTRO ALAMBRE DULCE QUE CRUZO FUSIBLE | M22031200028 | New_Event |  |  | Include | Wildlife | 82 | 2022-03-12 | 656 | keep | 0 | Mar | 2022 | 0.0004468 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-12 11:30 | 2022-03-12 21:50 | 200 | 010:20 | P | DESGANCHE | 1 X 80 Y 2 X 140 EN CORTE DE LINEA | S22031200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 620 | 2022-03-12 | 124000 | keep | 0 | Mar | 2022 | 0.084456 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-03-12 11:49 | 2022-03-12 12:46 | 20 | 000:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABREN PUENTES PRIMARIOS Y SE CIERRAN CAJAS DE CORTE DE LINEA PARA DAR SERVICIO A 20 CLIENTES ADICIONALES | P22031200029 | Partial_restoration |  |  | Include | Wildlife | 57 | 2022-03-12 | 1140 | keep | 0 | Mar | 2022 | 0.00077645 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-12 11:49 | 2022-03-12 14:20 | 3147 | 002:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO ZAFADO EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22031200037 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2022-03-12 | 475197 | keep | 0 | Mar | 2022 | 0.32365 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
BAYAMON | 2022-03-12 11:50 | 2022-03-13 01:00 | 41 | 013:10 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA T-14 A T-13 | B22031200009 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 790 | 2022-03-12 | 32390 | keep | 0 | Mar | 2022 | 0.022061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-12 12:46 | 2022-03-12 17:25 | 66 | 004:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PRIMARIO PARTIDO EN ACCIDENTE DE AUTO SE ABRE CORTE DE LINEA PARA CERRAR PUENTES | P22031200084 | Additional_clients |  |  | Include | Wildlife | 279 | 2022-03-12 | 18414 | keep | 0 | Mar | 2022 | 0.012542 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-12 13:13 | 2022-03-13 10:40 | 90 | 021:27 | P | ESTRUCTURA AVERIADA | POSTE PARTIDO | M22031200106 | New_Event | Defective Pole | Include | Include | Equipment | 1287 | 2022-03-12 | 115830 | keep | 0 | Mar | 2022 | 0.078891 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
GUAYAMA | 2022-03-12 13:19 | 2022-03-12 13:22 | 100 | 000:03 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22031200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-03-12 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-12 13:20 | 2022-03-12 14:45 | 100 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22031200052 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2022-03-12 | 8500 | keep | 0 | Mar | 2022 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-12 13:20 | 2022-03-12 14:43 | 10 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REEMPLAZO BAJANTE SECUNDARIO XMR | C22031200055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-03-12 | 830 | keep | 0 | Mar | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-12 13:24 | 2022-03-12 19:07 | 10 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031200017 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2022-03-12 | 3430 | keep | 0 | Mar | 2022 | 0.0023362 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-12 13:29 | 2022-03-12 17:00 | 36 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22031200334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-03-12 | 7596 | keep | 0 | Mar | 2022 | 0.0051736 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-03-12 13:30 | 2022-03-12 15:45 | 14 | 002:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22031200062 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2022-03-12 | 1890 | keep | 0 | Mar | 2022 | 0.0012873 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-03-12 13:36 | 2022-03-12 17:20 | 60 | 003:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22031200095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-03-12 | 13440 | keep | 0 | Mar | 2022 | 0.0091539 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-12 13:36 | 2022-03-12 15:17 | 5042 | 001:41 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | A22031200000 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2022-03-12 | 509242 | keep | 0 | Mar | 2022 | 0.34684 | 0.0034341 | Sustained | FALSE | FALSE | Not_TMED_Event | 5042
VEGA BAJA | 2022-03-12 13:37 | 2022-03-12 17:44 | 36 | 004:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REMPLAZO AISLADORES | B22031200337 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 247 | 2022-03-12 | 8892 | keep | 0 | Mar | 2022 | 0.0060563 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-03-12 13:38 | 2022-03-12 14:17 | 1368 | 000:39 | T | NO SE REPORTO CAUSA | SE ENCONTRO INTERRUPTOR ABIERTO EN SUBESTACION Y SE CERRO EN EL CAMPO (RTU DOWN) | S22031200078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-03-12 | 53352 | keep | 0 | Mar | 2022 | 0.036338 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2022-03-12 13:39 | 2022-03-12 19:12 | 12 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN PM-NO IDENTIFICADO | S22031200095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2022-03-12 | 3996 | keep | 0 | Mar | 2022 | 0.0027217 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-12 13:41 | 2022-03-12 16:30 | 60 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22031200072 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2022-03-12 | 10140 | keep | 0 | Mar | 2022 | 0.0069063 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-03-12 13:44 | 2022-03-12 13:45 | 1262 | 000:01 | T | LINEA DE TRANSMISION | RECIERRE LINEA 300 | P220312000XX | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 1 | 2022-03-12 | 1262 | keep | 0 | Mar | 2022 | 0.00085954 | 0.00085954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1262
BAYAMON | 2022-03-12 13:49 | 2022-03-12 18:30 | 262 | 004:41 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO POR PARTE DE WTS Y SE REMPLAZO AISLADOR LUEGO DE TODO EL DESGANCHE Y SE CERRO MACHETES EN URB. AVENTURA | B22031200283 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 281 | 2022-03-12 | 73622 | keep | 0 | Mar | 2022 | 0.050144 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-12 13:51 | 2022-03-12 16:28 | 110 | 002:37 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22031200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-03-12 | 17270 | keep | 0 | Mar | 2022 | 0.011763 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
VEGA BAJA | 2022-03-12 13:51 | 2022-03-12 18:13 | 80 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22031200347 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2022-03-12 | 20960 | keep | 0 | Mar | 2022 | 0.014276 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-12 13:54 | 2022-03-12 20:16 | 40 | 006:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L Y SE CERRO PUENTE DE CAJA A LINEA (NO FUNDIO FUSIBLE) | S22031200098 | New_Event | Wire Down | Include | Include | Equipment | 382 | 2022-03-12 | 15280 | keep | 0 | Mar | 2022 | 0.010407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-12 13:55 | 2022-03-12 23:05 | 300 | 009:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L 1 X 25 EN XMR 1 X 100 EN C/L Y 2 X 50 EN C/L EN DIERENTES C/L MAL TIEMPO | P22031200057 | New_Event | Bad Weather | Include | Include | Weather | 550 | 2022-03-12 | 165000 | keep | 0 | Mar | 2022 | 0.11238 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2022-03-12 13:57 | 2022-03-12 16:57 | 25 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE DESENRREDO LINEA PRIMARIA | P22031200059 | New_Event | Wire Down | Include | Include | Equipment | 180 | 2022-03-12 | 4500 | keep | 0 | Mar | 2022 | 0.0030649 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-12 13:59 | 2022-03-12 17:29 | 90 | 003:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22031200077 | New_Event |  |  | Include | Wildlife | 210 | 2022-03-12 | 18900 | keep | 0 | Mar | 2022 | 0.012873 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-03-12 14:07 | 2022-03-12 22:07 | 100 | 008:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031200088 | New_Event | Bad Weather | Include | Include | Weather | 480 | 2022-03-12 | 48000 | keep | 0 | Mar | 2022 | 0.032693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-12 14:10 | 2022-03-12 15:35 | 16 | 001:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25KVA POR UNO DE 37.5KVA | B22031200353 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2022-03-12 | 1360 | keep | 0 | Mar | 2022 | 0.00092629 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-03-12 14:14 | 2022-03-12 14:15 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031200154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 1597 | keep | 0 | Mar | 2022 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
VEGA BAJA | 2022-03-12 14:16 | 2022-03-12 18:55 | 45 | 004:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22031200364 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2022-03-12 | 12555 | keep | 0 | Mar | 2022 | 0.0085512 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-03-12 14:23 | 2022-03-12 15:25 | 4 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES Y LINEAS SECUNDARIAS | A22031200048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2022-03-12 | 248 | keep | 0 | Mar | 2022 | 0.00016891 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-03-12 14:25 | 2022-03-12 15:35 | 1 | 001:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22031200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-03-12 | 70 | keep | 0 | Mar | 2022 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-12 14:26 | 2022-03-12 21:23 | 120 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y VIENTO | M22031200100 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2022-03-12 | 50040 | keep | 0 | Mar | 2022 | 0.034082 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-03-12 14:30 | 2022-03-12 14:32 | 539 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-12 | 1078 | keep | 0 | Mar | 2022 | 0.00073422 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
CAGUAS | 2022-03-12 14:34 | 2022-03-13 09:50 | 10 | 019:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C22031200084 | New_Event |  |  | Include | Wildlife | 1156 | 2022-03-12 | 11560 | keep | 0 | Mar | 2022 | 0.0078735 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-12 14:37 | 2022-03-12 15:14 | 40 | 000:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22031200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-03-12 | 1480 | keep | 0 | Mar | 2022 | 0.001008 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-12 14:44 | 2022-03-13 10:30 | 23 | 019:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75 X 75KVA | R22031200075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1186 | 2022-03-12 | 27278 | keep | 0 | Mar | 2022 | 0.018579 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2022-03-12 14:45 | 2022-03-12 18:55 | 200 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA Y FUERTE VIENTO | M22031200109 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2022-03-12 | 50000 | keep | 0 | Mar | 2022 | 0.034055 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-03-12 14:48 | 2022-03-12 16:49 | 5 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES NO CAUSA | R22031200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-03-12 | 605 | keep | 0 | Mar | 2022 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-12 14:48 | 2022-03-12 17:29 | 200 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CULEBRA CRUZO FASE A TIERRA | M22031200110 | New_Event |  |  | Include | Wildlife | 161 | 2022-03-12 | 32200 | keep | 0 | Mar | 2022 | 0.021931 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-12 14:50 | 2022-03-12 15:50 | 7 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22031200377 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-12 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-03-12 14:58 | 2022-03-12 18:22 | 25 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | R22031200080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-03-12 | 5100 | keep | 0 | Mar | 2022 | 0.0034736 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-12 15:04 | 2022-03-13 06:39 | 110 | 015:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22031200093 | New_Event | Bad Weather | Include | Include | Weather | 935 | 2022-03-12 | 102850 | keep | 0 | Mar | 2022 | 0.070051 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-03-12 15:06 | 2022-03-12 18:40 | 40 | 003:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTE HACIA CONDUCTOR ROTO POR DERRUMBE DE ARBOL | C22031200094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-03-12 | 8560 | keep | 0 | Mar | 2022 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-12 16:17 | 2022-03-13 09:40 | 224 | 017:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031200149 | New_Event | Bad Weather | Include | Include | Weather | 1043 | 2022-03-12 | 233632 | keep | 0 | Mar | 2022 | 0.15913 | 0.00015257 | Sustained | FALSE | FALSE | Not_TMED_Event | 224
SAN JUAN | 2022-03-12 16:24 | 2022-03-12 17:00 | 40 | 000:36 | P | TRANSFORMADOR AVERIADO | SE ABRIO EN SU-1 @ PM-21 AFECTANDO 7 PM'S ADICIONALES PARA REEMPLAZO PM-21 MEDIANTE GOI SJ-220312-01. SE REEMPLAZO PM-21 | S22031200127 | New_Event | Service Transformer Failure | Include | Include | Equipment | 36 | 2022-03-12 | 1440 | keep | 0 | Mar | 2022 | 0.00098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-12 17:00 | 2022-03-12 18:12 | 26 | 001:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L Y SE LEVANTO PRIMARIA | B22031200454 | New_Event | Wire Down | Include | Include | Equipment | 72 | 2022-03-12 | 1872 | keep | 0 | Mar | 2022 | 0.001275 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2022-03-12 17:00 | 2022-03-12 18:30 | 10 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 XMR REPARO SECUNDARIA AVERIADA | C22031200127 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-03-12 | 900 | keep | 0 | Mar | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-12 17:02 | 2022-03-13 11:47 | 7 | 018:45 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | C22031200123 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1125 | 2022-03-12 | 7875 | keep | 0 | Mar | 2022 | 0.0053636 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-03-12 17:09 | 2022-03-13 10:40 | 6 | 017:31 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22031200130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1051 | 2022-03-12 | 6306 | keep | 0 | Mar | 2022 | 0.004295 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-03-12 17:24 | 2022-03-12 18:40 | 90 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN SALIDA CONVERTIDOR MAL TIEMPO | C22031200132 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2022-03-12 | 6840 | keep | 0 | Mar | 2022 | 0.0046587 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2022-03-12 17:25 | 2022-03-12 17:35 | 76 | 000:10 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA CERRAR PUENTES PRIMARIOS | P22031200084 | New_Event | Defective Pole | Include | Include | Equipment | 10 | 2022-03-12 | 760 | keep | 0 | Mar | 2022 | 0.00051763 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
FAJARDO | 2022-03-12 17:26 | 2022-03-12 18:24 | 11 | 000:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA PRIMARIA | R22031200092 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2022-03-12 | 638 | keep | 0 | Mar | 2022 | 0.00043454 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2022-03-12 17:57 | 2022-03-12 19:56 | 100 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P22031200122 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2022-03-12 | 11900 | keep | 0 | Mar | 2022 | 0.008105 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-12 18:05 | 2022-03-12 20:10 | 100 | 002:05 | P | PROTECCION DEFECTUOSA | SE SECCIONALIZO 1711-02 EN AVE PERIFERICA MAS ADELANTE Y SE Y SE CERRO MACHETES EN LA PERIFERICA | B22031200178 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 125 | 2022-03-12 | 12500 | keep | 0 | Mar | 2022 | 0.0085137 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-12 18:10 | 2022-03-12 19:58 | 36 | 001:48 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22031200522 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-03-12 | 3888 | keep | 0 | Mar | 2022 | 0.0026481 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-03-12 18:40 | 2022-03-13 00:40 | 20 | 006:00 | P | DESGANCHE | LEVANTO CONDUCTOR DERRUMBADO POR ARBOL | C22031200094 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 360 | 2022-03-12 | 7200 | keep | 0 | Mar | 2022 | 0.0049039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-12 18:49 | 2022-03-12 19:50 | 300 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 100 EN CORTES DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031200170 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2022-03-12 | 18300 | keep | 0 | Mar | 2022 | 0.012464 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-03-12 19:00 | 2022-03-12 20:39 | 41 | 001:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR | R22031200110 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 99 | 2022-03-12 | 4059 | keep | 0 | Mar | 2022 | 0.0027646 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
SAN JUAN | 2022-03-12 19:09 | 2022-03-13 09:59 | 10 | 014:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CAJA HACIA TRANSFORMADOR ZAFAJO | R22031200111 | New_Event | Wire Down | Include | Include | Equipment | 890 | 2022-03-12 | 8900 | keep | 0 | Mar | 2022 | 0.0060617 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-12 19:24 | 2022-03-13 19:07 | 100 | 023:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA EN RISER | B22031200547 | New_Event | Wire Down | Include | Include | Equipment | 1423 | 2022-03-12 | 142300 | keep | 0 | Mar | 2022 | 0.09692 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-12 19:25 | 2022-03-13 02:16 | 20 | 006:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO EN SU-15 HACIA PROVISIONAL | B22031200548 | New_Event | Wire Down | Include | Include | Equipment | 411 | 2022-03-12 | 8220 | keep | 0 | Mar | 2022 | 0.0055986 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-12 19:28 | 2022-03-13 11:23 | 45 | 015:55 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | S22031200188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 955 | 2022-03-12 | 42975 | keep | 0 | Mar | 2022 | 0.02927 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-03-12 19:35 | 2022-03-12 21:50 | 20 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22031200136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2022-03-12 | 2700 | keep | 0 | Mar | 2022 | 0.001839 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-12 19:47 | 2022-03-12 19:48 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22031200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-12 | 2234 | keep | 0 | Mar | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2022-03-12 19:55 | 2022-03-13 08:28 | 12 | 012:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22031200173 | New_Event | Bad Weather | Include | Include | Weather | 753 | 2022-03-12 | 9036 | keep | 0 | Mar | 2022 | 0.0061544 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-12 19:58 | 2022-03-13 19:39 | 2 | 023:41 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | R22031200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1421 | 2022-03-12 | 2842 | keep | 0 | Mar | 2022 | 0.0019357 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-03-12 20:10 | 2022-03-12 22:50 | 50 | 002:40 | P | PROTECCION DEFECTUOSA | SE REMPLAZO AISLADOR Y SE CERRO MACHETE | B22031200178 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 160 | 2022-03-12 | 8000 | keep | 0 | Mar | 2022 | 0.0054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-12 20:26 | 2022-03-13 18:26 | 67 | 022:00 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN RISER SE REEMPLAZO PARARRAYO AVERIADO | P22031200138 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1320 | 2022-03-12 | 88440 | keep | 0 | Mar | 2022 | 0.060236 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2022-03-12 20:26 | 2022-03-13 00:47 | 5 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22031200554 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2022-03-12 | 1305 | keep | 0 | Mar | 2022 | 0.00088883 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-12 20:44 | 2022-03-13 07:30 | 130 | 010:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARARLO SABANA GRANDE LO ATIENDE YAUCO-PONCE | P22031200141 | New_Event | Wire Down | Include | Include | Equipment | 646 | 2022-03-12 | 83980 | keep | 0 | Mar | 2022 | 0.057198 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2022-03-12 20:56 | 2022-03-13 08:42 | 33 | 011:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 Y 2 X 30 EN CORTES DE LINEA SE DESCRUZARON LINEAS CON GUY WIRE | C22031200118 | New_Event | Wire Down | Include | Include | Equipment | 706 | 2022-03-12 | 23298 | keep | 0 | Mar | 2022 | 0.015868 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-03-12 21:15 | 2022-03-12 23:05 | 40 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO Y BAJANTE DE TRANSFORMADOR Y SE HIZO DESGANCHE | B22031200543 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-03-12 | 4400 | keep | 0 | Mar | 2022 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-12 21:44 | 2022-03-13 08:49 | 49 | 011:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L 1 X 65 EN RISER | S22031200228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 665 | 2022-03-12 | 32585 | keep | 0 | Mar | 2022 | 0.022193 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CANOVANAS | 2022-03-12 21:53 | 2022-03-13 13:07 | 70 | 015:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | R22031200136 | New_Event | Wire Down | Include | Include | Equipment | 914 | 2022-03-12 | 63980 | keep | 0 | Mar | 2022 | 0.043576 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-03-12 22:47 | 2022-03-13 13:00 | 300 | 014:13 | P | CABLE SOTERRADO AVERIADO | SE CERRO PUENTE PRIMARIO, 2 X 80 EN RISER A SU-5, AVERIA SOTERRADA DEL SU-5 AL SU-4, 1 X 25 SMU EN SU-1. TODO EN SERVICIO | P22031200158 | New_Event | UG Cable Fault | Include | Include | Equipment | 853 | 2022-03-12 | 255900 | keep | 0 | Mar | 2022 | 0.17429 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2022-03-12 23:13 | 2022-03-13 07:51 | 4 | 008:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR AVE | P22031200162 | New_Event |  |  | Include | Wildlife | 518 | 2022-03-12 | 2072 | keep | 0 | Mar | 2022 | 0.0014112 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-03-13 00:19 | 2022-03-13 09:05 | 30 | 008:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22031300001 | New_Event | Bad Weather | Include | Include | Weather | 526 | 2022-03-13 | 15780 | keep | 0 | Mar | 2022 | 0.010748 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-13 00:36 | 2022-03-13 10:12 | 255 | 009:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 576 | 2022-03-13 | 146880 | keep | 0 | Mar | 2022 | 0.10004 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
ARECIBO | 2022-03-13 00:58 | 2022-03-13 10:05 | 25 | 009:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031300002 | New_Event | Bad Weather | Include | Include | Weather | 547 | 2022-03-13 | 13675 | keep | 0 | Mar | 2022 | 0.009314 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-13 02:16 | 2022-03-13 02:19 | 723 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA CARGA 1711-5 SE PROBO QUEDO EN SERVICIO | B22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-13 | 2169 | keep | 0 | Mar | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-03-13 02:16 | 2022-03-13 02:19 | 723 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA 1711-2 SE PROBO QUEDO EN SERVICIO | B22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-13 | 2169 | keep | 0 | Mar | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-03-13 02:19 | 2022-03-13 06:16 | 20 | 003:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO EN SU-15 HACIA PROVISIONAL | B22031200548 | Partial_restoration | Wire Down | Include | Include | Equipment | 237 | 2022-03-13 | 4740 | keep | 0 | Mar | 2022 | 0.0032284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-13 02:33 | 2022-03-13 19:13 | 10 | 016:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22031300113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1000 | 2022-03-13 | 10000 | keep | 0 | Mar | 2022 | 0.006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-13 02:35 | 2022-03-13 12:20 | 1 | 009:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 585 | 2022-03-13 | 585 | keep | 0 | Mar | 2022 | 0.00039844 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-13 03:32 | 2022-03-13 03:33 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1806-02 QUE LLEVA 10% DEL 1717-01 | B22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 4622 | keep | 0 | Mar | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2022-03-13 04:07 | 2022-03-13 08:43 | 100 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER HACIA RESIDENCIAL | B22031300033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-03-13 | 27600 | keep | 0 | Mar | 2022 | 0.018798 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-13 04:33 | 2022-03-13 08:56 | 50 | 004:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22031300002 | New_Event |  |  | Include | Wildlife | 263 | 2022-03-13 | 13150 | keep | 0 | Mar | 2022 | 0.0089564 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-13 05:46 | 2022-03-13 08:50 | 60 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 40 EN C/L | B22031300035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-03-13 | 11040 | keep | 0 | Mar | 2022 | 0.0075193 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-13 05:59 | 2022-03-13 13:35 | 50 | 007:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | M22031300012 | New_Event | Wire Down | Include | Include | Equipment | 456 | 2022-03-13 | 22800 | keep | 0 | Mar | 2022 | 0.015529 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-13 06:35 | 2022-03-13 15:12 | 100 | 008:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22031300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2022-03-13 | 51700 | keep | 0 | Mar | 2022 | 0.035213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-13 07:16 | 2022-03-13 07:17 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3406-02 CERRADO POR CONTROL | C22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 2435 | keep | 0 | Mar | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-13 07:16 | 2022-03-13 07:17 | 1565 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 3406-02 CERRADO POR CONTROL | C22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 1565 | keep | 0 | Mar | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
MAYAGÃœEZ | 2022-03-13 07:24 | 2022-03-13 16:32 | 244 | 009:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO GLOBO METALICO SOBRE LAS LINEAS | M22031300016 | New_Event |  |  | Include | Wildlife | 548 | 2022-03-13 | 133712 | keep | 0 | Mar | 2022 | 0.091071 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
MAYAGÃœEZ | 2022-03-13 07:30 | 2022-03-13 08:10 | 387 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO SE CERRO CORTE DE LINEA SABANA GRANDE LO ATIENDE YAUCO-PONCE | P22031200141 | Additional_clients | Wire Down | Include | Include | Equipment | 40 | 2022-03-13 | 15480 | keep | 0 | Mar | 2022 | 0.010543 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-13 07:33 | 2022-03-13 07:34 | 718 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22031300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-13 | 718 | keep | 0 | Mar | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
CAGUAS | 2022-03-13 07:34 | 2022-03-13 10:50 | 246 | 003:16 | P | DESGANCHE | 1 X 200 Y 1 X 40 EN CORTES DE LINEA SE DESPEGO BAJANTE Y SE RETIRO PENCA DE LA LINEA | C22031300011 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-03-13 | 48216 | keep | 0 | Mar | 2022 | 0.03284 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
CAGUAS | 2022-03-13 07:54 | 2022-03-13 10:52 | 130 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22031300013 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2022-03-13 | 23140 | keep | 0 | Mar | 2022 | 0.015761 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-03-13 07:58 | 2022-03-14 07:04 | 10 | 023:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRAR PUENTE DE LINEA A CAJA | S22031400019 | New_Event | Wire Down | Include | Include | Equipment | 1386 | 2022-03-13 | 13860 | keep | 0 | Mar | 2022 | 0.00944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-03-13 08:04 | 2022-03-13 10:05 | 100 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | R22031300034 | New_Event |  |  | Include | Wildlife | 121 | 2022-03-13 | 12100 | keep | 0 | Mar | 2022 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-13 08:09 | 2022-03-13 13:19 | 6 | 005:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE POR TENSOR | C22031300017 | New_Event |  |  | Include | Wildlife | 310 | 2022-03-13 | 1860 | keep | 0 | Mar | 2022 | 0.0012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-13 08:13 | 2022-03-13 08:14 | 2781 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1118-09 QUE A SU VEZ LLEVA LA CARGA DEL 1118-08. ADEMAS LLEVA LA CARGA EN TRANSFERENCIAS DE VIA LIBRE D2022-00451 1114-1 75% SE CERRO POR SCADA | S22031300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-13 | 2781 | keep | 0 | Mar | 2022 | 0.0018941 | 0.0018941 | Momentary | FALSE | FALSE | Not_TMED_Event | 2781
BAYAMON | 2022-03-13 08:13 | 2022-03-13 08:14 | 1825 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1118-09 | S22031300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-13 | 1825 | keep | 0 | Mar | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-03-13 08:13 | 2022-03-13 08:14 | 4398 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1118-08 | S22031300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-13 | 4398 | keep | 0 | Mar | 2022 | 0.0029955 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2022-03-13 08:14 | 2022-03-13 09:31 | 2781 | 001:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR POR EMERGENCIA, SE INFORMA ALAMBRE EN EL SUELO DEBIDO A TRANSFERENCIAS. SOLICITADO POR PERSONAL DE CAMPO. VIA LIBRE D2022-00451 SJ-220313-01 | S22031300178 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 77 | 2022-03-13 | 214137 | keep | 0 | Mar | 2022 | 0.14585 | 0.0018941 | Sustained | FALSE | FALSE | Not_TMED_Event | 2781
BAYAMON | 2022-03-13 08:14 | 2022-03-13 09:31 | 1825 | 001:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR POR EMERGENCIA, SE INFORMA ALAMBRE EN EL SUELO DEBIDO A TRANSFERENCIAS. SOLICITADO POR PERSONAL DE CAMPO. VIA LIBRE D2022-00451 SJ-220313-01 CARGA POR EL 1118-09 | S22031300178 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 77 | 2022-03-13 | 140525 | keep | 0 | Mar | 2022 | 0.095711 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-03-13 08:14 | 2022-03-13 09:31 | 4398 | 001:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR POR EMERGENCIA, SE INFORMA ALAMBRE EN EL SUELO DEBIDO A TRANSFERENCIAS. SOLICITADO POR PERSONAL DE CAMPO. VIA LIBRE D2022-00451 SJ-220313-01 LLEVA LA CARGA DEL 1118-08 | S22031300178 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 77 | 2022-03-13 | 338646 | keep | 0 | Mar | 2022 | 0.23065 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
ARECIBO | 2022-03-13 08:25 | 2022-03-13 11:10 | 1 | 002:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22031300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-03-13 | 165 | keep | 0 | Mar | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-13 08:51 | 2022-03-13 08:52 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA | M22031300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 4304 | keep | 0 | Mar | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 849 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 128199 | keep | 0 | Mar | 2022 | 0.087316 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 893 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 LLEVANDO 10% DEL 1422-02 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 134843 | keep | 0 | Mar | 2022 | 0.091841 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 602 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 90902 | keep | 0 | Mar | 2022 | 0.061913 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 43 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 6493 | keep | 0 | Mar | 2022 | 0.0044224 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 1389 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 209739 | keep | 0 | Mar | 2022 | 0.14285 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 67 | 002:31 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISIO 7200 10% DE LA CARGA 1418-02 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 10117 | keep | 0 | Mar | 2022 | 0.0068906 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 605 | 002:31 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 90% DE LA CARGA POR EL 1423-04 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 91355 | keep | 0 | Mar | 2022 | 0.062221 | 0.00041206 | Sustained | FALSE | FALSE | Not_TMED_Event | 605
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 372 | 002:31 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 CARGA POR EL 1423-04 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 56172 | keep | 0 | Mar | 2022 | 0.038258 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 732 | 002:31 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 CARGA POR EL 1423-04 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 110532 | keep | 0 | Mar | 2022 | 0.075283 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 721 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 LLEVA 1437-03 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 108871 | keep | 0 | Mar | 2022 | 0.074152 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 325 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 49075 | keep | 0 | Mar | 2022 | 0.033425 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 600 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 90600 | keep | 0 | Mar | 2022 | 0.061707 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 267 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 40317 | keep | 0 | Mar | 2022 | 0.02746 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 621 | 002:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 93771 | keep | 0 | Mar | 2022 | 0.063867 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-03-13 08:53 | 2022-03-13 11:24 | 1699 | 002:31 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 7200 CARGA POR EL 1423-01 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 151 | 2022-03-13 | 256549 | keep | 0 | Mar | 2022 | 0.17473 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
HUMACAO | 2022-03-13 09:28 | 2022-03-13 15:23 | 65 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN C/L NO CAUSA | C22031300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2022-03-13 | 23075 | keep | 0 | Mar | 2022 | 0.015716 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-03-13 09:31 | 2022-03-13 12:33 | 365 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR EN SUELO GOI SJ-220313-01 | S22031300178 | Partial_restoration | Wire Down | Include | Include | Equipment | 182 | 2022-03-13 | 66430 | keep | 0 | Mar | 2022 | 0.045245 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-13 09:34 | 2022-03-13 12:10 | 1 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22031300008 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2022-03-13 | 156 | keep | 0 | Mar | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-13 09:38 | 2022-03-13 19:15 | 104 | 009:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REEMPLAZO AISLADOR | C22031300025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 577 | 2022-03-13 | 60008 | keep | 0 | Mar | 2022 | 0.040871 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
CAGUAS | 2022-03-13 09:40 | 2022-03-13 15:26 | 10 | 005:46 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 50 KVA X 50 KVA | C22031300028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 346 | 2022-03-13 | 3460 | keep | 0 | Mar | 2022 | 0.0023566 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-13 09:46 | 2022-03-13 15:42 | 50 | 005:56 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22031300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2022-03-13 | 17800 | keep | 0 | Mar | 2022 | 0.012123 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-13 09:50 | 2022-03-13 13:22 | 6 | 003:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | R22031300049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 212 | 2022-03-13 | 1272 | keep | 0 | Mar | 2022 | 0.00086635 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-13 10:05 | 2022-03-13 10:55 | 60 | 000:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | P22031300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2022-03-13 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-13 10:26 | 2022-03-13 18:08 | 100 | 007:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO EN TRONCAL DEL 1530-07 | S22031300233 | New_Event | Wire Down | Include | Include | Equipment | 462 | 2022-03-13 | 46200 | keep | 0 | Mar | 2022 | 0.031467 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-03-13 10:30 | 2022-03-13 13:15 | 200 | 002:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-03-13 | 33000 | keep | 0 | Mar | 2022 | 0.022476 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-03-13 10:34 | 2022-03-13 21:35 | 60 | 011:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | P22031300032 | New_Event | Cutout Failure | Include | Include | Equipment | 661 | 2022-03-13 | 39660 | keep | 0 | Mar | 2022 | 0.027012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-13 10:40 | 2022-03-13 10:50 | 185 | 000:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TERMINO DE ABRIR C/L QUE HABIA FUNDIDO LUEGO DE REMPLAZAR POSTE PARTIDO 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS Y SE RETIRO RAMAS SOBRE LAS LINEAS | M22031200106 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2022-03-13 | 1850 | keep | 0 | Mar | 2022 | 0.00126 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
BAYAMON | 2022-03-13 10:41 | 2022-03-13 12:52 | 150 | 002:11 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | B22031300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-13 | 19650 | keep | 0 | Mar | 2022 | 0.013384 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-03-13 10:46 | 2022-03-13 10:47 | 591 | 000:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1400 SE APAGO BARRA YAUCO | P22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 591 | keep | 0 | Mar | 2022 | 0.00040253 | 0.00040253 | Momentary | FALSE | FALSE | Not_TMED_Event | 591
MAYAGÃœEZ | 2022-03-13 10:46 | 2022-03-13 10:47 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1400 APAGANDOSE BARRA YAUCO 38K | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 281 | keep | 0 | Mar | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-03-13 10:46 | 2022-03-13 10:47 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1400 APAGANDOSE BARRA YAUCO 38K | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 1252 | keep | 0 | Mar | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-03-13 10:46 | 2022-03-13 10:47 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | SABANA GRANDE LO ATIENDE YAUCO-PONCE | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 595 | keep | 0 | Mar | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-03-13 10:46 | 2022-03-13 10:47 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1400 APAGANDOSE BARRA DE YAUCO | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 51 | keep | 0 | Mar | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-13 10:46 | 2022-03-13 10:47 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISAPRO LINEA 1400 APAGANDOSE BARRA DE YAUCO | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 721 | keep | 0 | Mar | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-03-13 10:46 | 2022-03-13 10:47 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1400 APAGANDOSE BARRA YAUCO 38KV | A22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 1382 | keep | 0 | Mar | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-03-13 10:46 | 2022-03-13 10:47 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1400 APAGANDOSE BARRA YAUCO 38K | A22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 654 | keep | 0 | Mar | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
HUMACAO | 2022-03-13 11:06 | 2022-03-13 12:04 | 4 | 000:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR CONTAMINACION EN CAJA PRIMARIA | C22031300046 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2022-03-13 | 232 | keep | 0 | Mar | 2022 | 0.00015801 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-13 11:11 | 2022-03-14 03:10 | 4 | 015:59 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA | M22031300060 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 959 | 2022-03-13 | 3836 | keep | 0 | Mar | 2022 | 0.0026127 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-03-13 11:21 | 2022-03-13 11:24 | 1384 | 000:03 | S | LINEA DE TRANSMISION 38KV | OPERACIONES DE TRANSMISION PARA CERRAR N/O DE ESCUELA INDUSTRIAL | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-13 | 4152 | keep | 0 | Mar | 2022 | 0.0028279 | 0.00094264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2022-03-13 11:21 | 2022-03-13 11:24 | 869 | 000:03 | S | LINEA DE TRANSMISION 38KV | OPERACIONES DE TRANSMISION PARA CERRAR N/O DE ESCUELA INDUSTRIAL | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-13 | 2607 | keep | 0 | Mar | 2022 | 0.0017756 | 0.00059187 | Momentary | FALSE | FALSE | Not_TMED_Event | 869
UTUADO | 2022-03-13 11:27 | 2022-03-13 14:16 | 6 | 002:49 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA | A22031300013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 169 | 2022-03-13 | 1014 | keep | 0 | Mar | 2022 | 0.00069063 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-13 11:46 | 2022-03-13 14:40 | 170 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22031300292 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-03-13 | 29580 | keep | 0 | Mar | 2022 | 0.020147 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
CANOVANAS | 2022-03-13 11:46 | 2022-03-13 15:49 | 75 | 004:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | R22031300062 | New_Event | Cutout Failure | Include | Include | Equipment | 243 | 2022-03-13 | 18225 | keep | 0 | Mar | 2022 | 0.012413 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-03-13 11:50 | 2022-03-14 15:21 | 1 | 027:31 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR Y 1 X 40 EN C/L | S22031300293 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1651 | 2022-03-13 | 1651 | keep | 0 | Mar | 2022 | 0.0011245 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-13 11:51 | 2022-03-13 12:46 | 162 | 000:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22031300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-03-13 | 8910 | keep | 0 | Mar | 2022 | 0.0060686 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
CANOVANAS | 2022-03-13 11:52 | 2022-03-13 11:53 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 7621 | keep | 0 | Mar | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-03-13 12:03 | 2022-03-13 14:45 | 35 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO CULEBRA Y SE REALIZO DESGANCHE | S22031300298 | New_Event |  |  | Include | Wildlife | 162 | 2022-03-13 | 5670 | keep | 0 | Mar | 2022 | 0.0038618 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-03-13 12:09 | 2022-03-13 12:35 | 34 | 000:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22031300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-03-13 | 884 | keep | 0 | Mar | 2022 | 0.00060209 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CANOVANAS | 2022-03-13 12:09 | 2022-03-13 14:46 | 100 | 002:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R22031300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-03-13 | 15700 | keep | 0 | Mar | 2022 | 0.010693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-13 12:28 | 2022-03-13 15:03 | 100 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031300078 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2022-03-13 | 15500 | keep | 0 | Mar | 2022 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-13 12:42 | 2022-03-13 14:50 | 50 | 002:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22031300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-13 | 6400 | keep | 0 | Mar | 2022 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-13 12:55 | 2022-03-14 11:53 | 100 | 022:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA Y 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22031300083 | New_Event | Bad Weather | Include | Include | Weather | 1378 | 2022-03-13 | 137800 | keep | 0 | Mar | 2022 | 0.093855 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-13 13:11 | 2022-03-13 15:30 | 74 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA SE RETIRO GLOBO METALICO | B22031300065 | New_Event |  |  | Include | Wildlife | 139 | 2022-03-13 | 10286 | keep | 0 | Mar | 2022 | 0.0070057 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-03-13 13:20 | 2022-03-14 11:39 | 80 | 022:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22031300325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1339 | 2022-03-13 | 107120 | keep | 0 | Mar | 2022 | 0.072959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-13 13:21 | 2022-03-13 17:02 | 1 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN SUBESTACION CUARTEL POLICIA | B22031300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-03-13 | 221 | keep | 0 | Mar | 2022 | 0.00015052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-13 13:21 | 2022-03-13 15:50 | 60 | 002:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031300089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-03-13 | 8940 | keep | 0 | Mar | 2022 | 0.006089 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-13 13:34 | 2022-03-13 16:24 | 10 | 002:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN XMR SE REPARO PUENTE DE CAJA A XMR | S22031300094 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2022-03-13 | 1700 | keep | 0 | Mar | 2022 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-13 13:48 | 2022-03-14 00:55 | 50 | 011:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22031300096 | New_Event | Bad Weather | Include | Include | Weather | 667 | 2022-03-13 | 33350 | keep | 0 | Mar | 2022 | 0.022715 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-13 13:53 | 2022-03-13 17:22 | 120 | 003:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22031300098 | New_Event |  |  | Include | Wildlife | 209 | 2022-03-13 | 25080 | keep | 0 | Mar | 2022 | 0.017082 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-03-13 14:00 | 2022-03-13 15:00 | 20 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M22031300091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-13 | 1200 | keep | 0 | Mar | 2022 | 0.00081731 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-03-13 14:10 | 2022-03-13 14:50 | 3 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA | P22031300065 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-03-13 | 120 | keep | 0 | Mar | 2022 | 8.1731e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-13 14:24 | 2022-03-13 14:25 | 154 | 000:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4400 1910-01 LLEVA 10% 1519-05 Y 80% 1519-03 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 154 | keep | 0 | Mar | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
BAYAMON | 2022-03-13 14:24 | 2022-03-13 14:25 | 56 | 000:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4400 1910-01 LLEVA 10% 1519-05 Y 80% 1519-03 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 56 | keep | 0 | Mar | 2022 | 3.8141e-05 | 3.8141e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-03-13 14:24 | 2022-03-13 14:25 | 37 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4400 1910-01 LLEVA 10% 1519-05 Y 80% 1519-03 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 37 | keep | 0 | Mar | 2022 | 2.5201e-05 | 2.5201e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-03-13 14:24 | 2022-03-13 14:25 | 7 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4400 1910-01 LLEVA 10% 1519-05 Y 80% 1519-03 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 7 | keep | 0 | Mar | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-13 14:24 | 2022-03-13 14:25 | 2 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4400 1910-01 LLEVA 10% 1519-05 Y 80% 1519-03 | S22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-13 | 2 | keep | 0 | Mar | 2022 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-03-13 14:35 | 2022-03-13 14:36 | 878 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 878 | keep | 0 | Mar | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
ARECIBO | 2022-03-13 14:41 | 2022-03-13 17:40 | 50 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031300019 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2022-03-13 | 8950 | keep | 0 | Mar | 2022 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-13 14:44 | 2022-03-14 14:40 | 24 | 023:56 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22031300372 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1436 | 2022-03-13 | 34464 | keep | 0 | Mar | 2022 | 0.023473 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
PONCE | 2022-03-13 14:45 | 2022-03-13 16:25 | 1078 | 001:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR DE EMERGENCIA LINEA PRIMARIA EN EL PISO EN TRONCAL DEL ALIMENTADOR SE LEVANTO LINEA Y SE CERRO INTERRUPTOR | P22031300069 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2022-03-13 | 107800 | keep | 0 | Mar | 2022 | 0.073422 | 0.00073422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1078
ARECIBO | 2022-03-13 14:57 | 2022-03-13 23:34 | 80 | 008:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22031300021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2022-03-13 | 41360 | keep | 0 | Mar | 2022 | 0.02817 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-13 15:03 | 2022-03-13 15:05 | 2178 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22031300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-13 | 4356 | keep | 0 | Mar | 2022 | 0.0029669 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2022-03-13 15:19 | 2022-03-13 15:20 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIEERE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 222 | keep | 0 | Mar | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-03-13 15:19 | 2022-03-13 15:20 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIEERE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 4456 | keep | 0 | Mar | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
VEGA BAJA | 2022-03-13 15:19 | 2022-03-13 16:00 | 653 | 000:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO Y SE SUBIO CONDUCTOR PRIMARIO SE CAMBIO AISLADOR Y SE LLEVO LINEA AISLADOR | B22031300049 | New_Event | Wire Down | Include | Include | Equipment | 41 | 2022-03-13 | 26773 | keep | 0 | Mar | 2022 | 0.018235 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
BAYAMON | 2022-03-13 15:20 | 2022-03-13 23:53 | 636 | 008:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A MACHETE | S22031300404 | New_Event | Wire Down | Include | Include | Equipment | 513 | 2022-03-13 | 326268 | keep | 0 | Mar | 2022 | 0.22222 | 0.00043318 | Sustained | FALSE | FALSE | Not_TMED_Event | 636
ARECIBO | 2022-03-13 15:38 | 2022-03-13 18:42 | 300 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22031300025 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2022-03-13 | 55200 | keep | 0 | Mar | 2022 | 0.037596 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-03-13 15:50 | 2022-03-13 16:03 | 36 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22031300416 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-03-13 | 468 | keep | 0 | Mar | 2022 | 0.00031875 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-03-13 15:55 | 2022-03-13 17:00 | 25 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22031300135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-03-13 | 1625 | keep | 0 | Mar | 2022 | 0.0011068 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-13 16:10 | 2022-03-13 16:11 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | C22031300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-13 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-13 16:11 | 2022-03-14 16:43 | 40 | 024:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L CRUCE X AVE | C22031300073 | 1st_after_momentary |  |  | Include | Wildlife | 1472 | 2022-03-13 | 58880 | keep | 0 | Mar | 2022 | 0.040103 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-13 16:15 | 2022-03-13 18:32 | 375 | 002:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO CAJA QUEMADA | S22031300428 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2022-03-13 | 51375 | keep | 0 | Mar | 2022 | 0.034991 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
MAYAGÃœEZ | 2022-03-13 16:27 | 2022-03-14 12:39 | 45 | 020:12 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS | M22031300145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1212 | 2022-03-13 | 54540 | keep | 0 | Mar | 2022 | 0.037147 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-03-13 16:30 | 2022-03-13 17:55 | 5 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22031300018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2022-03-13 | 425 | keep | 0 | Mar | 2022 | 0.00028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 888 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 62160 | keep | 0 | Mar | 2022 | 0.042337 | 0.00060481 | Sustained | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 393 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 27510 | keep | 0 | Mar | 2022 | 0.018737 | 0.00026767 | Sustained | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 4 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 280 | keep | 0 | Mar | 2022 | 0.00019071 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 372 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 26040 | keep | 0 | Mar | 2022 | 0.017736 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 2530 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 177100 | keep | 0 | Mar | 2022 | 0.12062 | 0.0017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 199 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 13930 | keep | 0 | Mar | 2022 | 0.0094877 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 312 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 21840 | keep | 0 | Mar | 2022 | 0.014875 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-03-13 17:22 | 2022-03-13 18:32 | 4641 | 001:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22031300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-03-13 | 324870 | keep | 0 | Mar | 2022 | 0.22127 | 0.003161 | Sustained | FALSE | FALSE | Not_TMED_Event | 4641
BAYAMON | 2022-03-13 17:47 | 2022-03-13 19:49 | 25 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER HACIA T638 Y 1 X 80 EN SU4 | B22031300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-03-13 | 3050 | keep | 0 | Mar | 2022 | 0.0020773 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-13 18:08 | 2022-03-13 18:51 | 1420 | 000:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN TRONCAL DEL 1530-07 AFECTANDO LAS CARGAS TOTALES DEL 1530-06 Y 1526-02 QUE ESTAN POR EL 1530-07 | S22031300233 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-03-13 | 61060 | keep | 0 | Mar | 2022 | 0.041588 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2022-03-13 18:08 | 2022-03-13 18:51 | 437 | 000:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN TRONCAL DEL 1530-07 AFECTANDO LAS CARGAS TOTALES DEL 1530-06 Y 1526-02 QUE ESTAN POR EL 1530-07 | S22031300233 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-03-13 | 18791 | keep | 0 | Mar | 2022 | 0.012798 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-03-13 18:08 | 2022-03-13 18:51 | 250 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO MEDIANTE GOI SJ-220313-02 AFECTANDO LAS CARGAS DEL 1530-06 Y 1526-02 | S22031300233 | Additional_clients | Wire Down | Include | Include | Equipment | 43 | 2022-03-13 | 10750 | keep | 0 | Mar | 2022 | 0.0073218 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-13 18:22 | 2022-03-13 18:27 | 1818 | 000:05 | T | DESGANCHE | SE ABRIO EL INTERRUPTOR A PETICION DE SIXTO CANDELARIA YA QUE HABIA BAMBUS QUEMANDOSE SOBRE LA LINEA | M22031300272 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-03-13 | 9090 | keep | 0 | Mar | 2022 | 0.0061912 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
MAYAGÃœEZ | 2022-03-13 18:57 | 2022-03-13 21:52 | 70 | 002:55 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22031300316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-03-13 | 12250 | keep | 0 | Mar | 2022 | 0.0083434 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-03-13 18:57 | 2022-03-13 23:49 | 60 | 004:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO Y SE REALIZO DESGANCHE | M22031300316 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 292 | 2022-03-13 | 17520 | keep | 0 | Mar | 2022 | 0.011933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-13 19:04 | 2022-03-14 13:45 | 10 | 018:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | A22031300064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1121 | 2022-03-13 | 11210 | keep | 0 | Mar | 2022 | 0.0076351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-13 19:08 | 2022-03-13 19:09 | 485 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 485 | keep | 0 | Mar | 2022 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
VEGA BAJA | 2022-03-13 19:08 | 2022-03-13 21:03 | 10 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | B22031300086 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2022-03-13 | 1150 | keep | 0 | Mar | 2022 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-13 19:26 | 2022-03-13 19:36 | 800 | 000:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PARA EVITAR AVERIA NUEVAMENTE DE ALAMBRE EN EL SUELO SE ABRIERON MACHETES N/O FID 33726729 Y SE CERRARON MACHETES FID 33791450 PARA NORMALIZAR LAS CARGAS TRASNFERIDAS EN LA MAÃ‘ANA POR AVERIA DE CONDUCTOR EN OPERACIONES VIA LIBRE D2022-00451 | S22031300207 | New_Event | Wire Down | Include | Include | Equipment | 10 | 2022-03-13 | 8000 | keep | 0 | Mar | 2022 | 0.0054488 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2022-03-13 19:36 | 2022-03-13 21:48 | 30 | 002:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZARON BAJANTE Y DOS CAJAS PRIMARIAS | S22031300545 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2022-03-13 | 3960 | keep | 0 | Mar | 2022 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-13 20:06 | 2022-03-14 11:07 | 51 | 015:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22031300317 | New_Event | Cutout Failure | Include | Include | Equipment | 901 | 2022-03-13 | 45951 | keep | 0 | Mar | 2022 | 0.031297 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
HUMACAO | 2022-03-13 20:16 | 2022-03-14 11:37 | 100 | 015:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZARON DISCOS | C22031300076 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 921 | 2022-03-13 | 92100 | keep | 0 | Mar | 2022 | 0.062729 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-13 20:32 | 2022-03-13 20:35 | 922 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR LLEVANDO CARGA 1346-05 | S22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-13 | 2766 | keep | 0 | Mar | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-13 20:32 | 2022-03-13 20:35 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR LLEVANDO CARGA 1346-05 | S22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-13 | 405 | keep | 0 | Mar | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-03-13 20:52 | 2022-03-13 23:05 | 1131 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | S22031300640 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2022-03-13 | 150423 | keep | 0 | Mar | 2022 | 0.10245 | 0.00077032 | Sustained | FALSE | FALSE | Not_TMED_Event | 1131
FAJARDO | 2022-03-13 20:55 | 2022-03-13 20:56 | 1902 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22031300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 1902 | keep | 0 | Mar | 2022 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
SAN JUAN | 2022-03-13 21:21 | 2022-03-14 16:05 | 60 | 018:44 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22031300701 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1124 | 2022-03-13 | 67440 | keep | 0 | Mar | 2022 | 0.045933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-03-13 21:42 | 2022-03-14 05:40 | 1000 | 007:58 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR BAMBUS | P22031300157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 478 | 2022-03-13 | 478000 | keep | 0 | Mar | 2022 | 0.32556 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2022-03-13 23:29 | 2022-03-14 09:53 | 66 | 010:24 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER A T638 HAY AVERIA DE T 637 A T 636 Y AVERIA VIEJA DE T 636 A T 635 | B22031300093 | New_Event | UG Cable Fault | Include | Include | Equipment | 624 | 2022-03-13 | 41184 | keep | 0 | Mar | 2022 | 0.02805 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-03-13 23:44 | 2022-03-14 13:42 | 60 | 013:58 | P | DESGANCHE | SE REALIZO DESGANCHE 1X65 Y 1X80 EN CORTES DE LINEA | S22031300789 | New_Event | Vegetation Contact | Include | Include | Vegetation | 838 | 2022-03-13 | 50280 | keep | 0 | Mar | 2022 | 0.034245 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-13 23:53 | 2022-03-13 23:54 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-13 | 3431 | keep | 0 | Mar | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
HUMACAO | 2022-03-14 00:45 | 2022-03-14 15:49 | 12 | 015:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22031400002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 904 | 2022-03-14 | 10848 | keep | 0 | Mar | 2022 | 0.0073885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-14 02:09 | 2022-03-14 02:10 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6014-02 | M22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 1444 | keep | 0 | Mar | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-03-14 02:09 | 2022-03-14 02:10 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | M22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 3630 | keep | 0 | Mar | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
CAGUAS | 2022-03-14 02:15 | 2022-03-14 02:18 | 2435 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 3602-01 | C22031400000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-03-14 | 7305 | keep | 0 | Mar | 2022 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-14 02:15 | 2022-03-14 02:18 | 1565 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO LLEVA LA CARGA DEL 3406-02 | C22031400000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-03-14 | 4695 | keep | 0 | Mar | 2022 | 0.0031977 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
VEGA BAJA | 2022-03-14 02:18 | 2022-03-14 02:19 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
CAGUAS | 2022-03-14 02:22 | 2022-03-14 02:24 | 2435 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 3602-01 | C22031400000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-03-14 | 4870 | keep | 0 | Mar | 2022 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-14 02:22 | 2022-03-14 02:24 | 1565 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO LLEVA LA CARGA DEL 3406-02 | C22031400000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-03-14 | 3130 | keep | 0 | Mar | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
FAJARDO | 2022-03-14 02:24 | 2022-03-14 09:07 | 80 | 006:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | R22031400001 | New_Event | Wire Down | Include | Include | Equipment | 403 | 2022-03-14 | 32240 | keep | 0 | Mar | 2022 | 0.021959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-14 03:06 | 2022-03-14 20:45 | 40 | 017:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN SU-1 | S22031400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1059 | 2022-03-14 | 42360 | keep | 0 | Mar | 2022 | 0.028851 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-14 03:17 | 2022-03-14 12:45 | 200 | 009:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A22031400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 568 | 2022-03-14 | 113600 | keep | 0 | Mar | 2022 | 0.077372 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-14 03:40 | 2022-03-14 03:42 | 2435 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 3602-01 | C22031400000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-03-14 | 4870 | keep | 0 | Mar | 2022 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-14 03:40 | 2022-03-14 03:42 | 1565 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO LLEVA LA CARGA DEL 3406-02 | C22031400000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-03-14 | 3130 | keep | 0 | Mar | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-03-14 03:43 | 2022-03-14 07:04 | 2435 | 003:21 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 3602-01 | C22031400022 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2022-03-14 | 489435 | keep | 0 | Mar | 2022 | 0.33335 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-14 03:43 | 2022-03-14 07:04 | 1565 | 003:21 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C22031400022 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2022-03-14 | 314565 | keep | 0 | Mar | 2022 | 0.21425 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
HUMACAO | 2022-03-14 03:49 | 2022-03-14 07:17 | 29 | 003:28 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C22031400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-03-14 | 6032 | keep | 0 | Mar | 2022 | 0.0041084 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
ARECIBO | 2022-03-14 03:50 | 2022-03-14 10:43 | 1464 | 006:53 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO EN TRONCAL DEL ALIMENTADOR | A22031400005 | New_Event | Wire Down | Include | Include | Equipment | 413 | 2022-03-14 | 604632 | keep | 0 | Mar | 2022 | 0.41181 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
CAGUAS | 2022-03-14 04:00 | 2022-03-14 12:21 | 50 | 008:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22031400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2022-03-14 | 25050 | keep | 0 | Mar | 2022 | 0.017061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-14 04:30 | 2022-03-14 04:32 | 3464 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO | R22031400002 | New_Event |  |  | Include | Wildlife | 2 | 2022-03-14 | 6928 | keep | 0 | Mar | 2022 | 0.0047186 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2022-03-14 04:32 | 2022-03-14 13:03 | 50 | 008:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU DE 25 AMP. EN SU-1 CRUCE POR RATA | R22031400027 | 1st_after_momentary |  |  | Include | Wildlife | 511 | 2022-03-14 | 25550 | keep | 0 | Mar | 2022 | 0.017402 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-14 04:49 | 2022-03-14 04:50 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 3431 | keep | 0 | Mar | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2022-03-14 04:54 | 2022-03-14 14:34 | 100 | 009:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L REMPLAZO AISLADORES | C22031400035 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 580 | 2022-03-14 | 58000 | keep | 0 | Mar | 2022 | 0.039504 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-03-14 05:33 | 2022-03-14 05:34 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 1827 | keep | 0 | Mar | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2022-03-14 05:34 | 2022-03-14 05:35 | 840 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 95% POR 1119-4 | S22031400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 840 | keep | 0 | Mar | 2022 | 0.00057212 | 0.00057212 | Momentary | FALSE | FALSE | Not_TMED_Event | 840
BAYAMON | 2022-03-14 05:34 | 2022-03-14 05:35 | 800 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 120 AMP. POR 1119-4 | S22031400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 800 | keep | 0 | Mar | 2022 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2022-03-14 05:34 | 2022-03-14 05:35 | 2720 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA 95% DEL 1115-5 Y 120 AMP. DEL 1119-2 | S22031400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2720 | keep | 0 | Mar | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-03-14 05:43 | 2022-03-14 09:28 | 110 | 003:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA Y SE RETEZO LA MISMA | R22031400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-03-14 | 24750 | keep | 0 | Mar | 2022 | 0.016857 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-03-14 05:45 | 2022-03-14 14:47 | 6 | 009:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22031400046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 542 | 2022-03-14 | 3252 | keep | 0 | Mar | 2022 | 0.0022149 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-03-14 06:27 | 2022-03-14 11:55 | 50 | 005:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22031400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 328 | 2022-03-14 | 16400 | keep | 0 | Mar | 2022 | 0.01117 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-03-14 06:28 | 2022-03-14 08:27 | 7 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C22031400071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-03-14 | 833 | keep | 0 | Mar | 2022 | 0.00056735 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-14 06:31 | 2022-03-14 06:32 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B220300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2605 | keep | 0 | Mar | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-03-14 06:42 | 2022-03-14 15:51 | 30 | 009:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22031400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 549 | 2022-03-14 | 16470 | keep | 0 | Mar | 2022 | 0.011218 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-14 06:54 | 2022-03-14 09:04 | 80 | 002:10 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R22031400009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 130 | 2022-03-14 | 10400 | keep | 0 | Mar | 2022 | 0.0070834 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-14 06:56 | 2022-03-14 21:38 | 271 | 014:42 | T | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA EN LA SALIDA DEL ALIMENTADOR MEDIANTE GOI SJ-220314-01 | S22031400010 | New_Event | UG Cable Fault | Include | Include | Equipment | 882 | 2022-03-14 | 239022 | keep | 0 | Mar | 2022 | 0.1628 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2022-03-14 07:04 | 2022-03-14 07:05 | 929 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1421-04 Y 1421-03 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 929 | keep | 0 | Mar | 2022 | 0.00063274 | 0.00063274 | Momentary | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2022-03-14 07:04 | 2022-03-14 07:05 | 533 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1414-04 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 533 | keep | 0 | Mar | 2022 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2022-03-14 07:04 | 2022-03-14 07:05 | 451 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1414-04 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 451 | keep | 0 | Mar | 2022 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
CAGUAS | 2022-03-14 07:04 | 2022-03-14 09:55 | 400 | 002:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZADO TRAMO EN CARR 184 KM 28.5 | C22031400022 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 171 | 2022-03-14 | 68400 | keep | 0 | Mar | 2022 | 0.046587 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-14 07:05 | 2022-03-14 11:31 | 10 | 004:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRAR PUENTE DE LINEA A CAJA | S22031400019 | Partial_restoration | Wire Down | Include | Include | Equipment | 266 | 2022-03-14 | 2660 | keep | 0 | Mar | 2022 | 0.0018117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-14 07:21 | 2022-03-14 14:30 | 20 | 007:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2022-03-14 | 8580 | keep | 0 | Mar | 2022 | 0.0058438 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-03-14 07:25 | 2022-03-14 15:37 | 10 | 008:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | B22031400006 | New_Event |  |  | Include | Wildlife | 492 | 2022-03-14 | 4920 | keep | 0 | Mar | 2022 | 0.003351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-14 07:27 | 2022-03-14 07:28 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1907-03 LLEVA 1909-09 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 222 | keep | 0 | Mar | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-03-14 07:27 | 2022-03-14 07:28 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1907-03 LLEVA 1909-09 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 4456 | keep | 0 | Mar | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-03-14 07:49 | 2022-03-14 07:50 | 765 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1709-3 LLEVA 1709-05. 50% DEL 1709-3 POR 1909-07 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 765 | keep | 0 | Mar | 2022 | 0.00052104 | 0.00052104 | Momentary | FALSE | FALSE | Not_TMED_Event | 765
BAYAMON | 2022-03-14 07:49 | 2022-03-14 07:50 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-3 LLEVA 1709-05. | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2364 | keep | 0 | Mar | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
HUMACAO | 2022-03-14 08:08 | 2022-03-14 16:39 | 12 | 008:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO BARRAS EN 3 PEDESTALES | C22031400120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 511 | 2022-03-14 | 6132 | keep | 0 | Mar | 2022 | 0.0041765 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-14 08:10 | 2022-03-14 17:55 | 80 | 009:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22031400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 585 | 2022-03-14 | 46800 | keep | 0 | Mar | 2022 | 0.031875 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-14 08:11 | 2022-03-14 17:19 | 65 | 009:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22031400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 548 | 2022-03-14 | 35620 | keep | 0 | Mar | 2022 | 0.024261 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-03-14 08:14 | 2022-03-14 13:20 | 20 | 005:06 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22031400028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-03-14 | 6120 | keep | 0 | Mar | 2022 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-14 08:15 | 2022-03-14 14:38 | 15 | 006:23 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22031400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-03-14 | 5745 | keep | 0 | Mar | 2022 | 0.0039129 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-14 08:25 | 2022-03-14 16:18 | 1 | 007:53 | P | DESGANCHE | 3 X 80 EN C/L DESGANCHO, REMPLAZO 2 CRUCETAS, DISCOS Y 2 CAJAS QUEMADAS | C22031400125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2022-03-14 | 473 | keep | 0 | Mar | 2022 | 0.00032216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-14 08:25 | 2022-03-14 10:41 | 2 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 50 EN RISER PRIVADO DE ANTENA DE COMUNICACIONES NO SE REPORTA CAUSA | P22031400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-03-14 | 272 | keep | 0 | Mar | 2022 | 0.00018526 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-03-14 08:29 | 2022-03-14 11:47 | 125 | 003:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | R22031400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-03-14 | 24750 | keep | 0 | Mar | 2022 | 0.016857 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-03-14 08:43 | 2022-03-14 09:30 | 1 | 000:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR AVE CRUZO FASES | A22031400023 | New_Event |  |  | Include | Wildlife | 47 | 2022-03-14 | 47 | keep | 0 | Mar | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-14 08:54 | 2022-03-14 12:27 | 30 | 003:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-03-14 | 6390 | keep | 0 | Mar | 2022 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-14 08:55 | 2022-03-14 08:56 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 199 | keep | 0 | Mar | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
GUAYAMA | 2022-03-14 09:05 | 2022-03-14 11:20 | 12 | 002:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22031400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-03-14 | 1620 | keep | 0 | Mar | 2022 | 0.0011034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-14 09:19 | 2022-03-14 18:54 | 7 | 009:35 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22031400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 575 | 2022-03-14 | 4025 | keep | 0 | Mar | 2022 | 0.0027414 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-03-14 09:26 | 2022-03-14 14:40 | 50 | 005:14 | P | DESGANCHE | 1 X 65 EN C/L | C22031400131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-03-14 | 15700 | keep | 0 | Mar | 2022 | 0.010693 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-14 09:30 | 2022-03-14 14:50 | 500 | 005:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A22031400027 | New_Event | Cutout Failure | Include | Include | Equipment | 320 | 2022-03-14 | 160000 | keep | 0 | Mar | 2022 | 0.10898 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-03-14 09:31 | 2022-03-14 09:42 | 68 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 748 | keep | 0 | Mar | 2022 | 0.00050946 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-03-14 09:31 | 2022-03-14 09:42 | 171 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 1881 | keep | 0 | Mar | 2022 | 0.0012811 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-03-14 09:31 | 2022-03-14 09:42 | 1837 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 20207 | keep | 0 | Mar | 2022 | 0.013763 | 0.0012512 | Sustained | FALSE | FALSE | Not_TMED_Event | 1837
BAYAMON | 2022-03-14 09:31 | 2022-03-14 09:42 | 536 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-01 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 5896 | keep | 0 | Mar | 2022 | 0.0040157 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2022-03-14 09:31 | 2022-03-14 09:42 | 348 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-01 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 3828 | keep | 0 | Mar | 2022 | 0.0026072 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2022-03-14 09:31 | 2022-03-14 09:42 | 559 | 000:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-01 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 6149 | keep | 0 | Mar | 2022 | 0.0041881 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2022-03-14 09:31 | 2022-03-14 09:42 | 370 | 000:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-01 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 4070 | keep | 0 | Mar | 2022 | 0.0027721 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2022-03-14 09:31 | 2022-03-14 09:42 | 455 | 000:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-02 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 5005 | keep | 0 | Mar | 2022 | 0.0034089 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2022-03-14 09:31 | 2022-03-14 09:42 | 283 | 000:11 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA POR EL 1102-02 | S22031400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 3113 | keep | 0 | Mar | 2022 | 0.0021203 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
BAYAMON | 2022-03-14 09:53 | 2022-03-14 09:54 | 453 | 000:01 | P | CABLE SOTERRADO AVERIADO | RECIERRE DEL 1806-02 LLEVA 10% DEL 1717-01 | B22031400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-14 | 453 | keep | 0 | Mar | 2022 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2022-03-14 09:53 | 2022-03-14 09:54 | 4622 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE DEL 1806-02 LLEVA 10% DEL 1717-01 | B22031400000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-14 | 4622 | keep | 0 | Mar | 2022 | 0.003148 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-14 09:54 | 2022-03-14 15:32 | 66 | 005:38 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER A T638 HAY AVERIA DE T 637 A T 636 Y AVERIA VIEJA DE T 636 A T 635 | B22031300093 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 338 | 2022-03-14 | 22308 | keep | 0 | Mar | 2022 | 0.015194 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
FAJARDO | 2022-03-14 09:55 | 2022-03-14 12:47 | 52 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | R22031400030 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2022-03-14 | 8944 | keep | 0 | Mar | 2022 | 0.0060917 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2022-03-14 09:55 | 2022-03-14 10:16 | 2435 | 000:21 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL 3602-01 | C22031400022 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2022-03-14 | 51135 | keep | 0 | Mar | 2022 | 0.034828 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-14 09:55 | 2022-03-14 10:16 | 1565 | 000:21 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C22031400022 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2022-03-14 | 32865 | keep | 0 | Mar | 2022 | 0.022384 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-14 09:57 | 2022-03-14 09:58 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2022-03-14 10:14 | 2022-03-14 12:44 | 4080 | 002:30 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO ABRIENDO PUENTES EN CALLE GARDENIA Y CERRANDO MACHETES DE TRONCAL EN CALLE RAMON RIOS 1717-01 70% EN SERVICIO Y 10% DE SU CARGA POR 1806-02 GOI BY220314-01A | B22031400021 | New_Event | Defective Pole | Include | Include | Equipment | 150 | 2022-03-14 | 612000 | keep | 0 | Mar | 2022 | 0.41683 | 0.0027789 | Sustained | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2022-03-14 10:14 | 2022-03-14 12:13 | 341 | 001:59 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO ABRIENDO MACHETES DEL 1717-01 Y CERRADO POR SCADA LLEVA 1717-05 | B22031400021 | New_Event | Defective Pole | Include | Include | Equipment | 119 | 2022-03-14 | 40579 | keep | 0 | Mar | 2022 | 0.027638 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
CAGUAS | 2022-03-14 10:16 | 2022-03-14 13:01 | 500 | 002:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS ROTOS, SE REALIZO DESGANCHE CRITICO Y SE CERRO PUENTE ABIERTO | C22031400022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 165 | 2022-03-14 | 82500 | keep | 0 | Mar | 2022 | 0.05619 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-03-14 10:38 | 2022-03-14 10:39 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 4176 | keep | 0 | Mar | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
AGUADILLA | 2022-03-14 10:42 | 2022-03-14 12:53 | 1337 | 002:11 | T | DESGANCHE | DISPARO DEL INTERRUPTOR BAMBUS CRUZARON LAS LINEAS LLEVA LA CARGA DEL 7303-03 | M22031400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-14 | 175147 | keep | 0 | Mar | 2022 | 0.11929 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-03-14 10:42 | 2022-03-14 12:53 | 709 | 002:11 | T | DESGANCHE | SU CARGA POR EL 7303-02 | M22031400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-14 | 92879 | keep | 0 | Mar | 2022 | 0.063259 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
BAYAMON | 2022-03-14 11:02 | 2022-03-14 17:59 | 1243 | 006:57 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE REMPLAZO MACHETE QUEMADO CON GOI BY-220314-02A | B22031400024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2022-03-14 | 518331 | keep | 0 | Mar | 2022 | 0.35303 | 0.0008466 | Sustained | FALSE | FALSE | Not_TMED_Event | 1243
BAYAMON | 2022-03-14 11:10 | 2022-03-14 11:11 | 2147 | 000:01 | T | DESGANCHE | RECIERRE | B22031400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-14 | 2147 | keep | 0 | Mar | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-03-14 11:14 | 2022-03-14 11:15 | 2147 | 000:01 | T | DESGANCHE | RECIERRE | B22031400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-14 | 2147 | keep | 0 | Mar | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
MAYAGÃœEZ | 2022-03-14 11:18 | 2022-03-14 11:19 | 1185 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 1185 | keep | 0 | Mar | 2022 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
UTUADO | 2022-03-14 11:30 | 2022-03-14 11:51 | 1 | 000:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A22031400000 | New_Event | Bad Weather | Include | Include | Weather | 21 | 2022-03-14 | 21 | keep | 0 | Mar | 2022 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-14 11:30 | 2022-03-14 12:20 | 3 | 000:50 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO EN CAJAS SECAS Y SE REPARO Y SE AJUSTO PISTOLA | B22031400000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 50 | 2022-03-14 | 150 | keep | 0 | Mar | 2022 | 0.00010216 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-14 11:51 | 2022-03-14 12:02 | 595 | 000:11 | S | FUEGO | SE ABRIO INTERRUPTORES 7902-01 Y 7902-03 A PETICION DE CHARLES TATUM PARA TRABAJAR SITUACION DE EMERGENCIA EN ACB 8105C DE LINEA 38KV | M22031400000 | New_Event | Fire | Include | Include | Public | 11 | 2022-03-14 | 6545 | keep | 0 | Mar | 2022 | 0.0044578 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-03-14 11:51 | 2022-03-14 12:02 | 51 | 000:11 | S | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTORES 7902-01 Y 7902-03 A PETICION DE CHARLES TATUM PARA TRABAJAR SITUACION DE EMERGENCIA EN ACB 8105C DE LINEA 38KV | M22031400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-03-14 | 561 | keep | 0 | Mar | 2022 | 0.00038209 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-14 11:51 | 2022-03-14 12:02 | 721 | 000:11 | S | FUEGO | SE ABRIO INTERRUPTORES 7902-01 Y 7902-03 A PETICION DE CHARLES TATUM PARA TRABAJAR SITUACION DE EMERGENCIA EN ACB 8105C DE LINEA 38KV | M22031400000 | New_Event | Fire | Include | Include | Public | 11 | 2022-03-14 | 7931 | keep | 0 | Mar | 2022 | 0.0054018 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
MAYAGÃœEZ | 2022-03-14 11:57 | 2022-03-14 12:00 | 281 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22031400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-14 | 843 | keep | 0 | Mar | 2022 | 0.00057416 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-03-14 11:57 | 2022-03-14 12:00 | 1252 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22031400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-14 | 3756 | keep | 0 | Mar | 2022 | 0.0025582 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
UTUADO | 2022-03-14 11:57 | 2022-03-14 12:00 | 1382 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22031400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-14 | 4146 | keep | 0 | Mar | 2022 | 0.0028238 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-03-14 11:57 | 2022-03-14 12:00 | 654 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22031400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-14 | 1962 | keep | 0 | Mar | 2022 | 0.0013363 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
BAYAMON | 2022-03-14 12:24 | 2022-03-14 12:25 | 2147 | 000:01 | T | DESGANCHE | RECIERRE | B22031400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-14 | 2147 | keep | 0 | Mar | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BARRANQUITAS | 2022-03-14 12:25 | 2022-03-14 12:26 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2635 | keep | 0 | Mar | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BAYAMON | 2022-03-14 12:26 | 2022-03-14 15:06 | 2147 | 002:40 | T | DESGANCHE | SE CERRO INTERRUPTOR SECCIONALIZANDO PARA REALIZAR DESGANCHE 50% EN SERVICIO | B22031400021 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-03-14 | 343520 | keep | 0 | Mar | 2022 | 0.23397 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-03-14 12:44 | 2022-03-14 15:43 | 1224 | 002:59 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO ABRIENDO PUENTES EN CALLE GARDENIA Y CERRANDO MACHETES DE TRONCAL EN CALLE RAMON RIOS 1717-01 70% EN SERVICIO Y 10% DE SU CARGA POR 1806-02 GOI BY220314-01A | B22031400021 | Partial_restoration | Defective Pole | Include | Include | Equipment | 179 | 2022-03-14 | 219096 | keep | 0 | Mar | 2022 | 0.14923 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-14 12:45 | 2022-03-14 12:46 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-03-14 12:50 | 2022-03-14 12:51 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22031400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2022-03-14 12:51 | 2022-03-14 14:15 | 200 | 001:24 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S22031400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-03-14 | 16800 | keep | 0 | Mar | 2022 | 0.011442 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-03-14 13:01 | 2022-03-14 13:26 | 90 | 000:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22031400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2022-03-14 | 2250 | keep | 0 | Mar | 2022 | 0.0015325 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2022-03-14 13:06 | 2022-03-14 13:56 | 66 | 000:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22031400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2022-03-14 | 3300 | keep | 0 | Mar | 2022 | 0.0022476 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-03-14 13:16 | 2022-03-14 13:17 | 878 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 878 | keep | 0 | Mar | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2022-03-14 13:16 | 2022-03-14 13:50 | 20 | 000:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50KVA POR 50KVA | S22031400050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 34 | 2022-03-14 | 680 | keep | 0 | Mar | 2022 | 0.00046314 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-14 13:19 | 2022-03-14 13:20 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22021400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
BAYAMON | 2022-03-14 13:27 | 2022-03-14 13:28 | 878 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 878 | keep | 0 | Mar | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
UTUADO | 2022-03-14 14:30 | 2022-03-14 16:15 | 50 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA Y SE REALIZO DESGANCHE | A22031400035 | New_Event | Wire Down | Include | Include | Equipment | 105 | 2022-03-14 | 5250 | keep | 0 | Mar | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-03-14 14:38 | 2022-03-14 14:39 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2635 | keep | 0 | Mar | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-03-14 14:39 | 2022-03-14 15:08 | 66 | 000:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22031300138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-03-14 | 1914 | keep | 0 | Mar | 2022 | 0.0013036 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CANOVANAS | 2022-03-14 14:50 | 2022-03-14 16:59 | 7 | 002:09 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIR XMR PARA REPARAR SECUNDARIA Y POSTE PARTIDO | R22031400033 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 129 | 2022-03-14 | 903 | keep | 0 | Mar | 2022 | 0.00061503 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-14 15:02 | 2022-03-15 21:00 | 100 | 029:58 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE CERRO PUENTES | M22031500045 | New_Event | Defective Pole | Include | Include | Equipment | 1798 | 2022-03-14 | 179800 | keep | 0 | Mar | 2022 | 0.12246 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-14 15:06 | 2022-03-14 18:21 | 1073 | 003:15 | P | DESGANCHE | SE CERRO INTERRUPTOR SECCIONALIZANDO PARA REALIZAR DESGANCHE 100% EN SERVICIO | B22031400021 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-03-14 | 209235 | keep | 0 | Mar | 2022 | 0.14251 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-14 15:09 | 2022-03-14 19:40 | 6 | 004:31 | P | ESTRUCTURA AVERIADA | SE ABRIERON PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO | M22031400119 | New_Event | Defective Pole | Include | Include | Equipment | 271 | 2022-03-14 | 1626 | keep | 0 | Mar | 2022 | 0.0011075 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-14 15:11 | 2022-03-14 18:12 | 100 | 003:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-03-14 | 18100 | keep | 0 | Mar | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-14 15:12 | 2022-03-14 16:58 | 52 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER 1 X 50 EN RISER 1 X 80 EN C/L 52 CLIENTES | R22031400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-03-14 | 5512 | keep | 0 | Mar | 2022 | 0.0037542 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
ARECIBO | 2022-03-14 15:12 | 2022-03-14 16:44 | 40 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031400043 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2022-03-14 | 3680 | keep | 0 | Mar | 2022 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-14 15:12 | 2022-03-14 17:57 | 50 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22031400041 | New_Event |  |  | Include | Wildlife | 165 | 2022-03-14 | 8250 | keep | 0 | Mar | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-14 15:14 | 2022-03-14 17:30 | 2 | 002:16 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE EN GOI BY-220314-02A | B22031400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-03-14 | 272 | keep | 0 | Mar | 2022 | 0.00018526 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-03-14 15:14 | 2022-03-14 17:20 | 400 | 002:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22031400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-03-14 | 50400 | keep | 0 | Mar | 2022 | 0.034327 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2022-03-14 15:18 | 2022-03-14 19:05 | 85 | 003:47 | P | DESGANCHE | 2 X 50 EN C/L | C22031400149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-03-14 | 19295 | keep | 0 | Mar | 2022 | 0.013142 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2022-03-14 15:22 | 2022-03-14 18:25 | 40 | 003:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22031400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-03-14 | 7320 | keep | 0 | Mar | 2022 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-03-14 15:30 | 2022-03-14 19:08 | 4 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE SECUNDARIO PARTIDO POR CAMION SE ATACHAN LINEAS SECUNDARIAS A POSTE SECUNDARIO CERCANO | P22031400037 | New_Event |  |  | Include | Wildlife | 218 | 2022-03-14 | 872 | keep | 0 | Mar | 2022 | 0.00059392 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-03-14 15:34 | 2022-03-14 19:07 | 54 | 003:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22031400156 | New_Event |  |  | Include | Wildlife | 213 | 2022-03-14 | 11502 | keep | 0 | Mar | 2022 | 0.007834 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2022-03-14 15:43 | 2022-03-14 15:49 | 4080 | 000:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR SCADA 90% DE SU CARGA Y LLEVANDO CARGA 1717-05 10% DE SU CARGA POR 1806-02. CAJA PRIMARIA QUEMADA EN RISER PERTENECIENTE A 1717-05 | B22031400021 | New_Event | Cutout Failure | Include | Include | Equipment | 6 | 2022-03-14 | 24480 | keep | 0 | Mar | 2022 | 0.016673 | 0.0027789 | Sustained | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2022-03-14 15:43 | 2022-03-14 15:49 | 341 | 000:06 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR CONTROL CARGA POR INTERRUPTOR 1717-01 POSTE PARTIDO EN 1717-01 ESTABA SECCIONALIZADO. CAJA PRIMARIA QUEMADA EN RISER PERTENECIENTE A 1717-05 | B22031400000 | New_Event | Cutout Failure | Include | Include | Equipment | 6 | 2022-03-14 | 2046 | keep | 0 | Mar | 2022 | 0.0013935 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2022-03-14 15:49 | 2022-03-14 18:01 | 1224 | 002:12 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO ABRIENDO PUENTES EN CALLE GARDENIA Y CERRANDO MACHETES DE TRONCAL EN CALLE RAMON RIOS 1717-01 70% EN SERVICIO Y 10% DE SU CARGA POR 1806-02 GOI BY220314-01A | B22031400021 | Partial_restoration | Defective Pole | Include | Include | Equipment | 132 | 2022-03-14 | 161568 | keep | 0 | Mar | 2022 | 0.11004 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-14 15:49 | 2022-03-14 18:15 | 120 | 002:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REMPLAZO CAJA QUEMADA EN RISER | B22031400210 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 146 | 2022-03-14 | 17520 | keep | 0 | Mar | 2022 | 0.011933 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-14 15:49 | 2022-03-14 15:50 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 176 | keep | 0 | Mar | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
GUAYAMA | 2022-03-14 16:00 | 2022-03-14 17:00 | 33 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA FUERTE BRISA | P22031400055 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2022-03-14 | 1980 | keep | 0 | Mar | 2022 | 0.0013486 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-03-14 16:27 | 2022-03-14 18:10 | 100 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031400145 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2022-03-14 | 10300 | keep | 0 | Mar | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-14 16:44 | 2022-03-15 16:27 | 1 | 023:43 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | R22031400036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1423 | 2022-03-14 | 1423 | keep | 0 | Mar | 2022 | 0.0009692 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-14 16:44 | 2022-03-14 17:10 | 2 | 000:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL SECUNDARIO | M22031400074 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 26 | 2022-03-14 | 52 | keep | 0 | Mar | 2022 | 3.5417e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-03-14 16:45 | 2022-03-14 17:48 | 17 | 001:03 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22031400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-03-14 | 1071 | keep | 0 | Mar | 2022 | 0.00072945 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2022-03-14 16:45 | 2022-03-15 10:43 | 1 | 017:58 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | C22031400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1078 | 2022-03-14 | 1078 | keep | 0 | Mar | 2022 | 0.00073422 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-14 16:45 | 2022-03-14 17:39 | 60 | 000:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031400080 | New_Event | Bad Weather | Include | Include | Weather | 54 | 2022-03-14 | 3240 | keep | 0 | Mar | 2022 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-03-14 16:45 | 2022-03-15 16:30 | 10 | 023:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE FIJARON CAJAS PRIMARIAS SAFADAS DE LA CRUCETA | A22031400058 | New_Event | Cutout Failure | Include | Include | Equipment | 1425 | 2022-03-14 | 14250 | keep | 0 | Mar | 2022 | 0.0097056 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-14 16:45 | 2022-03-14 19:00 | 15 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031400059 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2022-03-14 | 2025 | keep | 0 | Mar | 2022 | 0.0013792 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-14 16:48 | 2022-03-15 08:57 | 110 | 016:09 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEAS | C22031400160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 969 | 2022-03-14 | 106590 | keep | 0 | Mar | 2022 | 0.072598 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2022-03-14 16:51 | 2022-03-14 18:14 | 7 | 001:23 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE SECUNDARIO | C22031400165 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 83 | 2022-03-14 | 581 | keep | 0 | Mar | 2022 | 0.00039572 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-03-14 16:56 | 2022-03-14 19:16 | 39 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTE BRISA | P22031400059 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2022-03-14 | 5460 | keep | 0 | Mar | 2022 | 0.0037188 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
ARECIBO | 2022-03-14 16:56 | 2022-03-14 19:45 | 150 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031400069 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2022-03-14 | 25350 | keep | 0 | Mar | 2022 | 0.017266 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-03-14 16:58 | 2022-03-14 21:08 | 40 | 004:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE DE LINEA A CAJA NO FUNDIO | C22031400167 | New_Event | Wire Down | Include | Include | Equipment | 250 | 2022-03-14 | 10000 | keep | 0 | Mar | 2022 | 0.006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-14 17:05 | 2022-03-14 18:35 | 100 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22031400105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-03-14 | 9000 | keep | 0 | Mar | 2022 | 0.0061299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-14 17:16 | 2022-03-15 11:00 | 15 | 017:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50 KVA POR 50 KVA | R22031400049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1064 | 2022-03-14 | 15960 | keep | 0 | Mar | 2022 | 0.01087 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-03-14 17:25 | 2022-03-14 17:40 | 12 | 000:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031400083 | New_Event | Bad Weather | Include | Include | Weather | 15 | 2022-03-14 | 180 | keep | 0 | Mar | 2022 | 0.0001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-03-14 17:29 | 2022-03-14 18:30 | 90 | 001:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P22031400064 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2022-03-14 | 5490 | keep | 0 | Mar | 2022 | 0.0037392 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-03-14 17:42 | 2022-03-14 19:32 | 50 | 001:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L SE REEMPLAZO PIN POLE TOP Y AISLADOR | R22031400052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2022-03-14 | 5500 | keep | 0 | Mar | 2022 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-14 17:45 | 2022-03-14 17:46 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 Y 50% DE SU CARGA TRANSFERIDA AL 1909-07 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 767 | keep | 0 | Mar | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-03-14 17:45 | 2022-03-14 17:46 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 Y 50% DE SU CARGA TRANSFERIDA AL 1909-07 | S22031400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-14 | 2364 | keep | 0 | Mar | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
SAN JUAN | 2022-03-14 17:54 | 2022-03-14 18:33 | 80 | 000:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ENCONTRO CAJA QUEMADA EN CORTE DE LINEA PERO POR SEGURIDAD SE ESTABLECIO GOI SJ-220314-03 DISPARANDO INTERRUPTOR 1330-02 YA QUE SERIA EN ESCALERA INFORMA ANGEL CALO | S22031400125 | New_Event | Cutout Failure | Include | Include | Equipment | 39 | 2022-03-14 | 3120 | keep | 0 | Mar | 2022 | 0.002125 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-14 18:01 | 2022-03-14 18:32 | 4080 | 000:31 | P | ESTRUCTURA AVERIADA | SE ABRIO MACHETES DE TRONCAL 1717-01 EN CALLE RAMON RIOS PARA CERRAR PUENTES PRIMARIOS EN CALLE GARDENIA SABANA SECA Y SE VOLVIERON A CERRAR 100% DE ALIMENTADOR EN SERVICIO | B22031400021 | Additional_clients | Defective Pole | Include | Include | Equipment | 31 | 2022-03-14 | 126480 | keep | 0 | Mar | 2022 | 0.086145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-03-14 18:04 | 2022-03-14 20:15 | 25 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P22031400077 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2022-03-14 | 3275 | keep | 0 | Mar | 2022 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-03-14 18:09 | 2022-03-15 09:34 | 80 | 015:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22031400200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 925 | 2022-03-14 | 74000 | keep | 0 | Mar | 2022 | 0.050401 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-14 18:15 | 2022-03-14 18:18 | 341 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR CONTROL CARGA POR INTERRUPTOR 1717-01 CARGA DE 1717-01 ESTABA SECCIONALIZADA POR POSTE PARTIDO. CAJA PRIMARIA QUEMADA EN RISER PERTENECIENTE A 1717-05 | B22031400000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 3 | 2022-03-14 | 1023 | keep | 0 | Mar | 2022 | 0.00069676 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-14 18:18 | 2022-03-14 20:49 | 120 | 002:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REMPLAZO CAJA QUEMADA EN RISER | B22031400210 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 151 | 2022-03-14 | 18120 | keep | 0 | Mar | 2022 | 0.012341 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-03-14 18:20 | 2022-03-15 10:26 | 15 | 016:06 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE ABIERTO | R22031400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 966 | 2022-03-14 | 14490 | keep | 0 | Mar | 2022 | 0.0098691 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-03-14 18:28 | 2022-03-14 20:04 | 20 | 001:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031400175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-03-14 | 1920 | keep | 0 | Mar | 2022 | 0.0013077 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-14 18:31 | 2022-03-14 22:46 | 15 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M22031400176 | New_Event | Bad Weather | Include | Include | Weather | 255 | 2022-03-14 | 3825 | keep | 0 | Mar | 2022 | 0.0026052 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-14 18:33 | 2022-03-14 19:12 | 533 | 000:39 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA REEMPLAZO DE CAJA QUEMADA EN CORTE DE LINEA A ESCALERA A PETICION DE ANGEL CALO GOI SJ-220314-03 | S22031400146 | Additional_clients | Cutout Failure | Include | Include | Equipment | 39 | 2022-03-14 | 20787 | keep | 0 | Mar | 2022 | 0.014158 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-14 18:35 | 2022-03-15 10:18 | 60 | 015:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22031400202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 943 | 2022-03-14 | 56580 | keep | 0 | Mar | 2022 | 0.038536 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-03-14 18:41 | 2022-03-15 04:05 | 40 | 009:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22031400182 | New_Event | Bad Weather | Include | Include | Weather | 564 | 2022-03-14 | 22560 | keep | 0 | Mar | 2022 | 0.015366 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-14 18:50 | 2022-03-14 18:51 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22031400208 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-14 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-14 18:51 | 2022-03-14 20:04 | 40 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C22031400209 | 1st_after_momentary |  |  | Include | Wildlife | 73 | 2022-03-14 | 2920 | keep | 0 | Mar | 2022 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-14 18:53 | 2022-03-14 19:55 | 90 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031400185 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2022-03-14 | 5580 | keep | 0 | Mar | 2022 | 0.0038005 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-03-14 19:00 | 2022-03-14 21:46 | 30 | 002:46 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA | B22031400187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-03-14 | 4980 | keep | 0 | Mar | 2022 | 0.0033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-03-14 19:00 | 2022-03-14 19:03 | 2192 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO | C22031400211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-14 | 6576 | keep | 0 | Mar | 2022 | 0.0044789 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
MAYAGÃœEZ | 2022-03-14 19:05 | 2022-03-15 01:48 | 6 | 006:43 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | M22031400193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2022-03-14 | 2418 | keep | 0 | Mar | 2022 | 0.0016469 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-03-14 19:06 | 2022-03-15 11:30 | 400 | 016:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | M22031400194 | New_Event | Wire Down | Include | Include | Equipment | 984 | 2022-03-14 | 393600 | keep | 0 | Mar | 2022 | 0.26808 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2022-03-14 19:12 | 2022-03-15 11:15 | 10 | 016:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22031400198 | New_Event | Wire Down | Include | Include | Equipment | 963 | 2022-03-14 | 9630 | keep | 0 | Mar | 2022 | 0.0065589 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-14 19:13 | 2022-03-15 09:22 | 90 | 014:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22031400199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 849 | 2022-03-14 | 76410 | keep | 0 | Mar | 2022 | 0.052043 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-03-14 19:16 | 2022-03-14 22:51 | 5 | 003:35 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | B22031400200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-03-14 | 1075 | keep | 0 | Mar | 2022 | 0.00073218 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-14 19:18 | 2022-03-15 11:05 | 12 | 015:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO EN XMR | C22031400214 | New_Event | Secondary Wire Down | Include | Include | Equipment | 947 | 2022-03-14 | 11364 | keep | 0 | Mar | 2022 | 0.00774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-03-14 19:23 | 2022-03-15 06:25 | 30 | 011:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031400204 | New_Event | Bad Weather | Include | Include | Weather | 662 | 2022-03-14 | 19860 | keep | 0 | Mar | 2022 | 0.013527 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-14 19:33 | 2022-03-15 11:34 | 100 | 016:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22031400207 | New_Event | Bad Weather | Include | Include | Weather | 961 | 2022-03-14 | 96100 | keep | 0 | Mar | 2022 | 0.065453 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-14 19:42 | 2022-03-14 22:44 | 48 | 003:02 | P | DESGANCHE | 3 X 65 EN RISER | S22031400164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-03-14 | 8736 | keep | 0 | Mar | 2022 | 0.00595 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2022-03-14 19:57 | 2022-03-14 20:24 | 8 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PAR REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | S22031400101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-03-14 | 216 | keep | 0 | Mar | 2022 | 0.00014712 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-03-14 20:21 | 2022-03-15 10:00 | 4 | 013:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO ZAFADO EN TRANSFORMADOR | A22031400134 | New_Event | Wire Down | Include | Include | Equipment | 819 | 2022-03-14 | 3276 | keep | 0 | Mar | 2022 | 0.0022313 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-03-14 20:29 | 2022-03-14 21:05 | 8 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22031400135 | New_Event | Wire Down | Include | Include | Equipment | 36 | 2022-03-14 | 288 | keep | 0 | Mar | 2022 | 0.00019616 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-03-14 20:38 | 2022-03-15 07:53 | 170 | 011:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 Y 1 X 80 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C22031400228 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 675 | 2022-03-14 | 114750 | keep | 0 | Mar | 2022 | 0.078156 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
MAYAGÃœEZ | 2022-03-14 20:47 | 2022-03-15 12:45 | 15 | 015:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031400222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 958 | 2022-03-14 | 14370 | keep | 0 | Mar | 2022 | 0.0097873 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-14 21:10 | 2022-03-15 09:30 | 80 | 012:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-1 | S22031400173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 740 | 2022-03-14 | 59200 | keep | 0 | Mar | 2022 | 0.040321 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-14 21:31 | 2022-03-15 11:30 | 30 | 013:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22031400226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 839 | 2022-03-14 | 25170 | keep | 0 | Mar | 2022 | 0.017143 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-14 21:38 | 2022-03-15 06:12 | 200 | 008:34 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | C22031400256 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 514 | 2022-03-14 | 102800 | keep | 0 | Mar | 2022 | 0.070017 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-03-14 21:49 | 2022-03-15 08:20 | 80 | 010:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031400228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 631 | 2022-03-14 | 50480 | keep | 0 | Mar | 2022 | 0.034382 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-14 22:05 | 2022-03-14 23:48 | 58 | 001:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B22031400229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-03-14 | 5974 | keep | 0 | Mar | 2022 | 0.0040689 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-03-14 22:05 | 2022-03-14 23:40 | 12 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE TRAS PATIO | B22031400221 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2022-03-14 | 1140 | keep | 0 | Mar | 2022 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-14 22:15 | 2022-03-15 13:30 | 20 | 015:15 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031400232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 915 | 2022-03-14 | 18300 | keep | 0 | Mar | 2022 | 0.012464 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-14 22:43 | 2022-03-15 13:15 | 15 | 014:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22031400178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 872 | 2022-03-14 | 13080 | keep | 0 | Mar | 2022 | 0.0089087 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-14 22:48 | 2022-03-14 22:49 | 2450 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22031400281 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-03-14 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-14 22:49 | 2022-03-15 07:57 | 80 | 009:08 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA REEMPLAZO PARARRAYO Y CAJA DE XMR DEFECTUOSA. | C22031400288 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 548 | 2022-03-14 | 43840 | keep | 0 | Mar | 2022 | 0.029859 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-14 23:24 | 2022-03-15 16:48 | 400 | 017:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 Y 3 X 100 EN CORTES DE LINEAS SE REMPLAZARON CAJAS PRIMARIAS AVERIADAS | A22031400142 | New_Event | Cutout Failure | Include | Include | Equipment | 1044 | 2022-03-14 | 417600 | keep | 0 | Mar | 2022 | 0.28443 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-03-14 23:40 | 2022-03-14 23:52 | 19 | 000:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE TRAS PATIO Y SE REMPLAZO CAJA | B22031400221 | Additional_clients | Wire Down | Include | Include | Equipment | 12 | 2022-03-14 | 228 | keep | 0 | Mar | 2022 | 0.00015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-14 23:55 | 2022-03-15 08:40 | 50 | 008:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22031400237 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 525 | 2022-03-14 | 26250 | keep | 0 | Mar | 2022 | 0.017879 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-15 00:29 | 2022-03-15 02:50 | 100 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M22031500003 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2022-03-15 | 14100 | keep | 0 | Mar | 2022 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-15 01:12 | 2022-03-15 01:13 | 908 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 908 | keep | 0 | Mar | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
CANOVANAS | 2022-03-15 01:16 | 2022-03-15 01:17 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | R22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 2106 | keep | 0 | Mar | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2022-03-15 02:29 | 2022-03-15 02:30 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 1894 | keep | 0 | Mar | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
SAN JUAN | 2022-03-15 02:49 | 2022-03-15 05:42 | 858 | 002:53 | P | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA FTE. CHALET DEL PARQUE CARR.844 | S22031500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-03-15 | 148434 | keep | 0 | Mar | 2022 | 0.1011 | 0.00058438 | Sustained | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-03-15 02:49 | 2022-03-15 05:21 | 2435 | 002:32 | T | DESGANCHE | SE ENCONTRO BAMBUAS SOBRE LINEA CARR.844 CHALET DEL PARQUE SE ABRIO MACHETE PARA SECCIONALIZAR | S22031500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-03-15 | 370120 | keep | 0 | Mar | 2022 | 0.25209 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2022-03-15 05:21 | 2022-03-15 05:42 | 500 | 000:21 | P | DESGANCHE | SE RETIRO BAMBUAS Y SE CERRO MACHETE | S22031500001 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 21 | 2022-03-15 | 10500 | keep | 0 | Mar | 2022 | 0.0071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-15 06:13 | 2022-03-15 06:14 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 108 | keep | 0 | Mar | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
CANOVANAS | 2022-03-15 06:51 | 2022-03-15 06:52 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 2708 | keep | 0 | Mar | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BAYAMON | 2022-03-15 06:52 | 2022-03-15 06:53 | 2735 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B22031500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-15 | 2735 | keep | 0 | Mar | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
PONCE | 2022-03-15 07:00 | 2022-03-15 14:32 | 1 | 007:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | P22031500072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 452 | 2022-03-15 | 452 | keep | 0 | Mar | 2022 | 0.00030786 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-15 07:03 | 2022-03-15 08:04 | 2107 | 001:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AISLADORES ROTOS Y CAJA PRIMARIA QUEMADA EN BANCO DE TRANSFORMADORES Y SE CERRO EL INTERRUPTOR | A22031500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 61 | 2022-03-15 | 128527 | keep | 0 | Mar | 2022 | 0.087539 | 0.0014351 | Sustained | FALSE | FALSE | Not_TMED_Event | 2107
BAYAMON | 2022-03-15 07:57 | 2022-03-15 09:20 | 2735 | 001:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR MEDIANTE GOI BY-220315-01 75% EN SERVICIO | B22031500022 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 83 | 2022-03-15 | 227005 | keep | 0 | Mar | 2022 | 0.15461 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
ARECIBO | 2022-03-15 08:04 | 2022-03-15 10:05 | 1264 | 002:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DOS AISLADORES ROTOS Y UNA CAJA PRIMARIA QUEMADA EN MONTURA DE TRANSFORMADORES Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A22031500000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 121 | 2022-03-15 | 152944 | keep | 0 | Mar | 2022 | 0.10417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-15 08:19 | 2022-03-15 08:20 | 73 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 73 | keep | 0 | Mar | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2022-03-15 08:28 | 2022-03-15 11:53 | 6 | 003:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN AEREO PROVISIONAL SE REMPLAZO TERMINACION AEREA Y PISTOLA | S22031500071 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 205 | 2022-03-15 | 1230 | keep | 0 | Mar | 2022 | 0.00083775 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-15 08:36 | 2022-03-15 13:02 | 20 | 004:26 | P | PARARRAYOS DEFECTUOSO | 1 X65 EN C/L SE RETIRO PARARRAYO SE DESGANCHO Y SE REPARO SECUNDARIA TRASPATIO | S22031500031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 266 | 2022-03-15 | 5320 | keep | 0 | Mar | 2022 | 0.0036234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-15 08:36 | 2022-03-15 18:10 | 15 | 009:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN PROVISIONAL SE REMPLAZO TERMINACION EN RISER | B22031500012 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 574 | 2022-03-15 | 8610 | keep | 0 | Mar | 2022 | 0.0058642 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-15 08:36 | 2022-03-15 11:25 | 40 | 002:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22031500007 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2022-03-15 | 6760 | keep | 0 | Mar | 2022 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-15 08:36 | 2022-03-15 16:12 | 15 | 007:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA | A22031500009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 456 | 2022-03-15 | 6840 | keep | 0 | Mar | 2022 | 0.0046587 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-03-15 08:36 | 2022-03-15 18:52 | 50 | 010:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22031500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 616 | 2022-03-15 | 30800 | keep | 0 | Mar | 2022 | 0.020978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-15 08:37 | 2022-03-15 10:45 | 200 | 002:08 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22031500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-15 | 25600 | keep | 0 | Mar | 2022 | 0.017436 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-03-15 08:37 | 2022-03-15 09:55 | 2 | 001:18 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR POR DESGANCHE | P22031500004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 78 | 2022-03-15 | 156 | keep | 0 | Mar | 2022 | 0.00010625 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-03-15 08:37 | 2022-03-15 11:02 | 200 | 002:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA POR AVE | P22031500008 | New_Event |  |  | Include | Wildlife | 145 | 2022-03-15 | 29000 | keep | 0 | Mar | 2022 | 0.019752 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-03-15 08:37 | 2022-03-15 20:49 | 75 | 012:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | B22031500026 | New_Event |  |  | Include | Wildlife | 732 | 2022-03-15 | 54900 | keep | 0 | Mar | 2022 | 0.037392 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-03-15 08:38 | 2022-03-15 19:35 | 45 | 010:57 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S22031500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 657 | 2022-03-15 | 29565 | keep | 0 | Mar | 2022 | 0.020137 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-03-15 08:38 | 2022-03-15 15:16 | 25 | 006:38 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22031500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2022-03-15 | 9950 | keep | 0 | Mar | 2022 | 0.0067769 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-03-15 08:38 | 2022-03-15 12:30 | 50 | 003:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22031500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-03-15 | 11600 | keep | 0 | Mar | 2022 | 0.0079007 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-15 08:40 | 2022-03-16 05:53 | 20 | 021:13 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22031500074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1273 | 2022-03-15 | 25460 | keep | 0 | Mar | 2022 | 0.017341 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-15 08:45 | 2022-03-15 17:42 | 1 | 008:57 | P | NO SE REPORTO CAUSA | 2 X 10 EN XMR | S22031500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 537 | 2022-03-15 | 537 | keep | 0 | Mar | 2022 | 0.00036575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-15 08:58 | 2022-03-15 14:30 | 15 | 005:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22031500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 332 | 2022-03-15 | 4980 | keep | 0 | Mar | 2022 | 0.0033919 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-15 09:05 | 2022-03-15 18:44 | 25 | 009:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L DESGANCHE Y SE FIJO LINEA A AISLADOR | S22031500107 | New_Event | Wire Down | Include | Include | Equipment | 579 | 2022-03-15 | 14475 | keep | 0 | Mar | 2022 | 0.0098589 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-03-15 09:07 | 2022-03-15 12:12 | 50 | 003:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22031500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-03-15 | 9250 | keep | 0 | Mar | 2022 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-15 09:08 | 2022-03-15 12:03 | 35 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22031500116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2022-03-15 | 6125 | keep | 0 | Mar | 2022 | 0.0041717 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-03-15 09:20 | 2022-03-15 15:57 | 683 | 006:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR CON GOI BY-220315-01 100% EN SERVICIO | B22031500022 | Partial_restoration | Wire Down | Include | Include | Equipment | 397 | 2022-03-15 | 271151 | keep | 0 | Mar | 2022 | 0.18468 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-15 09:27 | 2022-03-15 14:52 | 10 | 005:25 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO AL T-636 | B22031500070 | New_Event | UG Cable Fault | Include | Include | Equipment | 325 | 2022-03-15 | 3250 | keep | 0 | Mar | 2022 | 0.0022136 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-15 09:48 | 2022-03-15 12:40 | 60 | 002:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22031500152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-03-15 | 10320 | keep | 0 | Mar | 2022 | 0.0070289 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-15 09:55 | 2022-03-15 14:40 | 40 | 004:45 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | M22031500051 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 285 | 2022-03-15 | 11400 | keep | 0 | Mar | 2022 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-15 10:03 | 2022-03-15 11:40 | 90 | 001:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22031500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-03-15 | 8730 | keep | 0 | Mar | 2022 | 0.005946 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-03-15 10:05 | 2022-03-15 10:06 | 878 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 878 | keep | 0 | Mar | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
ARECIBO | 2022-03-15 10:08 | 2022-03-15 15:41 | 1 | 005:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO VIENTOS FUERTES | A22031500119 | New_Event | Bad Weather | Include | Include | Weather | 333 | 2022-03-15 | 333 | keep | 0 | Mar | 2022 | 0.0002268 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-15 10:17 | 2022-03-15 12:30 | 50 | 002:13 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | MEDIANTE GOI BY-220315-02 SE REMPLAZO PISTOLA QUEMADA | B22031500085 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 133 | 2022-03-15 | 6650 | keep | 0 | Mar | 2022 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-15 10:19 | 2022-03-15 11:57 | 10 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P22031500034 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-03-15 | 980 | keep | 0 | Mar | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-15 10:19 | 2022-03-15 18:40 | 100 | 008:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22031500082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 501 | 2022-03-15 | 50100 | keep | 0 | Mar | 2022 | 0.034123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-03-15 10:20 | 2022-03-15 14:19 | 35 | 003:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22031500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-03-15 | 8365 | keep | 0 | Mar | 2022 | 0.0056974 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-03-15 10:25 | 2022-03-15 18:05 | 1 | 007:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031500060 | New_Event | Bad Weather | Include | Include | Weather | 460 | 2022-03-15 | 460 | keep | 0 | Mar | 2022 | 0.0003133 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-15 10:28 | 2022-03-15 10:29 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 3114 | keep | 0 | Mar | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2022-03-15 10:32 | 2022-03-15 13:52 | 40 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ROTA SE ABRE CORTE DE LINEA PARA ABRIR PUENTES | M22031500062 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2022-03-15 | 8000 | keep | 0 | Mar | 2022 | 0.0054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-15 10:41 | 2022-03-15 12:48 | 20 | 002:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | R22031500059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2022-03-15 | 2540 | keep | 0 | Mar | 2022 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-03-15 11:19 | 2022-03-15 13:59 | 2 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO 50 PIES DE SECUNDARIA | C22031500052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2022-03-15 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-03-15 11:19 | 2022-03-15 14:51 | 50 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA ARRIADA | A22031500134 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2022-03-15 | 10600 | keep | 0 | Mar | 2022 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-15 11:22 | 2022-03-15 15:45 | 50 | 004:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | P22031500056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-03-15 | 13150 | keep | 0 | Mar | 2022 | 0.0089564 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-03-15 11:23 | 2022-03-15 12:45 | 710 | 001:22 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO RISER DE SALIDA EN EL SU-1 Y SE TRANSFIRIO LA CARGA AL 2201-04 90% EN SERVICIO | R22031500072 | New_Event | UG Cable Fault | Include | Include | Equipment | 82 | 2022-03-15 | 58220 | keep | 0 | Mar | 2022 | 0.039653 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
BAYAMON | 2022-03-15 11:30 | 2022-03-15 14:15 | 100 | 002:45 | P | DESGANCHE | 1 X 50 EN CONVERTIDOS SE RETIRO BAMBUA | B22031500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-03-15 | 16500 | keep | 0 | Mar | 2022 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-15 11:35 | 2022-03-15 18:25 | 81 | 006:50 | P | DESGANCHE | 1 X 100 EN C/L | R22031500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2022-03-15 | 33210 | keep | 0 | Mar | 2022 | 0.022619 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
CAGUAS | 2022-03-15 11:40 | 2022-03-15 15:10 | 125 | 003:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22031500055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-03-15 | 26250 | keep | 0 | Mar | 2022 | 0.017879 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2022-03-15 11:49 | 2022-03-15 19:33 | 1 | 007:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22031500057 | New_Event | Bad Weather | Include | Include | Weather | 464 | 2022-03-15 | 464 | keep | 0 | Mar | 2022 | 0.00031603 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-15 11:53 | 2022-03-15 14:31 | 40 | 002:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031500139 | New_Event | Bad Weather | Include | Include | Weather | 158 | 2022-03-15 | 6320 | keep | 0 | Mar | 2022 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-15 12:09 | 2022-03-15 12:11 | 2192 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-15 | 4384 | keep | 0 | Mar | 2022 | 0.0029859 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
SAN JUAN | 2022-03-15 12:21 | 2022-03-15 16:14 | 21 | 003:53 | P | DESGANCHE | 1 X 30 EN AEREO PROVISIONAL SE RETIRO RAMA | S22031500196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-03-15 | 4893 | keep | 0 | Mar | 2022 | 0.0033326 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2022-03-15 12:30 | 2022-03-15 17:49 | 65 | 005:19 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO ALIMENTADOR PARA TRABAJOS DE GOI BY-220315-02 | B22031500085 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 319 | 2022-03-15 | 20735 | keep | 0 | Mar | 2022 | 0.014123 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-15 12:34 | 2022-03-15 15:04 | 470 | 002:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO AMARRE CON EL 7003-02 PARA REPARAR LINEA PRIMARIA ROTA | M22031500117 | New_Event | Wire Down | Include | Include | Equipment | 150 | 2022-03-15 | 70500 | keep | 0 | Mar | 2022 | 0.048017 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
AGUADILLA | 2022-03-15 12:34 | 2022-03-15 16:51 | 1345 | 004:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO AMARRE | M22031500177 | New_Event | Wire Down | Include | Include | Equipment | 257 | 2022-03-15 | 345665 | keep | 0 | Mar | 2022 | 0.23543 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
BAYAMON | 2022-03-15 12:36 | 2022-03-15 15:20 | 10 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REALIZO DESGANCHE ARBOL TRASPATIO Y SE REEMPLAZARON 50 PIES DE 3 UN CERO ALUMINIO | S22031400011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2022-03-15 | 1640 | keep | 0 | Mar | 2022 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-15 12:36 | 2022-03-15 17:24 | 50 | 004:48 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE Y SE REPARO BAJANTE SECUNDARIO | R22031500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-03-15 | 14400 | keep | 0 | Mar | 2022 | 0.0098078 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-15 12:40 | 2022-03-15 18:41 | 34 | 006:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22001500203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-03-15 | 12274 | keep | 0 | Mar | 2022 | 0.0083598 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CANOVANAS | 2022-03-15 12:43 | 2022-03-15 14:35 | 50 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22031500083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-03-15 | 5600 | keep | 0 | Mar | 2022 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-15 12:44 | 2022-03-15 13:17 | 20 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y TOMA | C22031500063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-03-15 | 660 | keep | 0 | Mar | 2022 | 0.00044952 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-03-15 12:45 | 2022-03-15 18:47 | 71 | 006:02 | P | CABLE SOTERRADO AVERIADO | SE DEJO ABIERTO DE BKR HACIA EL SU#1 DADO QUE ENCONTRO AVERIA SOTERRADA. SE CERRO DEL SU#2 HACIA EL SU#1 100% EN SERVICIO ATRAVEZ DEL 2201-04 | R22031500072 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 362 | 2022-03-15 | 25702 | keep | 0 | Mar | 2022 | 0.017506 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-15 12:53 | 2022-03-16 10:30 | 1 | 021:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER REEMPLAZO CAJA PRIMARIA DEFECTUOSA | C22031500006 | New_Event | Cutout Failure | Include | Include | Equipment | 1297 | 2022-03-15 | 1297 | keep | 0 | Mar | 2022 | 0.00088338 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-15 13:05 | 2022-03-15 13:06 | 519 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-03-15 | 519 | keep | 0 | Mar | 2022 | 0.00035349 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2022-03-15 13:05 | 2022-03-15 13:06 | 1117 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-03-15 | 1117 | keep | 0 | Mar | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2022-03-15 13:05 | 2022-03-15 13:06 | 4161 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-03-15 | 4161 | keep | 0 | Mar | 2022 | 0.002834 | 0.002834 | Momentary | FALSE | FALSE | Not_TMED_Event | 4161
HUMACAO | 2022-03-15 13:05 | 2022-03-15 16:48 | 2450 | 003:43 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV EN HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 223 | 2022-03-15 | 546350 | keep | 0 | Mar | 2022 | 0.37212 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-15 13:05 | 2022-03-15 16:48 | 640 | 003:43 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV EN HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 223 | 2022-03-15 | 142720 | keep | 0 | Mar | 2022 | 0.097206 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
HUMACAO | 2022-03-15 13:05 | 2022-03-15 13:25 | 676 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-03-15 | 13520 | keep | 0 | Mar | 2022 | 0.0092084 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-03-15 13:05 | 2022-03-15 13:25 | 2873 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-03-15 | 57460 | keep | 0 | Mar | 2022 | 0.039136 | 0.0019568 | Sustained | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2022-03-15 13:05 | 2022-03-15 13:25 | 3902 | 000:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV HUMACAO TC | C22031500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-03-15 | 78040 | keep | 0 | Mar | 2022 | 0.053153 | 0.0026576 | Sustained | FALSE | FALSE | Not_TMED_Event | 3902
UTUADO | 2022-03-15 13:05 | 2022-03-15 15:54 | 2 | 002:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22031500148 | New_Event | Secondary Wire Down | Include | Include | Equipment | 169 | 2022-03-15 | 338 | keep | 0 | Mar | 2022 | 0.00023021 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-15 13:07 | 2022-03-15 13:47 | 100 | 000:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M22031500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-03-15 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-15 13:18 | 2022-03-15 20:25 | 3 | 007:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22031500152 | New_Event | Bad Weather | Include | Include | Weather | 427 | 2022-03-15 | 1281 | keep | 0 | Mar | 2022 | 0.00087248 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-03-15 13:36 | 2022-03-15 14:35 | 8 | 000:59 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | P22031500067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-03-15 | 472 | keep | 0 | Mar | 2022 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-15 13:37 | 2022-03-15 22:29 | 8 | 008:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA Y SE REPARO PUENTE Y CONECTOR | S22031500216 | New_Event | Wire Down | Include | Include | Equipment | 532 | 2022-03-15 | 4256 | keep | 0 | Mar | 2022 | 0.0028987 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-15 13:51 | 2022-03-16 11:14 | 45 | 021:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | M22031500119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1283 | 2022-03-15 | 57735 | keep | 0 | Mar | 2022 | 0.039323 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-03-15 13:52 | 2022-03-15 14:20 | 90 | 000:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA ABRIR PUENTE PRIMARIO Y SECCIONALIZAR LINEA PRIMARIA ROTA | M22031500070 | Additional_clients | Wire Down | Include | Include | Equipment | 28 | 2022-03-15 | 2520 | keep | 0 | Mar | 2022 | 0.0017164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-15 14:02 | 2022-03-15 15:55 | 1 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22031500159 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-03-15 | 113 | keep | 0 | Mar | 2022 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-15 14:20 | 2022-03-16 12:52 | 40 | 022:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22031500070 | Partial_restoration | Wire Down | Include | Include | Equipment | 1352 | 2022-03-15 | 54080 | keep | 0 | Mar | 2022 | 0.036834 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-15 14:22 | 2022-03-15 14:25 | 1681 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06. CARGA DE 1303-04 POR 1303-05 | S22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-15 | 5043 | keep | 0 | Mar | 2022 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-03-15 14:22 | 2022-03-15 14:25 | 1598 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06. CARGA DE 1303-04 POR 1303-05 | S22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-15 | 4794 | keep | 0 | Mar | 2022 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
VEGA BAJA | 2022-03-15 14:23 | 2022-03-15 14:26 | 776 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR CONTROL | B22031500000 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2022-03-15 | 2328 | keep | 0 | Mar | 2022 | 0.0015856 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2022-03-15 14:26 | 2022-03-15 16:45 | 335 | 002:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA MEDIANTE GOI BY-220315-03 | B22031500130 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 139 | 2022-03-15 | 46565 | keep | 0 | Mar | 2022 | 0.031715 | 0.00022817 | Sustained | FALSE | FALSE | Not_TMED_Event | 335
SAN JUAN | 2022-03-15 14:31 | 2022-03-15 14:46 | 36 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SEC | S22031400163 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-03-15 | 540 | keep | 0 | Mar | 2022 | 0.00036779 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BARRANQUITAS | 2022-03-15 14:47 | 2022-03-15 19:34 | 8 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22031500158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-03-15 | 2296 | keep | 0 | Mar | 2022 | 0.0015638 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-03-15 14:53 | 2022-03-15 16:32 | 20 | 001:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22031500162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-03-15 | 1980 | keep | 0 | Mar | 2022 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-15 15:06 | 2022-03-15 16:20 | 8 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR PAJARO CRUZO FASE | P22031500079 | New_Event |  |  | Include | Wildlife | 74 | 2022-03-15 | 592 | keep | 0 | Mar | 2022 | 0.00040321 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-03-15 15:21 | 2022-03-15 19:59 | 8 | 004:38 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS SECUNDARIA | M22031500135 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 278 | 2022-03-15 | 2224 | keep | 0 | Mar | 2022 | 0.0015148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-15 15:28 | 2022-03-15 18:00 | 20 | 002:32 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 15 EN TRANSFORMADOR HAY QUE REMPLAZAR POSTE SECUNDARIO | M22031500158 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 152 | 2022-03-15 | 3040 | keep | 0 | Mar | 2022 | 0.0020705 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-15 15:32 | 2022-03-15 16:00 | 15 | 000:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L SE LEVANTO CONDUCTOR PRIMARIO Y REEMPLAZO PIN POLE TOP | R22031500071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2022-03-15 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-03-15 15:32 | 2022-03-15 18:38 | 50 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031500138 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2022-03-15 | 9300 | keep | 0 | Mar | 2022 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-15 15:34 | 2022-03-15 17:40 | 50 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031500139 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2022-03-15 | 6300 | keep | 0 | Mar | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-15 15:48 | 2022-03-15 15:49 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M22031500145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 4381 | keep | 0 | Mar | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
BAYAMON | 2022-03-15 15:56 | 2022-03-15 16:00 | 4050 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL 10% DE LA CARGA TRANSFERIDA AL 1806-02 LLEVA 100% 1717-05 | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-15 | 16200 | keep | 0 | Mar | 2022 | 0.011034 | 0.0027584 | Momentary | FALSE | FALSE | Not_TMED_Event | 4050
BAYAMON | 2022-03-15 15:56 | 2022-03-15 16:00 | 341 | 000:04 | T | NO SE REPORTO CAUSA | 100% DE ESTA CARGA TRANSFERIDA AL 1717-01 SE DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-15 | 1364 | keep | 0 | Mar | 2022 | 0.00092901 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
CAGUAS | 2022-03-15 15:56 | 2022-03-15 19:13 | 40 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22031500191 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2022-03-15 | 7880 | keep | 0 | Mar | 2022 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-15 16:01 | 2022-03-15 17:08 | 7 | 001:07 | P | DESGANCHE | 1 X 10 EN XMR | R22031500115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-03-15 | 469 | keep | 0 | Mar | 2022 | 0.00031943 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-15 16:03 | 2022-03-15 18:34 | 1 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C22031500193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-03-15 | 151 | keep | 0 | Mar | 2022 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-15 16:21 | 2022-03-15 18:39 | 350 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22031500202 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-03-15 | 48300 | keep | 0 | Mar | 2022 | 0.032897 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
CAGUAS | 2022-03-15 16:37 | 2022-03-15 17:29 | 5 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 15 PIES DE SECUNDARIA | C22031500212 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-03-15 | 260 | keep | 0 | Mar | 2022 | 0.00017708 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-15 16:38 | 2022-03-16 07:08 | 1 | 014:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | C22031500215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 870 | 2022-03-15 | 870 | keep | 0 | Mar | 2022 | 0.00059255 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-15 16:42 | 2022-03-15 20:50 | 50 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031500181 | New_Event | Bad Weather | Include | Include | Weather | 248 | 2022-03-15 | 12400 | keep | 0 | Mar | 2022 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-15 16:45 | 2022-03-15 16:48 | 776 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO Y PODER REMPLAZAR CAJA PRIMARIA MEDIANTE GOI BY-220315-03 | B22031500130 | Additional_clients | Cutout Failure | Include | Include | Equipment | 3 | 2022-03-15 | 2328 | keep | 0 | Mar | 2022 | 0.0015856 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-15 16:48 | 2022-03-15 17:49 | 335 | 001:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | MEDIANTE GOI BY-220315-03 SE REMPLAZO CAJA PRIMARIA | B22031500130 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 61 | 2022-03-15 | 20435 | keep | 0 | Mar | 2022 | 0.013918 | 0.00022817 | Sustained | FALSE | FALSE | Not_TMED_Event | 335
BAYAMON | 2022-03-15 16:55 | 2022-03-15 17:05 | 12 | 000:10 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR Y SE DEJO CLIENTE FUERA POR TOMA AVERIADA | S22031400035 | New_Event | Other Causes | Include | Include | Other | 10 | 2022-03-15 | 120 | keep | 0 | Mar | 2022 | 8.1731e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-15 16:58 | 2022-03-16 16:00 | 12 | 023:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y BAJANTE SECUNDARIO | C22031500221 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1382 | 2022-03-15 | 16584 | keep | 0 | Mar | 2022 | 0.011295 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-15 17:05 | 2022-03-15 18:17 | 15 | 001:12 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22031500118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2022-03-15 | 1080 | keep | 0 | Mar | 2022 | 0.00073558 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-03-15 17:09 | 2022-03-15 21:14 | 1 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B22031500174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2022-03-15 | 245 | keep | 0 | Mar | 2022 | 0.00016687 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-15 17:20 | 2022-03-15 19:19 | 1 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A XMR | B22031500177 | New_Event | Wire Down | Include | Include | Equipment | 119 | 2022-03-15 | 119 | keep | 0 | Mar | 2022 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-15 17:21 | 2022-03-16 15:15 | 15 | 021:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M22031500155 | New_Event | Wire Down | Include | Include | Equipment | 1314 | 2022-03-15 | 19710 | keep | 0 | Mar | 2022 | 0.013424 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-15 17:23 | 2022-03-15 18:33 | 4537 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE SECCIONALIZO CERRADO POR CONTROL SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031500263 | New_Event |  |  | Include | Wildlife | 70 | 2022-03-15 | 317590 | keep | 0 | Mar | 2022 | 0.21631 | 0.0030901 | Sustained | FALSE | FALSE | Not_TMED_Event | 4537
FAJARDO | 2022-03-15 17:28 | 2022-03-15 17:29 | 1571 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 1571 | keep | 0 | Mar | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
HUMACAO | 2022-03-15 17:34 | 2022-03-16 14:13 | 8 | 020:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22031600225 | New_Event |  |  | Include | Wildlife | 1239 | 2022-03-15 | 9912 | keep | 0 | Mar | 2022 | 0.006751 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-03-15 17:34 | 2022-03-15 18:10 | 10 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22031500193 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2022-03-15 | 360 | keep | 0 | Mar | 2022 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-15 17:36 | 2022-03-16 02:27 | 10 | 008:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | M22031500159 | New_Event | Bad Weather | Include | Include | Weather | 531 | 2022-03-15 | 5310 | keep | 0 | Mar | 2022 | 0.0036166 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-15 17:49 | 2022-03-15 17:59 | 50 | 000:10 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | MEDIANTE GOI BY-220315-02 SE REMPLAZO PISTOLA QUEMADA | B22031500085 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 10 | 2022-03-15 | 500 | keep | 0 | Mar | 2022 | 0.00034055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-15 17:55 | 2022-03-15 19:15 | 3 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE SUELTO EN TRANSFORMADOR | P22031500106 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2022-03-15 | 240 | keep | 0 | Mar | 2022 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-03-15 17:58 | 2022-03-15 19:07 | 25 | 001:09 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22031500209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-03-15 | 1725 | keep | 0 | Mar | 2022 | 0.0011749 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-03-15 18:00 | 2022-03-15 20:15 | 6 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y CONECTOR EN PUENTE PRIMARIO | P22031500109 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2022-03-15 | 810 | keep | 0 | Mar | 2022 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-15 18:09 | 2022-03-15 23:25 | 52 | 005:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE DE LINEA A CAJA | S22031500267 | New_Event | Wire Down | Include | Include | Equipment | 316 | 2022-03-15 | 16432 | keep | 0 | Mar | 2022 | 0.011192 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2022-03-15 18:12 | 2022-03-15 20:20 | 25 | 002:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22031500268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-15 | 3200 | keep | 0 | Mar | 2022 | 0.0021795 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-15 18:18 | 2022-03-15 21:11 | 30 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22031500188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2022-03-15 | 5190 | keep | 0 | Mar | 2022 | 0.0035349 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-03-15 18:31 | 2022-03-16 07:30 | 2 | 012:59 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | C22031500234 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 779 | 2022-03-15 | 1558 | keep | 0 | Mar | 2022 | 0.0010611 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-15 18:33 | 2022-03-15 18:58 | 3889 | 000:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO Y SE CERRO MACHETES FID 31973516 AL FID 225560198 | S22031500263 | Partial_restoration |  |  | Include | Wildlife | 25 | 2022-03-15 | 97225 | keep | 0 | Mar | 2022 | 0.06622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-15 18:43 | 2022-03-15 19:51 | 1045 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MAIN BREAKER DE PORTATIL EN SUBESTACION SECCIONALIZANDO ALIMENTADOR 1348-08 POR CONDUCTOR EN EL PISO. LLEVA 1348-08, 20% 1348-06 Y 20% 1336-08. 85% 1348-08 EN SERVICIO LOS DEMAS 100% | S22031500000 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-03-15 | 71060 | keep | 0 | Mar | 2022 | 0.048399 | 0.00071174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1045
SAN JUAN | 2022-03-15 18:43 | 2022-03-15 19:51 | 251 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MAIN BREAKER DE PORTATIL EN SUBESTACION SECCIONALIZANDO ALIMENTADOR 1348-08 POR CONDUCTOR EN EL PISO. LLEVA 1348-08, 20% 1348-06 Y 20% 1336-08. 85% 1348-08 EN SERVICIO LOS DEMAS 100% | S22031500000 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-03-15 | 17068 | keep | 0 | Mar | 2022 | 0.011625 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
SAN JUAN | 2022-03-15 18:43 | 2022-03-15 19:51 | 1290 | 001:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MAIN BREAKER DE PORTATIL EN SUBESTACION SECCIONALIZANDO ALIMENTADOR 1348-08 POR CONDUCTOR EN EL PISO. LLEVA 1348-08,% 20%1348-06 Y 20% 1336-08. 85% 1348-08 EN SERVICIO LOS DEMAS 100% | S22031500000 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-03-15 | 87720 | keep | 0 | Mar | 2022 | 0.059746 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-03-15 18:58 | 2022-03-15 20:40 | 2269 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO CONECTOR Y SE SECCIONALIZO GATO EN SU-6 CERRARON MACHETES EN AVE. PONTEZUELA 65% EN SERVICIO | S22031500263 | Partial_restoration |  |  | Include | Wildlife | 102 | 2022-03-15 | 231438 | keep | 0 | Mar | 2022 | 0.15763 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-15 19:25 | 2022-03-16 00:12 | 179 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22031500294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-03-15 | 51373 | keep | 0 | Mar | 2022 | 0.03499 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
CANOVANAS | 2022-03-15 19:25 | 2022-03-15 19:26 | 2580 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 2580 | keep | 0 | Mar | 2022 | 0.0017572 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
MAYAGÃœEZ | 2022-03-15 19:38 | 2022-03-15 21:18 | 30 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031500188 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2022-03-15 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-15 19:49 | 2022-03-15 21:11 | 125 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | S22031500311 | New_Event |  |  | Include | Wildlife | 82 | 2022-03-15 | 10250 | keep | 0 | Mar | 2022 | 0.0069812 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-03-15 19:51 | 2022-03-15 22:49 | 318 | 002:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y NEUTRAL Y SE CERRO MACHETE | S22031500313 | Partial_restoration | Wire Down | Include | Include | Equipment | 178 | 2022-03-15 | 56604 | keep | 0 | Mar | 2022 | 0.038553 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-15 20:00 | 2022-03-16 10:17 | 1 | 014:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22031500240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 857 | 2022-03-15 | 857 | keep | 0 | Mar | 2022 | 0.0005837 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-15 20:04 | 2022-03-15 21:10 | 25 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CORTES DE LINEA MAL TIEMPO | C22031500242 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2022-03-15 | 1650 | keep | 0 | Mar | 2022 | 0.0011238 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-03-15 20:40 | 2022-03-15 20:43 | 4537 | 000:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE SECCIONALIZO CERRADO POR CONTROL SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031500263 | Additional_clients |  |  | Include | Wildlife | 3 | 2022-03-15 | 13611 | keep | 0 | Mar | 2022 | 0.0092704 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-15 20:43 | 2022-03-15 22:25 | 200 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO SU-6 GATO CRUZO LAS FASES CERRADO DEL SU-43 AL SU-40 | S22031500263 | 1st_after_momentary |  |  | Include | Wildlife | 102 | 2022-03-15 | 20400 | keep | 0 | Mar | 2022 | 0.013894 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-15 20:56 | 2022-03-15 23:28 | 300 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN RISER Y SE REMPLAZO CAJA | B22031500325 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2022-03-15 | 45600 | keep | 0 | Mar | 2022 | 0.031058 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-03-15 20:56 | 2022-03-15 23:03 | 200 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CONVERTIDOR SE REEMPLAZO PORTAFUSIBLE | M22031500214 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2022-03-15 | 25400 | keep | 0 | Mar | 2022 | 0.0173 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-15 21:10 | 2022-03-15 21:36 | 10 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22031500308 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-03-15 | 260 | keep | 0 | Mar | 2022 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-15 21:52 | 2022-03-15 22:57 | 140 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22031500200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-03-15 | 9100 | keep | 0 | Mar | 2022 | 0.006198 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2022-03-15 22:25 | 2022-03-15 22:55 | 4537 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR GATO CRUZO FASES EN SU-6 CERRADO POR CONTROL SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031500246 | Additional_clients |  |  | Include | Wildlife | 30 | 2022-03-15 | 136110 | keep | 0 | Mar | 2022 | 0.092704 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-15 22:42 | 2022-03-16 09:34 | 50 | 010:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22031500249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 652 | 2022-03-15 | 32600 | keep | 0 | Mar | 2022 | 0.022204 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-15 22:55 | 2022-03-15 22:58 | 159 | 000:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO SU-6 GATO CRUZO LAS FASES CERRADO DEL SU-40 AL SU-16 | S22031500263 | Partial_restoration |  |  | Include | Wildlife | 3 | 2022-03-15 | 477 | keep | 0 | Mar | 2022 | 0.00032488 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-15 23:10 | 2022-03-15 23:11 | 382 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SU CARGA POR 1620-3 | S22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 382 | keep | 0 | Mar | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
SAN JUAN | 2022-03-15 23:10 | 2022-03-15 23:11 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SU CARGA POR 1620-3 | S22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 36 | keep | 0 | Mar | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-03-15 23:10 | 2022-03-15 23:11 | 1073 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1620-1 Y 95% DEL 1336-10 SE PROBO QUEDO EN SERVICIO | S22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 1073 | keep | 0 | Mar | 2022 | 0.00073082 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
MAYAGÃœEZ | 2022-03-15 23:19 | 2022-03-16 03:15 | 10 | 003:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | M22031500241 | New_Event | Cutout Failure | Include | Include | Equipment | 236 | 2022-03-15 | 2360 | keep | 0 | Mar | 2022 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-15 23:32 | 2022-03-16 13:42 | 16 | 014:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM T-120 DE 100KVA X 100KVA | B22031500210 | New_Event | Service Transformer Failure | Include | Include | Equipment | 850 | 2022-03-15 | 13600 | keep | 0 | Mar | 2022 | 0.0092629 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2022-03-15 23:34 | 2022-03-15 23:35 | 4027 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 4027 | keep | 0 | Mar | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
BAYAMON | 2022-03-15 23:48 | 2022-03-15 23:49 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1801-2 | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 1983 | keep | 0 | Mar | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-03-15 23:48 | 2022-03-15 23:49 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1801-2 | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-03-15 23:48 | 2022-03-15 23:49 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1711-4 Y PARTE DEL 1717-1 | B22031500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-15 | 186 | keep | 0 | Mar | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-03-15 23:55 | 2022-03-16 00:56 | 8 | 001:01 | P | OTRAS CAUSAS | SE ABRE MONTURA DE EMERGENCIA TOMA EXPOLTANDO Y SE RETIRO PELIGRO (PROA) | S22031600001 | New_Event | Other Causes | Include | Include | Other | 61 | 2022-03-15 | 488 | keep | 0 | Mar | 2022 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-03-15 23:59 | 2022-03-16 03:21 | 1 | 003:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | M22031500242 | New_Event | Secondary Wire Down | Include | Include | Equipment | 202 | 2022-03-15 | 202 | keep | 0 | Mar | 2022 | 0.00013758 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-16 00:23 | 2022-03-16 16:39 | 75 | 016:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22031600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 976 | 2022-03-16 | 73200 | keep | 0 | Mar | 2022 | 0.049856 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-03-16 00:31 | 2022-03-16 00:35 | 4537 | 000:04 | P | PARARRAYOS DEFECTUOSO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SE VERIFICO CON CAROLINA SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031600003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2022-03-16 | 18148 | keep | 0 | Mar | 2022 | 0.012361 | 0.0030901 | Momentary | FALSE | FALSE | Not_TMED_Event | 4537
SAN JUAN | 2022-03-16 00:42 | 2022-03-16 00:44 | 4537 | 000:02 | P | PARARRAYOS DEFECTUOSO | DISPARO CON R/R OFF SE VERIFICO CON COD CAROLINA Y SE PROBO QUEDO EN SERVICIO SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031600004 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-03-16 | 9074 | keep | 0 | Mar | 2022 | 0.0061803 | 0.0030901 | Momentary | FALSE | FALSE | Not_TMED_Event | 4537
BAYAMON | 2022-03-16 01:04 | 2022-03-16 01:05 | 377 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1011-04 LLEVANDO 95% 1011-01 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22031600006 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-16 | 377 | keep | 0 | Mar | 2022 | 0.00025677 | 0.00025677 | Momentary | FALSE | FALSE | Not_TMED_Event | 377
BAYAMON | 2022-03-16 01:04 | 2022-03-16 01:05 | 390 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1011-04 LLEVANDO 95% 1011-01 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22031600006 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-16 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2022-03-16 01:08 | 2022-03-16 07:24 | 377 | 006:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO N/O 1011-01 CON 1011-04 Y SE CERRO POR CONTROL. SE REPARO BAJANTE PRIMARIO PEGADO A ESTRUCTURA. GOI SJ220316-01A | S22031600006 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 376 | 2022-03-16 | 141752 | keep | 0 | Mar | 2022 | 0.096547 | 0.00025677 | Sustained | FALSE | FALSE | Not_TMED_Event | 377
BAYAMON | 2022-03-16 01:08 | 2022-03-16 03:56 | 390 | 002:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR 1011-04 LLEVANDO 95% 1011-01 SE ABRIO N/O CONTRA 1011-1 Y SE CERRO 1011-4 QUEDO EN SERVICIO 100% 1011-04 QUEDO FUERA CARGA 1011-01 | S22031600007 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 168 | 2022-03-16 | 65520 | keep | 0 | Mar | 2022 | 0.044625 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-03-16 01:56 | 2022-03-16 01:57 | 4537 | 000:01 | P | PARARRAYOS DEFECTUOSO | DISPARO INTERRUPTOR CERRADO POR CONTROL SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031600018 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-03-16 | 4537 | keep | 0 | Mar | 2022 | 0.0030901 | 0.0030901 | Momentary | FALSE | FALSE | Not_TMED_Event | 4537
SAN JUAN | 2022-03-16 02:03 | 2022-03-16 04:35 | 4537 | 002:32 | P | PARARRAYOS DEFECTUOSO | DISPARO INTERRUPTOR SE ABRIO EN SU-41 HACIA RISER CERRADO POR CONTROL SOLO LLEVA 70% DE SU CARGA EL OTRO 30% POR 1619-02 | S22031600019 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 152 | 2022-03-16 | 689624 | keep | 0 | Mar | 2022 | 0.4697 | 0.0030901 | Sustained | FALSE | FALSE | Not_TMED_Event | 4537
UTUADO | 2022-03-16 02:15 | 2022-03-16 02:23 | 650 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA | A22031600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-03-16 | 5200 | keep | 0 | Mar | 2022 | 0.0035417 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
SAN JUAN | 2022-03-16 03:16 | 2022-03-16 10:16 | 15 | 007:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE CERRO PUENTE ABIERTO | R22031600027 | New_Event | Wire Down | Include | Include | Equipment | 420 | 2022-03-16 | 6300 | keep | 0 | Mar | 2022 | 0.0042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-16 03:21 | 2022-03-16 03:24 | 2435 | 000:03 | T | DESGANCHE | DISPARO INTERRUPTOR CARGA POR EL 3602-01 CERRADO POR CONTROL | C22031600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-03-16 | 7305 | keep | 0 | Mar | 2022 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-16 03:21 | 2022-03-16 03:24 | 1565 | 000:03 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3406-02 CERRADO POR CONTROL | C22031600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-03-16 | 4695 | keep | 0 | Mar | 2022 | 0.0031977 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-03-16 03:29 | 2022-03-16 03:31 | 2435 | 000:02 | T | DESGANCHE | DISPARO INTERRUPTOR CARGA POR EL 3602-01 CERRADO POR CONTROL | C22031600000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-03-16 | 4870 | keep | 0 | Mar | 2022 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-16 03:29 | 2022-03-16 03:31 | 1565 | 000:02 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3406-02 CERRADO POR CONTROL | C22031600000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-03-16 | 3130 | keep | 0 | Mar | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2022-03-16 03:30 | 2022-03-16 03:34 | 723 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA 1711-5 | S22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-16 | 2892 | keep | 0 | Mar | 2022 | 0.0019697 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-03-16 03:30 | 2022-03-16 03:34 | 1976 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SU CARGA POR 1711-2 | S22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-16 | 7904 | keep | 0 | Mar | 2022 | 0.0053834 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2022-03-16 03:37 | 2022-03-16 03:38 | 1051 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22031600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1051 | keep | 0 | Mar | 2022 | 0.00071583 | 0.00071583 | Momentary | FALSE | FALSE | Not_TMED_Event | 1051
CAGUAS | 2022-03-16 03:38 | 2022-03-16 05:49 | 2435 | 002:11 | T | DESGANCHE | DISPARO INTERRUPTOR CARGA POR EL 3602-01 CERRADO POR CONTROL 100% EN SERVICIO | C22031600002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-16 | 318985 | keep | 0 | Mar | 2022 | 0.21726 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-16 03:38 | 2022-03-16 05:49 | 1565 | 002:11 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3406-02 CERRADO POR CONTROL 80% EN SERVICIO | C22031600002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-03-16 | 205015 | keep | 0 | Mar | 2022 | 0.13963 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
SAN JUAN | 2022-03-16 03:48 | 2022-03-16 10:20 | 40 | 006:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22031600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2022-03-16 | 15680 | keep | 0 | Mar | 2022 | 0.01068 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-16 04:35 | 2022-03-16 05:01 | 489 | 000:26 | P | PARARRAYOS DEFECTUOSO | SE ENCONTRO FUSIBLE FUNDIDO CERRARON EN SU-41 HACIA EL RISER CONTINUAN PATRULLANDO | S22031600019 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 26 | 2022-03-16 | 12714 | keep | 0 | Mar | 2022 | 0.0086594 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-16 05:01 | 2022-03-16 06:25 | 300 | 001:24 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN C/L SE REMPLAZO PARARRAYO | S22031600019 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 84 | 2022-03-16 | 25200 | keep | 0 | Mar | 2022 | 0.017164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-03-16 05:14 | 2022-03-16 12:18 | 50 | 007:04 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22031600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2022-03-16 | 21200 | keep | 0 | Mar | 2022 | 0.014439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-16 05:15 | 2022-03-16 07:24 | 390 | 002:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR 1011-04 CON N/O CONTRA 1011-1 ABIERTO SE REPARO BAJANTE PRIMARIO PEGADO A ESTRUCTURA SE CERRO N/O CONTRA 1011-01 Y SE CERRO POR SCADA. GOI SJ 220317-01A | S22031600007 | Partial_restoration | Wire Down | Include | Include | Equipment | 129 | 2022-03-16 | 50310 | keep | 0 | Mar | 2022 | 0.034266 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-16 05:49 | 2022-03-16 11:58 | 313 | 006:09 | P | DESGANCHE | SE ABRIO MACHETES EN CARR 184 KM 28.5 Y CERRO MACHETES EN CARR 184 KM 30.3 PARA SECCIONALIZAR AREA PARA DESGANCHE 90% EN SERVICIO | C22031600002 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-03-16 | 115497 | keep | 0 | Mar | 2022 | 0.078664 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-16 05:54 | 2022-03-16 13:53 | 40 | 007:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22031600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 479 | 2022-03-16 | 19160 | keep | 0 | Mar | 2022 | 0.01305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-16 06:25 | 2022-03-16 06:41 | 150 | 000:16 | P | PARARRAYOS DEFECTUOSO | 2 X 15 EN XMR SE REMPLAZO PARARRAYO | S22031600019 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 16 | 2022-03-16 | 2400 | keep | 0 | Mar | 2022 | 0.0016346 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-16 06:38 | 2022-03-16 09:38 | 52 | 003:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X40 EN C/L (POR AVE EN EL 13KV) | B22031600004 | New_Event |  |  | Include | Wildlife | 180 | 2022-03-16 | 9360 | keep | 0 | Mar | 2022 | 0.0063751 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-03-16 06:58 | 2022-03-16 06:59 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 1909-09 | B22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 222 | keep | 0 | Mar | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-03-16 06:58 | 2022-03-16 06:59 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 1907-03 | B22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 4456 | keep | 0 | Mar | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
ARECIBO | 2022-03-16 07:09 | 2022-03-16 10:35 | 10 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A22031600005 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2022-03-16 | 2060 | keep | 0 | Mar | 2022 | 0.0014031 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-16 07:21 | 2022-03-16 17:15 | 15 | 009:54 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | B22031600005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 594 | 2022-03-16 | 8910 | keep | 0 | Mar | 2022 | 0.0060686 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-03-16 07:34 | 2022-03-16 12:13 | 15 | 004:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | R22031600013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 279 | 2022-03-16 | 4185 | keep | 0 | Mar | 2022 | 0.0028504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-16 07:37 | 2022-03-16 10:21 | 9 | 002:44 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B22031600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-03-16 | 1476 | keep | 0 | Mar | 2022 | 0.0010053 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-03-16 07:39 | 2022-03-16 10:55 | 95 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S22031600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-03-16 | 18620 | keep | 0 | Mar | 2022 | 0.012682 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
AGUADILLA | 2022-03-16 07:58 | 2022-03-16 10:58 | 1 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M22031600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-03-16 | 180 | keep | 0 | Mar | 2022 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-16 08:01 | 2022-03-16 11:07 | 22 | 003:06 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | R22031600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-03-16 | 4092 | keep | 0 | Mar | 2022 | 0.002787 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2022-03-16 08:15 | 2022-03-16 12:31 | 1 | 004:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2X30 EN RISER SE RECONSTRUYO TRAMO AEREO AVERIADO | B22031600013 | New_Event | Wire Down | Include | Include | Equipment | 256 | 2022-03-16 | 256 | keep | 0 | Mar | 2022 | 0.00017436 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-16 08:15 | 2022-03-16 15:10 | 164 | 006:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 Y 1 X 40 EN DISTINTOS CORTES DE LINEA SE FIJO PUENTE SAFADO EN CORTE DE LINEA | P22031600014 | New_Event | Wire Down | Include | Include | Equipment | 415 | 2022-03-16 | 68060 | keep | 0 | Mar | 2022 | 0.046355 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
PONCE | 2022-03-16 08:16 | 2022-03-16 08:17 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 2113 | keep | 0 | Mar | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-03-16 08:30 | 2022-03-16 10:07 | 1076 | 001:37 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO SAFADO EN RISER | P22031600020 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2022-03-16 | 104372 | keep | 0 | Mar | 2022 | 0.071087 | 0.00073286 | Sustained | FALSE | FALSE | Not_TMED_Event | 1076
SAN JUAN | 2022-03-16 08:38 | 2022-03-16 12:59 | 10 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S22031600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2022-03-16 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-16 08:47 | 2022-03-16 17:14 | 5 | 008:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 KVA | R22031600104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 507 | 2022-03-16 | 2535 | keep | 0 | Mar | 2022 | 0.0017266 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-03-16 08:48 | 2022-03-16 13:50 | 60 | 005:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22031600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2022-03-16 | 18120 | keep | 0 | Mar | 2022 | 0.012341 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-16 09:06 | 2022-03-16 11:25 | 10 | 002:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | S22031600062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 139 | 2022-03-16 | 1390 | keep | 0 | Mar | 2022 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-16 09:20 | 2022-03-16 09:21 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 312 | keep | 0 | Mar | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-03-16 09:35 | 2022-03-16 09:36 | 1185 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1185 | keep | 0 | Mar | 2022 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
MAYAGÃœEZ | 2022-03-16 09:35 | 2022-03-16 12:39 | 3458 | 003:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO LINEA OVERHEAD CAIDA SOBRE EL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22031600019 | New_Event | Wire Down | Include | Include | Equipment | 184 | 2022-03-16 | 636272 | keep | 0 | Mar | 2022 | 0.43336 | 0.0023552 | Sustained | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-03-16 09:59 | 2022-03-16 11:07 | 1702 | 001:08 | T | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZARON POSTE ROTO POR CAMION CG-220316-02 98% EN SERVICIO | C22031600052 | New_Event |  |  | Include | Wildlife | 68 | 2022-03-16 | 115736 | keep | 0 | Mar | 2022 | 0.078827 | 0.0011592 | Sustained | FALSE | FALSE | Not_TMED_Event | 1702
SAN JUAN | 2022-03-16 10:03 | 2022-03-16 11:35 | 7 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22031500177 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-03-16 | 644 | keep | 0 | Mar | 2022 | 0.00043863 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-16 10:12 | 2022-03-16 16:45 | 125 | 006:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2022-03-16 | 49125 | keep | 0 | Mar | 2022 | 0.033459 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2022-03-16 10:16 | 2022-03-16 17:15 | 5 | 006:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22031600055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 419 | 2022-03-16 | 2095 | keep | 0 | Mar | 2022 | 0.0014269 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-16 10:36 | 2022-03-16 15:30 | 40 | 004:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-03-16 | 11760 | keep | 0 | Mar | 2022 | 0.0080097 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-16 10:37 | 2022-03-16 12:22 | 1364 | 001:45 | T | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZO POSTE ROTO POR CAMION Y TRANSFIRIO 95% DE LA CARGA DEL 9602-03 @ 9605-01 | C22031600065 | New_Event |  |  | Include | Wildlife | 105 | 2022-03-16 | 143220 | keep | 0 | Mar | 2022 | 0.097546 | 0.00092901 | Sustained | FALSE | FALSE | Not_TMED_Event | 1364
PONCE | 2022-03-16 10:42 | 2022-03-16 13:08 | 100 | 002:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CAMION IMPACTO POSTE | P22031600045 | New_Event |  |  | Include | Wildlife | 146 | 2022-03-16 | 14600 | keep | 0 | Mar | 2022 | 0.009944 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-03-16 10:44 | 2022-03-16 15:00 | 15 | 004:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | P22031600046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 256 | 2022-03-16 | 3840 | keep | 0 | Mar | 2022 | 0.0026154 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-16 11:07 | 2022-03-16 17:46 | 35 | 006:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRARON MACHETES 100% EN SERVICIO | C22031600052 | New_Event |  |  | Include | Wildlife | 399 | 2022-03-16 | 13965 | keep | 0 | Mar | 2022 | 0.0095115 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-03-16 11:09 | 2022-03-16 11:10 | 878 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 878 | keep | 0 | Mar | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
MAYAGÃœEZ | 2022-03-16 11:24 | 2022-03-16 20:13 | 50 | 008:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031600074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 529 | 2022-03-16 | 26450 | keep | 0 | Mar | 2022 | 0.018015 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-16 11:28 | 2022-03-16 14:15 | 35 | 002:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22031600076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-03-16 | 5845 | keep | 0 | Mar | 2022 | 0.003981 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-03-16 11:31 | 2022-03-16 12:25 | 10 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22031600057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-03-16 | 540 | keep | 0 | Mar | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-16 11:37 | 2022-03-16 17:40 | 136 | 006:03 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE ELIMINO PARARRAYO AVERIADO | S22031600095 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 363 | 2022-03-16 | 49368 | keep | 0 | Mar | 2022 | 0.033624 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
CANOVANAS | 2022-03-16 11:50 | 2022-03-16 11:52 | 1648 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-16 | 3296 | keep | 0 | Mar | 2022 | 0.0022449 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-03-16 11:56 | 2022-03-16 15:29 | 80 | 003:33 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN RISER Y 1X 40 EN SU-10 CONTAMINACION EN SU-10 | R22031600126 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 213 | 2022-03-16 | 17040 | keep | 0 | Mar | 2022 | 0.011606 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-16 11:57 | 2022-03-16 19:57 | 40 | 008:00 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22031600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2022-03-16 | 19200 | keep | 0 | Mar | 2022 | 0.013077 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-16 11:58 | 2022-03-16 13:18 | 157 | 001:20 | P | DESGANCHE | SE CERRARON MACHETES 100% EN SERVICIO | C22031600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-03-16 | 12560 | keep | 0 | Mar | 2022 | 0.0085546 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
MAYAGÃœEZ | 2022-03-16 12:08 | 2022-03-16 16:58 | 100 | 004:50 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | M22031600096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2022-03-16 | 29000 | keep | 0 | Mar | 2022 | 0.019752 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-16 12:09 | 2022-03-16 13:40 | 80 | 001:31 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | C22031600092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-03-16 | 7280 | keep | 0 | Mar | 2022 | 0.0049584 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-16 12:13 | 2022-03-16 13:00 | 6 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22031500166 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2022-03-16 | 282 | keep | 0 | Mar | 2022 | 0.00019207 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-16 12:15 | 2022-03-16 15:05 | 7 | 002:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REEMPLAZO SECUNDARIA AVERIADA | C22031600098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 170 | 2022-03-16 | 1190 | keep | 0 | Mar | 2022 | 0.0008105 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-16 12:18 | 2022-03-16 14:49 | 10 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR Y RETEZAR LINEA SECUNDARIA | S22031600099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2022-03-16 | 1510 | keep | 0 | Mar | 2022 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-03-16 12:22 | 2022-03-16 19:29 | 68 | 007:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PRIMARIO PARTIDO | C22031600065 | Partial_restoration |  |  | Include | Wildlife | 427 | 2022-03-16 | 29036 | keep | 0 | Mar | 2022 | 0.019776 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-16 12:24 | 2022-03-16 18:50 | 30 | 006:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22031600103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2022-03-16 | 11580 | keep | 0 | Mar | 2022 | 0.0078871 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-16 12:33 | 2022-03-16 15:05 | 80 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22031600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-03-16 | 12160 | keep | 0 | Mar | 2022 | 0.0082821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-16 12:35 | 2022-03-16 15:02 | 5 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU 38 | S22031600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-03-16 | 735 | keep | 0 | Mar | 2022 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-16 12:56 | 2022-03-16 18:02 | 1185 | 005:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO LINEAS PRIMARIAS CRUZADAS CON OVERHEAD DE DISTRIBUCION PARTIDO | M22031600112 | New_Event | Wire Down | Include | Include | Equipment | 306 | 2022-03-16 | 362610 | keep | 0 | Mar | 2022 | 0.24697 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
MAYAGÃœEZ | 2022-03-16 12:56 | 2022-03-16 12:57 | 3458 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M22031600125 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-16 | 3458 | keep | 0 | Mar | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-03-16 13:02 | 2022-03-16 13:03 | 3458 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M22031600125 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-03-16 | 3458 | keep | 0 | Mar | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-03-16 13:05 | 2022-03-16 14:50 | 125 | 001:45 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | C22031600116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-03-16 | 13125 | keep | 0 | Mar | 2022 | 0.0089394 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2022-03-16 13:05 | 2022-03-16 16:30 | 10 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA FUERTE BRISA | P22031600065 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2022-03-16 | 2050 | keep | 0 | Mar | 2022 | 0.0013962 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-16 13:10 | 2022-03-16 13:11 | 3458 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M22031600125 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-03-16 | 3458 | keep | 0 | Mar | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2022-03-16 13:12 | 2022-03-16 14:50 | 100 | 001:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL | S22031600093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-03-16 | 9800 | keep | 0 | Mar | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-16 13:16 | 2022-03-16 17:35 | 3458 | 004:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO LINEAS PRIMARIAS CRUZADAS POR OVERHEAD PARTIDO | M22031600125 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 259 | 2022-03-16 | 895622 | keep | 0 | Mar | 2022 | 0.61 | 0.0023552 | Sustained | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-03-16 13:18 | 2022-03-16 14:04 | 2435 | 000:46 | T | DESGANCHE | DISPARO INTERRUPTOR CARGA POR EL 3602-01 CERRADO POR CONTROL | C22031600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2022-03-16 | 112010 | keep | 0 | Mar | 2022 | 0.07629 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-16 13:18 | 2022-03-16 14:04 | 1565 | 000:46 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3406-02 CERRADO POR CONTROL | C22031600000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 46 | 2022-03-16 | 71990 | keep | 0 | Mar | 2022 | 0.049032 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-16 13:26 | 2022-03-16 17:17 | 232 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22031600104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2022-03-16 | 53592 | keep | 0 | Mar | 2022 | 0.036501 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
SAN JUAN | 2022-03-16 13:27 | 2022-03-16 17:57 | 50 | 004:30 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO AVERIA EN SU-6 Y SE DEJO N/O EN SU-2 | R22031600001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 270 | 2022-03-16 | 13500 | keep | 0 | Mar | 2022 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-16 13:28 | 2022-03-16 13:40 | 150 | 000:12 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22031600124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2022-03-16 | 1800 | keep | 0 | Mar | 2022 | 0.001226 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-03-16 13:38 | 2022-03-16 16:20 | 120 | 002:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22031600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-03-16 | 19440 | keep | 0 | Mar | 2022 | 0.01324 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-03-16 13:47 | 2022-03-16 19:23 | 150 | 005:36 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22031600124 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 336 | 2022-03-16 | 50400 | keep | 0 | Mar | 2022 | 0.034327 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-16 13:47 | 2022-03-16 19:52 | 80 | 006:05 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C22031600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2022-03-16 | 29200 | keep | 0 | Mar | 2022 | 0.019888 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-16 14:00 | 2022-03-16 15:30 | 1 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONECTORES | A22031600046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-03-16 | 90 | keep | 0 | Mar | 2022 | 6.1299e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-16 14:04 | 2022-03-16 19:30 | 50 | 005:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22031600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-03-16 | 16300 | keep | 0 | Mar | 2022 | 0.011102 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-16 14:04 | 2022-03-16 16:16 | 157 | 002:12 | P | DESGANCHE | SE CERRARON MACHETES 100% EN SERVICIO | C22031600002 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-03-16 | 20724 | keep | 0 | Mar | 2022 | 0.014115 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-16 14:08 | 2022-03-16 14:43 | 1 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | S22031500194 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-03-16 | 35 | keep | 0 | Mar | 2022 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-16 14:25 | 2022-03-16 18:44 | 35 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | P22031600093 | New_Event | Wire Down | Include | Include | Equipment | 259 | 2022-03-16 | 9065 | keep | 0 | Mar | 2022 | 0.0061741 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-03-16 14:45 | 2022-03-16 14:50 | 4431 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B22031600000 | New_Event | Cutout Failure | Include | Include | Equipment | 5 | 2022-03-16 | 22155 | keep | 0 | Mar | 2022 | 0.01509 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-03-16 14:45 | 2022-03-16 16:45 | 5 | 002:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR CON DERRAME DE ACEITE | B22031600058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2022-03-16 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-03-16 14:48 | 2022-03-16 17:15 | 50 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R22030160174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-03-16 | 7350 | keep | 0 | Mar | 2022 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-03-16 14:48 | 2022-03-16 20:25 | 10 | 005:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22031600056 | New_Event | Wire Down | Include | Include | Equipment | 337 | 2022-03-16 | 3370 | keep | 0 | Mar | 2022 | 0.0022953 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-16 14:58 | 2022-03-16 16:37 | 7 | 001:39 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | R22031600176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-03-16 | 693 | keep | 0 | Mar | 2022 | 0.000472 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-16 15:00 | 2022-03-16 17:15 | 15 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22031600148 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2022-03-16 | 2025 | keep | 0 | Mar | 2022 | 0.0013792 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-16 15:02 | 2022-03-16 15:20 | 40 | 000:18 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22031600224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2022-03-16 | 720 | keep | 0 | Mar | 2022 | 0.00049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-16 15:05 | 2022-03-16 15:08 | 4431 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B22031600000 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 3 | 2022-03-16 | 13293 | keep | 0 | Mar | 2022 | 0.0090538 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-16 15:11 | 2022-03-16 20:04 | 40 | 004:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031600171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-03-16 | 11720 | keep | 0 | Mar | 2022 | 0.0079824 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-16 15:20 | 2022-03-16 15:21 | 4431 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B22031600000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-16 | 4431 | keep | 0 | Mar | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-03-16 15:21 | 2022-03-16 16:06 | 4431 | 000:45 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO ALIMENTADOR Y ENTRO 90% DE SU CARGA SWITCH FORM BY-220316-01 | B22031600000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 45 | 2022-03-16 | 199395 | keep | 0 | Mar | 2022 | 0.13581 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
VEGA BAJA | 2022-03-16 15:25 | 2022-03-16 17:00 | 15 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22031600023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2022-03-16 | 1425 | keep | 0 | Mar | 2022 | 0.00097056 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-16 15:56 | 2022-03-16 18:43 | 20 | 002:47 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | C22031600274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-03-16 | 3340 | keep | 0 | Mar | 2022 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-03-16 15:58 | 2022-03-16 17:12 | 1 | 001:14 | P | OTRAS CAUSAS | SE RECONECTARON BAJANTES EN TRANSFORMADOR DESCONECTADOS POR TRABAJOS INTERNOS DEL CLIENTE | A22031600059 | New_Event | Other Causes | Include | Include | Other | 74 | 2022-03-16 | 74 | keep | 0 | Mar | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-16 16:06 | 2022-03-16 17:15 | 443 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 100% EN SERVICIO CON SWITCH FORM BY 220316-01 SE REMPLAZO CAJA PRIMARIA | B22031600000 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 69 | 2022-03-16 | 30567 | keep | 0 | Mar | 2022 | 0.020819 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-16 16:06 | 2022-03-16 22:38 | 50 | 006:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | A22031600063 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 392 | 2022-03-16 | 19600 | keep | 0 | Mar | 2022 | 0.013349 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-16 16:15 | 2022-03-16 19:52 | 11 | 003:37 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 7620 VOLTS | P22031600109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 217 | 2022-03-16 | 2387 | keep | 0 | Mar | 2022 | 0.0016258 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-03-16 16:24 | 2022-03-16 17:27 | 8 | 001:03 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR SOBRECARGA | R22031600182 | New_Event | Trip Due To Overload | Include | Include | Other | 63 | 2022-03-16 | 504 | keep | 0 | Mar | 2022 | 0.00034327 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-16 16:28 | 2022-03-16 19:00 | 60 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22031600131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-03-16 | 9120 | keep | 0 | Mar | 2022 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-16 16:38 | 2022-03-16 18:22 | 20 | 001:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031600200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-03-16 | 2080 | keep | 0 | Mar | 2022 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-03-16 17:12 | 2022-03-17 10:57 | 1 | 017:45 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHO | C22031600318 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1065 | 2022-03-16 | 1065 | keep | 0 | Mar | 2022 | 0.00072537 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-16 17:19 | 2022-03-16 18:27 | 65 | 001:08 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22031600326 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-03-16 | 4420 | keep | 0 | Mar | 2022 | 0.0030104 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-03-16 17:28 | 2022-03-16 18:36 | 234 | 001:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22031600120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-03-16 | 15912 | keep | 0 | Mar | 2022 | 0.010838 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
MAYAGÃœEZ | 2022-03-16 17:29 | 2022-03-16 19:31 | 40 | 002:02 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031600213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-03-16 | 4880 | keep | 0 | Mar | 2022 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-16 17:38 | 2022-03-16 18:01 | 4431 | 000:23 | T | DESGANCHE | 90% EN SERVICIO SE SECCIONALIZO ALIMENTADOR | B22031600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-03-16 | 101913 | keep | 0 | Mar | 2022 | 0.069412 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
UTUADO | 2022-03-16 17:42 | 2022-03-16 19:30 | 20 | 001:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA Y SE REMPLAZARON CONECTORES | A22031600069 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2022-03-16 | 2160 | keep | 0 | Mar | 2022 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-16 17:45 | 2022-03-16 21:21 | 50 | 003:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | B22031600147 | New_Event | Cutout Failure | Include | Include | Equipment | 216 | 2022-03-16 | 10800 | keep | 0 | Mar | 2022 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-03-16 17:49 | 2022-03-16 21:37 | 20 | 003:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22031600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-03-16 | 4560 | keep | 0 | Mar | 2022 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-03-16 17:54 | 2022-03-16 19:53 | 30 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A22031600074 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2022-03-16 | 3570 | keep | 0 | Mar | 2022 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-16 18:00 | 2022-03-16 18:40 | 12 | 000:40 | P | PARARRAYOS DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR PARARRAYO | A22031600084 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 40 | 2022-03-16 | 480 | keep | 0 | Mar | 2022 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-16 18:01 | 2022-03-16 18:51 | 443 | 000:50 | P | DESGANCHE | 100% EN SERVICIO SE REALIZO DESGANCHE DE PISO CON VARETA 10% QUEDABA FUERA | B22031600000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-03-16 | 22150 | keep | 0 | Mar | 2022 | 0.015086 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-16 18:10 | 2022-03-16 18:31 | 1 | 000:21 | P | DESGANCHE | 1 X 25 EN RISER POR DESGANCHE | M22031600219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 21 | 2022-03-16 | 21 | keep | 0 | Mar | 2022 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-16 18:15 | 2022-03-16 19:17 | 60 | 001:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031600220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-03-16 | 3720 | keep | 0 | Mar | 2022 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-03-16 18:18 | 2022-03-16 18:19 | 1463 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22031600197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1463 | keep | 0 | Mar | 2022 | 0.00099644 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
FAJARDO | 2022-03-16 18:20 | 2022-03-16 18:21 | 1463 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22031600197 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1463 | keep | 0 | Mar | 2022 | 0.00099644 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
SAN JUAN | 2022-03-16 18:25 | 2022-03-16 20:31 | 35 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 30 SUM-20 EN SU-5B | R22031600196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-03-16 | 4410 | keep | 0 | Mar | 2022 | 0.0030036 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-03-16 18:30 | 2022-03-16 21:18 | 53 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 65 EN C/L | C22031600358 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-03-16 | 8904 | keep | 0 | Mar | 2022 | 0.0060645 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
PONCE | 2022-03-16 18:53 | 2022-03-16 18:54 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031600138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 3718 | keep | 0 | Mar | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2022-03-16 18:56 | 2022-03-16 20:53 | 35 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C22031600368 | New_Event |  |  | Include | Wildlife | 117 | 2022-03-16 | 4095 | keep | 0 | Mar | 2022 | 0.0027891 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-03-16 19:02 | 2022-03-16 19:09 | 2435 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 3602-01 CERRADO POR CONTROL | C22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-16 | 17045 | keep | 0 | Mar | 2022 | 0.011609 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-16 19:02 | 2022-03-16 19:09 | 1565 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 3406-02 CERRADO POR CONTROL | C22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-16 | 10955 | keep | 0 | Mar | 2022 | 0.0074614 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2022-03-16 19:14 | 2022-03-16 21:45 | 75 | 002:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B22031600178 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2022-03-16 | 11325 | keep | 0 | Mar | 2022 | 0.0077134 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-03-16 19:30 | 2022-03-16 20:00 | 5 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | A22031600089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-03-16 | 150 | keep | 0 | Mar | 2022 | 0.00010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-16 19:36 | 2022-03-16 20:35 | 9 | 000:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A22031600097 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2022-03-16 | 531 | keep | 0 | Mar | 2022 | 0.00036166 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-03-16 19:36 | 2022-03-17 08:19 | 400 | 012:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | A22031600097 | New_Event | Wire Down | Include | Include | Equipment | 763 | 2022-03-16 | 305200 | keep | 0 | Mar | 2022 | 0.20787 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-03-16 19:37 | 2022-03-16 19:38 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 90% CARGA DEL 1705-03 | B22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 478 | keep | 0 | Mar | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-03-16 19:37 | 2022-03-16 19:38 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL BKR 1705-01 LLEVA 90% DE LA CARGA DEL 1705-03 | B22031600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 854 | keep | 0 | Mar | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
BAYAMON | 2022-03-16 19:38 | 2022-03-16 22:58 | 94 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO SE DESCRUZO LINEA CON VARETA SE CERRO INTERRUPTOR QUEDO EN SERVICIO 10% POR 1705-5 | B22031600222 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2022-03-16 | 18800 | keep | 0 | Mar | 2022 | 0.012805 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
BAYAMON | 2022-03-16 19:38 | 2022-03-16 22:58 | 67 | 003:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO SE DESCRUZO LINEA CON VARETA SE CERRO INTERRUPTOR QUEDO EN SERVICIO SU CARGA POR 1705-5 | B22031600222 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2022-03-16 | 13400 | keep | 0 | Mar | 2022 | 0.0091267 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-03-16 19:38 | 2022-03-16 22:58 | 637 | 003:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO SE DESCRUZO LINEA CON VARETA SE CERRO INTERRUPTOR QUEDO EN SERVICIO SU CARGA POR 1705-5 | B22031600222 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2022-03-16 | 127400 | keep | 0 | Mar | 2022 | 0.086772 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
SAN JUAN | 2022-03-16 19:42 | 2022-03-16 23:00 | 8 | 003:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA Y TOMA Y SE DESGANCHO | S22031600170 | New_Event | Secondary Wire Down | Include | Include | Equipment | 198 | 2022-03-16 | 1584 | keep | 0 | Mar | 2022 | 0.0010789 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-03-16 19:50 | 2022-03-17 11:00 | 60 | 015:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO IGUANA | R22031600201 | New_Event |  |  | Include | Wildlife | 910 | 2022-03-16 | 54600 | keep | 0 | Mar | 2022 | 0.037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-03-16 19:59 | 2022-03-16 21:48 | 100 | 001:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22031600205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-03-16 | 10900 | keep | 0 | Mar | 2022 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-16 20:37 | 2022-03-17 00:31 | 1085 | 003:54 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE ENCONTRO ALAMBRE PRIMARIO EN EL MONTE Y DESGANCHE SE ABRIO MACHETE CALLE ELIDA Y SE CERRO INTERRUPTOR PARA CONTINUAR DESGANCHANDO 72% EN SERVICIO | S22031600182 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2022-03-16 | 253890 | keep | 0 | Mar | 2022 | 0.17292 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
CANOVANAS | 2022-03-16 21:10 | 2022-03-17 09:45 | 50 | 012:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE ELIMINO BAJANTE PRIMARIO VACANTE | R22031600210 | New_Event | Wire Down | Include | Include | Equipment | 755 | 2022-03-16 | 37750 | keep | 0 | Mar | 2022 | 0.025711 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-16 21:17 | 2022-03-16 21:18 | 1268 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22031600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-16 | 1268 | keep | 0 | Mar | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-03-16 21:17 | 2022-03-16 21:18 | 2064 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22031600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-16 | 2064 | keep | 0 | Mar | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2022-03-16 21:17 | 2022-03-16 21:18 | 3036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22031600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-16 | 3036 | keep | 0 | Mar | 2022 | 0.0020678 | 0.0020678 | Momentary | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2022-03-16 21:17 | 2022-03-16 21:18 | 2952 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22031600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-16 | 2952 | keep | 0 | Mar | 2022 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2022-03-16 21:34 | 2022-03-17 07:19 | 1 | 009:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE VIENTO | M22031600237 | New_Event | Bad Weather | Include | Include | Weather | 585 | 2022-03-16 | 585 | keep | 0 | Mar | 2022 | 0.00039844 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-16 21:55 | 2022-03-17 08:08 | 180 | 010:13 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C22031600419 | New_Event | Vegetation Contact | Include | Include | Vegetation | 613 | 2022-03-16 | 110340 | keep | 0 | Mar | 2022 | 0.075152 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2022-03-16 22:06 | 2022-03-17 14:11 | 29 | 016:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031600205 | New_Event | Secondary Wire Down | Include | Include | Equipment | 965 | 2022-03-16 | 27985 | keep | 0 | Mar | 2022 | 0.01906 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BARRANQUITAS | 2022-03-16 22:09 | 2022-03-16 23:00 | 5 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA PARA REPARAR SECUNDARIA | C22031600363 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-03-16 | 255 | keep | 0 | Mar | 2022 | 0.00017368 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-03-16 22:27 | 2022-03-17 08:29 | 120 | 010:02 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | C22031600421 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 602 | 2022-03-16 | 72240 | keep | 0 | Mar | 2022 | 0.049202 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-03-16 23:03 | 2022-03-16 23:04 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-4 SE PROBO QUEDO EN SERVICIO | S22031600219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1681 | keep | 0 | Mar | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-03-16 23:03 | 2022-03-16 23:04 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-4 SE PROBO QUEDO EN SERVICIO | S22031600219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1598 | keep | 0 | Mar | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2022-03-16 23:06 | 2022-03-17 00:56 | 2435 | 001:50 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES CARR. 184 K.M. 30.2 BO. GUAVATE EN SERVICIO CON 100% CARGA POR EL 3602-01 | C22031600429 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2022-03-16 | 267850 | keep | 0 | Mar | 2022 | 0.18243 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2022-03-16 23:06 | 2022-03-17 00:56 | 1565 | 001:50 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES CARR. 184 K.M. 30.2 BO. GUAVATE EN SERVICIO CON 80% LLEVA LA CARGA DEL 3406-02 | C22031600429 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2022-03-16 | 172150 | keep | 0 | Mar | 2022 | 0.11725 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2022-03-16 23:06 | 2022-03-16 23:07 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22031600223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
SAN JUAN | 2022-03-16 23:14 | 2022-03-17 10:00 | 50 | 010:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL | S22031600222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 646 | 2022-03-16 | 32300 | keep | 0 | Mar | 2022 | 0.021999 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-16 23:27 | 2022-03-17 01:48 | 182 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22031600475 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2022-03-16 | 25662 | keep | 0 | Mar | 2022 | 0.017478 | 0.00012396 | Sustained | FALSE | FALSE | Not_TMED_Event | 182
AGUADILLA | 2022-03-16 23:31 | 2022-03-17 04:21 | 50 | 004:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CONVERTIDOR SE REPARO CONECTOR QUEMADO | M22031600240 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2022-03-16 | 14500 | keep | 0 | Mar | 2022 | 0.0098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-16 23:42 | 2022-03-16 23:43 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22031600225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 325 | keep | 0 | Mar | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2022-03-16 23:47 | 2022-03-17 01:54 | 227 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA SE DEJO UNA FASE TAGUEADA PARA EN LA MAÃ‘ANA PATRULLARLO | B22031600226 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2022-03-16 | 28829 | keep | 0 | Mar | 2022 | 0.019635 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
HUMACAO | 2022-03-16 23:52 | 2022-03-17 09:59 | 8 | 010:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | C22031600503 | New_Event | Secondary Wire Down | Include | Include | Equipment | 607 | 2022-03-16 | 4856 | keep | 0 | Mar | 2022 | 0.0033074 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-16 23:53 | 2022-03-16 23:54 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031600153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-16 | 3744 | keep | 0 | Mar | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
BARRANQUITAS | 2022-03-17 00:09 | 2022-03-17 08:00 | 160 | 007:51 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA REPARO CONDUCTOR ROTO POR RAMA DE ARBOL | C22031700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2022-03-17 | 75360 | keep | 0 | Mar | 2022 | 0.051327 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
SAN JUAN | 2022-03-17 00:18 | 2022-03-17 08:45 | 60 | 008:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R22031700002 | New_Event | Cutout Failure | Include | Include | Equipment | 507 | 2022-03-17 | 30420 | keep | 0 | Mar | 2022 | 0.020719 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-17 00:31 | 2022-03-17 01:03 | 310 | 000:32 | P | DESGANCHE | AL CERRAR 2 MACHETE SE ABRIO INTERRUPTOR POR SEGURIDAD ARBOL ARQUEANDO CRUZANDO FASE | S22031600182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2022-03-17 | 9920 | keep | 0 | Mar | 2022 | 0.0067565 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
BAYAMON | 2022-03-17 00:31 | 2022-03-17 01:03 | 10 | 000:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031600203 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 32 | 2022-03-17 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-17 00:56 | 2022-03-17 17:15 | 313 | 016:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON 2 AISLADORES Y 2 PARARRAYOS SE CERRARON MACHETES EN CARR 184 KM 30.3 BO GUAVATE 100% EN SERVICIO | C22031600429 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 979 | 2022-03-17 | 306427 | keep | 0 | Mar | 2022 | 0.20871 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-17 01:03 | 2022-03-17 01:04 | 1085 | 000:01 | T | DESGANCHE | SE ABRE INTERRUPTOR AL CERRAR 2 MACHETE CALLE ELIDA ARBOL ARQUEANDO ENCIMA DE FASE POR SEGURIDAD | S22031600182 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-17 | 1085 | keep | 0 | Mar | 2022 | 0.00073899 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-17 01:04 | 2022-03-17 01:21 | 310 | 000:17 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEAS Y SE CERRARON LOS MACHETES | S22031600182 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-03-17 | 5270 | keep | 0 | Mar | 2022 | 0.0035894 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
BAYAMON | 2022-03-17 01:04 | 2022-03-17 11:35 | 10 | 010:31 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031600203 | Partial_restoration | Secondary Vegetation | Include | Include | Vegetation | 631 | 2022-03-17 | 6310 | keep | 0 | Mar | 2022 | 0.0042977 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-03-17 01:17 | 2022-03-17 01:18 | 2343 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO EL 99% DE LA CARGA DEL 2201-02 CERRADO POR CONTROL | R22031700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 2343 | keep | 0 | Mar | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-03-17 01:17 | 2022-03-17 01:18 | 1811 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR EL 99% DE LA CARGA POR EL 2201-01 CERRADO POR CONTROL | R22031700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 1811 | keep | 0 | Mar | 2022 | 0.0012335 | 0.0012335 | Momentary | FALSE | FALSE | Not_TMED_Event | 1811
BAYAMON | 2022-03-17 01:54 | 2022-03-17 01:57 | 3070 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO AL CERRAR CAJA QUE HABIA CAMBIADO SE VERIFICO Y SE CERRO INTERRUPTOR | B22031700000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 3 | 2022-03-17 | 9210 | keep | 0 | Mar | 2022 | 0.0062729 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-17 01:57 | 2022-03-17 02:20 | 227 | 000:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA SE DEJO UNA FASE TAGUEADA PARA EN LA MAÃ‘ANA PATRULLARLO | B22031600226 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 23 | 2022-03-17 | 5221 | keep | 0 | Mar | 2022 | 0.003556 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
GUAYAMA | 2022-03-17 01:58 | 2022-03-17 12:10 | 27 | 010:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO PARTIDO | P22031700007 | New_Event | Wire Down | Include | Include | Equipment | 612 | 2022-03-17 | 16524 | keep | 0 | Mar | 2022 | 0.011254 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2022-03-17 03:13 | 2022-03-17 15:58 | 30 | 012:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031700006 | New_Event | Bad Weather | Include | Include | Weather | 765 | 2022-03-17 | 22950 | keep | 0 | Mar | 2022 | 0.015631 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-17 05:54 | 2022-03-17 21:20 | 20 | 015:26 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO PISTOLA EN T-18 Y SE REPARO SECUNDARIAS | S22031700004 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 926 | 2022-03-17 | 18520 | keep | 0 | Mar | 2022 | 0.012614 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-17 05:54 | 2022-03-17 15:52 | 27 | 009:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN C/L REMPLAZARON SECUNDARIA | C22031700032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 598 | 2022-03-17 | 16146 | keep | 0 | Mar | 2022 | 0.010997 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2022-03-17 06:27 | 2022-03-17 07:57 | 100 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEAUTRAL PRIMARIO PARTIDO | P22031700009 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2022-03-17 | 9000 | keep | 0 | Mar | 2022 | 0.0061299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-17 06:38 | 2022-03-17 06:39 | 4079 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 1717-05 | B22031700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 4079 | keep | 0 | Mar | 2022 | 0.0027782 | 0.0027782 | Momentary | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2022-03-17 06:38 | 2022-03-17 06:39 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 1717-01 | B22031700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 341 | keep | 0 | Mar | 2022 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2022-03-17 06:39 | 2022-03-17 15:13 | 80 | 008:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU 2 HACIA SU 5 | B22031700086 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 514 | 2022-03-17 | 41120 | keep | 0 | Mar | 2022 | 0.028007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-17 06:52 | 2022-03-17 17:13 | 35 | 010:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22031700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 621 | 2022-03-17 | 21735 | keep | 0 | Mar | 2022 | 0.014804 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-03-17 07:04 | 2022-03-17 19:29 | 250 | 012:25 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO | B22031700081 | New_Event | Defective Pole | Include | Include | Equipment | 745 | 2022-03-17 | 186250 | keep | 0 | Mar | 2022 | 0.12685 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-03-17 07:30 | 2022-03-17 12:00 | 40 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22031700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2022-03-17 | 10800 | keep | 0 | Mar | 2022 | 0.0073558 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-17 07:39 | 2022-03-17 13:39 | 28 | 006:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X30 EN C/L (POR AVE EN LA LINEA) | B22031700084 | New_Event |  |  | Include | Wildlife | 360 | 2022-03-17 | 10080 | keep | 0 | Mar | 2022 | 0.0068654 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2022-03-17 07:41 | 2022-03-17 13:40 | 60 | 005:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22031700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2022-03-17 | 21540 | keep | 0 | Mar | 2022 | 0.014671 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-17 08:15 | 2022-03-17 08:16 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031700016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 312 | keep | 0 | Mar | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2022-03-17 08:19 | 2022-03-17 09:39 | 830 | 001:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE CERRO PUENTE | A22031600097 | Additional_clients | Wire Down | Include | Include | Equipment | 80 | 2022-03-17 | 66400 | keep | 0 | Mar | 2022 | 0.045225 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-17 08:27 | 2022-03-17 11:25 | 150 | 002:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | M22031700017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-03-17 | 26700 | keep | 0 | Mar | 2022 | 0.018185 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-03-17 09:02 | 2022-03-17 09:03 | 658 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 658 | keep | 0 | Mar | 2022 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
SAN JUAN | 2022-03-17 09:03 | 2022-03-17 09:04 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-04 QUE ESTA TRANSFERIDO AL 1303-05 PERO QUE LLEVA 1303-01 | S22031700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 1681 | keep | 0 | Mar | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-03-17 09:03 | 2022-03-17 09:04 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-04 QUE ESTA TRANSFERIDO AL 1303-05 PERO QUE LLEVA 1346-06 | S22031700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 1598 | keep | 0 | Mar | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2022-03-17 09:07 | 2022-03-17 09:14 | 1976 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A22031700082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-17 | 13832 | keep | 0 | Mar | 2022 | 0.0094209 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2022-03-17 09:16 | 2022-03-17 11:02 | 10 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | M22031700022 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2022-03-17 | 1060 | keep | 0 | Mar | 2022 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-17 09:42 | 2022-03-17 14:53 | 200 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRO RECLOSER MAL TIEMPO VIENTOS FUERTES | M22031700028 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2022-03-17 | 62200 | keep | 0 | Mar | 2022 | 0.042364 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-17 09:52 | 2022-03-17 14:48 | 80 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22031700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-03-17 | 23680 | keep | 0 | Mar | 2022 | 0.016128 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-17 09:55 | 2022-03-17 13:20 | 1976 | 003:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE ENCONTRO CAUSA | A22031700082 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-03-17 | 405080 | keep | 0 | Mar | 2022 | 0.2759 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-17 10:01 | 2022-03-17 12:03 | 1222 | 002:02 | S | PROTECCION DEFECTUOSA | SE REEMPLAZO FUSIBLE EN LA ALTA DE 125 STAND INFORMA SUBESTACIONES RELE DE PROTECCION DE SOBRE CORRIENTE NO OPERO | A22031700086 | New_Event | Protection Miscoordination | Include | Include | Other | 122 | 2022-03-17 | 149084 | keep | 0 | Mar | 2022 | 0.10154 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2022-03-17 10:01 | 2022-03-17 12:03 | 2756 | 002:02 | S | PROTECCION DEFECTUOSA | SE REEMPLAZO FUSIBLE EN LA ALTA DE 125 STAND INFORMA SUBESTACIONES RELE DE PROTECCION DE SOBRE CORRIENTE NO OPERO | A22031700086 | New_Event | Protection Miscoordination | Include | Include | Other | 122 | 2022-03-17 | 336232 | keep | 0 | Mar | 2022 | 0.22901 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2022-03-17 10:01 | 2022-03-17 12:03 | 2833 | 002:02 | S | PROTECCION DEFECTUOSA | SE REEMPLAZO FUSIBLE EN LA ALTA DE 125 STAND INFORMA SUBESTACIONES RELE DE PROTECCION DE SOBRE CORRIENTE NO OPERO | A22031700086 | New_Event | Protection Miscoordination | Include | Include | Other | 122 | 2022-03-17 | 345626 | keep | 0 | Mar | 2022 | 0.2354 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2022-03-17 10:06 | 2022-03-17 12:42 | 60 | 002:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | A22031700089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-03-17 | 9360 | keep | 0 | Mar | 2022 | 0.0063751 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-17 10:16 | 2022-03-17 12:45 | 60 | 002:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | M22031700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-03-17 | 8940 | keep | 0 | Mar | 2022 | 0.006089 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-17 10:17 | 2022-03-17 22:00 | 40 | 011:43 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | A22031700094 | New_Event | Defective Pole | Include | Include | Equipment | 703 | 2022-03-17 | 28120 | keep | 0 | Mar | 2022 | 0.019152 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-17 10:30 | 2022-03-17 18:25 | 1 | 007:55 | P | OTRAS CAUSAS | SE ABRIO RISER PARA REMPLAZO DE PT'S Y CT'S | M22031700032 | New_Event | Other Causes | Include | Include | Other | 475 | 2022-03-17 | 475 | keep | 0 | Mar | 2022 | 0.00032352 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-17 10:43 | 2022-03-17 15:42 | 50 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN T14 Y 1 X 40 EN CL PROV EN SERVICIO | B22031700102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-03-17 | 14950 | keep | 0 | Mar | 2022 | 0.010182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-17 10:46 | 2022-03-17 14:38 | 6 | 003:52 | P | NO SE REPORTO CAUSA | ABRIR XMR PARA REEMPLAZAR SECUNDARIA Y TOMAS | C22031700135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-03-17 | 1392 | keep | 0 | Mar | 2022 | 0.00094808 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-03-17 10:52 | 2022-03-17 10:53 | 2937 | 000:01 | T | DESGANCHE | RECIERRE | C22031700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-17 | 2937 | keep | 0 | Mar | 2022 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
BAYAMON | 2022-03-17 10:59 | 2022-03-17 11:00 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 4176 | keep | 0 | Mar | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
AGUADILLA | 2022-03-17 11:16 | 2022-03-17 12:40 | 45 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA / CAMION IMPACTO POSTE Y CAUSO CRUCE DE LINEAS | M22031700044 | New_Event |  |  | Include | Wildlife | 84 | 2022-03-17 | 3780 | keep | 0 | Mar | 2022 | 0.0025745 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
FAJARDO | 2022-03-17 11:20 | 2022-03-17 14:04 | 45 | 002:44 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | R22031700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-03-17 | 7380 | keep | 0 | Mar | 2022 | 0.0050265 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-03-17 11:20 | 2022-03-17 11:21 | 2937 | 000:01 | T | DESGANCHE | RECIERRE | C22031700000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-17 | 2937 | keep | 0 | Mar | 2022 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
MAYAGÃœEZ | 2022-03-17 11:24 | 2022-03-17 11:25 | 2073 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M22031700046 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-17 | 2073 | keep | 0 | Mar | 2022 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2022-03-17 11:25 | 2022-03-17 21:25 | 500 | 010:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22031700077 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 600 | 2022-03-17 | 300000 | keep | 0 | Mar | 2022 | 0.20433 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2022-03-17 11:30 | 2022-03-17 11:45 | 15 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R22031600209 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-03-17 | 225 | keep | 0 | Mar | 2022 | 0.00015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-17 11:49 | 2022-03-17 11:50 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 4176 | keep | 0 | Mar | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BARRANQUITAS | 2022-03-17 11:50 | 2022-03-17 11:51 | 2937 | 000:01 | T | DESGANCHE | RECIERRE | C22031700000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-17 | 2937 | keep | 0 | Mar | 2022 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
VEGA BAJA | 2022-03-17 12:00 | 2022-03-17 14:07 | 12 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22031700099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2022-03-17 | 1524 | keep | 0 | Mar | 2022 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-17 12:35 | 2022-03-18 00:18 | 1 | 011:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR, SE REEMPLAZO DOS CAJAS EN XMR | B22031700120 | New_Event | Cutout Failure | Include | Include | Equipment | 703 | 2022-03-17 | 703 | keep | 0 | Mar | 2022 | 0.00047881 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-17 12:37 | 2022-03-17 17:21 | 17 | 004:44 | P | DESGANCHE | 1 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE DESGANCHE | C22031700122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2022-03-17 | 4828 | keep | 0 | Mar | 2022 | 0.0032883 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2022-03-17 12:40 | 2022-03-17 13:45 | 15 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | R22031600193 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-03-17 | 975 | keep | 0 | Mar | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-17 12:55 | 2022-03-17 14:59 | 100 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031700056 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2022-03-17 | 12400 | keep | 0 | Mar | 2022 | 0.0084456 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-03-17 13:09 | 2022-03-17 14:58 | 1 | 001:49 | P | OTRAS CAUSAS | 1 X 50 EN RISER FUSIBLE SULFATADO | P22031700040 | New_Event | Other Causes | Include | Include | Other | 109 | 2022-03-17 | 109 | keep | 0 | Mar | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-17 13:12 | 2022-03-17 16:47 | 1 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO PAJARO DE LINEA PRIMARIA | P22031700041 | New_Event |  |  | Include | Wildlife | 215 | 2022-03-17 | 215 | keep | 0 | Mar | 2022 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-17 13:25 | 2022-03-17 14:05 | 9 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22031700135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-17 | 360 | keep | 0 | Mar | 2022 | 0.00024519 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-03-17 13:30 | 2022-03-17 17:22 | 100 | 003:52 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031700070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-03-17 | 23200 | keep | 0 | Mar | 2022 | 0.015801 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-03-17 13:49 | 2022-03-17 13:50 | 1109 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031700044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-17 | 1109 | keep | 0 | Mar | 2022 | 0.00075533 | 0.00075533 | Momentary | FALSE | FALSE | Not_TMED_Event | 1109
ARECIBO | 2022-03-17 13:49 | 2022-03-17 15:55 | 4 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DEL TRANSFORMADOR | A22031700142 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2022-03-17 | 504 | keep | 0 | Mar | 2022 | 0.00034327 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-17 13:53 | 2022-03-17 16:40 | 80 | 002:47 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031700082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-03-17 | 13360 | keep | 0 | Mar | 2022 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-03-17 13:55 | 2022-03-17 14:20 | 2 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REMPLAZO DE BAJANTE PRIMARIO EN TRANSFORMADOR | P22031700045 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2022-03-17 | 50 | keep | 0 | Mar | 2022 | 3.4055e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 297 | 002:51 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE VILLA PRADES 1335-05 LLEVA 40% DE LA CARGA DEL 1301-02 | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 50787 | keep | 0 | Mar | 2022 | 0.034591 | 0.00020229 | Sustained | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 1397 | 002:51 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE VILLA PRADES 1335-04 LLEVA CARGA DEL 1301-04 | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 238887 | keep | 0 | Mar | 2022 | 0.1627 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 1208 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VILLA PRADES 38KV | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 206568 | keep | 0 | Mar | 2022 | 0.14069 | 0.00082276 | Sustained | FALSE | FALSE | Not_TMED_Event | 1208
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 375 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VILLA PRADES 38KV | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 64125 | keep | 0 | Mar | 2022 | 0.043675 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 608 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VILLA PRADES 38KV | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 103968 | keep | 0 | Mar | 2022 | 0.070812 | 0.00041411 | Sustained | FALSE | FALSE | Not_TMED_Event | 608
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 602 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VILLA PRADES 38KV 1335-04 LLEVA 1301-04 | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 102942 | keep | 0 | Mar | 2022 | 0.070113 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-03-17 13:56 | 2022-03-17 16:47 | 314 | 002:51 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VILLA PRADES 38KV 1335-05 LLEVA 40% DEL 1301-02 | S22031700118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 171 | 2022-03-17 | 53694 | keep | 0 | Mar | 2022 | 0.036571 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2022-03-17 14:00 | 2022-03-17 14:30 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031700047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-03-17 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-17 14:09 | 2022-03-17 14:12 | 614 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 1842 | keep | 0 | Mar | 2022 | 0.0012546 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-03-17 14:09 | 2022-03-17 14:12 | 770 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 2310 | keep | 0 | Mar | 2022 | 0.0015733 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-03-17 14:09 | 2022-03-17 14:12 | 1271 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 3813 | keep | 0 | Mar | 2022 | 0.002597 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-03-17 14:09 | 2022-03-17 14:12 | 247 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 741 | keep | 0 | Mar | 2022 | 0.00050469 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
CANOVANAS | 2022-03-17 14:13 | 2022-03-17 18:00 | 50 | 003:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA Y SE REEMPLAZARON TRES ASILADORES | R22031700043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 227 | 2022-03-17 | 11350 | keep | 0 | Mar | 2022 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-17 14:14 | 2022-03-17 18:30 | 30 | 004:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22031700148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-03-17 | 7680 | keep | 0 | Mar | 2022 | 0.0052308 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-17 14:18 | 2022-03-17 16:00 | 100 | 001:42 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | S22031700068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-03-17 | 10200 | keep | 0 | Mar | 2022 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-17 14:20 | 2022-03-17 17:28 | 10 | 003:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO RISER SECUNDARIO | R22031700041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 188 | 2022-03-17 | 1880 | keep | 0 | Mar | 2022 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-17 14:20 | 2022-03-17 17:16 | 46 | 002:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | P22031700051 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2022-03-17 | 8096 | keep | 0 | Mar | 2022 | 0.0055141 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
ARECIBO | 2022-03-17 14:28 | 2022-03-17 16:48 | 28 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA SE REMPLAZO CAJA PRIMARIA AVERIADA CAUSADO POR IMPACTO DE UN AUTOMOVIL | A22031700149 | New_Event |  |  | Include | Wildlife | 140 | 2022-03-17 | 3920 | keep | 0 | Mar | 2022 | 0.0026699 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2022-03-17 14:31 | 2022-03-17 15:57 | 12 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031700092 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2022-03-17 | 1032 | keep | 0 | Mar | 2022 | 0.00070289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-17 14:36 | 2022-03-17 16:30 | 1 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA DE NEUTRAL A PEDESTAL SECUNDARIO | A22031700150 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2022-03-17 | 114 | keep | 0 | Mar | 2022 | 7.7645e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-17 14:40 | 2022-03-17 15:39 | 6 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22031700153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-03-17 | 354 | keep | 0 | Mar | 2022 | 0.00024111 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-17 14:40 | 2022-03-17 19:15 | 100 | 004:35 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22031700096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-03-17 | 27500 | keep | 0 | Mar | 2022 | 0.01873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-17 14:55 | 2022-03-17 20:55 | 1000 | 006:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO AISLADOR ROTO Y SE SECCIONALIZO CERRANDO AMARRE 7505-05 CON 7505-01 EL INTERRUPTOR NO PUEDE CERRARSE POR COMPLETO YA QUE TIENE BOBINA DE CLOSE AVERIADA Y LOS PARARRAYOS SE ENCUENTRAN QUEMADOS A CAUSA DE LA AVERIA | A22031700153 | New_Event | Wire Down | Include | Include | Equipment | 360 | 2022-03-17 | 360000 | keep | 0 | Mar | 2022 | 0.24519 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-17 14:58 | 2022-03-17 14:59 | 614 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-17 | 614 | keep | 0 | Mar | 2022 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-03-17 14:58 | 2022-03-17 14:59 | 770 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-17 | 770 | keep | 0 | Mar | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-03-17 14:58 | 2022-03-17 14:59 | 1271 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-17 | 1271 | keep | 0 | Mar | 2022 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-03-17 14:58 | 2022-03-17 14:59 | 247 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-17 | 247 | keep | 0 | Mar | 2022 | 0.00016823 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
BAYAMON | 2022-03-17 15:05 | 2022-03-17 15:11 | 4079 | 000:06 | P | CABLE SOTERRADO AVERIADO | SE DISPARO ALIMENTADOR HACIENDO PRUEBA EN LINEA SOTERRADA SE CERRO POR SCADA LUEGO DE VERIFICAR PERSONAL FUERA | B22031700000 | New_Event | UG Cable Fault | Include | Include | Equipment | 6 | 2022-03-17 | 24474 | keep | 0 | Mar | 2022 | 0.016669 | 0.0027782 | Sustained | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2022-03-17 15:09 | 2022-03-17 21:25 | 50 | 006:16 | P | NO SE REPORTO CAUSA | 3 X 80 EN RISER | S22031700142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 376 | 2022-03-17 | 18800 | keep | 0 | Mar | 2022 | 0.012805 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-17 15:09 | 2022-03-17 17:49 | 7 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | C22031700162 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2022-03-17 | 1120 | keep | 0 | Mar | 2022 | 0.00076283 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-17 15:13 | 2022-03-17 20:36 | 130 | 005:23 | P | DESCONECTIVO DEFECTUOSO | 20% DE LA CARGA POR EL 1717-04 GOI BY-220317-01 | B22031700000 | New_Event | Switch Failure | Include | Include | Equipment | 323 | 2022-03-17 | 41990 | keep | 0 | Mar | 2022 | 0.028599 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-03-17 15:13 | 2022-03-17 20:36 | 4079 | 005:23 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON MACHETES QUEMADOS EN INTERRUPTOR 1717-01 Y 1717-05 GOI BY-220317-01 10% DE LA CARGA POR EL 1806-02 | B22031700000 | New_Event | Switch Failure | Include | Include | Equipment | 323 | 2022-03-17 | 1317517 | keep | 0 | Mar | 2022 | 0.89735 | 0.0027782 | Sustained | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2022-03-17 15:13 | 2022-03-17 20:36 | 45 | 005:23 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON MACHETES QUEMADOS EN INTERRUPTOR 1717-01 Y 1717-05 GOI BY-220317-01 95% DE LA CARGA POR EL 1713-05 | B22031700000 | New_Event | Switch Failure | Include | Include | Equipment | 323 | 2022-03-17 | 14535 | keep | 0 | Mar | 2022 | 0.0098997 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-17 15:13 | 2022-03-17 20:36 | 4431 | 005:23 | S | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON MACHETES QUEMADOS EN BRAKER 1717-01 Y 1717-05 GOI BY-220317-01 | B22031700000 | New_Event | Switch Failure | Include | Include | Equipment | 323 | 2022-03-17 | 1431213 | keep | 0 | Mar | 2022 | 0.97479 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2022-03-17 15:13 | 2022-03-17 20:36 | 1362 | 005:23 | S | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETES QUEMADOS EN INTERRUPTOR 1717-01 BY-220317-01 LLEVA 20% DE LA CARGA DEL 1716-02 | B22031700000 | New_Event | Switch Failure | Include | Include | Equipment | 323 | 2022-03-17 | 439926 | keep | 0 | Mar | 2022 | 0.29963 | 0.00092765 | Sustained | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-03-17 15:13 | 2022-03-17 20:36 | 341 | 005:23 | S | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON MACHETES QUEMADOS EN BRAKER 1717-01 Y 1717-05 GOI BY-220317-01 | B22031700000 | New_Event | Switch Failure | Include | Include | Equipment | 323 | 2022-03-17 | 110143 | keep | 0 | Mar | 2022 | 0.075018 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
YAUCO | 2022-03-17 16:00 | 2022-03-17 17:15 | 8 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | P22031700043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-03-17 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-03-17 16:03 | 2022-03-18 09:36 | 15 | 017:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CONVERTIDOR IGUANA CRUZO FASE A TIERRA | A22031700222 | New_Event |  |  | Include | Wildlife | 1053 | 2022-03-17 | 15795 | keep | 0 | Mar | 2022 | 0.010758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-17 16:06 | 2022-03-17 17:57 | 30 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L CRUCE POR AVE | C22031700178 | New_Event |  |  | Include | Wildlife | 111 | 2022-03-17 | 3330 | keep | 0 | Mar | 2022 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-17 16:10 | 2022-03-17 18:50 | 20 | 002:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22031700228 | New_Event | Wire Down | Include | Include | Equipment | 160 | 2022-03-17 | 3200 | keep | 0 | Mar | 2022 | 0.0021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-17 16:13 | 2022-03-17 19:47 | 60 | 003:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN PROVISIONAL SE REMPLAZO CAJA PRIMARIA | S22031700190 | New_Event | Cutout Failure | Include | Include | Equipment | 214 | 2022-03-17 | 12840 | keep | 0 | Mar | 2022 | 0.0087453 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-17 16:23 | 2022-03-17 16:45 | 1 | 000:22 | P | NO SE REPORTO CAUSA | 2 X 50 HACIA BOMBAS DE LA AAA | B22031700197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2022-03-17 | 22 | keep | 0 | Mar | 2022 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-17 16:25 | 2022-03-17 19:00 | 100 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN C/L SE ELIMINO BAJANTE ENCIMA DE LA CRUCETA | C22031700183 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2022-03-17 | 15500 | keep | 0 | Mar | 2022 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-17 16:32 | 2022-03-17 19:25 | 15 | 002:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE POR RAMA | C22031700186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-03-17 | 2595 | keep | 0 | Mar | 2022 | 0.0017674 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-17 16:35 | 2022-03-17 16:38 | 614 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 1842 | keep | 0 | Mar | 2022 | 0.0012546 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-03-17 16:35 | 2022-03-17 16:38 | 770 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 2310 | keep | 0 | Mar | 2022 | 0.0015733 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-03-17 16:35 | 2022-03-17 16:38 | 1271 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 3813 | keep | 0 | Mar | 2022 | 0.002597 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-03-17 16:35 | 2022-03-17 16:38 | 247 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | R22031700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-17 | 741 | keep | 0 | Mar | 2022 | 0.00050469 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
CAGUAS | 2022-03-17 16:37 | 2022-03-17 17:42 | 6 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BARRA EN PEDESTAL | C22031700189 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-03-17 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-17 16:51 | 2022-03-17 18:00 | 85 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22031700263 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2022-03-17 | 5865 | keep | 0 | Mar | 2022 | 0.0039946 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-03-17 17:04 | 2022-03-18 13:44 | 8 | 020:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031700218 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1240 | 2022-03-17 | 9920 | keep | 0 | Mar | 2022 | 0.0067565 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-17 17:04 | 2022-03-17 18:47 | 25 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE LINEA A CAJA | B22031700340 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-03-17 | 2575 | keep | 0 | Mar | 2022 | 0.0017538 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-17 17:05 | 2022-03-17 19:36 | 15 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | C22031700196 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2022-03-17 | 2265 | keep | 0 | Mar | 2022 | 0.0015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-17 17:17 | 2022-03-17 22:03 | 35 | 004:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S22031700219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2022-03-17 | 10010 | keep | 0 | Mar | 2022 | 0.0068178 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-03-17 17:20 | 2022-03-17 20:00 | 30 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031700167 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2022-03-17 | 4800 | keep | 0 | Mar | 2022 | 0.0032693 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-17 17:38 | 2022-03-17 19:25 | 50 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031700176 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2022-03-17 | 5350 | keep | 0 | Mar | 2022 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-03-17 17:43 | 2022-03-18 10:52 | 30 | 017:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | A20031700305 | New_Event | Bad Weather | Include | Include | Weather | 1029 | 2022-03-17 | 30870 | keep | 0 | Mar | 2022 | 0.021025 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-17 17:50 | 2022-03-17 19:06 | 35 | 001:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO PRIMARIO DE LINEA A CAJA DE C/L (NO FUNDIO) | R22031700051 | New_Event | Wire Down | Include | Include | Equipment | 76 | 2022-03-17 | 2660 | keep | 0 | Mar | 2022 | 0.0018117 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-03-17 18:07 | 2022-03-17 21:45 | 385 | 003:38 | S | ANIMAL U OBJETO EXTRAÃ‘O | SE ENERGIZO PORTATIL #13, GLOBO CRUZO MACHETES | A22031700327 | New_Event |  |  | Include | Wildlife | 218 | 2022-03-17 | 83930 | keep | 0 | Mar | 2022 | 0.057164 | 0.00026222 | Sustained | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2022-03-17 18:07 | 2022-03-17 21:45 | 264 | 003:38 | S | ANIMAL U OBJETO EXTRAÃ‘O | SE ENERGIZO PORTATIL #13, GLOBO CRUZO MACHETES | A22031700327 | New_Event |  |  | Include | Wildlife | 218 | 2022-03-17 | 57552 | keep | 0 | Mar | 2022 | 0.039198 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
BAYAMON | 2022-03-17 18:13 | 2022-03-17 19:51 | 80 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22031700462 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-03-17 | 7840 | keep | 0 | Mar | 2022 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-03-17 18:51 | 2022-03-17 20:11 | 40 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L Y 1 X 30 EN RISER | R22031700053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2022-03-17 | 3200 | keep | 0 | Mar | 2022 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-17 18:58 | 2022-03-17 19:05 | 1 | 000:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22031700207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-03-17 | 7 | keep | 0 | Mar | 2022 | 4.7677e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-17 19:08 | 2022-03-17 21:25 | 200 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M22031700222 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2022-03-17 | 27400 | keep | 0 | Mar | 2022 | 0.018662 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-17 19:28 | 2022-03-18 08:04 | 210 | 012:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22031700211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 756 | 2022-03-17 | 158760 | keep | 0 | Mar | 2022 | 0.10813 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
SAN JUAN | 2022-03-17 19:39 | 2022-03-17 21:25 | 20 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S22031700224 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-03-17 | 2120 | keep | 0 | Mar | 2022 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-03-17 19:52 | 2022-03-17 20:40 | 36 | 000:48 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22031700428 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-03-17 | 1728 | keep | 0 | Mar | 2022 | 0.0011769 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-03-17 19:57 | 2022-03-18 09:25 | 4 | 013:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22031700259 | New_Event | Bad Weather | Include | Include | Weather | 808 | 2022-03-17 | 3232 | keep | 0 | Mar | 2022 | 0.0022013 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-03-17 20:11 | 2022-03-17 22:09 | 25 | 001:58 | P | DESGANCHE | DESGANCHE Y 1 X 30 EN RISER | B22031700726 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-03-17 | 2950 | keep | 0 | Mar | 2022 | 0.0020092 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-17 20:36 | 2022-03-17 21:39 | 80 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU 2 HACIA SU 5 | B22031700086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-03-17 | 5040 | keep | 0 | Mar | 2022 | 0.0034327 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-03-17 20:44 | 2022-03-18 11:50 | 4 | 015:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22031700286 | New_Event | Secondary Wire Down | Include | Include | Equipment | 906 | 2022-03-17 | 3624 | keep | 0 | Mar | 2022 | 0.0024683 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-03-17 20:48 | 2022-03-18 00:45 | 120 | 003:57 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22031700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-03-17 | 28440 | keep | 0 | Mar | 2022 | 0.01937 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-03-17 20:49 | 2022-03-18 01:20 | 15 | 004:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | M22031700288 | New_Event | Cutout Failure | Include | Include | Equipment | 271 | 2022-03-17 | 4065 | keep | 0 | Mar | 2022 | 0.0027687 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-17 20:53 | 2022-03-17 20:54 | 300 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A22031700237 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-17 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-03-17 21:14 | 2022-03-17 23:15 | 1 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B22031700119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-03-17 | 121 | keep | 0 | Mar | 2022 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-17 21:14 | 2022-03-17 22:51 | 45 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22031700787 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-03-17 | 4365 | keep | 0 | Mar | 2022 | 0.002973 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-03-17 21:15 | 2022-03-18 10:45 | 100 | 013:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22031700245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 810 | 2022-03-17 | 81000 | keep | 0 | Mar | 2022 | 0.055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-17 21:20 | 2022-03-18 15:12 | 7 | 017:52 | P | CABLE SOTERRADO AVERIADO | SE ABRIO DE T-17 @ T-18 PARA TRATAR DE REPARAR 3 CLIENTES PERO SON SUS TOMAS QUE LOS CLIENTES TIENEN QUE REPARAR | S22031700004 | New_Event | UG Cable Fault | Include | Include | Equipment | 1072 | 2022-03-17 | 7504 | keep | 0 | Mar | 2022 | 0.0051109 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-17 21:25 | 2022-03-18 12:30 | 50 | 015:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTE PRIMARIO | M22031700077 | Partial_restoration | Wire Down | Include | Include | Equipment | 905 | 2022-03-17 | 45250 | keep | 0 | Mar | 2022 | 0.03082 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-17 21:43 | 2022-03-18 10:12 | 80 | 012:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO CORTE DE LINEA NO FUNDIO FUSIBLE | C22031700244 | New_Event | Wire Down | Include | Include | Equipment | 749 | 2022-03-17 | 59920 | keep | 0 | Mar | 2022 | 0.040811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-17 21:56 | 2022-03-18 02:51 | 80 | 004:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50, 1 X 40 Y 1 X 25 EN CORTES DE LINEA POR MAL TIEMPO | A22031700482 | New_Event | Bad Weather | Include | Include | Weather | 295 | 2022-03-17 | 23600 | keep | 0 | Mar | 2022 | 0.016074 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-17 22:06 | 2022-03-18 11:00 | 100 | 012:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M22031700317 | New_Event | Wire Down | Include | Include | Equipment | 774 | 2022-03-17 | 77400 | keep | 0 | Mar | 2022 | 0.052717 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-17 22:10 | 2022-03-18 10:30 | 15 | 012:20 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN C/L, 1 X 50 EN RISER Y SE REMPLAZO PISTOLA EN T-7 | R22031700057 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 740 | 2022-03-17 | 11100 | keep | 0 | Mar | 2022 | 0.0075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-17 22:21 | 2022-03-18 09:40 | 315 | 011:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN CORTE DE LINEA | M22031700322 | New_Event | Wire Down | Include | Include | Equipment | 679 | 2022-03-17 | 213885 | keep | 0 | Mar | 2022 | 0.14568 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
MAYAGÃœEZ | 2022-03-17 22:26 | 2022-03-18 11:25 | 80 | 012:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22031700323 | New_Event | Cutout Failure | Include | Include | Equipment | 779 | 2022-03-17 | 62320 | keep | 0 | Mar | 2022 | 0.042446 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-03-17 22:51 | 2022-03-18 09:50 | 10 | 010:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | M22031700329 | New_Event | Cutout Failure | Include | Include | Equipment | 659 | 2022-03-17 | 6590 | keep | 0 | Mar | 2022 | 0.0044884 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-17 22:56 | 2022-03-18 09:45 | 120 | 010:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L SE RETIRO GLOBO | S22031700230 | New_Event |  |  | Include | Wildlife | 649 | 2022-03-17 | 77880 | keep | 0 | Mar | 2022 | 0.053044 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-03-17 22:59 | 2022-03-18 10:39 | 32 | 011:40 | P | DESGANCHE | 1X25 EN RISER (SE LIMPIO ENRREDADERA) | B22031700795 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2022-03-17 | 22400 | keep | 0 | Mar | 2022 | 0.015257 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2022-03-17 23:32 | 2022-03-18 02:45 | 40 | 003:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO PORTAFUSIBLE | B22031700797 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2022-03-17 | 7720 | keep | 0 | Mar | 2022 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-18 00:18 | 2022-03-18 10:07 | 15 | 009:49 | P | DESGANCHE | 1X50 EN C/L | B22031800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 589 | 2022-03-18 | 8835 | keep | 0 | Mar | 2022 | 0.0060175 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-18 00:33 | 2022-03-18 11:44 | 150 | 011:11 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA REPARO TERMINACION BAJANTE PRIMARIO DEL PROVISIONAL @ T-23 | R22031800001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 671 | 2022-03-18 | 100650 | keep | 0 | Mar | 2022 | 0.068552 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-03-18 00:44 | 2022-03-18 02:45 | 30 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M22031800007 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2022-03-18 | 3630 | keep | 0 | Mar | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-18 01:00 | 2022-03-18 09:45 | 100 | 008:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L, 1 X 50 EN C/L, 1 X 65 EN C/L Y SE REMPLAZO AISLADOR | R22031800003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 525 | 2022-03-18 | 52500 | keep | 0 | Mar | 2022 | 0.035758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-18 01:09 | 2022-03-18 01:11 | 85 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1658-14 SE CERRO POR CONTROL | R22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-18 | 170 | keep | 0 | Mar | 2022 | 0.00011579 | 5.7893e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-03-18 01:09 | 2022-03-18 01:11 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-18 | 2 | keep | 0 | Mar | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-18 02:04 | 2022-03-18 03:41 | 100 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO CONDUCTOR VIVO EN EL SUELO Y SE ABRIO INTERRUPTOR A PETICION DE FOREMAN YORLEIBIS TISSERT | B22031800002 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2022-03-18 | 9700 | keep | 0 | Mar | 2022 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-18 02:35 | 2022-03-18 06:20 | 53 | 003:45 | P | NO SE REPORTO CAUSA | 1X50 EN C/L & 1X40 EN C/L | B22031800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2022-03-18 | 11925 | keep | 0 | Mar | 2022 | 0.0081221 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2022-03-18 02:36 | 2022-03-18 10:17 | 60 | 007:41 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R22031800011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2022-03-18 | 27660 | keep | 0 | Mar | 2022 | 0.018839 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-18 02:37 | 2022-03-18 20:35 | 15 | 017:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR UNO DE 25KVA | M22031800012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1078 | 2022-03-18 | 16170 | keep | 0 | Mar | 2022 | 0.011013 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-18 03:03 | 2022-03-18 10:02 | 6 | 006:59 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22031800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 419 | 2022-03-18 | 2514 | keep | 0 | Mar | 2022 | 0.0017123 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-18 03:41 | 2022-03-18 03:53 | 4176 | 000:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE SECCIONALIZO CONDUCTOR VIVO EN EL SUELO ABRIENDO CORTE DE LINEA TOTAL EN CARR 164 BO. GUADIANA SECTOR CAMINO LOS NEGRONES, NARANJITO. 95% EN SERVICIO A LAS 03:53. BY-220318-01 | B22031800009 | Additional_clients | Wire Down | Include | Include | Equipment | 12 | 2022-03-18 | 50112 | keep | 0 | Mar | 2022 | 0.034131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-18 03:53 | 2022-03-18 14:00 | 226 | 010:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B22031800009 | Partial_restoration | Wire Down | Include | Include | Equipment | 607 | 2022-03-18 | 137182 | keep | 0 | Mar | 2022 | 0.093434 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-18 04:16 | 2022-03-18 09:00 | 29 | 004:44 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22031800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2022-03-18 | 8236 | keep | 0 | Mar | 2022 | 0.0056095 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BARRANQUITAS | 2022-03-18 06:27 | 2022-03-18 08:44 | 80 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22031800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-03-18 | 10960 | keep | 0 | Mar | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-18 06:45 | 2022-03-19 02:40 | 10 | 019:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22031800005 | New_Event | Wire Down | Include | Include | Equipment | 1195 | 2022-03-18 | 11950 | keep | 0 | Mar | 2022 | 0.0081391 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-18 07:36 | 2022-03-18 09:23 | 1 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A22031800007 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2022-03-18 | 107 | keep | 0 | Mar | 2022 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-18 08:28 | 2022-03-18 09:11 | 150 | 000:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN C/L PALOMAS CRUZARON LINEAS | S22031800007 | New_Event |  |  | Include | Wildlife | 43 | 2022-03-18 | 6450 | keep | 0 | Mar | 2022 | 0.0043931 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-03-18 08:30 | 2022-03-18 08:31 | 293 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 293 | keep | 0 | Mar | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
MAYAGÃœEZ | 2022-03-18 08:30 | 2022-03-18 09:23 | 1 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M22031700248 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-03-18 | 53 | keep | 0 | Mar | 2022 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-18 08:33 | 2022-03-18 12:12 | 22 | 003:39 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | R22031800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-03-18 | 4818 | keep | 0 | Mar | 2022 | 0.0032815 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2022-03-18 08:35 | 2022-03-18 11:58 | 70 | 003:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L (POR AVE EN LA LINEA) | B22031800034 | New_Event |  |  | Include | Wildlife | 203 | 2022-03-18 | 14210 | keep | 0 | Mar | 2022 | 0.0096784 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-03-18 08:50 | 2022-03-18 19:00 | 25 | 010:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22031800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 610 | 2022-03-18 | 15250 | keep | 0 | Mar | 2022 | 0.010387 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-18 09:07 | 2022-03-18 11:45 | 1 | 002:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C22031800030 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2022-03-18 | 158 | keep | 0 | Mar | 2022 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-18 09:11 | 2022-03-18 11:32 | 829 | 002:21 | P | DESCONECTIVO DEFECTUOSO | DISPARO 1206-04 LLEVA 60% DEL 1204-03 SE SECCIONALIZO Y SE CERRO N/O CONTRA 1303-02 | S22031800014 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2022-03-18 | 116889 | keep | 0 | Mar | 2022 | 0.079613 | 0.00056463 | Sustained | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2022-03-18 09:11 | 2022-03-18 13:52 | 1978 | 004:41 | P | DESCONECTIVO DEFECTUOSO | DISPARO 1206-04 LLEVA 40% DEL 1204-04 SE REMPLAZO MACHETES Y SE CERRO AMARRE | S22031800014 | New_Event | Switch Failure | Include | Include | Equipment | 281 | 2022-03-18 | 555818 | keep | 0 | Mar | 2022 | 0.37857 | 0.0013472 | Sustained | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2022-03-18 09:11 | 2022-03-18 10:10 | 1799 | 000:59 | T | DESCONECTIVO DEFECTUOSO | DISPARO 1206-04 SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 20% DEL 1303-02, 40% DEL 1204-04 Y 60% DEL 1204-03 | S22031800014 | New_Event | Switch Failure | Include | Include | Equipment | 59 | 2022-03-18 | 106141 | keep | 0 | Mar | 2022 | 0.072292 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-03-18 09:11 | 2022-03-18 11:32 | 487 | 002:21 | P | DESCONECTIVO DEFECTUOSO | DISPARO 1206-04 SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 20% DEL 1303-02 SE CERRO AMARRE CONTRA EL 1303-02 | S22031800014 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2022-03-18 | 68667 | keep | 0 | Mar | 2022 | 0.046769 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
VEGA BAJA | 2022-03-18 09:20 | 2022-03-18 11:40 | 150 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTE/NEUTRAL REMPLAZO JUEGO DE DISCOS PRIMARIOS, GRAPAS Y CAJA PRIMARIA Y SE VOLVIO A CERRAR C/L (NO FUNDIO) | B22031800024 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2022-03-18 | 21000 | keep | 0 | Mar | 2022 | 0.014303 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-03-18 09:22 | 2022-03-18 10:36 | 3 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO AVERIADO. | C22031800033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2022-03-18 | 222 | keep | 0 | Mar | 2022 | 0.0001512 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-03-18 09:27 | 2022-03-18 14:17 | 25 | 004:50 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REPARAR POSTE SECUNDARIO ROTO | C22031800002 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 290 | 2022-03-18 | 7250 | keep | 0 | Mar | 2022 | 0.0049379 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-03-18 09:32 | 2022-03-18 11:32 | 15 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L AVE | R22031800035 | New_Event |  |  | Include | Wildlife | 120 | 2022-03-18 | 1800 | keep | 0 | Mar | 2022 | 0.001226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-18 09:33 | 2022-03-18 09:34 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1716-03 | B22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 5809 | keep | 0 | Mar | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-03-18 09:33 | 2022-03-18 09:34 | 1612 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL - LLEVA LA CARGA DEL 1710-01 | B22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 1612 | keep | 0 | Mar | 2022 | 0.0010979 | 0.0010979 | Momentary | FALSE | FALSE | Not_TMED_Event | 1612
BARRANQUITAS | 2022-03-18 09:57 | 2022-03-18 12:20 | 80 | 002:23 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | C22031800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-03-18 | 11440 | keep | 0 | Mar | 2022 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-18 10:10 | 2022-03-18 14:10 | 150 | 004:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN C/L PALOMAS CRUZARON LINEAS | S22031800007 | New_Event |  |  | Include | Wildlife | 240 | 2022-03-18 | 36000 | keep | 0 | Mar | 2022 | 0.024519 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-18 10:11 | 2022-03-18 13:08 | 50 | 002:57 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22031800055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-03-18 | 8850 | keep | 0 | Mar | 2022 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-18 10:12 | 2022-03-18 12:50 | 22 | 002:38 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22031800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-03-18 | 3476 | keep | 0 | Mar | 2022 | 0.0023675 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2022-03-18 10:13 | 2022-03-18 12:14 | 1 | 002:01 | P | DESGANCHE | 3 X 15 EN CORTE DE LINEA | C22031800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-03-18 | 121 | keep | 0 | Mar | 2022 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-18 10:15 | 2022-03-18 10:16 | 3433 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1204-02 Y 20% POR EL 1303-02 | S22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 3433 | keep | 0 | Mar | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
CAGUAS | 2022-03-18 10:19 | 2022-03-18 13:25 | 100 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | C22031800042 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2022-03-18 | 18600 | keep | 0 | Mar | 2022 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-18 10:32 | 2022-03-18 21:37 | 25 | 011:05 | P | CABLE SOTERRADO AVERIADO | 1 X 50 DE PROVISIONAL @ T-15. AVERIA NUEVA DE T-15 @ T-16 Y AVERIA VIEJA DE T-16 @ T-17 | S22031800062 | New_Event | UG Cable Fault | Include | Include | Equipment | 665 | 2022-03-18 | 16625 | keep | 0 | Mar | 2022 | 0.011323 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-03-18 10:34 | 2022-03-18 16:00 | 60 | 005:26 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-03-18 | 19560 | keep | 0 | Mar | 2022 | 0.013322 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-18 10:37 | 2022-03-18 15:34 | 36 | 004:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | S22031800066 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2022-03-18 | 10692 | keep | 0 | Mar | 2022 | 0.0072823 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-03-18 10:40 | 2022-03-18 11:08 | 1 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031800068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-03-18 | 28 | keep | 0 | Mar | 2022 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-18 10:42 | 2022-03-18 15:00 | 10 | 004:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO DE LINEA SECUNDARIA | P22031800010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 258 | 2022-03-18 | 2580 | keep | 0 | Mar | 2022 | 0.0017572 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-03-18 10:47 | 2022-03-18 15:18 | 3 | 004:31 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 37.5 KVA AVERIADO EN MONTURA TRIFASICA | P22031800011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 271 | 2022-03-18 | 813 | keep | 0 | Mar | 2022 | 0.00055373 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-03-18 10:48 | 2022-03-18 17:15 | 50 | 006:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22031800051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 387 | 2022-03-18 | 19350 | keep | 0 | Mar | 2022 | 0.013179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-18 10:53 | 2022-03-18 15:35 | 300 | 004:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M22031800065 | New_Event | Wire Down | Include | Include | Equipment | 282 | 2022-03-18 | 84600 | keep | 0 | Mar | 2022 | 0.057621 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-03-18 11:08 | 2022-03-18 13:27 | 90 | 002:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 Y 1 X 30 EN CORTES DE LINEAS REPARO CONDUCTOR ROTO | C22031800044 | New_Event | Wire Down | Include | Include | Equipment | 139 | 2022-03-18 | 12510 | keep | 0 | Mar | 2022 | 0.0085205 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-03-18 11:15 | 2022-03-18 11:55 | 15 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR REMPLAZO CONECTORES SECUNDARIOS | M22031800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-18 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-03-18 11:16 | 2022-03-18 11:17 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 2286 | keep | 0 | Mar | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
CAGUAS | 2022-03-18 11:17 | 2022-03-18 14:32 | 200 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR PRIMARIO | C20031800045 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2022-03-18 | 39000 | keep | 0 | Mar | 2022 | 0.026563 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-03-18 11:18 | 2022-03-18 14:30 | 15 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M22031800072 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2022-03-18 | 2880 | keep | 0 | Mar | 2022 | 0.0019616 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-18 11:29 | 2022-03-18 11:49 | 16 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO CONECTOR EN BAJANTE SECUNDARIO/SE REPARARON VARIOS NEUTRALES SECUNDARIOS (NO FUNDIO) | B22031800061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-03-18 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-03-18 11:39 | 2022-03-18 13:35 | 80 | 001:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA ARRIADA | A22031800021 | New_Event | Wire Down | Include | Include | Equipment | 116 | 2022-03-18 | 9280 | keep | 0 | Mar | 2022 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-18 11:45 | 2022-03-18 18:05 | 100 | 006:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031800079 | New_Event | Bad Weather | Include | Include | Weather | 380 | 2022-03-18 | 38000 | keep | 0 | Mar | 2022 | 0.025882 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-18 11:54 | 2022-03-18 18:15 | 100 | 006:21 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTES DE LINEA INFORMA EL JOURNEYMAN QUE NO SE ENCONTRO CAUSA | A22031800023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2022-03-18 | 38100 | keep | 0 | Mar | 2022 | 0.02595 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-18 12:00 | 2022-03-18 13:40 | 827 | 001:40 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES POR SEGURIDAD MACHETE DEL 1206-04 FLOTANDO SE REPARO Y SE CERRARON | S22031800014 | New_Event | Switch Failure | Include | Include | Equipment | 100 | 2022-03-18 | 82700 | keep | 0 | Mar | 2022 | 0.056327 | 0.00056327 | Sustained | FALSE | FALSE | Not_TMED_Event | 827
BAYAMON | 2022-03-18 12:14 | 2022-03-18 14:00 | 50 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22031800066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-03-18 | 5300 | keep | 0 | Mar | 2022 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-18 12:14 | 2022-03-18 14:40 | 60 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22031800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-03-18 | 8760 | keep | 0 | Mar | 2022 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-18 12:19 | 2022-03-18 12:23 | 878 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL (LUEGO DE VERIFICAR PERSONAL FUERA) | B22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-18 | 3512 | keep | 0 | Mar | 2022 | 0.002392 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
PONCE | 2022-03-18 12:36 | 2022-03-18 14:50 | 150 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P22031800017 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2022-03-18 | 20100 | keep | 0 | Mar | 2022 | 0.01369 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-18 13:05 | 2022-03-18 13:46 | 137 | 000:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO TRAMO POR PUENTE ABIERTO Y SE CERRO TRAMO DE OTRO PUNTO | S22031800107 | New_Event | Wire Down | Include | Include | Equipment | 41 | 2022-03-18 | 5617 | keep | 0 | Mar | 2022 | 0.0038257 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2022-03-18 13:08 | 2022-03-18 15:35 | 30 | 002:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | B22031800073 | New_Event |  |  | Include | Wildlife | 147 | 2022-03-18 | 4410 | keep | 0 | Mar | 2022 | 0.0030036 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-18 13:10 | 2022-03-18 13:49 | 1 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | P22031800020 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2022-03-18 | 39 | keep | 0 | Mar | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-18 13:11 | 2022-03-19 15:18 | 2 | 026:07 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO DE 37.5 KV SE ENERGIZO LOS 2 CLIENTES A TRAVES DE UN TRANSFORMADOR CERCANO | M22031800088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1567 | 2022-03-18 | 3134 | keep | 0 | Mar | 2022 | 0.0021346 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-03-18 13:32 | 2022-03-18 15:10 | 40 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA JOURNEYMAN INFORMA QUE NO SE ENCONTRO CAUSA | A22031800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-03-18 | 3920 | keep | 0 | Mar | 2022 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-03-18 13:38 | 2022-03-18 13:39 | 630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 630 | keep | 0 | Mar | 2022 | 0.00042909 | 0.00042909 | Momentary | FALSE | FALSE | Not_TMED_Event | 630
YAUCO | 2022-03-18 13:42 | 2022-03-19 12:15 | 1 | 022:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 4.16 KV AVERIADO | P22031800025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1353 | 2022-03-18 | 1353 | keep | 0 | Mar | 2022 | 0.00092152 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-18 13:46 | 2022-03-18 13:47 | 1681 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1303-04 QUE LLEVA 1303-01 | S22031800000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-03-18 | 1681 | keep | 0 | Mar | 2022 | 0.0011449 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-18 13:46 | 2022-03-18 13:47 | 1598 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1303-04 QUE LLEVA 1346-06 | S22031800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-18 | 1598 | keep | 0 | Mar | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-03-18 13:47 | 2022-03-18 20:18 | 60 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO TRAMO POR PUENTE ABIERTO Y SE CERRO TRAMO DE OTRO PUNTO | S22031800107 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 391 | 2022-03-18 | 23460 | keep | 0 | Mar | 2022 | 0.015978 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-18 14:17 | 2022-03-18 18:30 | 12 | 004:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S22031800124 | New_Event | Cutout Failure | Include | Include | Equipment | 253 | 2022-03-18 | 3036 | keep | 0 | Mar | 2022 | 0.0020678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-18 14:21 | 2022-03-18 16:14 | 100 | 001:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PARA CERRAR PUENTE ABIERTO DEL TRONCAL CON SJ-220318-02 | S22031800125 | New_Event | Wire Down | Include | Include | Equipment | 113 | 2022-03-18 | 11300 | keep | 0 | Mar | 2022 | 0.0076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-18 14:30 | 2022-03-18 15:21 | 10 | 000:51 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | R22031800054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 51 | 2022-03-18 | 510 | keep | 0 | Mar | 2022 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-18 14:30 | 2022-03-18 14:31 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 3114 | keep | 0 | Mar | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-03-18 14:45 | 2022-03-18 15:25 | 12 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | P22031800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-18 | 480 | keep | 0 | Mar | 2022 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-18 15:05 | 2022-03-18 15:07 | 770 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DE 7801-04 | M22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-18 | 1540 | keep | 0 | Mar | 2022 | 0.0010489 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2022-03-18 15:05 | 2022-03-18 15:07 | 1772 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA LA CARGA DE 7801-04 ESTA POR 7801-02 | M22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-18 | 3544 | keep | 0 | Mar | 2022 | 0.0024138 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
BAYAMON | 2022-03-18 15:09 | 2022-03-18 15:11 | 878 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22031800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-18 | 1756 | keep | 0 | Mar | 2022 | 0.001196 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2022-03-18 15:15 | 2022-03-18 20:42 | 12 | 005:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE XMR | B22031800086 | New_Event | Wire Down | Include | Include | Equipment | 327 | 2022-03-18 | 3924 | keep | 0 | Mar | 2022 | 0.0026726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-18 15:24 | 2022-03-18 18:35 | 65 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22031800065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-03-18 | 12415 | keep | 0 | Mar | 2022 | 0.0084558 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-03-18 15:42 | 2022-03-18 15:43 | 2678 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B22031800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-18 | 2678 | keep | 0 | Mar | 2022 | 0.001824 | 0.001824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2678
BAYAMON | 2022-03-18 15:43 | 2022-03-18 19:02 | 892 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO A SALIDA DEL ALIMENTADOR | B22031800000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 199 | 2022-03-18 | 177508 | keep | 0 | Mar | 2022 | 0.1209 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
BAYAMON | 2022-03-18 15:48 | 2022-03-18 17:40 | 30 | 001:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-03-18 | 3360 | keep | 0 | Mar | 2022 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-18 15:58 | 2022-03-18 19:19 | 15 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22031800049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-03-18 | 3015 | keep | 0 | Mar | 2022 | 0.0020535 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-18 16:14 | 2022-03-18 17:34 | 400 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PARA CERRAR PUENTE ABIERTO DEL TRONCAL CON SJ-220318-02 Y SE NORMALIZO | S22031800125 | Additional_clients | Wire Down | Include | Include | Equipment | 80 | 2022-03-18 | 32000 | keep | 0 | Mar | 2022 | 0.021795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-18 16:14 | 2022-03-18 18:45 | 1 | 002:31 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22031800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-03-18 | 151 | keep | 0 | Mar | 2022 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-18 16:22 | 2022-03-18 17:16 | 15 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22031800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-03-18 | 810 | keep | 0 | Mar | 2022 | 0.00055169 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-18 16:24 | 2022-03-18 17:28 | 40 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | R22031800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-03-18 | 2560 | keep | 0 | Mar | 2022 | 0.0017436 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-18 16:27 | 2022-03-18 17:55 | 20 | 001:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA | R22031800054 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2022-03-18 | 1760 | keep | 0 | Mar | 2022 | 0.0011987 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-03-18 16:54 | 2022-03-18 18:25 | 29 | 001:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P22031800038 | New_Event |  |  | Include | Wildlife | 91 | 2022-03-18 | 2639 | keep | 0 | Mar | 2022 | 0.0017974 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
AGUADILLA | 2022-03-18 16:59 | 2022-03-18 22:25 | 2 | 005:26 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE MASIVO | M22031800142 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 326 | 2022-03-18 | 652 | keep | 0 | Mar | 2022 | 0.00044407 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-03-18 17:08 | 2022-03-18 17:28 | 20 | 000:20 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | R22031800060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-03-18 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-18 17:28 | 2022-03-18 19:00 | 15 | 001:32 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | R22031800060 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-03-18 | 1380 | keep | 0 | Mar | 2022 | 0.00093991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-18 17:47 | 2022-03-18 17:49 | 320 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-18 | 640 | keep | 0 | Mar | 2022 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
MAYAGÃœEZ | 2022-03-18 18:03 | 2022-03-18 18:55 | 10 | 000:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M22031800149 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2022-03-18 | 520 | keep | 0 | Mar | 2022 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-18 18:05 | 2022-03-19 09:50 | 60 | 015:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22031800150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 945 | 2022-03-18 | 56700 | keep | 0 | Mar | 2022 | 0.038618 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-18 18:20 | 2022-03-19 09:14 | 50 | 014:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M22031800153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 894 | 2022-03-18 | 44700 | keep | 0 | Mar | 2022 | 0.030445 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-18 18:58 | 2022-03-18 20:08 | 50 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22031800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-03-18 | 3500 | keep | 0 | Mar | 2022 | 0.0023838 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-18 18:58 | 2022-03-19 10:46 | 30 | 015:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR GLOBO | C22031800074 | New_Event |  |  | Include | Wildlife | 948 | 2022-03-18 | 28440 | keep | 0 | Mar | 2022 | 0.01937 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-18 19:02 | 2022-03-18 21:03 | 2678 | 002:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | B22031800000 | Additional_clients | Wire Down | Include | Include | Equipment | 121 | 2022-03-18 | 324038 | keep | 0 | Mar | 2022 | 0.2207 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-18 19:22 | 2022-03-19 17:30 | 1 | 022:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22031800038 | New_Event | Bad Weather | Include | Include | Weather | 1328 | 2022-03-18 | 1328 | keep | 0 | Mar | 2022 | 0.00090449 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-18 19:51 | 2022-03-19 11:17 | 10 | 015:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 25 EN CORTE DE LINEA SE DESENREDO LINEAS CRUZADAS | M22031800167 | New_Event | Wire Down | Include | Include | Equipment | 926 | 2022-03-18 | 9260 | keep | 0 | Mar | 2022 | 0.0063069 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-18 20:15 | 2022-03-18 22:28 | 65 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | P22031800048 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2022-03-18 | 8645 | keep | 0 | Mar | 2022 | 0.0058881 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-03-18 20:57 | 2022-03-19 09:38 | 100 | 012:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22021800183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 761 | 2022-03-18 | 76100 | keep | 0 | Mar | 2022 | 0.051831 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-18 21:35 | 2022-03-18 21:36 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 7621 | keep | 0 | Mar | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
BARRANQUITAS | 2022-03-18 22:41 | 2022-03-19 05:03 | 400 | 006:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTES DE LINEA SE SECCIONALIZO POSTE IMPACTADO | C22031800083 | New_Event |  |  | Include | Wildlife | 382 | 2022-03-18 | 152800 | keep | 0 | Mar | 2022 | 0.10407 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2022-03-18 22:42 | 2022-03-19 10:30 | 50 | 011:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22031800192 | New_Event | Bad Weather | Include | Include | Weather | 708 | 2022-03-18 | 35400 | keep | 0 | Mar | 2022 | 0.024111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-03-18 23:19 | 2022-03-19 10:30 | 80 | 011:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M22031800194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 671 | 2022-03-18 | 53680 | keep | 0 | Mar | 2022 | 0.036561 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-18 23:30 | 2022-03-18 23:31 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 10 SMU20 | B22031800178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-18 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-19 01:03 | 2022-03-19 10:38 | 10 | 009:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P22031900001 | New_Event | Wire Down | Include | Include | Equipment | 575 | 2022-03-19 | 5750 | keep | 0 | Mar | 2022 | 0.0039163 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-19 01:25 | 2022-03-19 01:26 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 312 | keep | 0 | Mar | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2022-03-19 02:08 | 2022-03-19 02:09 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22031900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 3431 | keep | 0 | Mar | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-03-19 03:01 | 2022-03-19 09:40 | 60 | 006:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES AVERIADO | A22031900004 | New_Event | Cutout Failure | Include | Include | Equipment | 399 | 2022-03-19 | 23940 | keep | 0 | Mar | 2022 | 0.016305 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-19 03:20 | 2022-03-19 03:21 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-03 Y SE CERRO POR SCADA | B22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 1746 | keep | 0 | Mar | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-03-19 03:21 | 2022-03-19 14:15 | 3 | 010:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-13A | B22031900033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 654 | 2022-03-19 | 1962 | keep | 0 | Mar | 2022 | 0.0013363 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-03-19 03:34 | 2022-03-19 03:35 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9202-04 | B22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 2926 | keep | 0 | Mar | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
CANOVANAS | 2022-03-19 03:36 | 2022-03-19 09:50 | 3464 | 006:14 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA AL 2402-01 | R22031900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 374 | 2022-03-19 | 1295536 | keep | 0 | Mar | 2022 | 0.88238 | 0.0023593 | Sustained | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2022-03-19 03:36 | 2022-03-19 08:51 | 7621 | 005:15 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA A 2402-03 | R22031190000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 315 | 2022-03-19 | 2400615 | keep | 0 | Mar | 2022 | 1.635 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2022-03-19 03:36 | 2022-03-19 08:24 | 3699 | 004:48 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA AL 2402-04 | R22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2022-03-19 | 1065312 | keep | 0 | Mar | 2022 | 0.72558 | 0.0025194 | Sustained | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2022-03-19 03:36 | 2022-03-19 10:38 | 2675 | 007:02 | S | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA AL 2404-05 QUE A SU VEZ ESTA POR 2402-02 | R22031900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 422 | 2022-03-19 | 1128850 | keep | 0 | Mar | 2022 | 0.76885 | 0.0018219 | Sustained | FALSE | FALSE | Not_TMED_Event | 2675
SAN JUAN | 2022-03-19 03:51 | 2022-03-19 07:38 | 1681 | 003:47 | T | DESGANCHE | DISPARO DE 1303-04 LLEVANDO 1303-01 Y 1346-06 SE SECCIONALIZO EN CARR. 199 CON 176 Y SE CERRO POR SCADA | S22031900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-03-19 | 381587 | keep | 0 | Mar | 2022 | 0.2599 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-03-19 03:51 | 2022-03-19 09:06 | 1598 | 005:15 | T | DESGANCHE | DISPARO DE 1303-04 LLEVANDO 1303-01 Y 1346-06 SE SECCIONALIZO EN CARR. 176 CON 199 PRA RETIRAR BAMBUAS Y SE CERRO EN LA VICTOR LABIOSA | S22031900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2022-03-19 | 503370 | keep | 0 | Mar | 2022 | 0.34284 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BARRANQUITAS | 2022-03-19 05:03 | 2022-03-19 16:40 | 100 | 011:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PRIMARIO IMPACTADO EN ACCIDENTE DE VEHICULO CG-220319-01 GOI SE REEMPLAZO POSTE PRIMARIO | C22031800083 | Partial_restoration |  |  | Include | Wildlife | 697 | 2022-03-19 | 69700 | keep | 0 | Mar | 2022 | 0.047472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-19 05:10 | 2022-03-19 05:11 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1711-03 LLEVANDO PARTE DEL 1716-03 | B22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 13 | keep | 0 | Mar | 2022 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-03-19 05:10 | 2022-03-19 05:11 | 200 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1711-03 LLEVANDO PARTE DEL 1716-03 | B22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 200 | keep | 0 | Mar | 2022 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-03-19 05:29 | 2022-03-19 13:07 | 46 | 007:38 | P | DESGANCHE | 1X100 EN C/L & SE RETIRO BAMBUA | B22031900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2022-03-19 | 21068 | keep | 0 | Mar | 2022 | 0.014349 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
FAJARDO | 2022-03-19 06:00 | 2022-03-19 11:58 | 60 | 005:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA REEMPLAZO POSTE ROTO POR VEHÃCULO | R22031900102 | New_Event |  |  | Include | Wildlife | 358 | 2022-03-19 | 21480 | keep | 0 | Mar | 2022 | 0.01463 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-03-19 06:07 | 2022-03-19 06:08 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 1830 | keep | 0 | Mar | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
BAYAMON | 2022-03-19 06:15 | 2022-03-19 20:48 | 81 | 014:33 | T | PROTECCION DEFECTUOSA | SUBESTACIONES TRABAJO CON RELE DE PROTECCION | B22031900000 | New_Event | Protection Miscoordination | Include | Include | Other | 873 | 2022-03-19 | 70713 | keep | 0 | Mar | 2022 | 0.048162 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
VEGA BAJA | 2022-03-19 07:10 | 2022-03-19 09:15 | 48 | 002:05 | P | NO SE REPORTO CAUSA | 1X50 EN C/L & 1X30 EN C/L | B22031900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-03-19 | 6000 | keep | 0 | Mar | 2022 | 0.0040866 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CAGUAS | 2022-03-19 07:15 | 2022-03-19 09:09 | 90 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22031900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-03-19 | 10260 | keep | 0 | Mar | 2022 | 0.006988 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2022-03-19 07:27 | 2022-03-19 07:29 | 215 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL | B22031900000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2022-03-19 | 430 | keep | 0 | Mar | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-03-19 07:29 | 2022-03-19 12:31 | 65 | 005:02 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1X100 EN SU-1 Y SE LLEVO A SU LUGAR TERMINACION EN CAJA SECA | B22031900009 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 302 | 2022-03-19 | 19630 | keep | 0 | Mar | 2022 | 0.01337 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2022-03-19 07:30 | 2022-03-19 07:31 | 65 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN C/L (POR AVE EN EL 13KV) | B22031900004 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-19 | 65 | keep | 0 | Mar | 2022 | 4.4271e-05 | 4.4271e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-03-19 07:38 | 2022-03-19 08:33 | 600 | 000:55 | P | DESGANCHE | DISPARO DE 1303-04 LLEVANDO 1303-01 Y 1346-06 SE SECCIONALIZO EN CARR. VICTOR LABIOSA PARA DESGANCHAR Y SE CERRO CARR. 199 CON 176 | S22031900002 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-03-19 | 33000 | keep | 0 | Mar | 2022 | 0.022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-19 07:40 | 2022-03-19 13:15 | 80 | 005:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22031900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2022-03-19 | 26800 | keep | 0 | Mar | 2022 | 0.018253 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-19 07:44 | 2022-03-19 13:24 | 140 | 005:40 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 80 EN CORTES DE LINEAS | C22031900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2022-03-19 | 47600 | keep | 0 | Mar | 2022 | 0.03242 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
ARECIBO | 2022-03-19 08:33 | 2022-03-19 13:19 | 120 | 004:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22031900010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 286 | 2022-03-19 | 34320 | keep | 0 | Mar | 2022 | 0.023375 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-03-19 08:42 | 2022-03-19 08:43 | 34 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF PERMANENTE | C22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 34 | keep | 0 | Mar | 2022 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
CANOVANAS | 2022-03-19 08:43 | 2022-03-19 08:44 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 4188 | keep | 0 | Mar | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CAGUAS | 2022-03-19 08:47 | 2022-03-19 08:51 | 34 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF PERMANENTE | C22031900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-19 | 136 | keep | 0 | Mar | 2022 | 9.2629e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
ARECIBO | 2022-03-19 08:47 | 2022-03-19 15:45 | 3 | 006:58 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR PRIMARIA | A22031900011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2022-03-19 | 1254 | keep | 0 | Mar | 2022 | 0.00085409 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-19 08:52 | 2022-03-19 08:53 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 3871 | keep | 0 | Mar | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
SAN JUAN | 2022-03-19 09:04 | 2022-03-19 11:00 | 30 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL | S22031900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-03-19 | 3480 | keep | 0 | Mar | 2022 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-19 09:06 | 2022-03-19 09:25 | 500 | 000:19 | P | DESGANCHE | DISPARO DE 1303-04 LLEVANDO 1303-01 Y 1346-06 SE SECCIONALIZO SE RETIRO BAMBUAS Y SE CERRO EN LA CARR. 177 CON CARR. 176 | S22031900002 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 19 | 2022-03-19 | 9500 | keep | 0 | Mar | 2022 | 0.0064704 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-19 09:08 | 2022-03-19 09:17 | 3 | 000:09 | P | ERROR HUMANO | SE CERRARON PUENTES HACIA CLIENTES SE HABIAN DEJADO ABIERTOS DURANTE VIA LIBRE PENSANDO TRAMO ESTABA VACANTE | S22031800012 | New_Event | Human Error | Include | Include | Other | 9 | 2022-03-19 | 27 | keep | 0 | Mar | 2022 | 1.839e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-03-19 09:08 | 2022-03-19 14:49 | 1 | 005:41 | P | DESGANCHE | 1 X 65 EN RISER SECTOR REQUIERE DESGANCHE | M22031900065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2022-03-19 | 341 | keep | 0 | Mar | 2022 | 0.00023225 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-19 09:21 | 2022-03-19 18:57 | 45 | 009:36 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 50 EN C/L | C22031900031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 576 | 2022-03-19 | 25920 | keep | 0 | Mar | 2022 | 0.017654 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-03-19 09:23 | 2022-03-19 13:34 | 12 | 004:11 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-16 | S22031900045 | New_Event | UG Cable Fault | Include | Include | Equipment | 251 | 2022-03-19 | 3012 | keep | 0 | Mar | 2022 | 0.0020515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-03-19 09:25 | 2022-03-19 11:23 | 7 | 001:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 2.4/4.16 KV CON LIQUEO DE ACEITE | P22031900006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 118 | 2022-03-19 | 826 | keep | 0 | Mar | 2022 | 0.00056258 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-03-19 09:50 | 2022-03-19 10:34 | 1464 | 000:44 | P | NO SE REPORTO CAUSA | DISPARO DE SUBESTACION SE TRANSFIRIO LA CARGA AL 2402-02 | R22031900007 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 44 | 2022-03-19 | 64416 | keep | 0 | Mar | 2022 | 0.043873 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-19 09:51 | 2022-03-19 11:48 | 1 | 001:57 | P | NO SE REPORTO CAUSA | 2X10 EN BANCO DE TRANSFORMADORES | B22031900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2022-03-19 | 117 | keep | 0 | Mar | 2022 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-19 09:56 | 2022-03-19 13:00 | 80 | 003:04 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S22031900079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-03-19 | 14720 | keep | 0 | Mar | 2022 | 0.010026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-19 10:25 | 2022-03-19 14:43 | 6 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR SE REPARO BAJANTE | S22031900081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2022-03-19 | 1548 | keep | 0 | Mar | 2022 | 0.0010543 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-03-19 10:55 | 2022-03-19 12:52 | 15 | 001:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE PRIMARIO A CAJA | R22031900276 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2022-03-19 | 1755 | keep | 0 | Mar | 2022 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-19 10:55 | 2022-03-19 12:33 | 6 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR 200 PIES DE ALAMBRE 3/2 | P22031900009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-03-19 | 588 | keep | 0 | Mar | 2022 | 0.00040048 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-19 11:29 | 2022-03-19 15:55 | 10 | 004:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22031800080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 266 | 2022-03-19 | 2660 | keep | 0 | Mar | 2022 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-19 11:48 | 2022-03-19 13:29 | 20 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22031900085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-03-19 | 2020 | keep | 0 | Mar | 2022 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-19 12:19 | 2022-03-19 16:27 | 9 | 004:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M22031900056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 248 | 2022-03-19 | 2232 | keep | 0 | Mar | 2022 | 0.0015202 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-03-19 12:27 | 2022-03-19 16:29 | 15 | 004:02 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22031900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-03-19 | 3630 | keep | 0 | Mar | 2022 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-03-19 12:29 | 2022-03-19 14:41 | 20 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR AVE | R22031900280 | New_Event |  |  | Include | Wildlife | 132 | 2022-03-19 | 2640 | keep | 0 | Mar | 2022 | 0.0017981 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-19 12:58 | 2022-03-19 16:51 | 120 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031900062 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2022-03-19 | 27960 | keep | 0 | Mar | 2022 | 0.019043 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-03-19 13:22 | 2022-03-19 17:07 | 62 | 003:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE DESGANCHO Y SE REMPLAZO AISLADOR | S22031900089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 225 | 2022-03-19 | 13950 | keep | 0 | Mar | 2022 | 0.0095013 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
PONCE | 2022-03-19 13:26 | 2022-03-19 17:09 | 3744 | 003:43 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE INSTALO AISLADOR PARA SEPARAR FASES LUEGO DEL CONVERTIDOR | P22031900014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 223 | 2022-03-19 | 834912 | keep | 0 | Mar | 2022 | 0.56865 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-03-19 13:34 | 2022-03-19 18:32 | 100 | 004:58 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN DIFERENTES CORTES DE LINEA POR DESGANCHE | P22031900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-03-19 | 29800 | keep | 0 | Mar | 2022 | 0.020297 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-03-19 13:35 | 2022-03-19 15:35 | 15 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 3 X 5 EN XMR SE RETIRO SECUNDARIA | R22031900281 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2022-03-19 | 1800 | keep | 0 | Mar | 2022 | 0.001226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-19 13:53 | 2022-03-19 15:32 | 23 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO Y SE SUBIO TAP | C22031800058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2022-03-19 | 2277 | keep | 0 | Mar | 2022 | 0.0015509 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
YAUCO | 2022-03-19 14:06 | 2022-03-19 14:07 | 1637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22031900023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 1637 | keep | 0 | Mar | 2022 | 0.001115 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
BAYAMON | 2022-03-19 14:15 | 2022-03-19 15:30 | 12 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22031900027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-03-19 | 900 | keep | 0 | Mar | 2022 | 0.00061299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-19 14:19 | 2022-03-19 16:40 | 1 | 002:21 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 25 SMU20 EN SU-6 CONTAMINACION | R22031900282 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 141 | 2022-03-19 | 141 | keep | 0 | Mar | 2022 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-19 14:24 | 2022-03-19 16:48 | 2484 | 002:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR RTU DOWN SE ABRIERON MACHETES EN BO LA MONTALVA CAR 325 KM 1.0 Y SE COLOCO INTERRUPTOR EN SERVICIO MANUAL ELECTRICAMENTE | P22031900028 | New_Event | Wire Down | Include | Include | Equipment | 144 | 2022-03-19 | 357696 | keep | 0 | Mar | 2022 | 0.24363 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2022-03-19 14:28 | 2022-03-19 20:30 | 30 | 006:02 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22031900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-03-19 | 10860 | keep | 0 | Mar | 2022 | 0.0073967 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-03-19 14:48 | 2022-03-19 16:00 | 20 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN COVERTIDOR SE CERRO CONVERTIDOR MAL TIEMPO VIENTOS FUERTES | A22031900029 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2022-03-19 | 1440 | keep | 0 | Mar | 2022 | 0.00098078 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-19 14:52 | 2022-03-19 14:53 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031900147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 2067 | keep | 0 | Mar | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
HUMACAO | 2022-03-19 15:10 | 2022-03-19 15:11 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 3025 | keep | 0 | Mar | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2022-03-19 15:22 | 2022-03-19 17:04 | 12 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1 X 140 EN C/L | C22031900048 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-03-19 | 1224 | keep | 0 | Mar | 2022 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-19 15:37 | 2022-03-19 18:44 | 863 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22031900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2022-03-19 | 161381 | keep | 0 | Mar | 2022 | 0.10992 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-03-19 15:37 | 2022-03-19 18:44 | 309 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22031900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2022-03-19 | 57783 | keep | 0 | Mar | 2022 | 0.039356 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-03-19 15:37 | 2022-03-19 18:44 | 176 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22031900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2022-03-19 | 32912 | keep | 0 | Mar | 2022 | 0.022416 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-03-19 15:37 | 2022-03-19 18:44 | 974 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22031900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2022-03-19 | 182138 | keep | 0 | Mar | 2022 | 0.12405 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
VEGA BAJA | 2022-03-19 15:56 | 2022-03-19 18:40 | 30 | 002:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B22031900036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 164 | 2022-03-19 | 4920 | keep | 0 | Mar | 2022 | 0.003351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-19 15:58 | 2022-03-19 17:30 | 65 | 001:32 | P | DESGANCHE | 1 X65 EN C/L SE RETIRO BAMBUA DE LINEA | C22031900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-03-19 | 5980 | keep | 0 | Mar | 2022 | 0.004073 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-03-19 16:06 | 2022-03-20 09:23 | 90 | 017:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22031900083 | New_Event | Bad Weather | Include | Include | Weather | 1037 | 2022-03-19 | 93330 | keep | 0 | Mar | 2022 | 0.063567 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-03-19 16:07 | 2022-03-19 18:00 | 50 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S22031900100 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-03-19 | 5650 | keep | 0 | Mar | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-19 16:23 | 2022-03-20 09:27 | 15 | 017:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22031900090 | New_Event | Bad Weather | Include | Include | Weather | 1024 | 2022-03-19 | 15360 | keep | 0 | Mar | 2022 | 0.010462 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-19 16:35 | 2022-03-20 09:05 | 5 | 016:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | P22031900053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 990 | 2022-03-19 | 4950 | keep | 0 | Mar | 2022 | 0.0033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-19 16:36 | 2022-03-19 19:25 | 150 | 002:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22020300096 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2022-03-19 | 25350 | keep | 0 | Mar | 2022 | 0.017266 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-03-19 16:47 | 2022-03-19 19:11 | 20 | 002:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | B22031900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-03-19 | 2880 | keep | 0 | Mar | 2022 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-03-19 16:48 | 2022-03-19 17:09 | 488 | 000:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABREN MACHETES EN CARR 325 KM 1.0 Y SE CIERRAN MACHETES EN CARR 325 KM 3.1 | P22031900060 | Partial_restoration | Wire Down | Include | Include | Equipment | 21 | 2022-03-19 | 10248 | keep | 0 | Mar | 2022 | 0.0069799 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-19 17:04 | 2022-03-19 19:27 | 85 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO PORTAFUSIBLE | S22031900105 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-03-19 | 12155 | keep | 0 | Mar | 2022 | 0.0082787 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
YAUCO | 2022-03-19 17:09 | 2022-03-19 21:54 | 300 | 004:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO Y SE CERRARON MACHETES | P22031900060 | Partial_restoration | Wire Down | Include | Include | Equipment | 285 | 2022-03-19 | 85500 | keep | 0 | Mar | 2022 | 0.058234 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-19 17:56 | 2022-03-19 22:24 | 45 | 004:28 | P | DESGANCHE | 1 X 80 EN C/L Y SE DESGANCHO | S22031900115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-03-19 | 12060 | keep | 0 | Mar | 2022 | 0.008214 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-03-19 18:03 | 2022-03-19 19:46 | 390 | 001:43 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETES PARA CONTINUAR PATRULLANDO | M22031900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-03-19 | 40170 | keep | 0 | Mar | 2022 | 0.02736 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
MAYAGÃœEZ | 2022-03-19 18:16 | 2022-03-20 08:59 | 80 | 014:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22031900133 | New_Event | Bad Weather | Include | Include | Weather | 883 | 2022-03-19 | 70640 | keep | 0 | Mar | 2022 | 0.048113 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-19 18:16 | 2022-03-20 17:00 | 500 | 022:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M22032000017 | New_Event | Wire Down | Include | Include | Equipment | 1364 | 2022-03-19 | 682000 | keep | 0 | Mar | 2022 | 0.46451 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-03-19 18:33 | 2022-03-19 18:34 | 316 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A22031900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-19 | 316 | keep | 0 | Mar | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-03-19 18:34 | 2022-03-19 20:23 | 120 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22031900050 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 109 | 2022-03-19 | 13080 | keep | 0 | Mar | 2022 | 0.0089087 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-03-19 18:43 | 2022-03-19 23:50 | 320 | 005:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | MEDIANTE GOI BY-220319-02 SE CORTO BAJANTE PRIMARIO DONDE CHANGO HIZO CONTACTO | B22031900072 | New_Event |  |  | Include | Wildlife | 307 | 2022-03-19 | 98240 | keep | 0 | Mar | 2022 | 0.066911 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-03-19 19:00 | 2022-03-20 00:49 | 40 | 005:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE LEVANTO CONDUCTOR | B22031900074 | New_Event | Wire Down | Include | Include | Equipment | 349 | 2022-03-19 | 13960 | keep | 0 | Mar | 2022 | 0.0095081 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-19 19:05 | 2022-03-19 21:04 | 40 | 001:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22031900087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-03-19 | 4760 | keep | 0 | Mar | 2022 | 0.003242 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-19 19:41 | 2022-03-20 13:46 | 8 | 018:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22031900163 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1085 | 2022-03-19 | 8680 | keep | 0 | Mar | 2022 | 0.0059119 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-19 19:43 | 2022-03-20 09:40 | 60 | 013:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE REPARO PUENTE ABIERTO | S22031900165 | New_Event | Wire Down | Include | Include | Equipment | 837 | 2022-03-19 | 50220 | keep | 0 | Mar | 2022 | 0.034205 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-19 19:45 | 2022-03-20 08:40 | 7 | 012:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO DE XMR Y SE REPARO BAJANTE | S22031900166 | New_Event | Secondary Wire Down | Include | Include | Equipment | 775 | 2022-03-19 | 5425 | keep | 0 | Mar | 2022 | 0.0036949 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-19 19:46 | 2022-03-19 21:13 | 50 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22031900167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-03-19 | 4350 | keep | 0 | Mar | 2022 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-03-19 19:46 | 2022-03-19 20:00 | 50 | 000:14 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES NO SE ENCONTRO AVERIA EN ALIMENTADOR | M22031900191 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 14 | 2022-03-19 | 700 | keep | 0 | Mar | 2022 | 0.00047677 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-19 19:53 | 2022-03-20 01:03 | 25 | 005:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031900189 | New_Event | Bad Weather | Include | Include | Weather | 310 | 2022-03-19 | 7750 | keep | 0 | Mar | 2022 | 0.0052785 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-03-19 19:58 | 2022-03-19 21:55 | 12 | 001:57 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR PRIMARIA | A22031900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-03-19 | 1404 | keep | 0 | Mar | 2022 | 0.00095626 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-19 20:25 | 2022-03-19 20:27 | 906 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-19 | 1812 | keep | 0 | Mar | 2022 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
MAYAGÃœEZ | 2022-03-19 20:49 | 2022-03-19 20:50 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22031900202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 3458 | keep | 0 | Mar | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-03-19 20:51 | 2022-03-20 08:56 | 8 | 012:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22031900065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 725 | 2022-03-19 | 5800 | keep | 0 | Mar | 2022 | 0.0039504 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-19 21:03 | 2022-03-20 03:03 | 200 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22031900204 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2022-03-19 | 72000 | keep | 0 | Mar | 2022 | 0.049039 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-03-19 21:56 | 2022-03-20 10:00 | 100 | 012:04 | P | DESGANCHE | 1 X 40 1 X 100 EN CORTE DE LINEA | R22031900444 | New_Event | Vegetation Contact | Include | Include | Vegetation | 724 | 2022-03-19 | 72400 | keep | 0 | Mar | 2022 | 0.049311 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-19 22:50 | 2022-03-19 22:51 | 3295 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 9502-02 AL CERRAR BKR 9503-05 MEDIANTE EL GOI BY-220319-02. SE CERRO Y QUEDO EN SERVICIO. SE PICO BAJANTE CONDUCTOR DONDE CHANGO CRUZO LINEA | B22031900000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-19 | 3295 | keep | 0 | Mar | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
HUMACAO | 2022-03-19 23:56 | 2022-03-19 23:57 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22031900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-19 | 824 | keep | 0 | Mar | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-03-19 23:56 | 2022-03-20 01:47 | 320 | 001:51 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR NUEVAMENTE DEBDIO A QUE SE QUEMO MACHETE DE SALIDA. SE REEMPLAZO MACHETE AVERIADO MEDIANTE GOI BY-220319-02 | B22032000072 | New_Event | Switch Failure | Include | Include | Equipment | 111 | 2022-03-19 | 35520 | keep | 0 | Mar | 2022 | 0.024193 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
AGUADILLA | 2022-03-19 23:57 | 2022-03-20 09:05 | 12 | 009:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | M22031900236 | New_Event | Wire Down | Include | Include | Equipment | 548 | 2022-03-19 | 6576 | keep | 0 | Mar | 2022 | 0.0044789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-20 00:20 | 2022-03-20 14:09 | 4 | 013:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22032000001 | New_Event | Bad Weather | Include | Include | Weather | 829 | 2022-03-20 | 3316 | keep | 0 | Mar | 2022 | 0.0022585 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-03-20 01:38 | 2022-03-20 01:39 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1907-03 LLEVANDO EL 1909-09 | S22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 222 | keep | 0 | Mar | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-03-20 01:38 | 2022-03-20 01:39 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1907-03 LLEVANDO EL 1909-09 | B22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 4456 | keep | 0 | Mar | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-03-20 01:39 | 2022-03-20 14:35 | 150 | 012:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22032000121 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 776 | 2022-03-20 | 116400 | keep | 0 | Mar | 2022 | 0.07928 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-03-20 02:49 | 2022-03-20 09:37 | 1 | 006:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22032000005 | New_Event | Bad Weather | Include | Include | Weather | 408 | 2022-03-20 | 408 | keep | 0 | Mar | 2022 | 0.00027789 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-20 03:29 | 2022-03-20 03:30 | 3012 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 3012 | keep | 0 | Mar | 2022 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
FAJARDO | 2022-03-20 05:04 | 2022-03-20 11:04 | 123 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER Y 1 X 25 SUM-20 EN SU-1 Y 1 X 20 SUM-20 EN SU-2 SE REMPLAZO PORTAFUSIBLE EN SU-2 | R22032000003 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2022-03-20 | 44280 | keep | 0 | Mar | 2022 | 0.030159 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
BAYAMON | 2022-03-20 05:45 | 2022-03-20 09:56 | 25 | 004:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-03-20 | 6275 | keep | 0 | Mar | 2022 | 0.0042739 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-03-20 05:55 | 2022-03-20 19:08 | 80 | 013:13 | P | DESGANCHE | 1 X 80 SE REALIZO DESGANCHE | S22032000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 793 | 2022-03-20 | 63440 | keep | 0 | Mar | 2022 | 0.043209 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-20 06:17 | 2022-03-20 12:50 | 120 | 006:33 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN C/L Y 1 X 65 EN RISER SE REPARO TERMINACION | S22032000027 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 393 | 2022-03-20 | 47160 | keep | 0 | Mar | 2022 | 0.03212 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-03-20 07:10 | 2022-03-20 07:11 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22032000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 1478 | keep | 0 | Mar | 2022 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
SAN JUAN | 2022-03-20 07:29 | 2022-03-20 22:38 | 3 | 015:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S22032000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 909 | 2022-03-20 | 2727 | keep | 0 | Mar | 2022 | 0.0018573 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-03-20 08:01 | 2022-03-20 08:59 | 129 | 000:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C22032000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-03-20 | 7482 | keep | 0 | Mar | 2022 | 0.005096 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BAYAMON | 2022-03-20 08:07 | 2022-03-20 08:08 | 77 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 77 | keep | 0 | Mar | 2022 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
ARECIBO | 2022-03-20 08:16 | 2022-03-20 11:47 | 100 | 003:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-03-20 | 21100 | keep | 0 | Mar | 2022 | 0.014371 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-20 08:21 | 2022-03-20 08:22 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 325 | keep | 0 | Mar | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2022-03-20 08:24 | 2022-03-20 13:31 | 1105 | 005:07 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO OHGW DE LINEA PARTIDO SE REMPLAZARON 2 FUSIBLES 125 STD SPEED Y SE NORMALIZO LAS CARGAS | S22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 307 | 2022-03-20 | 339235 | keep | 0 | Mar | 2022 | 0.23105 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2022-03-20 08:24 | 2022-03-20 13:31 | 181 | 005:07 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO OHGW DE LINEA PARTIDO SE REMPLAZARON 2 FUSIBLES 125 STD SPEED Y SE NORMALIZO LAS CARGAS | S22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 307 | 2022-03-20 | 55567 | keep | 0 | Mar | 2022 | 0.037846 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2022-03-20 08:24 | 2022-03-20 13:31 | 351 | 005:07 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO OHGW DE LINEA PARTIDO SE REMPLAZARON 2 FUSIBLES 125 STD SPEED Y SE NORMALIZO LAS CARGAS | S22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 307 | 2022-03-20 | 107757 | keep | 0 | Mar | 2022 | 0.073393 | 0.00023906 | Sustained | FALSE | FALSE | Not_TMED_Event | 351
SAN JUAN | 2022-03-20 08:24 | 2022-03-20 13:31 | 570 | 005:07 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO OHGW DE LINEA PARTIDO SE REMPLAZARON 2 FUSIBLES 125 STD SPEED Y SE NORMALIZO LAS CARGAS | S22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 307 | 2022-03-20 | 174990 | keep | 0 | Mar | 2022 | 0.11918 | 0.00038822 | Sustained | FALSE | FALSE | Not_TMED_Event | 570
SAN JUAN | 2022-03-20 08:25 | 2022-03-20 10:57 | 165 | 002:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22032000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-03-20 | 25080 | keep | 0 | Mar | 2022 | 0.017082 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
CAGUAS | 2022-03-20 08:27 | 2022-03-20 09:55 | 16 | 001:28 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR ENREDADERA | C22032000005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 88 | 2022-03-20 | 1408 | keep | 0 | Mar | 2022 | 0.00095898 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
UTUADO | 2022-03-20 08:32 | 2022-03-20 10:09 | 15 | 001:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE DE BAMBUAS | A22032000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-03-20 | 1455 | keep | 0 | Mar | 2022 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-20 08:36 | 2022-03-20 10:11 | 40 | 001:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE | R22032000018 | New_Event |  |  | Include | Wildlife | 95 | 2022-03-20 | 3800 | keep | 0 | Mar | 2022 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-20 08:46 | 2022-03-20 14:33 | 12 | 005:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2022-03-20 | 4164 | keep | 0 | Mar | 2022 | 0.0028361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-20 09:00 | 2022-03-20 11:58 | 1 | 002:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA EN BANCO DE TRANSFORMADORES | C22032000006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 178 | 2022-03-20 | 178 | keep | 0 | Mar | 2022 | 0.00012123 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-03-20 09:15 | 2022-03-20 10:28 | 390 | 001:13 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE CERRO INTERRUPTOR | M22032000028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2022-03-20 | 28470 | keep | 0 | Mar | 2022 | 0.019391 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
CANOVANAS | 2022-03-20 09:48 | 2022-03-20 12:08 | 3 | 002:20 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN CORTE DE LINEA PARARRAYO AVERIADO | R22032000023 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 140 | 2022-03-20 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-03-20 09:55 | 2022-03-20 12:36 | 5 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE | R22032000024 | New_Event |  |  | Include | Wildlife | 161 | 2022-03-20 | 805 | keep | 0 | Mar | 2022 | 0.00054828 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-20 09:55 | 2022-03-20 12:40 | 25 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22032000021 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2022-03-20 | 4125 | keep | 0 | Mar | 2022 | 0.0028095 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-03-20 10:03 | 2022-03-20 13:00 | 184 | 002:57 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA SE CORRIGE CLIENTES | P22032000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-03-20 | 32568 | keep | 0 | Mar | 2022 | 0.022182 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
ARECIBO | 2022-03-20 10:05 | 2022-03-20 10:06 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 1227 | keep | 0 | Mar | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CAGUAS | 2022-03-20 10:12 | 2022-03-20 10:13 | 2907 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22032000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 2907 | keep | 0 | Mar | 2022 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
CAGUAS | 2022-03-20 10:16 | 2022-03-20 12:41 | 5 | 002:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR CHANGO | C22032000013 | New_Event |  |  | Include | Wildlife | 145 | 2022-03-20 | 725 | keep | 0 | Mar | 2022 | 0.00049379 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-20 10:17 | 2022-03-20 10:18 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22032000015 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-20 | 870 | keep | 0 | Mar | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-03-20 10:34 | 2022-03-20 11:29 | 870 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE SECCIONALIZO TRAMO PARA RETIRAR ENREDADERA Y CERRAR PUENTES CERRADO POR CONTROL | C22032000018 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 55 | 2022-03-20 | 47850 | keep | 0 | Mar | 2022 | 0.03259 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-03-20 10:45 | 2022-03-20 11:45 | 15 | 001:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA PROVISIONAL | R22032000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-03-20 | 900 | keep | 0 | Mar | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-20 11:01 | 2022-03-20 11:03 | 3115 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1710-05 SE CERRO POR SCADA. 40% DE SU CARGA POR 1718-03 | B22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-20 | 6230 | keep | 0 | Mar | 2022 | 0.0042432 | 0.0021216 | Momentary | FALSE | FALSE | Not_TMED_Event | 3115
BAYAMON | 2022-03-20 11:15 | 2022-03-20 11:16 | 271 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 271 | keep | 0 | Mar | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
MAYAGÃœEZ | 2022-03-20 11:16 | 2022-03-20 12:16 | 12 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M22032000044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-20 | 720 | keep | 0 | Mar | 2022 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-03-20 11:25 | 2022-03-20 11:36 | 140 | 000:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22032000008 | New_Event | Bad Weather | Include | Include | Weather | 11 | 2022-03-20 | 1540 | keep | 0 | Mar | 2022 | 0.0010489 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2022-03-20 11:29 | 2022-03-20 14:53 | 102 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO ENREDADERA Y SE DEJO PUENTES ABIERTOS PARA SER TRABAJADOS MAÃ‘ANA CERRARON MACHETE DEL N/O | C22032000018 | Partial_restoration | Wire Down | Include | Include | Equipment | 204 | 2022-03-20 | 20808 | keep | 0 | Mar | 2022 | 0.014172 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-20 11:46 | 2022-03-20 11:47 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1206-03 LLEVA 1204-05 | S22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 10211 | keep | 0 | Mar | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-03-20 11:46 | 2022-03-20 11:47 | 3800 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE 1206-03 LLEVA 1204-05 | S22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 3800 | keep | 0 | Mar | 2022 | 0.0025882 | 0.0025882 | Momentary | FALSE | FALSE | Not_TMED_Event | 3800
BAYAMON | 2022-03-20 11:50 | 2022-03-20 16:48 | 15 | 004:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | B22032000013 | New_Event |  |  | Include | Wildlife | 298 | 2022-03-20 | 4470 | keep | 0 | Mar | 2022 | 0.0030445 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-20 11:55 | 2022-03-20 12:45 | 17 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SEC | S22032000072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-03-20 | 850 | keep | 0 | Mar | 2022 | 0.00057893 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
FAJARDO | 2022-03-20 11:55 | 2022-03-20 12:56 | 15 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R22031900346 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-03-20 | 915 | keep | 0 | Mar | 2022 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-20 11:55 | 2022-03-20 17:22 | 6 | 005:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22032000024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2022-03-20 | 1962 | keep | 0 | Mar | 2022 | 0.0013363 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-20 11:59 | 2022-03-20 16:37 | 130 | 004:38 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-1C SE DIO SERVICIO 3 TRANSFORMADOR. AVERIA T-80 A T-79 NUEVA, AVERIA VIEJA SU-5 A T-72 SE QUEDAN FUERA 8 TRANSFORMADORES | B22032000014 | New_Event | UG Cable Fault | Include | Include | Equipment | 278 | 2022-03-20 | 36140 | keep | 0 | Mar | 2022 | 0.024615 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
HUMACAO | 2022-03-20 12:12 | 2022-03-20 15:06 | 6 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22032000026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2022-03-20 | 1044 | keep | 0 | Mar | 2022 | 0.00071106 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-20 12:33 | 2022-03-20 17:35 | 30 | 005:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22032000052 | New_Event | Bad Weather | Include | Include | Weather | 302 | 2022-03-20 | 9060 | keep | 0 | Mar | 2022 | 0.0061707 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-03-20 12:45 | 2022-03-20 15:15 | 15 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22032000035 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2022-03-20 | 2250 | keep | 0 | Mar | 2022 | 0.0015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-20 12:49 | 2022-03-20 23:07 | 20 | 010:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2022-03-20 | 12360 | keep | 0 | Mar | 2022 | 0.0084183 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-20 13:00 | 2022-03-20 19:10 | 60 | 006:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22032000056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2022-03-20 | 22200 | keep | 0 | Mar | 2022 | 0.01512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-20 13:13 | 2022-03-20 21:04 | 30 | 007:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22032000063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2022-03-20 | 14130 | keep | 0 | Mar | 2022 | 0.0096239 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-20 13:16 | 2022-03-20 14:30 | 1 | 001:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22032000038 | New_Event | Wire Down | Include | Include | Equipment | 74 | 2022-03-20 | 74 | keep | 0 | Mar | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-20 13:20 | 2022-03-20 15:00 | 7 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR PEDESTAL Y REPARAR SECUNDARIA | C22031800070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-03-20 | 700 | keep | 0 | Mar | 2022 | 0.00047677 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-20 13:31 | 2022-03-20 13:32 | 1145 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 1145 | keep | 0 | Mar | 2022 | 0.00077985 | 0.00077985 | Momentary | FALSE | FALSE | Not_TMED_Event | 1145
BAYAMON | 2022-03-20 13:46 | 2022-03-21 09:13 | 100 | 019:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22032000131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1167 | 2022-03-20 | 116700 | keep | 0 | Mar | 2022 | 0.079484 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-20 13:49 | 2022-03-20 17:24 | 90 | 003:35 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 50 EN C/L 1 X 40 EN RISER | S22032000132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-03-20 | 19350 | keep | 0 | Mar | 2022 | 0.013179 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-03-20 13:55 | 2022-03-20 17:10 | 25 | 003:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22032000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-03-20 | 4875 | keep | 0 | Mar | 2022 | 0.0033203 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-03-20 13:56 | 2022-03-20 13:57 | 351 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S22032000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 351 | keep | 0 | Mar | 2022 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
CAGUAS | 2022-03-20 14:03 | 2022-03-20 14:04 | 1271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22032000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 1271 | keep | 0 | Mar | 2022 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
GUAYAMA | 2022-03-20 14:19 | 2022-03-20 15:49 | 18 | 001:30 | P | DESGANCHE | 1 X 40 Y 1 X 50 DIFERENTES CORTES DE LINEA POR DESGANCHE | P22032000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-03-20 | 1620 | keep | 0 | Mar | 2022 | 0.0011034 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-03-20 14:53 | 2022-03-20 15:00 | 17 | 000:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO ENREDADERA Y SE DEJO PUENTES ABIERTOS PARA SER TRABAJADOS MAÃ‘ANA CERRARON MACHETE DEL N/O | C22032000018 | Partial_restoration | Wire Down | Include | Include | Equipment | 7 | 2022-03-20 | 119 | keep | 0 | Mar | 2022 | 8.105e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-20 15:01 | 2022-03-20 18:23 | 12 | 003:22 | P | DESGANCHE | 1 X 50 EN AEREO PROVISIONAL SE REALIZO DESGANCHE | B22032000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-03-20 | 2424 | keep | 0 | Mar | 2022 | 0.001651 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-20 15:09 | 2022-03-20 17:01 | 60 | 001:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA ASILADOR PARTIDO | R22032000032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2022-03-20 | 6720 | keep | 0 | Mar | 2022 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-03-20 15:28 | 2022-03-20 18:23 | 30 | 002:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22032000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-03-20 | 5250 | keep | 0 | Mar | 2022 | 0.0035758 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-20 15:38 | 2022-03-20 15:39 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22032000044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-20 | 1227 | keep | 0 | Mar | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-03-20 15:39 | 2022-03-20 22:41 | 7 | 007:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | A22032000043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 422 | 2022-03-20 | 2954 | keep | 0 | Mar | 2022 | 0.002012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-03-20 15:40 | 2022-03-20 15:55 | 4 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22032000042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-03-20 | 60 | keep | 0 | Mar | 2022 | 4.0866e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-03-20 15:43 | 2022-03-21 09:18 | 1 | 017:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN BANCO DE XMR NO HAY DESPEJE SUFICIENTE ENTRE EL BAJANTE PRIMARIO Y EL PERNO DE LA CRUCETA | C22032000033 | New_Event | Wire Down | Include | Include | Equipment | 1055 | 2022-03-20 | 1055 | keep | 0 | Mar | 2022 | 0.00071856 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-20 15:45 | 2022-03-20 19:35 | 10 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A22032000045 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2022-03-20 | 2300 | keep | 0 | Mar | 2022 | 0.0015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-20 16:00 | 2022-03-20 21:50 | 35 | 005:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA IGUANA CRUZO FASES | M22032000080 | New_Event |  |  | Include | Wildlife | 350 | 2022-03-20 | 12250 | keep | 0 | Mar | 2022 | 0.0083434 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-03-20 16:03 | 2022-03-20 17:45 | 3 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | P22032000022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2022-03-20 | 306 | keep | 0 | Mar | 2022 | 0.00020842 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-03-20 16:27 | 2022-03-20 18:10 | 40 | 001:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22032000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-03-20 | 4120 | keep | 0 | Mar | 2022 | 0.0028061 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-20 16:37 | 2022-03-21 16:19 | 90 | 023:42 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO GOI BY-220321-01A | B22032000014 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1422 | 2022-03-20 | 127980 | keep | 0 | Mar | 2022 | 0.087167 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 574 | keep | 0 | Mar | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 2493 | keep | 0 | Mar | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 1415 | keep | 0 | Mar | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 1428 | keep | 0 | Mar | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 1036 | keep | 0 | Mar | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 382 | keep | 0 | Mar | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 39 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 39 | keep | 0 | Mar | 2022 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 2366 | keep | 0 | Mar | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-03-20 16:49 | 2022-03-20 16:50 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 1337 | keep | 0 | Mar | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-03-20 16:49 | 2022-03-20 16:50 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22032000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-20 | 709 | keep | 0 | Mar | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
SAN JUAN | 2022-03-20 16:50 | 2022-03-20 20:29 | 48 | 003:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R2203200049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-03-20 | 10512 | keep | 0 | Mar | 2022 | 0.0071597 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2022-03-20 17:06 | 2022-03-20 20:19 | 200 | 003:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y 1 X 100 EN CORTES DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M22032000090 | New_Event | Wire Down | Include | Include | Equipment | 193 | 2022-03-20 | 38600 | keep | 0 | Mar | 2022 | 0.02629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-03-20 17:59 | 2022-03-21 13:44 | 5 | 019:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22032000040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1185 | 2022-03-20 | 5925 | keep | 0 | Mar | 2022 | 0.0040355 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-20 18:44 | 2022-03-21 02:17 | 10 | 007:33 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE NECESITA DESGANCHE | M22032000107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2022-03-20 | 4530 | keep | 0 | Mar | 2022 | 0.0030854 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-20 19:15 | 2022-03-21 02:15 | 170 | 007:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22032000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 420 | 2022-03-20 | 71400 | keep | 0 | Mar | 2022 | 0.04863 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
ARECIBO | 2022-03-20 19:34 | 2022-03-21 08:24 | 1 | 012:50 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | A22032000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 770 | 2022-03-20 | 770 | keep | 0 | Mar | 2022 | 0.00052444 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-20 19:35 | 2022-03-20 19:37 | 1227 | 000:02 | T | ERROR HUMANO | DISPARO DEL INTERRUPTOR RECIERRE EN OFF INFORMO MANUEL BONET QUE LA CAUSA DEL DISPARO FUE POR LINEAS CRUZADAS EN AREA DE TRABAJO | A22032000049 | New_Event | Human Error | Include | Include | Other | 2 | 2022-03-20 | 2454 | keep | 0 | Mar | 2022 | 0.0016714 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2022-03-20 19:37 | 2022-03-20 20:48 | 10 | 001:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A22032000045 | Partial_restoration | Wire Down | Include | Include | Equipment | 71 | 2022-03-20 | 710 | keep | 0 | Mar | 2022 | 0.00048358 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-20 19:40 | 2022-03-20 20:10 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M22032000076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-03-20 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-20 19:51 | 2022-03-21 02:34 | 70 | 006:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 40 A EN SU - 1 Y 1 X 50 EN RISER CRUCE X CULEBRA | C22032000045 | New_Event |  |  | Include | Wildlife | 403 | 2022-03-20 | 28210 | keep | 0 | Mar | 2022 | 0.019214 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-03-20 19:54 | 2022-03-21 09:49 | 4 | 013:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR PORTAFUSIBLE | S22032000145 | New_Event | Cutout Failure | Include | Include | Equipment | 835 | 2022-03-20 | 3340 | keep | 0 | Mar | 2022 | 0.0022749 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-03-20 20:05 | 2022-03-20 20:06 | 400 | 000:01 | P | DESGANCHE | RECIERRE DE INTERRUPTOR 9206-09 LLEVANDO PARTE DEL 9206-08 | B22032000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-20 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
VEGA BAJA | 2022-03-20 20:05 | 2022-03-20 20:06 | 6 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 9206-09 LLEVANDO PARTE DEL 9206-08 | B22032000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-20 | 6 | keep | 0 | Mar | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-03-20 20:06 | 2022-03-20 22:57 | 80 | 002:51 | P | DESGANCHE | 2 X 65 Y 1 X 80 EN C/L SE REALIZO DESGANCHE | B22032000034 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-03-20 | 13680 | keep | 0 | Mar | 2022 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-20 21:09 | 2022-03-21 12:35 | 84 | 015:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN AEREO PROVISIONAL SE REMPLAZO CAJA PRIMARIA | B22032000039 | New_Event | Cutout Failure | Include | Include | Equipment | 926 | 2022-03-20 | 77784 | keep | 0 | Mar | 2022 | 0.052978 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
ARECIBO | 2022-03-20 21:29 | 2022-03-21 10:05 | 4 | 012:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22032000053 | New_Event | Cutout Failure | Include | Include | Equipment | 756 | 2022-03-20 | 3024 | keep | 0 | Mar | 2022 | 0.0020596 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-03-20 22:06 | 2022-03-21 01:12 | 150 | 003:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | A22032000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-03-20 | 27900 | keep | 0 | Mar | 2022 | 0.019003 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-21 00:11 | 2022-03-21 00:12 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVANDO 1336-09 Y 30% DEL 1204-04 | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 1483 | keep | 0 | Mar | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-21 00:11 | 2022-03-21 00:12 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVANDO 1336-09 Y 30% DEL 1204-04 | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 5290 | keep | 0 | Mar | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-21 00:11 | 2022-03-21 00:12 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVANDO 1336-09 Y 30% DEL 1204-04 | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 207 | keep | 0 | Mar | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
HUMACAO | 2022-03-21 02:34 | 2022-03-21 05:18 | 327 | 002:44 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0040 LOCKOUT SE RETIRO GATO MUERTO DE LA PARTE BAJA DEL TRANSFORMADOR. SE ENCONTRO BUSHING SECUNDARIO AVERIADO DEL LA PARTE BAJA DEL INTERRUPTOR DEL 2603-09 SE LIBERO Y SE PASO LA CARGA AL 2603-06. | C22032100001 | New_Event |  |  | Include | Wildlife | 164 | 2022-03-21 | 53628 | keep | 0 | Mar | 2022 | 0.036526 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-03-21 02:34 | 2022-03-21 05:18 | 5630 | 002:44 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0040 LOCKOUT SE RETIRO GATO MUERTO DE LA PARTE BAJA DEL TRANSFORMADOR. SE ENCONTRO BUSHING SECUNDARIO AVERIADO DEL LA PARTE BAJA DEL INTERRUPTOR DEL 2603-09 SE LIBERO Y SE PASO LA CARGA AL 2603-06. | C22032100001 | New_Event |  |  | Include | Wildlife | 164 | 2022-03-21 | 923320 | keep | 0 | Mar | 2022 | 0.62887 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-03-21 02:34 | 2022-03-21 05:18 | 2126 | 002:44 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0040 LOCKOUT SE RETIRO GATO MUERTO DE LA PARTE BAJA DEL TRANSFORMADOR. SE ENCONTRO BUSHING SECUNDARIO AVERIADO DEL LA PARTE BAJA DEL INTERRUPTOR DEL 2603-09 SE LIBERO Y SE PASO LA CARGA AL 2603-06. | C22032100001 | Additional_clients |  |  | Include | Wildlife | 164 | 2022-03-21 | 348664 | keep | 0 | Mar | 2022 | 0.23747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-21 02:34 | 2022-03-21 05:17 | 551 | 002:43 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0040 LOCKOUT SE RETIRO GATO MUERTO DE LA PARTE BAJA DEL TRANSFORMADOR. SE ENCONTRO BUSHING SECUNDARIO AVERIADO DEL LA PARTE BAJA DEL INTERRUPTOR DEL 2603-09 SE LIBERO Y SE PASO LA CARGA AL 2603-06. | C22032100001 | New_Event |  |  | Include | Wildlife | 163 | 2022-03-21 | 89813 | keep | 0 | Mar | 2022 | 0.061171 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2022-03-21 03:02 | 2022-03-21 03:03 | 2391 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 2391 | keep | 0 | Mar | 2022 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
MAYAGÃœEZ | 2022-03-21 03:40 | 2022-03-21 07:00 | 100 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22032100001 | New_Event |  |  | Include | Wildlife | 200 | 2022-03-21 | 20000 | keep | 0 | Mar | 2022 | 0.013622 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-21 05:18 | 2022-03-21 11:27 | 70 | 006:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 40 A EN SU - 1 Y 1 X 50 EN RISER CRUCE X CULEBRA | C22032000045 | Partial_restoration |  |  | Include | Wildlife | 369 | 2022-03-21 | 25830 | keep | 0 | Mar | 2022 | 0.017593 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-21 06:08 | 2022-03-21 06:09 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
FAJARDO | 2022-03-21 07:04 | 2022-03-21 10:23 | 104 | 003:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22032100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-03-21 | 20696 | keep | 0 | Mar | 2022 | 0.014096 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
YAUCO | 2022-03-21 07:13 | 2022-03-21 08:27 | 4 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO EN PM T-20 PARA REMPLAZAR BARRA EN PEDESTAL SECUNDARIO | P22032100013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2022-03-21 | 296 | keep | 0 | Mar | 2022 | 0.0002016 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-03-21 07:17 | 2022-03-21 08:48 | 10 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y TOMAS | B22032000033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2022-03-21 | 910 | keep | 0 | Mar | 2022 | 0.0006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-21 07:22 | 2022-03-21 16:28 | 35 | 009:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE LINEA A CAJA EN CORTE DE LINEA | B22032100003 | New_Event | Wire Down | Include | Include | Equipment | 546 | 2022-03-21 | 19110 | keep | 0 | Mar | 2022 | 0.013016 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-03-21 07:23 | 2022-03-21 09:21 | 3 | 001:58 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | R22032100002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 118 | 2022-03-21 | 354 | keep | 0 | Mar | 2022 | 0.00024111 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-03-21 07:32 | 2022-03-21 08:47 | 50 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22032100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-03-21 | 3750 | keep | 0 | Mar | 2022 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-21 07:45 | 2022-03-21 11:49 | 42 | 004:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO CORTE DE LINEA | R22032100003 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2022-03-21 | 10248 | keep | 0 | Mar | 2022 | 0.0069799 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2022-03-21 08:05 | 2022-03-21 08:06 | 828 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 60% POR 1206-4 | S22032100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 828 | keep | 0 | Mar | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-03-21 08:05 | 2022-03-21 08:06 | 1977 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 40% POR 1206-4 | S22032100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 1977 | keep | 0 | Mar | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-03-21 08:05 | 2022-03-21 08:06 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA CARGA 20% 1303-02 LLEVA 40% DEL 1204-4 Y 60% 1204-3 | S22032100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 1799 | keep | 0 | Mar | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-03-21 08:05 | 2022-03-21 08:06 | 487 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 20% POR 1206-4 | S22032100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 487 | keep | 0 | Mar | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
BAYAMON | 2022-03-21 08:13 | 2022-03-21 13:13 | 10 | 005:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO Y SE REPARO SECUNDARIA PARTIDA | S22032100009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 300 | 2022-03-21 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-03-21 08:21 | 2022-03-21 09:19 | 1 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P22032100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-03-21 | 58 | keep | 0 | Mar | 2022 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-21 08:27 | 2022-03-21 16:48 | 100 | 008:21 | P | PARARRAYOS DEFECTUOSO | 1 X 30 Y 1 X 65 EN CORTES DE LINEA Y SE REMPLAZO PARARRAYO | B22032100010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 501 | 2022-03-21 | 50100 | keep | 0 | Mar | 2022 | 0.034123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-21 08:29 | 2022-03-21 13:06 | 80 | 004:37 | P | DESGANCHE | SE REPARO BAJANTE DE LINEA A CAJA Y DESGANCHE | S22032100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2022-03-21 | 22160 | keep | 0 | Mar | 2022 | 0.015093 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-21 08:29 | 2022-03-21 11:17 | 15 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22032100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-03-21 | 2520 | keep | 0 | Mar | 2022 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-21 08:36 | 2022-03-21 14:46 | 277 | 006:10 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER AVERIA NUEVA DE T 13 @ T 12 Y AVERIA VIEJA DE T 11 @ T10 14 CLTES FUERA | B22032100013 | New_Event | UG Cable Fault | Include | Include | Equipment | 370 | 2022-03-21 | 102490 | keep | 0 | Mar | 2022 | 0.069805 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
SAN JUAN | 2022-03-21 08:53 | 2022-03-21 08:57 | 922 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO FUERA SE PROBO QUEDO EN SERVICIO SU CARGA POR 1401-8 | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-21 | 3688 | keep | 0 | Mar | 2022 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-21 08:53 | 2022-03-21 08:57 | 135 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO FUERA SE PROBO QUEDO EN SERVICIO LLEVA 1346-5 | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-21 | 540 | keep | 0 | Mar | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2022-03-21 08:53 | 2022-03-21 08:54 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22032100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 990 | keep | 0 | Mar | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2022-03-21 08:57 | 2022-03-21 15:10 | 20 | 006:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES PARTIDOS | A22032100011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 373 | 2022-03-21 | 7460 | keep | 0 | Mar | 2022 | 0.005081 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-21 09:02 | 2022-03-21 09:06 | 922 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO FUERA SE PROBO QUEDO EN SERVICIO SU CARGA POR 1401-8 | S22032100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-21 | 3688 | keep | 0 | Mar | 2022 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-21 09:02 | 2022-03-21 09:06 | 135 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO FUERA SE PROBO QUEDO EN SERVICIO LLEVA 1346-5 | S22032100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-21 | 540 | keep | 0 | Mar | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-03-21 09:11 | 2022-03-21 12:08 | 200 | 002:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA CRUCE POR CHANGO | R22032100008 | New_Event |  |  | Include | Wildlife | 177 | 2022-03-21 | 35400 | keep | 0 | Mar | 2022 | 0.024111 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-21 09:26 | 2022-03-21 19:35 | 1 | 010:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CAJA A LINEA Y SE REALIZO DESGANCHE | B22032100021 | New_Event | Wire Down | Include | Include | Equipment | 609 | 2022-03-21 | 609 | keep | 0 | Mar | 2022 | 0.00041479 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-21 09:26 | 2022-03-22 22:06 | 1 | 036:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22032100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2200 | 2022-03-21 | 2200 | keep | 0 | Mar | 2022 | 0.0014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-21 09:32 | 2022-03-21 15:12 | 15 | 005:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | S22032100115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 340 | 2022-03-21 | 5100 | keep | 0 | Mar | 2022 | 0.0034736 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-03-21 09:45 | 2022-03-21 12:33 | 3 | 002:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A22032100012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 168 | 2022-03-21 | 504 | keep | 0 | Mar | 2022 | 0.00034327 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-03-21 09:49 | 2022-03-21 09:51 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 SE PROBO QUEDO EN SERVICIO | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-21 | 450 | keep | 0 | Mar | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-21 09:49 | 2022-03-21 09:51 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1303-4 SE PROBO QUEDO EN SERVICIO | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-21 | 1740 | keep | 0 | Mar | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-03-21 10:01 | 2022-03-21 14:11 | 170 | 004:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO MACHETES PARA CERRAR PUENTE Y NORMALIZO CARGAS | C22032100123 | New_Event | Wire Down | Include | Include | Equipment | 250 | 2022-03-21 | 42500 | keep | 0 | Mar | 2022 | 0.028947 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
BAYAMON | 2022-03-21 10:11 | 2022-03-21 12:25 | 15 | 002:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES EN BAJANTE SECUNDARIO | B22032100000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 134 | 2022-03-21 | 2010 | keep | 0 | Mar | 2022 | 0.001369 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-21 10:18 | 2022-03-21 10:45 | 100 | 000:27 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DEL CONVERTIDOR PARA REPARAR BUSHINGS AVERIADOS EN EL CONVERTIDOR. AUTORIZADO POR ING. LUIS FENEQUE. SE CERRO N/O PARA ENERGIZAR LOS CLIENTES. | M22032100012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 27 | 2022-03-21 | 2700 | keep | 0 | Mar | 2022 | 0.001839 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-21 10:35 | 2022-03-21 13:28 | 5 | 002:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | R22032100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 173 | 2022-03-21 | 865 | keep | 0 | Mar | 2022 | 0.00058915 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-21 10:40 | 2022-03-21 22:27 | 10 | 011:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO XMR Y SE CERRO BAJANTE DE LINEA A CAJA DE XMR (NO FUNDIO FUSIBLE) | S22032100031 | New_Event | Wire Down | Include | Include | Equipment | 707 | 2022-03-21 | 7070 | keep | 0 | Mar | 2022 | 0.0048153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 296 | 002:05 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV 1335-05 LLEVA 40% POR 1335-05 | S22032100033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 37000 | keep | 0 | Mar | 2022 | 0.025201 | 0.0002016 | Sustained | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 602 | 002:05 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV SE ENCONTRO NO TENIA TIERRAS LA UNIT SU CARGA POR 1335-4 | S22032100033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 75250 | keep | 0 | Mar | 2022 | 0.051252 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 1208 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV SE ENCONTRO NO TENIA TIERRAS LA UNIT | S22032100033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 151000 | keep | 0 | Mar | 2022 | 0.10285 | 0.00082276 | Sustained | FALSE | FALSE | Not_TMED_Event | 1208
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 375 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV SE ENCONTRO NO TENIA TIERRAS LA UNIT | S22032100033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 46875 | keep | 0 | Mar | 2022 | 0.031926 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 608 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV SE ENCONTRO NO TENIA TIERRAS LA UNIT | S22032100033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 76000 | keep | 0 | Mar | 2022 | 0.051763 | 0.00041411 | Sustained | FALSE | FALSE | Not_TMED_Event | 608
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 602 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV SE ENCONTRO NO TENIA TIERRAS LA UNIT | S22032100033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 75250 | keep | 0 | Mar | 2022 | 0.051252 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 13:03 | 314 | 002:05 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV SE ENCONTRO NO TENIA TIERRAS LA UNIT | S22032100033 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-03-21 | 39250 | keep | 0 | Mar | 2022 | 0.026733 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 11:07 | 614 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV | S22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-03-21 | 5526 | keep | 0 | Mar | 2022 | 0.0037637 | 0.00041819 | Sustained | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 11:07 | 770 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV | S22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-03-21 | 6930 | keep | 0 | Mar | 2022 | 0.00472 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 11:07 | 1271 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 DE SABANA LLANA @ VILLA PRADES Y BARRA VILLA PRADES 38KV | S22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-03-21 | 11439 | keep | 0 | Mar | 2022 | 0.0077911 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2022-03-21 10:58 | 2022-03-21 11:07 | 247 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE 38 KV DE SABANA LLANA A VILLA PRADES | S22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-03-21 | 2223 | keep | 0 | Mar | 2022 | 0.0015141 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
FAJARDO | 2022-03-21 11:15 | 2022-03-21 13:11 | 52 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA SE ENDEREZO POSTE PRIMARIO IMPACTADO POR CAMION | R22032100019 | New_Event |  |  | Include | Wildlife | 116 | 2022-03-21 | 6032 | keep | 0 | Mar | 2022 | 0.0041084 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2022-03-21 11:20 | 2022-03-21 11:21 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 1702 | keep | 0 | Mar | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2022-03-21 11:29 | 2022-03-21 16:36 | 1 | 005:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN BANCO XMR | B22032100036 | New_Event | Cutout Failure | Include | Include | Equipment | 307 | 2022-03-21 | 307 | keep | 0 | Mar | 2022 | 0.0002091 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-21 11:42 | 2022-03-21 16:23 | 40 | 004:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22032100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 281 | 2022-03-21 | 11240 | keep | 0 | Mar | 2022 | 0.0076555 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-03-21 11:48 | 2022-03-21 14:47 | 1 | 002:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES | R22032100021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 179 | 2022-03-21 | 179 | keep | 0 | Mar | 2022 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-21 12:13 | 2022-03-21 20:26 | 30 | 008:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2022-03-21 | 14790 | keep | 0 | Mar | 2022 | 0.010073 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-21 12:19 | 2022-03-21 13:34 | 150 | 001:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-03-21 | 11250 | keep | 0 | Mar | 2022 | 0.0076623 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-21 12:27 | 2022-03-21 12:38 | 353 | 000:11 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | S22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-03-21 | 3883 | keep | 0 | Mar | 2022 | 0.0026447 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2022-03-21 12:38 | 2022-03-21 23:58 | 40 | 011:20 | P | ESTRUCTURA AVERIADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO X METAL 45' SE REPARO NEUTRAL PRIMARIO Y SE RETIRO TENSOR | M22032100033 | New_Event | Defective Pole | Include | Include | Equipment | 680 | 2022-03-21 | 27200 | keep | 0 | Mar | 2022 | 0.018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-21 12:41 | 2022-03-21 12:42 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 3941 | keep | 0 | Mar | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2022-03-21 12:45 | 2022-03-21 17:00 | 300 | 004:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-03-21 | 76500 | keep | 0 | Mar | 2022 | 0.052104 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-03-21 12:51 | 2022-03-21 13:22 | 17 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | AE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B22032100052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2022-03-21 | 527 | keep | 0 | Mar | 2022 | 0.00035894 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-03-21 13:10 | 2022-03-22 10:20 | 1 | 021:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN CORTE DE LINEA SE SEPARO BAJANTE PRIMARIO EN CONTACTO CON ESTRUCTURA | A22032100036 | New_Event |  |  | Include | Wildlife | 1270 | 2022-03-21 | 1270 | keep | 0 | Mar | 2022 | 0.00086499 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-21 13:16 | 2022-03-21 14:38 | 36 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN PROVISIONAL SE INSTALO TIGUERO PARA EVITAR CUCE DE LINEAS A BRAZO DE FOCO | R22032100025 | New_Event |  |  | Include | Wildlife | 82 | 2022-03-21 | 2952 | keep | 0 | Mar | 2022 | 0.0020106 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
FAJARDO | 2022-03-21 13:21 | 2022-03-21 16:43 | 2286 | 003:22 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON AISLADORES Y SE CERRO POR SCADA | R22032100026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 202 | 2022-03-21 | 461772 | keep | 0 | Mar | 2022 | 0.31451 | 0.001557 | Sustained | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-03-21 13:30 | 2022-03-21 14:33 | 6 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | R22032100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-03-21 | 378 | keep | 0 | Mar | 2022 | 0.00025745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-21 13:44 | 2022-03-21 14:30 | 29 | 000:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA | B22032100056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 46 | 2022-03-21 | 1334 | keep | 0 | Mar | 2022 | 0.00090858 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
VEGA BAJA | 2022-03-21 14:01 | 2022-03-21 18:04 | 20 | 004:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22032100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2022-03-21 | 4860 | keep | 0 | Mar | 2022 | 0.0033101 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-21 14:25 | 2022-03-21 16:02 | 15 | 001:37 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR Y 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-03-21 | 1455 | keep | 0 | Mar | 2022 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-03-21 14:28 | 2022-03-21 17:27 | 10 | 002:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22032100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-03-21 | 1790 | keep | 0 | Mar | 2022 | 0.0012192 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-03-21 14:37 | 2022-03-21 16:24 | 20 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P22032100041 | New_Event |  |  | Include | Wildlife | 107 | 2022-03-21 | 2140 | keep | 0 | Mar | 2022 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-21 14:46 | 2022-03-22 12:00 | 14 | 021:14 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO PARA ENERGIZAR T-11 & T-12 | B22032100072 | New_Event | UG Cable Fault | Include | Include | Equipment | 1274 | 2022-03-21 | 17836 | keep | 0 | Mar | 2022 | 0.012148 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-03-21 14:52 | 2022-03-21 22:45 | 150 | 007:53 | P | DESGANCHE | 1 X 10 EN XMR, 2 X 65 EN C/L Y 2 X 100 EN C/L SE DESGANCHO Y SE RETIRO GLOBO | S22032100124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2022-03-21 | 70950 | keep | 0 | Mar | 2022 | 0.048324 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-03-21 15:16 | 2022-03-21 16:18 | 536 | 001:02 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REMOVIO ENREDADERA DE LINEA CON BARETA SJ-220321-02 40% DE LA CARGA POR EL 1204-01 BRAKER SPARE | S22032100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-03-21 | 33232 | keep | 0 | Mar | 2022 | 0.022634 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
YAUCO | 2022-03-21 15:21 | 2022-03-21 16:57 | 2 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRAANSFORMADOR PARA REPARAR 2 TOMAS CRUZADAS | P22032100043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2022-03-21 | 192 | keep | 0 | Mar | 2022 | 0.00013077 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-21 15:26 | 2022-03-21 22:56 | 20 | 007:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032100054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 450 | 2022-03-21 | 9000 | keep | 0 | Mar | 2022 | 0.0061299 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-21 15:33 | 2022-03-21 19:35 | 100 | 004:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA | S22032100132 | New_Event | Wire Down | Include | Include | Equipment | 242 | 2022-03-21 | 24200 | keep | 0 | Mar | 2022 | 0.016483 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-03-21 15:38 | 2022-03-22 08:25 | 10 | 016:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS SULFATADOS | P22032100047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1007 | 2022-03-21 | 10070 | keep | 0 | Mar | 2022 | 0.0068586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-03-21 16:11 | 2022-03-21 19:55 | 6 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | A22032100047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2022-03-21 | 1344 | keep | 0 | Mar | 2022 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-21 16:13 | 2022-03-21 16:14 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22032100072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-21 | 6285 | keep | 0 | Mar | 2022 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
SAN JUAN | 2022-03-21 16:14 | 2022-03-21 19:55 | 13 | 003:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR SECUNDARIA | S22032100149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 221 | 2022-03-21 | 2873 | keep | 0 | Mar | 2022 | 0.0019568 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2022-03-21 16:22 | 2022-03-21 17:02 | 1 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO CAUSA | P22032100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-03-21 | 40 | keep | 0 | Mar | 2022 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-21 16:28 | 2022-03-21 16:29 | 3431 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22032100000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-21 | 3431 | keep | 0 | Mar | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-03-21 16:29 | 2022-03-21 19:14 | 180 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 100 EN CORTES DE LINEA AVE CRUZO FASES | A22032100049 | 1st_after_momentary |  |  | Include | Wildlife | 165 | 2022-03-21 | 29700 | keep | 0 | Mar | 2022 | 0.020229 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2022-03-21 16:29 | 2022-03-21 17:55 | 50 | 001:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22032100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-03-21 | 4300 | keep | 0 | Mar | 2022 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-03-21 16:36 | 2022-03-21 17:50 | 5 | 001:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN XMR SE REPARO BAJANTE PRIMARIO | R22032100092 | New_Event | Wire Down | Include | Include | Equipment | 74 | 2022-03-21 | 370 | keep | 0 | Mar | 2022 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-21 16:37 | 2022-03-21 20:31 | 85 | 003:54 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO, REMPLAZO CAJA QUEMADA Y RETEZO LINEA | C22032100161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-03-21 | 19890 | keep | 0 | Mar | 2022 | 0.013547 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2022-03-21 17:00 | 2022-03-21 17:20 | 20 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO | A22032100040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-03-21 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-21 17:04 | 2022-03-21 18:29 | 70 | 001:25 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22032100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-03-21 | 5950 | keep | 0 | Mar | 2022 | 0.0040525 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-03-21 17:18 | 2022-03-21 20:19 | 25 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE PALOMA | R22032100101 | New_Event |  |  | Include | Wildlife | 181 | 2022-03-21 | 4525 | keep | 0 | Mar | 2022 | 0.003082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-03-21 17:28 | 2022-03-21 18:50 | 12 | 001:22 | P | FUEGO | 1 X 15 EN TRANSFORMADOR CASA SE QUEMO Y CRUZO FASES | A22032100054 | New_Event | Fire | Include | Include | Public | 82 | 2022-03-21 | 984 | keep | 0 | Mar | 2022 | 0.0006702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-21 17:51 | 2022-03-22 07:04 | 1 | 013:13 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO DE TRONCAL 1717-05 @ FASE: A DEL SU-3 | B22032300009 | New_Event | UG Cable Fault | Include | Include | Equipment | 793 | 2022-03-21 | 793 | keep | 0 | Mar | 2022 | 0.00054011 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-21 17:51 | 2022-03-21 17:59 | 426 | 000:08 | T | FUEGO | SE ABRE INTERRUPTOR POR FUEGO EN POSTES LINEA SE PEGO AL POSTE Y SE PRENDIO | P22032100062 | New_Event | Fire | Include | Include | Public | 8 | 2022-03-21 | 3408 | keep | 0 | Mar | 2022 | 0.0023212 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
YAUCO | 2022-03-21 18:01 | 2022-03-21 19:19 | 50 | 001:18 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22032100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-03-21 | 3900 | keep | 0 | Mar | 2022 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-21 18:44 | 2022-03-21 21:35 | 50 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN AEREO PROVISIONAL | S22032100171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-03-21 | 8550 | keep | 0 | Mar | 2022 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-21 18:57 | 2022-03-21 21:00 | 12 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22032100082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-03-21 | 1476 | keep | 0 | Mar | 2022 | 0.0010053 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-21 19:13 | 2022-03-22 06:35 | 7 | 011:22 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | C22032100199 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 682 | 2022-03-21 | 4774 | keep | 0 | Mar | 2022 | 0.0032515 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-03-21 19:15 | 2022-03-22 01:30 | 100 | 006:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2022-03-21 | 37500 | keep | 0 | Mar | 2022 | 0.025541 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-21 19:25 | 2022-03-21 21:52 | 25 | 002:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S22032100175 | New_Event | Secondary Wire Down | Include | Include | Equipment | 147 | 2022-03-21 | 3675 | keep | 0 | Mar | 2022 | 0.002503 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-03-21 20:56 | 2022-03-22 02:17 | 10 | 005:21 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22032100136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-03-21 | 3210 | keep | 0 | Mar | 2022 | 0.0021863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-21 21:04 | 2022-03-22 19:26 | 14 | 022:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR SECUNDARIA AVERIADA | S22032100182 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1342 | 2022-03-21 | 18788 | keep | 0 | Mar | 2022 | 0.012796 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2022-03-21 21:11 | 2022-03-22 10:03 | 11 | 012:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | R22032100115 | New_Event | Wire Down | Include | Include | Equipment | 772 | 2022-03-21 | 8492 | keep | 0 | Mar | 2022 | 0.0057839 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-03-21 21:36 | 2022-03-22 05:20 | 500 | 007:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO | C22032100213 | New_Event | Cutout Failure | Include | Include | Equipment | 464 | 2022-03-21 | 232000 | keep | 0 | Mar | 2022 | 0.15801 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2022-03-21 22:06 | 2022-03-22 03:50 | 31 | 005:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22032100161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2022-03-21 | 10664 | keep | 0 | Mar | 2022 | 0.0072632 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2022-03-22 00:10 | 2022-03-22 10:27 | 30 | 010:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CORTE DE LINEA PARA REMPLAZAR CAJA TRAS PATIO | S22032200001 | New_Event | Cutout Failure | Include | Include | Equipment | 617 | 2022-03-22 | 18510 | keep | 0 | Mar | 2022 | 0.012607 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-03-22 01:16 | 2022-03-22 07:50 | 150 | 006:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | P22032200003 | New_Event | Bad Weather | Include | Include | Weather | 394 | 2022-03-22 | 59100 | keep | 0 | Mar | 2022 | 0.040253 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-03-22 03:24 | 2022-03-22 09:41 | 8 | 006:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO PORTAFUSIBLE | R22032200001 | New_Event | Cutout Failure | Include | Include | Equipment | 377 | 2022-03-22 | 3016 | keep | 0 | Mar | 2022 | 0.0020542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-03-22 04:13 | 2022-03-22 07:45 | 50 | 003:32 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LAS LINEAS | M22032200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-03-22 | 10600 | keep | 0 | Mar | 2022 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-22 05:02 | 2022-03-22 05:03 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1859 | keep | 0 | Mar | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-03-22 05:02 | 2022-03-22 05:03 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 7 | keep | 0 | Mar | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-03-22 05:25 | 2022-03-22 05:26 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1894 | keep | 0 | Mar | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
VEGA BAJA | 2022-03-22 05:31 | 2022-03-22 05:32 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22032200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1859 | keep | 0 | Mar | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-03-22 05:31 | 2022-03-22 05:32 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO EL 9207-09 | B22032200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 7 | keep | 0 | Mar | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-22 06:08 | 2022-03-22 11:49 | 66 | 005:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y 1 X 30 EN PROVISIONAL SE REMPLAZO CAJA EN PROVISIONAL | S22032200003 | New_Event | Cutout Failure | Include | Include | Equipment | 341 | 2022-03-22 | 22506 | keep | 0 | Mar | 2022 | 0.015329 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CAGUAS | 2022-03-22 06:26 | 2022-03-22 17:46 | 7 | 011:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN BANCO DE TRANSFORMADORE MAL TIEMPO | C22032200002 | New_Event | Bad Weather | Include | Include | Weather | 680 | 2022-03-22 | 4760 | keep | 0 | Mar | 2022 | 0.003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-03-22 06:48 | 2022-03-22 11:44 | 5 | 004:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | A22032200002 | New_Event | Wire Down | Include | Include | Equipment | 296 | 2022-03-22 | 1480 | keep | 0 | Mar | 2022 | 0.001008 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-03-22 07:01 | 2022-03-22 14:25 | 35 | 007:24 | P | DESGANCHE | 1 X 50 Y 1 X 20 EN CORTES DE LINEA | R22032200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2022-03-22 | 15540 | keep | 0 | Mar | 2022 | 0.010584 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-03-22 07:03 | 2022-03-22 15:33 | 12 | 008:30 | P | DESGANCHE | 1 X 30 EN C/L Y 1 X 10 EN XMR DESGANCHO Y LEVANTO CONDUCTOR | R22032200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 510 | 2022-03-22 | 6120 | keep | 0 | Mar | 2022 | 0.0041683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-22 07:04 | 2022-03-22 12:00 | 40 | 004:56 | P | CABLE SOTERRADO AVERIADO | SE ABRIO PARA CONTRUIR PROVISIONAL AEREO DE TRONCAL 1717-05 @ FASE: A DEL SU-3 | B22032300009 | New_Event | UG Cable Fault | Include | Include | Equipment | 296 | 2022-03-22 | 11840 | keep | 0 | Mar | 2022 | 0.0080642 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-22 07:05 | 2022-03-22 09:58 | 1 | 002:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | B22032200004 | New_Event |  |  | Include | Wildlife | 173 | 2022-03-22 | 173 | keep | 0 | Mar | 2022 | 0.00011783 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-22 07:17 | 2022-03-22 16:49 | 337 | 009:32 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 3 X 100 EN RISER SE REPARO TERMINACION EN SU-7 | C22032200004 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 572 | 2022-03-22 | 192764 | keep | 0 | Mar | 2022 | 0.13129 | 0.00022953 | Sustained | FALSE | FALSE | Not_TMED_Event | 337
CAGUAS | 2022-03-22 07:20 | 2022-03-22 16:44 | 181 | 009:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22032200006 | New_Event | Bad Weather | Include | Include | Weather | 564 | 2022-03-22 | 102084 | keep | 0 | Mar | 2022 | 0.069529 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
MAYAGÃœEZ | 2022-03-22 07:27 | 2022-03-22 11:00 | 1 | 003:33 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M22032200036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2022-03-22 | 213 | keep | 0 | Mar | 2022 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-22 07:38 | 2022-03-22 08:33 | 50 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | B22032200010 | New_Event |  |  | Include | Wildlife | 55 | 2022-03-22 | 2750 | keep | 0 | Mar | 2022 | 0.001873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-22 07:42 | 2022-03-22 07:43 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO PARTE POR 1620-2 | S22032200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-22 07:42 | 2022-03-22 07:43 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA PARTE DEL 1206-3 SE PROBO QUEDO EN SERVICIO | S22032200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 3718 | keep | 0 | Mar | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-03-22 07:43 | 2022-03-22 09:44 | 310 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22032200012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-03-22 | 37510 | keep | 0 | Mar | 2022 | 0.025548 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
SAN JUAN | 2022-03-22 07:58 | 2022-03-22 14:08 | 25 | 006:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22032200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 370 | 2022-03-22 | 9250 | keep | 0 | Mar | 2022 | 0.0063001 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-22 07:58 | 2022-03-22 09:55 | 40 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S22032200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2022-03-22 | 4680 | keep | 0 | Mar | 2022 | 0.0031875 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-22 08:20 | 2022-03-22 14:24 | 100 | 006:04 | P | DESGANCHE | 1 X 80 EN C/L | R22032200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2022-03-22 | 36400 | keep | 0 | Mar | 2022 | 0.024792 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-22 08:20 | 2022-03-22 09:00 | 6 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C22032100190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-22 | 240 | keep | 0 | Mar | 2022 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-22 08:22 | 2022-03-22 12:32 | 43 | 004:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA, 2 AISLADORES Y MACHETE QUEMADO | R2203R220322 | New_Event | Cutout Failure | Include | Include | Equipment | 250 | 2022-03-22 | 10750 | keep | 0 | Mar | 2022 | 0.0073218 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
MAYAGÃœEZ | 2022-03-22 09:12 | 2022-03-22 12:40 | 25 | 003:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | M22032200057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 208 | 2022-03-22 | 5200 | keep | 0 | Mar | 2022 | 0.0035417 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-03-22 09:15 | 2022-03-22 15:09 | 400 | 005:54 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE ARBOL DE FLAMBOYAN QUEMANDO | M22032200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2022-03-22 | 141600 | keep | 0 | Mar | 2022 | 0.096443 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-03-22 09:23 | 2022-03-22 12:09 | 80 | 002:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A22032200008 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2022-03-22 | 13280 | keep | 0 | Mar | 2022 | 0.0090449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-03-22 09:24 | 2022-03-22 11:05 | 7 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22032200024 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2022-03-22 | 707 | keep | 0 | Mar | 2022 | 0.00048153 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-03-22 09:30 | 2022-03-22 10:10 | 10 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS AVERIADOS | P22032200012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-22 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-22 10:01 | 2022-03-22 11:14 | 40 | 001:13 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE DESGANCHO | S22032200039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-03-22 | 2920 | keep | 0 | Mar | 2022 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-22 10:15 | 2022-03-22 10:17 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF PARTE POR 1620-05 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-22 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-22 10:15 | 2022-03-22 10:17 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA PARTE 1206-3 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-22 | 3230 | keep | 0 | Mar | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
FAJARDO | 2022-03-22 10:16 | 2022-03-22 18:10 | 40 | 007:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN C/ INSTALO PROVICIONAL AEREO TUMBADO POR CAMION | R22032200030 | New_Event |  |  | Include | Wildlife | 474 | 2022-03-22 | 18960 | keep | 0 | Mar | 2022 | 0.012914 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-22 10:20 | 2022-03-22 12:15 | 12 | 001:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25 KVA A 2.4 KV AVERIADO | P22032200015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2022-03-22 | 1380 | keep | 0 | Mar | 2022 | 0.00093991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-03-22 10:26 | 2022-03-22 14:16 | 7 | 003:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | C22032200029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 230 | 2022-03-22 | 1610 | keep | 0 | Mar | 2022 | 0.0010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-03-22 10:27 | 2022-03-22 11:24 | 97 | 000:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CORTE DE LINEA PARA REMPLAZAR CAJA TRAS PATIO | S22032200001 | Additional_clients | Cutout Failure | Include | Include | Equipment | 57 | 2022-03-22 | 5529 | keep | 0 | Mar | 2022 | 0.0037658 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-03-22 10:27 | 2022-03-22 11:58 | 40 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | R22032200032 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2022-03-22 | 3640 | keep | 0 | Mar | 2022 | 0.0024792 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-22 10:39 | 2022-03-22 10:41 | 215 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-22 | 430 | keep | 0 | Mar | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-03-22 10:41 | 2022-03-22 13:19 | 40 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU | B22032200033 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-03-22 | 6320 | keep | 0 | Mar | 2022 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-22 10:48 | 2022-03-22 12:00 | 81 | 001:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER A SU 1 SE REMPLAZO CAJA | B22032200034 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2022-03-22 | 5832 | keep | 0 | Mar | 2022 | 0.0039721 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2022-03-22 11:31 | 2022-03-22 11:52 | 10 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS EN PEDESTAL | B22032200036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2022-03-22 | 210 | keep | 0 | Mar | 2022 | 0.00014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-22 11:35 | 2022-03-22 11:36 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 225 | keep | 0 | Mar | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-22 11:35 | 2022-03-22 11:36 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1303-4 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 870 | keep | 0 | Mar | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-03-22 11:35 | 2022-03-22 11:55 | 20 | 000:20 | P | PARARRAYOS DEFECTUOSO | SE ABRE CORTE DE LINEA PARA REMPLAZAR PARARRAYO TRAS PATIO | S22031600053 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 20 | 2022-03-22 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-22 11:38 | 2022-03-22 11:39 | 823 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF 95% POR 1119-4 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-22 | 823 | keep | 0 | Mar | 2022 | 0.00056054 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
BAYAMON | 2022-03-22 11:38 | 2022-03-22 11:39 | 863 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF 99% POR 1119-4 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-22 | 863 | keep | 0 | Mar | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
BAYAMON | 2022-03-22 11:38 | 2022-03-22 11:39 | 2720 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO CON R/R OFF LLEVA 95% DEL 1115-5 Y 99% DEL 1119-2 SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-22 | 2720 | keep | 0 | Mar | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2022-03-22 11:39 | 2022-03-22 15:36 | 15 | 003:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER A CAUSA DE RAYO | S22032200071 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 237 | 2022-03-22 | 3555 | keep | 0 | Mar | 2022 | 0.0024213 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-22 11:41 | 2022-03-22 11:46 | 172 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE VERIFICO CON COD CAROLINA SE PROBO QUEDO EN SERVICIO | S22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-03-22 | 860 | keep | 0 | Mar | 2022 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-03-22 11:56 | 2022-03-22 13:14 | 1058 | 001:18 | P | PARARRAYOS DEFECTUOSO | DISPARO PORTATIL#8 SE ENCONTRO PARARRAYO AVERIADO CARR.1 FTE. GARAGE TEXACO TRONCAL 1348-8 SE REPARO Y CERRO PORTATIL 20% POR 1348-8 | S22032200052 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 78 | 2022-03-22 | 82524 | keep | 0 | Mar | 2022 | 0.056207 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-03-22 11:56 | 2022-03-22 13:14 | 250 | 001:18 | P | PARARRAYOS DEFECTUOSO | DISPARO PORTATIL#8 SE ENCONTRO PARARRAYO AVERIADO CARR.1 FTE. GARAGE TEXACO TRONCAL 1348-8 SE REPARO Y CERRO PORTATIL 20% POR 1348-8 | S22032200052 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 78 | 2022-03-22 | 19500 | keep | 0 | Mar | 2022 | 0.013281 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-03-22 11:56 | 2022-03-22 13:14 | 1290 | 001:18 | T | PARARRAYOS DEFECTUOSO | DISPARO PORTATIL#8 SE ENCONTRO PARARRAYO AVERIADO CARR.1 FTE. GARAGE TEXACO TRONCAL 1348-8 SE REPARO Y CERRO PORTATIL | S22032200052 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 78 | 2022-03-22 | 100620 | keep | 0 | Mar | 2022 | 0.068532 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-03-22 12:00 | 2022-03-22 12:01 | 341 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR. SE CERRO POR SCADA | B22032200000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-22 | 341 | keep | 0 | Mar | 2022 | 0.00023225 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-22 12:01 | 2022-03-23 20:54 | 14 | 032:53 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO PARA ENERGIZAR T-11 & T-12 | B22032100072 | New_Event | UG Cable Fault | Include | Include | Equipment | 1973 | 2022-03-22 | 27622 | keep | 0 | Mar | 2022 | 0.018813 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-03-22 12:01 | 2022-03-23 14:55 | 40 | 026:54 | P | CABLE SOTERRADO AVERIADO | SE ABRIO PARA CONTRUIR PROVISIONAL AEREO DE TRONCAL 1717-05 @ FASE: A DEL SU-3 | B22032300009 | New_Event | UG Cable Fault | Include | Include | Equipment | 1614 | 2022-03-22 | 64560 | keep | 0 | Mar | 2022 | 0.043972 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-22 12:01 | 2022-03-22 12:22 | 81 | 000:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER A SU 1 SE REMPLAZO CAJA | B22032200034 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 21 | 2022-03-22 | 1701 | keep | 0 | Mar | 2022 | 0.0011585 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
CANOVANAS | 2022-03-22 12:02 | 2022-03-22 12:03 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1894 | keep | 0 | Mar | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
BAYAMON | 2022-03-22 12:08 | 2022-03-22 12:09 | 6136 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR 1709-01 LLEVANDO CARGA 1720-07 | B22032200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-22 | 6136 | keep | 0 | Mar | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-03-22 12:09 | 2022-03-22 15:26 | 46 | 003:17 | P | DESGANCHE | 1X65 EN C/L (SE DESGANCHO BAMBUA) | P22032200025 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-03-22 | 9062 | keep | 0 | Mar | 2022 | 0.0061721 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
SAN JUAN | 2022-03-22 12:21 | 2022-03-22 14:08 | 40 | 001:47 | P | DESGANCHE | 1 X 80 EN RISER DESGANCHE | S22032200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-03-22 | 4280 | keep | 0 | Mar | 2022 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-22 12:35 | 2022-03-22 15:14 | 329 | 002:39 | T | CABLE SOTERRADO AVERIADO | INTERRUPTOR RECERRO 3 VECES SE DEJO FUERA TIENE RISER DE SALIDA AVERIADO SE TRANSFIRIO LA CARGA AL 3006-03 | C22032200038 | New_Event | UG Cable Fault | Include | Include | Equipment | 159 | 2022-03-22 | 52311 | keep | 0 | Mar | 2022 | 0.035629 | 0.00022408 | Sustained | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-03-22 12:36 | 2022-03-22 15:20 | 12 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ELIMINO TENSOR, DESGANCHARON, SE REPARO BAJANTE DEL TRANSFORMADOR Y SE REEMPLAZARON CONECTORES | C22032200042 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2022-03-22 | 1968 | keep | 0 | Mar | 2022 | 0.0013404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-22 12:43 | 2022-03-22 15:31 | 30 | 002:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22032200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-03-22 | 5040 | keep | 0 | Mar | 2022 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-22 12:51 | 2022-03-22 18:56 | 15 | 006:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 50KVA X 50KVA, CRUCETA Y CONECTORES Y SE REALIZO DESGANCHE | S22032200093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 365 | 2022-03-22 | 5475 | keep | 0 | Mar | 2022 | 0.003729 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-22 12:59 | 2022-03-22 13:00 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22032200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1590 | keep | 0 | Mar | 2022 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
GUAYAMA | 2022-03-22 12:59 | 2022-03-22 13:40 | 140 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22032200020 | New_Event |  |  | Include | Wildlife | 41 | 2022-03-22 | 5740 | keep | 0 | Mar | 2022 | 0.0039095 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2022-03-22 12:59 | 2022-03-22 14:40 | 16 | 001:41 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22032200044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-03-22 | 1616 | keep | 0 | Mar | 2022 | 0.0011007 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2022-03-22 13:09 | 2022-03-22 13:12 | 2106 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R22032200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-22 | 6318 | keep | 0 | Mar | 2022 | 0.0043032 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2022-03-22 13:13 | 2022-03-22 15:36 | 40 | 002:23 | P | DESGANCHE | 1 X 50 EN C/L | R22032200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-03-22 | 5720 | keep | 0 | Mar | 2022 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-03-22 13:15 | 2022-03-22 14:25 | 12 | 001:10 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR AVERIADO DE 50KVA/7.20KV POR UNO MISMA CAPACIDAD | P22032200023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 70 | 2022-03-22 | 840 | keep | 0 | Mar | 2022 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-22 13:22 | 2022-03-22 13:24 | 1084 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR 1 VEZ Y QUEDO FUERA CERRADO POR CONTROL PROBO BUENO | C22032200052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-03-22 | 2168 | keep | 0 | Mar | 2022 | 0.0014766 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
CAGUAS | 2022-03-22 13:24 | 2022-03-22 18:10 | 487 | 004:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADORES ROTO SE CERRO INTELLIRRUPTER 3006-03 | C22032200055 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 286 | 2022-03-22 | 139282 | keep | 0 | Mar | 2022 | 0.094864 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
CAGUAS | 2022-03-22 13:32 | 2022-03-22 13:33 | 638 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO | C22032200058 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-22 | 638 | keep | 0 | Mar | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
PONCE | 2022-03-22 13:32 | 2022-03-22 15:01 | 100 | 001:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22032200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-03-22 | 8900 | keep | 0 | Mar | 2022 | 0.0060617 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-22 13:33 | 2022-03-22 18:51 | 70 | 005:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22032200059 | 1st_after_momentary |  |  | Include | Wildlife | 318 | 2022-03-22 | 22260 | keep | 0 | Mar | 2022 | 0.015161 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-03-22 13:41 | 2022-03-22 13:42 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22032200029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 464 | keep | 0 | Mar | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BARRANQUITAS | 2022-03-22 14:02 | 2022-03-22 17:07 | 4 | 003:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C22032200057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 185 | 2022-03-22 | 740 | keep | 0 | Mar | 2022 | 0.00050401 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-03-22 14:02 | 2022-03-22 18:20 | 20 | 004:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22032200069 | New_Event | Bad Weather | Include | Include | Weather | 258 | 2022-03-22 | 5160 | keep | 0 | Mar | 2022 | 0.0035145 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-03-22 14:02 | 2022-03-22 19:01 | 60 | 004:59 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22032200054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2022-03-22 | 17940 | keep | 0 | Mar | 2022 | 0.012219 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-22 14:07 | 2022-03-22 21:58 | 36 | 007:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22032200107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2022-03-22 | 16956 | keep | 0 | Mar | 2022 | 0.011549 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-03-22 14:25 | 2022-03-22 20:14 | 12 | 005:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | C22032200072 | New_Event | Wire Down | Include | Include | Equipment | 349 | 2022-03-22 | 4188 | keep | 0 | Mar | 2022 | 0.0028524 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-03-22 14:29 | 2022-03-22 15:23 | 3 | 000:54 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN XMR DESGANCHO | R22032200053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 54 | 2022-03-22 | 162 | keep | 0 | Mar | 2022 | 0.00011034 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-03-22 14:32 | 2022-03-22 19:55 | 30 | 005:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA EN CORTE DE LINEA Y SE REPARO LINEA ZAFADA DE AISLADORES POR CLIENTES QUE DESGANCHANDO TIRARON ARBOL SOBRE LAS LINEAS | A22032200033 | New_Event |  |  | Include | Wildlife | 323 | 2022-03-22 | 9690 | keep | 0 | Mar | 2022 | 0.0065998 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-22 14:38 | 2022-03-22 14:39 | 528 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M22032200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-22 | 528 | keep | 0 | Mar | 2022 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2022-03-22 14:39 | 2022-03-22 16:55 | 80 | 002:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22032200075 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 136 | 2022-03-22 | 10880 | keep | 0 | Mar | 2022 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-22 14:44 | 2022-03-22 17:19 | 40 | 002:35 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 80 EN RISER CONTAMINACION EN SU#1 | S22032200119 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 155 | 2022-03-22 | 6200 | keep | 0 | Mar | 2022 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-22 14:45 | 2022-03-22 16:31 | 12 | 001:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C22032200074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 106 | 2022-03-22 | 1272 | keep | 0 | Mar | 2022 | 0.00086635 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-22 14:46 | 2022-03-22 17:42 | 65 | 002:56 | P | DESGANCHE | 1 X 65 EN C/L | R22032200054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-03-22 | 11440 | keep | 0 | Mar | 2022 | 0.0077917 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-03-22 14:52 | 2022-03-22 19:22 | 3 | 004:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO LINEA SECUNDARIA | A22032200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 270 | 2022-03-22 | 810 | keep | 0 | Mar | 2022 | 0.00055169 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-03-22 15:03 | 2022-03-22 18:15 | 65 | 003:12 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L`S | R22032200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-03-22 | 12480 | keep | 0 | Mar | 2022 | 0.0085001 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2022-03-22 15:07 | 2022-03-22 20:31 | 10 | 005:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22032200077 | New_Event | Bad Weather | Include | Include | Weather | 324 | 2022-03-22 | 3240 | keep | 0 | Mar | 2022 | 0.0022067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-22 15:20 | 2022-03-22 17:05 | 120 | 001:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P22032200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-03-22 | 12600 | keep | 0 | Mar | 2022 | 0.0085818 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
FAJARDO | 2022-03-22 15:21 | 2022-03-22 17:07 | 40 | 001:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA Y REPARO BAJANTE NO FUNDIO | R22032200057 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2022-03-22 | 4240 | keep | 0 | Mar | 2022 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-22 15:27 | 2022-03-22 15:28 | 1 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTOR EN SECUNDARIA & TOMA DE SERVICIO DEL CLIENTE | B22032200058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2022-03-22 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-22 15:39 | 2022-03-22 18:48 | 126 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X100 EN C/L SE RETIRARON VARIOS GLOBOS | B22032200062 | New_Event |  |  | Include | Wildlife | 189 | 2022-03-22 | 23814 | keep | 0 | Mar | 2022 | 0.01622 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
ARECIBO | 2022-03-22 16:01 | 2022-03-22 19:52 | 2500 | 003:51 | P | ESTRUCTURA AVERIADA | SE ABRIO MACHETES PARA PODER PASAR LINEA PRIMARIAS A POSTE PRIMARIO NUEVO QUE SE INSTALO POR POSTE PRIMARIO DE METAL QUE SE DOBLO | A22032200041 | New_Event | Defective Pole | Include | Include | Equipment | 231 | 2022-03-22 | 577500 | keep | 0 | Mar | 2022 | 0.39333 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
BAYAMON | 2022-03-22 16:24 | 2022-03-22 16:25 | 168 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X80 EN C/L & 1X65 EN C/L & SE RETIRO AVE DEL 13KV | S22032200122 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-22 | 168 | keep | 0 | Mar | 2022 | 0.00011442 | 0.00011442 | Momentary | FALSE | FALSE | Not_TMED_Event | 168
SAN JUAN | 2022-03-22 16:26 | 2022-03-22 18:05 | 60 | 001:39 | P | NO SE REPORTO CAUSA | 2 X 200 EN C/L | S22032200133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-03-22 | 5940 | keep | 0 | Mar | 2022 | 0.0040457 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-22 16:26 | 2022-03-22 21:20 | 10 | 004:54 | P | SECUNDARIA/DESGANCHE | 1 X 40 EN XMR SE ABRIO XMR PARA REPARAR SECUNDARIA Y LEVANTAR CONDUCTOR SECUNDARIO. SE REALIZO DESGANCHE | S22032200112 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 294 | 2022-03-22 | 2940 | keep | 0 | Mar | 2022 | 0.0020024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-22 16:27 | 2022-03-22 19:10 | 100 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22032200081 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2022-03-22 | 16300 | keep | 0 | Mar | 2022 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-22 16:34 | 2022-03-22 20:05 | 60 | 003:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22032200083 | New_Event | Bad Weather | Include | Include | Weather | 211 | 2022-03-22 | 12660 | keep | 0 | Mar | 2022 | 0.0086227 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-22 16:46 | 2022-03-22 16:47 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 1X15 EN BANCO DE TRANSFORMADORES | S22032200121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-22 16:46 | 2022-03-22 21:25 | 14 | 004:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR & SE DIERON CONECTORES SECUNDARIOS | B22032200071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 279 | 2022-03-22 | 3906 | keep | 0 | Mar | 2022 | 0.0026604 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2022-03-22 17:17 | 2022-03-22 18:15 | 1 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR TENSOR PEGANDO A LINEA PRIMARIA | P22032200046 | New_Event |  |  | Include | Wildlife | 58 | 2022-03-22 | 58 | keep | 0 | Mar | 2022 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-22 17:38 | 2022-03-22 17:39 | 10 | 000:01 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 37.5 KVA X 37.5 KVA | R22032200049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-03-22 | 10 | keep | 0 | Mar | 2022 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-22 17:49 | 2022-03-23 08:06 | 174 | 014:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22032200103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 857 | 2022-03-22 | 149118 | keep | 0 | Mar | 2022 | 0.10156 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
SAN JUAN | 2022-03-22 17:56 | 2022-03-22 18:25 | 6 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22032200158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-03-22 | 174 | keep | 0 | Mar | 2022 | 0.00011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-22 17:58 | 2022-03-22 20:56 | 16 | 002:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO (NO FUNDIO) | B22032200080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 178 | 2022-03-22 | 2848 | keep | 0 | Mar | 2022 | 0.0019398 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-03-22 18:10 | 2022-03-22 18:20 | 226 | 000:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADORES ROTO SE CERRO MACHETES | C22032200055 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 10 | 2022-03-22 | 2260 | keep | 0 | Mar | 2022 | 0.0015393 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-22 19:22 | 2022-03-22 21:22 | 18 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA DE TRANSFORMADOR | C22032200118 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2022-03-22 | 2160 | keep | 0 | Mar | 2022 | 0.0014712 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-03-22 20:10 | 2022-03-23 07:06 | 36 | 010:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C22032200123 | New_Event | Cutout Failure | Include | Include | Equipment | 656 | 2022-03-22 | 23616 | keep | 0 | Mar | 2022 | 0.016085 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-03-22 20:11 | 2022-03-23 08:50 | 6 | 012:39 | P | SECUNDARIA/DESGANCHE | 1 X EN TRANSFORMADOR SE REALIZO DESGANCHE | C22032200124 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 759 | 2022-03-22 | 4554 | keep | 0 | Mar | 2022 | 0.0031017 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-22 20:17 | 2022-03-22 22:44 | 150 | 002:27 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA POR SOBRECARGA | M22032200093 | New_Event | Trip Due To Overload | Include | Include | Other | 147 | 2022-03-22 | 22050 | keep | 0 | Mar | 2022 | 0.015018 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-03-22 20:59 | 2022-03-22 21:40 | 15 | 000:41 | P | NO SE REPORTO CAUSA | 1X10 EN TRANSFORMADOR | B22032200090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2022-03-22 | 615 | keep | 0 | Mar | 2022 | 0.00041887 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-03-22 22:06 | 2022-03-22 22:07 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22032200000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-22 | 1284 | keep | 0 | Mar | 2022 | 0.00087453 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-22 22:51 | 2022-03-23 06:29 | 40 | 007:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA AVERIADA | C22032200133 | New_Event | Cutout Failure | Include | Include | Equipment | 458 | 2022-03-22 | 18320 | keep | 0 | Mar | 2022 | 0.012478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-22 23:25 | 2022-03-23 01:00 | 150 | 001:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22032200139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-03-22 | 14250 | keep | 0 | Mar | 2022 | 0.0097056 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-23 00:43 | 2022-03-23 00:44 | 2402 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO LEVA 1720-08 | S22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 2402 | keep | 0 | Mar | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-03-23 00:43 | 2022-03-23 00:44 | 1 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO 1709-02 Y LLEVA LA CARGA DEL 1720-08 | S22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-23 00:44 | 2022-03-23 01:50 | 80 | 001:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA SE RETIRO RATA | S22032300001 | 1st_after_momentary |  |  | Include | Wildlife | 66 | 2022-03-23 | 5280 | keep | 0 | Mar | 2022 | 0.0035962 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-23 03:24 | 2022-03-23 05:20 | 100 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER | B22032300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-03-23 | 11600 | keep | 0 | Mar | 2022 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-03-23 03:58 | 2022-03-23 15:25 | 7 | 011:27 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | A22032300001 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 687 | 2022-03-23 | 4809 | keep | 0 | Mar | 2022 | 0.0032754 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-23 05:01 | 2022-03-23 10:25 | 131 | 005:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22032300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-03-23 | 42444 | keep | 0 | Mar | 2022 | 0.028908 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
MAYAGÃœEZ | 2022-03-23 05:54 | 2022-03-23 08:08 | 80 | 002:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS | M22032300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-03-23 | 10720 | keep | 0 | Mar | 2022 | 0.0073013 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-23 06:07 | 2022-03-23 06:09 | 2053 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22032300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-23 | 4106 | keep | 0 | Mar | 2022 | 0.0027966 | 0.0013983 | Momentary | FALSE | FALSE | Not_TMED_Event | 2053
GUAYAMA | 2022-03-23 06:34 | 2022-03-23 06:35 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22032300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 4132 | keep | 0 | Mar | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2022-03-23 06:55 | 2022-03-23 11:20 | 60 | 004:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA 1 X 65 EN CORTE DE LINEA | S22032300005 | New_Event | Wire Down | Include | Include | Equipment | 265 | 2022-03-23 | 15900 | keep | 0 | Mar | 2022 | 0.010829 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-23 07:07 | 2022-03-23 07:08 | 1647 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 1647 | keep | 0 | Mar | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-03-23 07:08 | 2022-03-23 09:42 | 1 | 002:34 | P | NO SE REPORTO CAUSA | 2 X 15 EN MONTURA TRANSFORMADORES | B22032300012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-03-23 | 154 | keep | 0 | Mar | 2022 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-23 07:27 | 2022-03-23 08:32 | 10 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22032300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-03-23 | 650 | keep | 0 | Mar | 2022 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-23 07:37 | 2022-03-23 07:38 | 1500 | 000:01 | P | PARARRAYOS DEFECTUOSO | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO PARTE POR 1620-02 | S22032300014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-03-23 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-23 07:37 | 2022-03-23 07:38 | 3718 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA PARTE 1206-3 | S22032300014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-03-23 | 3718 | keep | 0 | Mar | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2022-03-23 07:38 | 2022-03-23 13:50 | 80 | 006:12 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA | S22032300017 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 372 | 2022-03-23 | 29760 | keep | 0 | Mar | 2022 | 0.020269 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-03-23 08:04 | 2022-03-23 08:05 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22032300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 908 | keep | 0 | Mar | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
ARECIBO | 2022-03-23 08:08 | 2022-03-23 12:26 | 30 | 004:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A22032300004 | New_Event |  |  | Include | Wildlife | 258 | 2022-03-23 | 7740 | keep | 0 | Mar | 2022 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-23 08:16 | 2022-03-23 08:54 | 9 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA SECUNDARIA EN TRANSFORMADOR | B22032200078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-03-23 | 342 | keep | 0 | Mar | 2022 | 0.00023293 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-03-23 08:37 | 2022-03-23 10:45 | 1 | 002:08 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA POR PARARRAYO BOMBAS AAA | A22032300008 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 128 | 2022-03-23 | 128 | keep | 0 | Mar | 2022 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-23 08:47 | 2022-03-24 13:10 | 1 | 028:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA POR 25 KVA | M22032300013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1703 | 2022-03-23 | 1703 | keep | 0 | Mar | 2022 | 0.0011599 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-23 08:55 | 2022-03-23 09:35 | 10 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR PEDESTAL | R22032200066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-23 | 400 | keep | 0 | Mar | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-23 08:56 | 2022-03-23 18:04 | 5 | 009:08 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA REALIZAR DESGANCHE | C22032300031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 548 | 2022-03-23 | 2740 | keep | 0 | Mar | 2022 | 0.0018662 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-23 08:58 | 2022-03-23 11:37 | 7 | 002:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65, 2 X 80 Y 2 X 100 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22032300033 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2022-03-23 | 1113 | keep | 0 | Mar | 2022 | 0.00075806 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-03-23 08:59 | 2022-03-23 12:38 | 1 | 003:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22032300034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-03-23 | 219 | keep | 0 | Mar | 2022 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-23 09:13 | 2022-03-23 15:29 | 10 | 006:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | P22032300005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 376 | 2022-03-23 | 3760 | keep | 0 | Mar | 2022 | 0.0025609 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-03-23 09:16 | 2022-03-23 10:39 | 6 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CABLE EN BARRA DEL PEDESTAL | C22032300037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-03-23 | 498 | keep | 0 | Mar | 2022 | 0.00033919 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-23 09:30 | 2022-03-23 11:05 | 14 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S22032300025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2022-03-23 | 1330 | keep | 0 | Mar | 2022 | 0.00090586 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-03-23 09:31 | 2022-03-23 17:00 | 1 | 007:29 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22032300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2022-03-23 | 449 | keep | 0 | Mar | 2022 | 0.00030581 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-23 09:49 | 2022-03-24 00:20 | 50 | 014:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22032300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 871 | 2022-03-23 | 43550 | keep | 0 | Mar | 2022 | 0.029662 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-23 10:06 | 2022-03-23 10:08 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO CONTROL QUEDO EN SERVICIO SE VERIFICO CON COD CAROLINA | S22032300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-23 | 344 | keep | 0 | Mar | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
PONCE | 2022-03-23 10:17 | 2022-03-23 15:15 | 10 | 004:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL SECUNDARIO | P22032300009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 298 | 2022-03-23 | 2980 | keep | 0 | Mar | 2022 | 0.0020297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-03-23 10:24 | 2022-03-23 11:46 | 7 | 001:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO CAJA PRIMARIA | R22032300015 | New_Event | Cutout Failure | Include | Include | Equipment | 82 | 2022-03-23 | 574 | keep | 0 | Mar | 2022 | 0.00039095 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-03-23 10:28 | 2022-03-23 11:57 | 8 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR CONECTORES SECUNDARIOS | R22032300016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2022-03-23 | 712 | keep | 0 | Mar | 2022 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-23 11:20 | 2022-03-23 16:19 | 30 | 004:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO AVERIA SOTERRADA CAUSADA POR ESCAVADORA ENTRE PM-16 Y PM-17 Y SE CERRO N/O EN PM-18 | M22032300030 | New_Event |  |  | Include | Wildlife | 299 | 2022-03-23 | 8970 | keep | 0 | Mar | 2022 | 0.0061094 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-23 11:24 | 2022-03-23 17:20 | 12 | 005:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | R22032300014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 356 | 2022-03-23 | 4272 | keep | 0 | Mar | 2022 | 0.0029096 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-23 11:27 | 2022-03-23 11:28 | 996 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO | S22032300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-23 | 996 | keep | 0 | Mar | 2022 | 0.00067837 | 0.00067837 | Momentary | FALSE | FALSE | Not_TMED_Event | 996
VEGA BAJA | 2022-03-23 11:27 | 2022-03-23 18:29 | 50 | 007:02 | P | DESGANCHE | 1X80 EN C/L Y SE REALIZO DESGANCHE PRIMARIO MASIVO | B22032300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2022-03-23 | 21100 | keep | 0 | Mar | 2022 | 0.014371 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-23 11:28 | 2022-03-23 15:48 | 25 | 004:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 80 EN RISER SE REMPLAZO CAJA PRIMARIA | S22032300047 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 260 | 2022-03-23 | 6500 | keep | 0 | Mar | 2022 | 0.0044271 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-03-23 11:57 | 2022-03-23 14:45 | 10 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22032300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-03-23 | 1680 | keep | 0 | Mar | 2022 | 0.0011442 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-03-23 12:00 | 2022-03-23 12:23 | 8 | 000:23 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REGRESAR CARGA SECUNDARIA A TRANSFORMADOR PREVIAMENTE REMPLAZADO | P22032300014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 23 | 2022-03-23 | 184 | keep | 0 | Mar | 2022 | 0.00012532 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-23 12:44 | 2022-03-23 19:55 | 80 | 007:11 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA FUERTE VIENTO | M22032300048 | New_Event | Bad Weather | Include | Include | Weather | 431 | 2022-03-23 | 34480 | keep | 0 | Mar | 2022 | 0.023484 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-23 12:54 | 2022-03-23 13:42 | 5 | 000:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN RISER SE RETIRO IGUANA QUE CRUZO LINEAS | B22032300032 | New_Event |  |  | Include | Wildlife | 48 | 2022-03-23 | 240 | keep | 0 | Mar | 2022 | 0.00016346 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-03-23 12:57 | 2022-03-23 16:30 | 1475 | 003:33 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR POR BAJANTE PRIMARIO ZAFADO DE RISER | P22032300018 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2022-03-23 | 314175 | keep | 0 | Mar | 2022 | 0.21398 | 0.0010046 | Sustained | FALSE | FALSE | Not_TMED_Event | 1475
CAGUAS | 2022-03-23 13:06 | 2022-03-24 11:13 | 17 | 022:07 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22032300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1327 | 2022-03-23 | 22559 | keep | 0 | Mar | 2022 | 0.015365 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-03-23 13:12 | 2022-03-23 14:48 | 10 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BAJANTES SECUNDARIOS EN XMR | B22032300033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2022-03-23 | 960 | keep | 0 | Mar | 2022 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-23 13:13 | 2022-03-24 06:10 | 50 | 016:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032300053 | New_Event | Bad Weather | Include | Include | Weather | 1017 | 2022-03-23 | 50850 | keep | 0 | Mar | 2022 | 0.034634 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-23 13:16 | 2022-03-24 04:35 | 80 | 015:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22032300054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 919 | 2022-03-23 | 73520 | keep | 0 | Mar | 2022 | 0.050074 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-23 13:19 | 2022-03-23 14:44 | 100 | 001:25 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L NO CAUSA | C22032300059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-03-23 | 8500 | keep | 0 | Mar | 2022 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-23 13:28 | 2022-03-23 13:29 | 329 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | C.C.E. ABRIO EL BANCO 115/38/13 PARA QUE PERSONAL DE SUBESTACIONES RETIRARA IGUANA DE BUSHING | C22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 329 | keep | 0 | Mar | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2022-03-23 13:28 | 2022-03-23 13:29 | 1879 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | C.C.E. ABRIO EL BANCO 115/38/13 PARA QUE PERSONAL DE SUBESTACIONES RETIRARA IGUANA DE BUSHING | C22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 1879 | keep | 0 | Mar | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2022-03-23 13:28 | 2022-03-23 13:29 | 1084 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | C.C.E. ABRIO EL BANCO 115/38/13 PARA QUE PERSONAL DE SUBESTACIONES RETIRARA IGUANA DE BUSHING | C22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 1084 | keep | 0 | Mar | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
CAGUAS | 2022-03-23 13:28 | 2022-03-23 13:29 | 817 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | C.C.E. ABRIO EL BANCO 115/38/13 PARA QUE PERSONAL DE SUBESTACIONES RETIRARA IGUANA DE BUSHING | C22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 817 | keep | 0 | Mar | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2022-03-23 13:28 | 2022-03-23 13:29 | 3005 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | C.C.E. ABRIO EL BANCO 115/38/13 PARA QUE PERSONAL DE SUBESTACIONES RETIRARA IGUANA DE BUSHING | C22032300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-23 | 3005 | keep | 0 | Mar | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
MAYAGÃœEZ | 2022-03-23 13:28 | 2022-03-23 18:25 | 50 | 004:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22032300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-03-23 | 14850 | keep | 0 | Mar | 2022 | 0.010114 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-03-23 13:28 | 2022-03-23 16:43 | 300 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 Y 1 X 200 EN CORTES DE LINEAS DISTINTOS FUERTE VIENTO | M22032300059 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2022-03-23 | 58500 | keep | 0 | Mar | 2022 | 0.039844 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-03-23 13:29 | 2022-03-23 23:28 | 6 | 009:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22032300025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 599 | 2022-03-23 | 3594 | keep | 0 | Mar | 2022 | 0.0024479 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-23 13:33 | 2022-03-23 18:15 | 39 | 004:42 | P | HERRAJE ROTO O PODRIDO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CRUCETA Y SE LEVANTO FASE | S22032300058 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 282 | 2022-03-23 | 10998 | keep | 0 | Mar | 2022 | 0.0074907 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
ARECIBO | 2022-03-23 13:42 | 2022-03-23 15:50 | 80 | 002:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22032300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-23 | 10240 | keep | 0 | Mar | 2022 | 0.0069744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-03-23 13:59 | 2022-03-23 14:39 | 8 | 000:40 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | R22032300022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 40 | 2022-03-23 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-03-23 14:00 | 2022-03-23 14:43 | 12 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS | A22032300028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-03-23 | 516 | keep | 0 | Mar | 2022 | 0.00035145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-03-23 14:02 | 2022-03-23 17:00 | 150 | 002:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | M22032300070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-03-23 | 26700 | keep | 0 | Mar | 2022 | 0.018185 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-03-23 14:10 | 2022-03-23 14:46 | 11 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22032300072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-03-23 | 396 | keep | 0 | Mar | 2022 | 0.00026971 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-03-23 14:11 | 2022-03-24 05:26 | 40 | 015:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 915 | 2022-03-23 | 36600 | keep | 0 | Mar | 2022 | 0.024928 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-03-23 14:15 | 2022-03-23 14:16 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22032300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 1268 | keep | 0 | Mar | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-03-23 14:15 | 2022-03-23 14:16 | 2952 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22032300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 2952 | keep | 0 | Mar | 2022 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2022-03-23 14:30 | 2022-03-23 16:30 | 10 | 002:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO CON ESCAPE DE ACEITE DE 25KVA POR LA MISMA CAPACIDAD | M22032300091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2022-03-23 | 1200 | keep | 0 | Mar | 2022 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-23 14:34 | 2022-03-23 14:37 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-5 | S22032300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-23 | 675 | keep | 0 | Mar | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-23 14:34 | 2022-03-23 14:37 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1303-4 | S22032300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-23 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2022-03-23 14:45 | 2022-03-23 15:10 | 1 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | R22032300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-03-23 | 25 | keep | 0 | Mar | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-23 14:48 | 2022-03-23 16:08 | 44 | 001:20 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22032300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-03-23 | 3520 | keep | 0 | Mar | 2022 | 0.0023975 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
ARECIBO | 2022-03-23 15:01 | 2022-03-23 16:21 | 2 | 001:20 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A22032300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-03-23 | 160 | keep | 0 | Mar | 2022 | 0.00010898 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-03-23 15:02 | 2022-03-23 16:38 | 5 | 001:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22032300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-03-23 | 480 | keep | 0 | Mar | 2022 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-23 15:12 | 2022-03-23 17:05 | 60 | 001:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22032300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-03-23 | 6780 | keep | 0 | Mar | 2022 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-03-23 15:13 | 2022-03-24 12:25 | 30 | 021:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032300099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1272 | 2022-03-23 | 38160 | keep | 0 | Mar | 2022 | 0.025991 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-23 15:58 | 2022-03-23 17:29 | 2 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA DEL CLIENTE | B22032300042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2022-03-23 | 182 | keep | 0 | Mar | 2022 | 0.00012396 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-23 16:13 | 2022-03-23 17:35 | 150 | 001:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22032300126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-03-23 | 12300 | keep | 0 | Mar | 2022 | 0.0083775 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-23 16:15 | 2022-03-23 18:34 | 6 | 002:19 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SECUNDARIO EN PEDESTAL | S22032300043 | New_Event | UG Cable Fault | Include | Include | Equipment | 139 | 2022-03-23 | 834 | keep | 0 | Mar | 2022 | 0.00056803 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-03-23 16:19 | 2022-03-24 12:45 | 11 | 020:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM-11 FID-1000284705 | M22032300030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1226 | 2022-03-23 | 13486 | keep | 0 | Mar | 2022 | 0.0091853 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2022-03-23 16:30 | 2022-03-23 17:27 | 1032 | 000:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE PRIMARIO DE RISER ZAFADO | P22032300018 | Partial_restoration | Wire Down | Include | Include | Equipment | 57 | 2022-03-23 | 58824 | keep | 0 | Mar | 2022 | 0.040065 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-03-23 16:39 | 2022-03-23 18:28 | 20 | 001:49 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LAS LINEAS | M22032300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-03-23 | 2180 | keep | 0 | Mar | 2022 | 0.0014848 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 574 | keep | 0 | Mar | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 2493 | keep | 0 | Mar | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 1415 | keep | 0 | Mar | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 1428 | keep | 0 | Mar | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 1036 | keep | 0 | Mar | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 2366 | keep | 0 | Mar | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-03-23 16:43 | 2022-03-23 16:44 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 1337 | keep | 0 | Mar | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-03-23 16:43 | 2022-03-23 16:44 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M22032300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-23 | 709 | keep | 0 | Mar | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
AGUADILLA | 2022-03-23 16:44 | 2022-03-23 21:12 | 300 | 004:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 Y 1 X 200 EN CORTES DE LINEAS DISTINTOS FUERTE VIENTO | M22032300059 | Partial_restoration | Bad Weather | Include | Include | Weather | 268 | 2022-03-23 | 80400 | keep | 0 | Mar | 2022 | 0.05476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-23 16:47 | 2022-03-23 16:54 | 108 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-23 | 756 | keep | 0 | Mar | 2022 | 0.00051491 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2022-03-23 16:58 | 2022-03-23 18:45 | 35 | 001:47 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A22032300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-03-23 | 3745 | keep | 0 | Mar | 2022 | 0.0025507 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-03-23 17:03 | 2022-03-23 17:11 | 8 | 000:08 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR BAJANTE SECUNDARIO | C22032300049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 8 | 2022-03-23 | 64 | keep | 0 | Mar | 2022 | 4.359e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-23 17:31 | 2022-03-23 19:51 | 16 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA (NO FUNDIO) | S22032300085 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2022-03-23 | 2240 | keep | 0 | Mar | 2022 | 0.0015257 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-03-23 17:46 | 2022-03-24 02:25 | 150 | 008:39 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032300156 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 519 | 2022-03-23 | 77850 | keep | 0 | Mar | 2022 | 0.053023 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-03-23 18:00 | 2022-03-23 18:28 | 8 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL PARTIDO | A22032300043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-03-23 | 224 | keep | 0 | Mar | 2022 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-03-23 18:14 | 2022-03-24 15:18 | 1 | 021:04 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22032300044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1264 | 2022-03-23 | 1264 | keep | 0 | Mar | 2022 | 0.0008609 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-23 18:24 | 2022-03-24 15:34 | 43 | 021:10 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DE SU 7 A T 48 CON GOI BY 220324-01A | B22032300047 | New_Event | UG Cable Fault | Include | Include | Equipment | 1270 | 2022-03-23 | 54610 | keep | 0 | Mar | 2022 | 0.037195 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2022-03-23 19:03 | 2022-03-23 19:04 | 1569 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 1569 | keep | 0 | Mar | 2022 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
MAYAGÃœEZ | 2022-03-23 19:04 | 2022-03-23 22:15 | 80 | 003:11 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22032300184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-03-23 | 15280 | keep | 0 | Mar | 2022 | 0.010407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-23 19:20 | 2022-03-23 19:21 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-23 | 2608 | keep | 0 | Mar | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
SAN JUAN | 2022-03-23 19:44 | 2022-03-23 23:00 | 50 | 003:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S22032300094 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2022-03-23 | 9800 | keep | 0 | Mar | 2022 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-03-23 20:01 | 2022-03-24 01:05 | 50 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R22032300034 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2022-03-23 | 15200 | keep | 0 | Mar | 2022 | 0.010353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-23 20:14 | 2022-03-23 23:53 | 30 | 003:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22032300048 | New_Event | Wire Down | Include | Include | Equipment | 219 | 2022-03-23 | 6570 | keep | 0 | Mar | 2022 | 0.0044748 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-23 20:48 | 2022-03-23 21:10 | 12 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R22032300038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2022-03-23 | 264 | keep | 0 | Mar | 2022 | 0.00017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-03-23 21:08 | 2022-03-24 02:00 | 14 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M22032300242 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2022-03-23 | 4088 | keep | 0 | Mar | 2022 | 0.0027843 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-03-23 21:13 | 2022-03-23 21:49 | 2 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22032300051 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2022-03-23 | 72 | keep | 0 | Mar | 2022 | 4.9039e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-03-23 22:07 | 2022-03-24 12:37 | 1 | 014:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22032100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 870 | 2022-03-23 | 870 | keep | 0 | Mar | 2022 | 0.00059255 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-23 22:31 | 2022-03-24 08:45 | 25 | 010:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA POR MAL TIEMPO | A22032300053 | New_Event | Bad Weather | Include | Include | Weather | 614 | 2022-03-23 | 15350 | keep | 0 | Mar | 2022 | 0.010455 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-03-23 22:32 | 2022-03-24 06:28 | 3 | 007:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22032300255 | New_Event | Bad Weather | Include | Include | Weather | 476 | 2022-03-23 | 1428 | keep | 0 | Mar | 2022 | 0.0009726 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-03-23 23:02 | 2022-03-24 03:31 | 100 | 004:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CERRO CAJA NO FUNDIO | C22032300096 | New_Event | Cutout Failure | Include | Include | Equipment | 269 | 2022-03-23 | 26900 | keep | 0 | Mar | 2022 | 0.018321 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-23 23:09 | 2022-03-24 09:41 | 7 | 010:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | C22032400097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 632 | 2022-03-23 | 4424 | keep | 0 | Mar | 2022 | 0.0030132 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-24 01:24 | 2022-03-24 01:26 | 169 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1116-05 | S22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 338 | keep | 0 | Mar | 2022 | 0.00023021 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-03-24 01:24 | 2022-03-24 01:26 | 5 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1116-06 & 1117-08 | S22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 10 | keep | 0 | Mar | 2022 | 6.811e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-24 01:24 | 2022-03-24 01:26 | 466 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1116-05 | S22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 932 | keep | 0 | Mar | 2022 | 0.00063478 | 0.00031739 | Momentary | FALSE | FALSE | Not_TMED_Event | 466
GUAYAMA | 2022-03-24 02:10 | 2022-03-24 06:35 | 4132 | 004:25 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. TRANSFORMADOR 4003-00 CON BUSHING DE ALTA AVERIADO. SE TRANSFIERE LA CARGA AL 4006-05. SUBESTACIONES INFORMA QUE FUE CAUSADO POR CRUCE POR IGUANA | P22032400024 | New_Event |  |  | Include | Wildlife | 265 | 2022-03-24 | 1094980 | keep | 0 | Mar | 2022 | 0.74579 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-03-24 02:10 | 2022-03-24 06:43 | 4279 | 004:33 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. TRANSFORMADOR 4003-00 CON BUSHING DE ALTA AVERIADO. SE TRANSFIERE LA CARGA AL 4006-05. SUBESTACIONES INFORMA QUE FUE CAUSADO POR CRUCE POR IGUANA | P22032400025 | New_Event |  |  | Include | Wildlife | 273 | 2022-03-24 | 1168167 | keep | 0 | Mar | 2022 | 0.79563 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-03-24 02:10 | 2022-03-24 06:59 | 1945 | 004:49 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION POR LOCKOUT. TRANSFORMADOR 4003-00 CON BUSHING DE ALTA AVERIADO. SE TRANSFIERE LA CARGA AL 4006-04. SUBESTACIONES INFORMA QUE FUE CAUSADO POR CRUCE POR IGUANA | P22032400026 | New_Event |  |  | Include | Wildlife | 289 | 2022-03-24 | 562105 | keep | 0 | Mar | 2022 | 0.38285 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
SAN JUAN | 2022-03-24 02:12 | 2022-03-24 02:13 | 3432 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO SOLO LLEVA EL 80% DE SU CARGA | S22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3432 | keep | 0 | Mar | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-03-24 02:24 | 2022-03-24 09:50 | 50 | 007:26 | P | DESGANCHE | 1 X 80 1 X 100 EN CORTE DE LINEA | S22032400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2022-03-24 | 22300 | keep | 0 | Mar | 2022 | 0.015188 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-24 03:26 | 2022-03-24 10:56 | 20 | 007:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22032400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 450 | 2022-03-24 | 9000 | keep | 0 | Mar | 2022 | 0.0061299 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-03-24 03:40 | 2022-03-24 03:41 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 2926 | keep | 0 | Mar | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
CAGUAS | 2022-03-24 03:51 | 2022-03-24 05:51 | 40 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO CAUSA | C22032400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-03-24 | 4800 | keep | 0 | Mar | 2022 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-24 04:06 | 2022-03-24 05:32 | 2720 | 001:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR ALAMBRE PARTIDO | A22032400009 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2022-03-24 | 233920 | keep | 0 | Mar | 2022 | 0.15932 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-03-24 04:06 | 2022-03-24 04:07 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3431 | keep | 0 | Mar | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
AGUADILLA | 2022-03-24 04:10 | 2022-03-24 12:30 | 10 | 008:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR 25 KVA | M22032400005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 500 | 2022-03-24 | 5000 | keep | 0 | Mar | 2022 | 0.0034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-24 05:29 | 2022-03-24 05:30 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-05 | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 723 | keep | 0 | Mar | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-03-24 05:29 | 2022-03-24 05:30 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1711-02 | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 1976 | keep | 0 | Mar | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2022-03-24 05:32 | 2022-03-24 11:56 | 350 | 006:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y SE CERRO MACHETES | A22032400012 | Partial_restoration | Wire Down | Include | Include | Equipment | 384 | 2022-03-24 | 134400 | keep | 0 | Mar | 2022 | 0.091539 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-24 05:38 | 2022-03-24 05:40 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R22032400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 2 | keep | 0 | Mar | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-24 05:54 | 2022-03-24 10:33 | 40 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A22032400015 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2022-03-24 | 11160 | keep | 0 | Mar | 2022 | 0.007601 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-24 05:56 | 2022-03-24 10:15 | 35 | 004:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22032400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-03-24 | 9065 | keep | 0 | Mar | 2022 | 0.0061741 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-03-24 06:33 | 2022-03-24 08:41 | 82 | 002:08 | P | DESGANCHE | 1 X 20 Y 1 X 25 EN CORTES DE LINEA SE RETIRO ENREDADERA | R22032400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-03-24 | 10496 | keep | 0 | Mar | 2022 | 0.0071488 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
PONCE | 2022-03-24 06:40 | 2022-03-24 09:46 | 55 | 003:06 | P | SOBRECARGA | 2 X 40 EN SU-1 POR CARGA | P22032400041 | New_Event | Trip Due To Overload | Include | Include | Other | 186 | 2022-03-24 | 10230 | keep | 0 | Mar | 2022 | 0.0069676 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-03-24 06:51 | 2022-03-24 08:50 | 10 | 001:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | S22032400011 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2022-03-24 | 1190 | keep | 0 | Mar | 2022 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-24 06:51 | 2022-03-24 06:52 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22032400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3699 | keep | 0 | Mar | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2022-03-24 06:52 | 2022-03-24 10:16 | 31 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y SE ELIMINO PARARRAYO DE AAA AVERIADO | R22032400007 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2022-03-24 | 6324 | keep | 0 | Mar | 2022 | 0.0043072 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CAGUAS | 2022-03-24 06:55 | 2022-03-24 08:24 | 1 | 001:29 | P | NO SE REPORTO CAUSA | 1 SMU20 X 50 NO CAUSA | C22032400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-03-24 | 89 | keep | 0 | Mar | 2022 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-03-24 07:05 | 2022-03-24 09:00 | 40 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032400008 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2022-03-24 | 4600 | keep | 0 | Mar | 2022 | 0.003133 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-24 07:20 | 2022-03-24 09:30 | 30 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22032400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-03-24 | 3900 | keep | 0 | Mar | 2022 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-24 07:40 | 2022-03-24 11:35 | 8 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22032400010 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2022-03-24 | 1880 | keep | 0 | Mar | 2022 | 0.0012805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-03-24 07:51 | 2022-03-24 08:36 | 5 | 000:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22032400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-03-24 | 225 | keep | 0 | Mar | 2022 | 0.00015325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-24 07:56 | 2022-03-24 21:40 | 10 | 013:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A22032400031 | New_Event | Bad Weather | Include | Include | Weather | 824 | 2022-03-24 | 8240 | keep | 0 | Mar | 2022 | 0.0056122 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-24 07:57 | 2022-03-24 07:58 | 3708 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1114-3 SE PROBO QUEDO EN SERVICIO | S22032400000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-24 | 3708 | keep | 0 | Mar | 2022 | 0.0025255 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
BAYAMON | 2022-03-24 07:57 | 2022-03-24 07:58 | 1 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1114-01 SE PROBO QUEDO EN SERVICIO | S22032400000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-24 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-24 08:00 | 2022-03-24 09:17 | 3708 | 001:17 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ENCONTRO MACHETE QUEMADO EN SALIDA RISER SE ABRIO V.S.MH-9 A RISER Y SE CERRO 1114-1 1% EN SERVICIO Y 100% DEL 1114-3 | S22032400051 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 77 | 2022-03-24 | 285516 | keep | 0 | Mar | 2022 | 0.19446 | 0.0025255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3708
BAYAMON | 2022-03-24 08:00 | 2022-03-24 09:17 | 1 | 001:17 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ENCONTRO MACHETE QUEMADO EN SALIDA RISER SE ABRIO V.S.MH-9 A RISER Y SE CERRO 1114-1 1% EN SERVICIO Y 100% DEL 1114-3 SU CARGA POR 1114-1 | S22032400051 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 77 | 2022-03-24 | 77 | keep | 0 | Mar | 2022 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-24 08:00 | 2022-03-24 10:20 | 80 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | B22032400005 | New_Event |  |  | Include | Wildlife | 140 | 2022-03-24 | 11200 | keep | 0 | Mar | 2022 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-24 08:09 | 2022-03-24 14:34 | 6 | 006:25 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA REEMPLAZAR POSTE SECUNDARIO | C22032400008 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 385 | 2022-03-24 | 2310 | keep | 0 | Mar | 2022 | 0.0015733 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-24 08:23 | 2022-03-24 14:39 | 2 | 006:16 | P | TRANSFORMADOR AVERIADO | 2 X 15 EN XMR SE ELIMINO TRANSFORMADOR EN MONTURA DE 2 TRANSFORMADORES. NO HAY CARGAS TRIFASICAS | B22032400008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 376 | 2022-03-24 | 752 | keep | 0 | Mar | 2022 | 0.00051218 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-03-24 08:23 | 2022-03-24 11:26 | 30 | 003:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-03-24 | 5490 | keep | 0 | Mar | 2022 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-24 08:31 | 2022-03-24 12:54 | 1 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN BOMBAS AAA | A22032400035 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-03-24 | 263 | keep | 0 | Mar | 2022 | 0.00017913 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-24 08:35 | 2022-03-24 10:04 | 30 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | B22032400009 | New_Event |  |  | Include | Wildlife | 89 | 2022-03-24 | 2670 | keep | 0 | Mar | 2022 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-03-24 08:36 | 2022-03-24 08:37 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9207-08 LLEVANDO CARGA 9207-09 | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 1859 | keep | 0 | Mar | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-03-24 08:36 | 2022-03-24 08:37 | 7 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9207-08 LLEVANDO CARGA 9207-09 | B22032400000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 7 | keep | 0 | Mar | 2022 | 4.7677e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-24 08:37 | 2022-03-24 11:38 | 5 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22032400004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-03-24 | 905 | keep | 0 | Mar | 2022 | 0.00061639 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-24 08:38 | 2022-03-24 08:39 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-02 | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3438 | keep | 0 | Mar | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
VEGA BAJA | 2022-03-24 08:45 | 2022-03-24 10:08 | 3 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR Y SUBIR SECUNDARIA | B22032400003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-03-24 | 249 | keep | 0 | Mar | 2022 | 0.00016959 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-03-24 08:46 | 2022-03-24 09:59 | 10 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR AVE CRUZO FASE | P22032400051 | New_Event |  |  | Include | Wildlife | 73 | 2022-03-24 | 730 | keep | 0 | Mar | 2022 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-24 08:57 | 2022-03-24 12:20 | 150 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22032400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-03-24 | 30450 | keep | 0 | Mar | 2022 | 0.020739 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-03-24 09:00 | 2022-03-24 11:00 | 1 | 002:00 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-03-24 | 120 | keep | 0 | Mar | 2022 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-24 09:17 | 2022-03-24 12:40 | 3706 | 003:23 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y 3 PUENTE PRIMARIO Y SE CERRO DE V.S. A RISER Y MACHETE 100% EN SERVICIO | S22032400051 | Partial_restoration | Switch Failure | Include | Include | Equipment | 203 | 2022-03-24 | 752318 | keep | 0 | Mar | 2022 | 0.5124 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-24 09:17 | 2022-03-24 11:41 | 13 | 002:24 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22032400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-03-24 | 1872 | keep | 0 | Mar | 2022 | 0.001275 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2022-03-24 09:30 | 2022-03-24 09:31 | 4085 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR CAJA PRIMARIA AVERIADA LLEVA LA CARGA DEL 2404-06 EN SERVICIO | R22032400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-24 | 4085 | keep | 0 | Mar | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-03-24 09:30 | 2022-03-24 09:31 | 7621 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR CAJA PRIMARIA AVERIADA CARGA POR EL 2402-03 EN SERVICIO | R22032400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-24 | 7621 | keep | 0 | Mar | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-03-24 09:31 | 2022-03-24 11:43 | 10 | 002:12 | P | HERRAJE ROTO O PODRIDO | 1 X 80 EN CORTE DE LINEA SE REDUJO PERNO EN CAJA PRIMARIA | R22032400042 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 132 | 2022-03-24 | 1320 | keep | 0 | Mar | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-24 09:35 | 2022-03-24 14:22 | 22 | 004:47 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22032400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-03-24 | 6314 | keep | 0 | Mar | 2022 | 0.0043004 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2022-03-24 09:42 | 2022-03-24 12:54 | 20 | 003:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-03-24 | 3840 | keep | 0 | Mar | 2022 | 0.0026154 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-03-24 09:52 | 2022-03-24 11:40 | 65 | 001:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LNEA POR DESGANCHE | P22032400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-03-24 | 7020 | keep | 0 | Mar | 2022 | 0.0047813 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-03-24 09:54 | 2022-03-24 11:46 | 8 | 001:52 | P | DESGANCHE | 1 X 80 Y 1 X 50 EN CORTE DE LINEAS SE REALIZO DESGANCHE | B22032400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-03-24 | 896 | keep | 0 | Mar | 2022 | 0.00061026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-24 10:00 | 2022-03-24 10:26 | 80 | 000:26 | P | ESTRUCTURA AVERIADA | POSTE PRIMARIO PARTIDO SE ABRE C/L Y SE CERRO N/O CON EL 4501-01 | P22032400069 | New_Event | Defective Pole | Include | Include | Equipment | 26 | 2022-03-24 | 2080 | keep | 0 | Mar | 2022 | 0.0014167 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-24 10:21 | 2022-03-24 16:50 | 200 | 006:29 | P | DESGANCHE | SE REALIZO DESGANCHE SE CERRO CORTE DE LINEA | M22032400024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 389 | 2022-03-24 | 77800 | keep | 0 | Mar | 2022 | 0.052989 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-03-24 10:29 | 2022-03-24 12:30 | 50 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L SE RETIRO LAGARTO | C22032400031 | New_Event |  |  | Include | Wildlife | 121 | 2022-03-24 | 6050 | keep | 0 | Mar | 2022 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-24 10:37 | 2022-03-24 13:10 | 27 | 002:33 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22032400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-03-24 | 4131 | keep | 0 | Mar | 2022 | 0.0028136 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
UTUADO | 2022-03-24 10:40 | 2022-03-24 15:12 | 50 | 004:32 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR UN POSTE PRIMARIO Y DOS SECUNDARIO | A22032400041 | New_Event | Defective Pole | Include | Include | Equipment | 272 | 2022-03-24 | 13600 | keep | 0 | Mar | 2022 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-24 10:44 | 2022-03-24 19:27 | 80 | 008:43 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN AEREO PROVISIONAL & 1 X 25 EN OTRO AEREO PROVISIONAL Y SE REMPLAZO TERMINACION OUTDOOR RABIZA DEL PROVISIONAL @ T-7 | S22032400074 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 523 | 2022-03-24 | 41840 | keep | 0 | Mar | 2022 | 0.028497 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-03-24 10:56 | 2022-03-24 14:30 | 1 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L NO CAUSA | C22032400045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-03-24 | 214 | keep | 0 | Mar | 2022 | 0.00014575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-24 11:00 | 2022-03-24 11:01 | 3650 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1710-05 SE CERRO POR SCADA 40% DE SU CARGA TRANSFERIDA AL 1718-03 | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3650 | keep | 0 | Mar | 2022 | 0.002486 | 0.002486 | Momentary | FALSE | FALSE | Not_TMED_Event | 3650
CAGUAS | 2022-03-24 11:17 | 2022-03-24 19:17 | 43 | 008:00 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22032400088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2022-03-24 | 20640 | keep | 0 | Mar | 2022 | 0.014058 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-03-24 11:30 | 2022-03-24 13:15 | 32 | 001:45 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION Y PISTOLA 1 X 50 EN PROVISIONAL | S22032400084 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 105 | 2022-03-24 | 3360 | keep | 0 | Mar | 2022 | 0.0022885 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
UTUADO | 2022-03-24 11:30 | 2022-03-24 12:06 | 40 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A22032400065 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2022-03-24 | 1440 | keep | 0 | Mar | 2022 | 0.00098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-03-24 11:39 | 2022-03-24 11:55 | 426 | 000:16 | T | ESTRUCTURA AVERIADA | SE ABRE INTERRUPTOR PARA ABRIR PUENTE PRIMARIO | P22032400075 | New_Event | Defective Pole | Include | Include | Equipment | 16 | 2022-03-24 | 6816 | keep | 0 | Mar | 2022 | 0.0046423 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
MAYAGÃœEZ | 2022-03-24 11:43 | 2022-03-24 14:13 | 30 | 002:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22032400035 | New_Event | Cutout Failure | Include | Include | Equipment | 150 | 2022-03-24 | 4500 | keep | 0 | Mar | 2022 | 0.0030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-24 11:47 | 2022-03-24 13:13 | 100 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CUCE X AVE | R22032400043 | New_Event |  |  | Include | Wildlife | 86 | 2022-03-24 | 8600 | keep | 0 | Mar | 2022 | 0.0058574 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-24 11:49 | 2022-03-24 15:22 | 150 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS Y SE CERRO PUENTE PRIMARIO ABIERTO | A22032400071 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2022-03-24 | 31950 | keep | 0 | Mar | 2022 | 0.021761 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-03-24 11:55 | 2022-03-24 18:25 | 1 | 006:30 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE TRANSFIRO LA CARGA AL 4501-01 QUEDANDO FUERA DE SERVCIO 1 CLIENTE INFORMACION SUMINISTRADA POR EL DISTRICT MANAGER DE GUAYAMA | P22032400078 | Partial_restoration | Defective Pole | Include | Include | Equipment | 390 | 2022-03-24 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-24 12:01 | 2022-03-24 12:09 | 4431 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-03-24 | 35448 | keep | 0 | Mar | 2022 | 0.024143 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
CAGUAS | 2022-03-24 12:03 | 2022-03-24 17:31 | 9 | 005:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO XMR PARA REPARAR SECUNDARIA IMPACTO POR CAMION | C22032400071 | New_Event |  |  | Include | Wildlife | 328 | 2022-03-24 | 2952 | keep | 0 | Mar | 2022 | 0.0020106 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-03-24 12:10 | 2022-03-24 19:06 | 8 | 006:56 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE REEMPLAZO PARARRAYO | C22032400069 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 416 | 2022-03-24 | 3328 | keep | 0 | Mar | 2022 | 0.0022667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-24 12:30 | 2022-03-24 19:30 | 150 | 007:00 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA Y SE LLEVO CAJA PRIMARIA A SU SITIO MEDIANTE G.O.I. SJ-220324-02 | S22032400094 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 420 | 2022-03-24 | 63000 | keep | 0 | Mar | 2022 | 0.042909 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-24 12:30 | 2022-03-24 15:09 | 25 | 002:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-03-24 | 3975 | keep | 0 | Mar | 2022 | 0.0027074 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-24 12:59 | 2022-03-24 14:00 | 8 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | C22032400087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-03-24 | 488 | keep | 0 | Mar | 2022 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-03-24 13:02 | 2022-03-24 13:57 | 2343 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DESPARO DE INTERRUPTOR SE SECCIONALIZO PARA REPARAR Y LEVANTAR CONDUCTOR PRIMARIO Y SE REEMPLAZO CAJA QUEMADA. 80% EN SERVICIO | C22032400092 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2022-03-24 | 128865 | keep | 0 | Mar | 2022 | 0.087769 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
AGUADILLA | 2022-03-24 13:17 | 2022-03-24 19:40 | 5 | 006:23 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M22032400051 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 383 | 2022-03-24 | 1915 | keep | 0 | Mar | 2022 | 0.0013043 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-03-24 13:21 | 2022-03-24 13:22 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3025 | keep | 0 | Mar | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
MAYAGÃœEZ | 2022-03-24 13:38 | 2022-03-24 14:20 | 15 | 000:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER AVE CRUZO LINEAS | M22032400059 | New_Event |  |  | Include | Wildlife | 42 | 2022-03-24 | 630 | keep | 0 | Mar | 2022 | 0.00042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-03-24 13:47 | 2022-03-24 16:21 | 40 | 002:34 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-03-24 | 6160 | keep | 0 | Mar | 2022 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-24 13:48 | 2022-03-24 13:49 | 3902 | 000:01 | T | NO SE REPORTO CAUSA | RECCIERRE DE INTERRUPTOR | C22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3902 | keep | 0 | Mar | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2022-03-24 13:49 | 2022-03-24 21:29 | 100 | 007:40 | P | ESTRUCTURA AVERIADA | 1 X 30 Y 1 X 65 EN C/L SE REEMPLAZO POSTE PRIMARIO PARTIDO | C22032400108 | New_Event | Defective Pole | Include | Include | Equipment | 460 | 2022-03-24 | 46000 | keep | 0 | Mar | 2022 | 0.03133 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-24 13:52 | 2022-03-24 16:56 | 24 | 003:04 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN SU HACIA T181 AVERIA NUEVA DE T 181 A T182 @ T186 AVERIA VIEJA DE T187 @ T186 SE ENERGIZO UN SOLO TRANSFORMADOR | B22032400069 | New_Event | UG Cable Fault | Include | Include | Equipment | 184 | 2022-03-24 | 4416 | keep | 0 | Mar | 2022 | 0.0030077 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CANOVANAS | 2022-03-24 13:52 | 2022-03-24 15:00 | 7 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R22032400055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-03-24 | 476 | keep | 0 | Mar | 2022 | 0.0003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-24 13:57 | 2022-03-24 18:30 | 469 | 004:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y SE CERRO MACHETES | C22032400092 | Partial_restoration | Wire Down | Include | Include | Equipment | 273 | 2022-03-24 | 128037 | keep | 0 | Mar | 2022 | 0.087205 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-24 14:00 | 2022-03-24 14:50 | 22 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA AVE CRUZO LINEAS | M22032400070 | New_Event |  |  | Include | Wildlife | 50 | 2022-03-24 | 1100 | keep | 0 | Mar | 2022 | 0.0007492 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2022-03-24 14:05 | 2022-03-24 14:30 | 900 | 000:25 | P | TRANSFORMADOR AVERIADO | SE NORMALIZO CONVERTIDOR | M22032400057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 25 | 2022-03-24 | 22500 | keep | 0 | Mar | 2022 | 0.015325 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
MAYAGÃœEZ | 2022-03-24 14:08 | 2022-03-24 16:50 | 150 | 002:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22032400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-03-24 | 24300 | keep | 0 | Mar | 2022 | 0.016551 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-03-24 14:19 | 2022-03-24 14:20 | 3000 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22032400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-24 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2022-03-24 14:20 | 2022-03-24 17:21 | 251 | 003:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y 1 X 100 EN CORTES DE LINEA SE RETEZO LINEA PRIMARIA | B22032400081 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 181 | 2022-03-24 | 45431 | keep | 0 | Mar | 2022 | 0.030943 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
CAGUAS | 2022-03-24 14:24 | 2022-03-24 14:26 | 2789 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR TARDO DOS MINUTOS EN RECERRAR | C22032400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 5578 | keep | 0 | Mar | 2022 | 0.0037992 | 0.0018996 | Momentary | FALSE | FALSE | Not_TMED_Event | 2789
CAGUAS | 2022-03-24 14:24 | 2022-03-24 14:26 | 4634 | 000:02 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 41400 | C22032400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-24 | 9268 | keep | 0 | Mar | 2022 | 0.0063124 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-03-24 14:24 | 2022-03-24 14:26 | 1378 | 000:02 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 41400 | C22032400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-24 | 2756 | keep | 0 | Mar | 2022 | 0.0018771 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
CAGUAS | 2022-03-24 14:24 | 2022-03-24 14:26 | 1307 | 000:02 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 41400 | C22032400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-24 | 2614 | keep | 0 | Mar | 2022 | 0.0017804 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-03-24 14:24 | 2022-03-24 14:26 | 293 | 000:02 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 41400 | C22032400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-24 | 586 | keep | 0 | Mar | 2022 | 0.00039912 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
CANOVANAS | 2022-03-24 14:26 | 2022-03-24 16:38 | 50 | 002:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR | R22032400059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 132 | 2022-03-24 | 6600 | keep | 0 | Mar | 2022 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-24 14:33 | 2022-03-24 14:35 | 908 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B22032400076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 1816 | keep | 0 | Mar | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-03-24 14:46 | 2022-03-24 14:49 | 172 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO POR CONTROL LUEGO DE CORROBORAR EN REGIONES SJ & CRD | S22032400000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-03-24 | 516 | keep | 0 | Mar | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-03-24 14:49 | 2022-03-24 19:41 | 1 | 004:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | GOI SJ-220324-51 REMPLAZO DISCO PARTIDO MACHETE QUEMADO Y CERRO PUENTE | R22032400063 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 292 | 2022-03-24 | 292 | keep | 0 | Mar | 2022 | 0.00019888 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-24 14:49 | 2022-03-24 16:49 | 3 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REMPLAZAR CONEXIONES | B22032400079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2022-03-24 | 360 | keep | 0 | Mar | 2022 | 0.00024519 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-03-24 15:15 | 2022-03-24 16:55 | 1 | 001:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO PORTAFUSIBLES AVERIADO | A22032400108 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2022-03-24 | 100 | keep | 0 | Mar | 2022 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-24 15:25 | 2022-03-24 17:19 | 30 | 001:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032400086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-03-24 | 3420 | keep | 0 | Mar | 2022 | 0.0023293 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-24 15:27 | 2022-03-24 19:44 | 40 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | A22032400105 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2022-03-24 | 10280 | keep | 0 | Mar | 2022 | 0.0070017 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-24 15:28 | 2022-03-25 08:07 | 1 | 016:39 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR PROBLEMA DEL CLIENTE | C22032400133 | New_Event | Other Causes | Include | Include | Other | 999 | 2022-03-24 | 999 | keep | 0 | Mar | 2022 | 0.00068041 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-24 15:32 | 2022-03-25 12:23 | 6 | 020:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA MAL TIEMPO | C22032400135 | New_Event | Bad Weather | Include | Include | Weather | 1251 | 2022-03-24 | 7506 | keep | 0 | Mar | 2022 | 0.0051123 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-03-24 15:32 | 2022-03-24 19:20 | 100 | 003:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22032400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-03-24 | 22800 | keep | 0 | Mar | 2022 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-24 15:52 | 2022-03-24 15:53 | 844 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | S22032400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-24 | 844 | keep | 0 | Mar | 2022 | 0.00057484 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2022-03-24 15:53 | 2022-03-24 18:05 | 279 | 002:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PARA REPARAR/SUBIR ALAMBRE PRIMARIO PARTIDO EN EL SUELO | S22032400126 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 132 | 2022-03-24 | 36828 | keep | 0 | Mar | 2022 | 0.025083 | 0.00019003 | Sustained | FALSE | FALSE | Not_TMED_Event | 279
MAYAGÃœEZ | 2022-03-24 16:04 | 2022-03-24 17:33 | 25 | 001:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22032400081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-03-24 | 2225 | keep | 0 | Mar | 2022 | 0.0015154 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-03-24 16:08 | 2022-03-24 18:13 | 41 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L SE REPARO Y LEVANTO CONDUCTOR PRIMARIO | C22032400140 | New_Event | Wire Down | Include | Include | Equipment | 125 | 2022-03-24 | 5125 | keep | 0 | Mar | 2022 | 0.0034906 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
ARECIBO | 2022-03-24 16:27 | 2022-03-24 18:47 | 60 | 002:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22032400109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-03-24 | 8400 | keep | 0 | Mar | 2022 | 0.0057212 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-03-24 16:34 | 2022-03-24 17:44 | 6 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN PEDESTAL | B22032400098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-03-24 | 420 | keep | 0 | Mar | 2022 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-24 16:42 | 2022-03-25 11:04 | 35 | 018:22 | P | OTRAS CAUSAS | 1 X 30 EN SU. SE ENCONTRO PROBLEMAS HACIA LA COMPAÃ‘IA DE AGUA POTABLE PRIVADA | C22032500150 | New_Event | Other Causes | Include | Include | Other | 1102 | 2022-03-24 | 38570 | keep | 0 | Mar | 2022 | 0.02627 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 873 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 6111 | keep | 0 | Mar | 2022 | 0.0041622 | 0.0005946 | Sustained | FALSE | FALSE | Not_TMED_Event | 873
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 1261 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 8827 | keep | 0 | Mar | 2022 | 0.006012 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 2713 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 18991 | keep | 0 | Mar | 2022 | 0.012935 | 0.0018478 | Sustained | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 51 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 357 | keep | 0 | Mar | 2022 | 0.00024315 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 285 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 1995 | keep | 0 | Mar | 2022 | 0.0013588 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 1253 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 8771 | keep | 0 | Mar | 2022 | 0.0059739 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 1266 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 8862 | keep | 0 | Mar | 2022 | 0.0060359 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 411 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 2877 | keep | 0 | Mar | 2022 | 0.0019595 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 1444 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO CARGA POR 6014-02 | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 10108 | keep | 0 | Mar | 2022 | 0.0068845 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 3630 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO LLEVA LA CARGA DEL 6014-01 | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 25410 | keep | 0 | Mar | 2022 | 0.017307 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 863 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 6041 | keep | 0 | Mar | 2022 | 0.0041145 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 309 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 2163 | keep | 0 | Mar | 2022 | 0.0014732 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 176 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 1232 | keep | 0 | Mar | 2022 | 0.00083911 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-03-24 16:47 | 2022-03-24 16:54 | 974 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 11 DE AGOSTO | M22032400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2022-03-24 | 6818 | keep | 0 | Mar | 2022 | 0.0046437 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2022-03-24 16:57 | 2022-03-24 22:15 | 65 | 005:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | M22032400114 | New_Event | Bad Weather | Include | Include | Weather | 318 | 2022-03-24 | 20670 | keep | 0 | Mar | 2022 | 0.014078 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-03-24 17:07 | 2022-03-24 17:46 | 40 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN C/L MAL TIEMPO | R22032400070 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2022-03-24 | 1560 | keep | 0 | Mar | 2022 | 0.0010625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-24 17:19 | 2022-03-24 19:25 | 80 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22032400107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-03-24 | 10080 | keep | 0 | Mar | 2022 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-24 17:26 | 2022-03-25 14:45 | 30 | 021:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 RISER Y 1 X 50 RISER Y 1 X 65 RISER SE CERRO PUENTE ABIERTO | S22032400132 | New_Event | Wire Down | Include | Include | Equipment | 1279 | 2022-03-24 | 38370 | keep | 0 | Mar | 2022 | 0.026134 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-24 17:28 | 2022-03-24 18:35 | 12 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | B22032400108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2022-03-24 | 804 | keep | 0 | Mar | 2022 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-24 17:31 | 2022-03-25 18:00 | 44 | 024:29 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA LAZO DE T-186 | B22032400109 | New_Event | UG Cable Fault | Include | Include | Equipment | 1469 | 2022-03-24 | 64636 | keep | 0 | Mar | 2022 | 0.044023 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
FAJARDO | 2022-03-24 17:36 | 2022-03-24 18:57 | 7 | 001:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA AVERIADA | R22032400074 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2022-03-24 | 567 | keep | 0 | Mar | 2022 | 0.00038618 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-24 17:49 | 2022-03-24 19:00 | 6 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22032400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-03-24 | 426 | keep | 0 | Mar | 2022 | 0.00029015 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-03-24 17:51 | 2022-03-24 19:58 | 8 | 002:07 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | R22032400075 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 127 | 2022-03-24 | 1016 | keep | 0 | Mar | 2022 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-24 18:04 | 2022-03-24 18:05 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTROR CON RECIERRE EN ON Y NO RECERRO SE CERRO POR CONTROL SCADA | M22032400133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-24 | 3630 | keep | 0 | Mar | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
SAN JUAN | 2022-03-24 18:05 | 2022-03-24 18:07 | 844 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR EL MACHETE (SIN CARGA) PARA SECCIONALIZAR ALAMBRE PRIMARIO PARTIDO EN EL SUELO | S22032400126 | Additional_clients | Wire Down | Include | Include | Equipment | 2 | 2022-03-24 | 1688 | keep | 0 | Mar | 2022 | 0.0011497 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-24 18:05 | 2022-03-25 08:16 | 100 | 014:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO DISCO | C22032400176 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 851 | 2022-03-24 | 85100 | keep | 0 | Mar | 2022 | 0.057961 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-24 18:07 | 2022-03-25 00:19 | 279 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARO Y SUBIO ALAMBRE PRIMARIO PARTIDO EN EL SUELO Y SE NORMALIZO LA CARGA | S22032400126 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 372 | 2022-03-24 | 103788 | keep | 0 | Mar | 2022 | 0.07069 | 0.00019003 | Sustained | FALSE | FALSE | Not_TMED_Event | 279
MAYAGÃœEZ | 2022-03-24 18:17 | 2022-03-24 20:36 | 990 | 002:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO BAJANTE DE TIERRA SOBRE LINEAS PRIMARIAS SE CERRO INTERRUPTOR | M22032400137 | New_Event | Wire Down | Include | Include | Equipment | 139 | 2022-03-24 | 137610 | keep | 0 | Mar | 2022 | 0.093726 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2022-03-24 18:26 | 2022-03-25 03:57 | 100 | 009:31 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22032400141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 571 | 2022-03-24 | 57100 | keep | 0 | Mar | 2022 | 0.038891 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-24 18:31 | 2022-03-25 10:34 | 1 | 016:03 | P | NO SE REPORTO CAUSA | 2 X 30 EN BANCO DE TRANSFORMADOR | S22032400142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 963 | 2022-03-24 | 963 | keep | 0 | Mar | 2022 | 0.00065589 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-24 19:05 | 2022-03-24 22:38 | 30 | 003:33 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22032400150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-03-24 | 6390 | keep | 0 | Mar | 2022 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-24 19:16 | 2022-03-24 21:33 | 40 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTE VIENTO | A22032400119 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2022-03-24 | 5480 | keep | 0 | Mar | 2022 | 0.0037324 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-03-24 19:26 | 2022-03-25 10:37 | 3 | 015:11 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA SE DESGANCHO EN LINEA SECUNDARIAS | M22032400171 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 911 | 2022-03-24 | 2733 | keep | 0 | Mar | 2022 | 0.0018614 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-24 20:01 | 2022-03-25 09:45 | 150 | 013:44 | P | DESGANCHE | SE REPARO PUENTE PRIMARIO SE RETIRO BAMBUS SOBRE LAS LINEAS | P22032400147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 824 | 2022-03-24 | 123600 | keep | 0 | Mar | 2022 | 0.084183 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-03-24 21:06 | 2022-03-24 23:39 | 206 | 002:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 1 X 50 Y 1 X 65 EN C/L'S CRUCE POR REPTIL | C22032400249 | New_Event |  |  | Include | Wildlife | 153 | 2022-03-24 | 31518 | keep | 0 | Mar | 2022 | 0.021467 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
CAGUAS | 2022-03-24 21:09 | 2022-03-25 14:10 | 300 | 017:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C22032400251 | New_Event | Wire Down | Include | Include | Equipment | 1021 | 2022-03-24 | 306300 | keep | 0 | Mar | 2022 | 0.20862 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2022-03-24 21:12 | 2022-03-25 09:14 | 10 | 012:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE | P22032400162 | New_Event |  |  | Include | Wildlife | 722 | 2022-03-24 | 7220 | keep | 0 | Mar | 2022 | 0.0049175 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-24 22:19 | 2022-03-24 22:21 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R22032400078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-24 | 2 | keep | 0 | Mar | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-03-24 22:47 | 2022-03-24 22:48 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE BKR 8510 Y DISPARO DEL BKR 4870 | C22032400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 2725 | keep | 0 | Mar | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-24 22:47 | 2022-03-24 22:48 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE BKR 8510 Y DISPARO DEL BKR 4870 | C22032400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-24 22:47 | 2022-03-24 22:48 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE BKR 8510 Y DISPARO DEL BKR 4870 | C22032400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 1437 | keep | 0 | Mar | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-03-24 22:47 | 2022-03-24 22:48 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE BKR 8510 Y DISPARO DEL BKR 4870 | C22032400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 2565 | keep | 0 | Mar | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-03-24 22:47 | 2022-03-24 22:48 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE BKR 8510 Y DISPARO DEL BKR 4870 | C22032400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 3565 | keep | 0 | Mar | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-03-24 22:47 | 2022-03-24 22:48 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22032400166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 2751 | keep | 0 | Mar | 2022 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-03-24 22:47 | 2022-03-24 22:48 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22032400166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 576 | keep | 0 | Mar | 2022 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-03-24 22:47 | 2022-03-24 22:48 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22032400166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 2584 | keep | 0 | Mar | 2022 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-03-24 22:47 | 2022-03-24 22:48 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22032400166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 1606 | keep | 0 | Mar | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-03-24 22:47 | 2022-03-24 22:48 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22032400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 4035 | keep | 0 | Mar | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-03-24 22:47 | 2022-03-24 22:48 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | P22032400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-24 | 3718 | keep | 0 | Mar | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-03-24 23:45 | 2022-03-25 01:14 | 56 | 001:29 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22032400130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-03-24 | 4984 | keep | 0 | Mar | 2022 | 0.0033946 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-03-25 01:28 | 2022-03-25 03:00 | 1 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22032500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-03-25 | 92 | keep | 0 | Mar | 2022 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-25 03:46 | 2022-03-25 03:47 | 715 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1709-3, 50% POR 1909-07, LLEVA 1709-05 | S22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 715 | keep | 0 | Mar | 2022 | 0.00048698 | 0.00048698 | Momentary | FALSE | FALSE | Not_TMED_Event | 715
BAYAMON | 2022-03-25 03:46 | 2022-03-25 03:47 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1709-3 Y LLEVA 1709-05 | S22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 2364 | keep | 0 | Mar | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
MAYAGÃœEZ | 2022-03-25 04:22 | 2022-03-25 14:51 | 60 | 010:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M22032500001 | New_Event | Wire Down | Include | Include | Equipment | 629 | 2022-03-25 | 37740 | keep | 0 | Mar | 2022 | 0.025705 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-25 04:42 | 2022-03-25 04:44 | 1746 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA | B22032500000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-03-25 | 3492 | keep | 0 | Mar | 2022 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-03-25 04:44 | 2022-03-25 07:19 | 250 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 125 EN SU-4 HACIA RISER 1 X 100 EN CL SE CERRO PUENTE ABIERTO | B22032500006 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 155 | 2022-03-25 | 38750 | keep | 0 | Mar | 2022 | 0.026392 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2022-03-25 06:03 | 2022-03-25 06:04 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 1342 | keep | 0 | Mar | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BAYAMON | 2022-03-25 06:19 | 2022-03-25 10:25 | 30 | 004:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L ROEDOR | S22032500003 | New_Event |  |  | Include | Wildlife | 246 | 2022-03-25 | 7380 | keep | 0 | Mar | 2022 | 0.0050265 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-25 06:38 | 2022-03-25 12:46 | 100 | 006:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22032500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2022-03-25 | 36800 | keep | 0 | Mar | 2022 | 0.025064 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-25 06:57 | 2022-03-25 06:58 | 473 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C22032500018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-03-25 | 473 | keep | 0 | Mar | 2022 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
CAGUAS | 2022-03-25 06:58 | 2022-03-25 13:25 | 29 | 6:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO LLUVIAS | C22032500020 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 387 | 2022-03-25 | 11223 | keep | 0 | Mar | 2022 | 0.0076439 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2022-03-25 07:19 | 2022-03-25 07:20 | 1746 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22032500000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-03-25 | 1746 | keep | 0 | Mar | 2022 | 0.0011892 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-25 07:20 | 2022-03-25 07:25 | 250 | 000:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 125 EN SU-4 HACIA RISER 1 X 100 EN CL SE CERRO PUENTE ABIERTO | B22032500006 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 5 | 2022-03-25 | 1250 | keep | 0 | Mar | 2022 | 0.00085137 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-03-25 07:26 | 2022-03-25 11:08 | 100 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22032500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2022-03-25 | 22200 | keep | 0 | Mar | 2022 | 0.01512 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-25 08:07 | 2022-03-25 10:23 | 60 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 30 EN CORTE DE LINEA | R22032500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-03-25 | 8160 | keep | 0 | Mar | 2022 | 0.0055577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-03-25 08:22 | 2022-03-25 09:32 | 1 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | P22032500005 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2022-03-25 | 70 | keep | 0 | Mar | 2022 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-03-25 08:44 | 2022-03-25 08:45 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 1894 | keep | 0 | Mar | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
PONCE | 2022-03-25 08:52 | 2022-03-25 12:31 | 115 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P22032500008 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2022-03-25 | 25185 | keep | 0 | Mar | 2022 | 0.017153 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
PONCE | 2022-03-25 08:54 | 2022-03-25 08:55 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 3114 | keep | 0 | Mar | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2022-03-25 08:56 | 2022-03-25 15:28 | 20 | 006:32 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22032500027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-03-25 | 7840 | keep | 0 | Mar | 2022 | 0.0053398 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-25 09:19 | 2022-03-25 11:04 | 50 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO LLUVIA | S22032500018 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-03-25 | 5250 | keep | 0 | Mar | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-25 09:40 | 2022-03-25 16:41 | 8 | 007:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22032500034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 421 | 2022-03-25 | 3368 | keep | 0 | Mar | 2022 | 0.0022939 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-25 09:49 | 2022-03-25 09:50 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032500018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 2163 | keep | 0 | Mar | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
CAGUAS | 2022-03-25 09:51 | 2022-03-25 09:52 | 1271 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22032500065 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-25 | 1271 | keep | 0 | Mar | 2022 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2022-03-25 09:53 | 2022-03-25 09:54 | 2608 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22032500000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-25 | 2608 | keep | 0 | Mar | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2022-03-25 09:54 | 2022-03-25 15:58 | 83 | 006:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C22032500046 | 1st_after_momentary |  |  | Include | Wildlife | 364 | 2022-03-25 | 30212 | keep | 0 | Mar | 2022 | 0.020577 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
CAGUAS | 2022-03-25 09:58 | 2022-03-25 09:59 | 4634 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C22032500068 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-03-25 | 4634 | keep | 0 | Mar | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
AGUADILLA | 2022-03-25 10:06 | 2022-03-25 14:00 | 7 | 003:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M22032500023 | New_Event |  |  | Include | Wildlife | 234 | 2022-03-25 | 1638 | keep | 0 | Mar | 2022 | 0.0011156 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-25 10:12 | 2022-03-26 13:20 | 10 | 027:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | M22032500090 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1628 | 2022-03-25 | 16280 | keep | 0 | Mar | 2022 | 0.011088 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-03-25 10:18 | 2022-03-25 20:04 | 20 | 009:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE SE RETIRO IGUANA DE LAS LINEAS Y SE CERRO PUENTE PRIMARIO | M22032500027 | New_Event | Wire Down | Include | Include | Equipment | 586 | 2022-03-25 | 11720 | keep | 0 | Mar | 2022 | 0.0079824 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-25 10:26 | 2022-03-25 15:08 | 100 | 004:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER Y CAJA PRIMARIA | S22032500028 | New_Event | Cutout Failure | Include | Include | Equipment | 282 | 2022-03-25 | 28200 | keep | 0 | Mar | 2022 | 0.019207 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-25 10:34 | 2022-03-25 18:47 | 25 | 008:13 | P | HERRAJE ROTO O PODRIDO | 2 X 15 EN CORTE DE LINEA SE REMPLAZO CRUCETA | M22032500031 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 493 | 2022-03-25 | 12325 | keep | 0 | Mar | 2022 | 0.0083945 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-03-25 10:34 | 2022-03-25 17:00 | 200 | 006:26 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22032500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2022-03-25 | 77200 | keep | 0 | Mar | 2022 | 0.052581 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-03-25 10:39 | 2022-03-25 16:58 | 15 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22032500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2022-03-25 | 5685 | keep | 0 | Mar | 2022 | 0.003872 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-03-25 11:00 | 2022-03-25 14:33 | 16 | 003:33 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR | R22032500011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2022-03-25 | 3408 | keep | 0 | Mar | 2022 | 0.0023212 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-03-25 11:15 | 2022-03-25 12:20 | 8 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22032500015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-03-25 | 520 | keep | 0 | Mar | 2022 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-25 11:19 | 2022-03-25 12:29 | 2566 | 001:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO POR SCADA. ADEMAS LLEVA EL 5% 1115-05. | S22032500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-03-25 | 179620 | keep | 0 | Mar | 2022 | 0.12234 | 0.0017477 | Sustained | FALSE | FALSE | Not_TMED_Event | 2566
SAN JUAN | 2022-03-25 11:19 | 2022-03-25 12:30 | 12 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22032500021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-03-25 | 852 | keep | 0 | Mar | 2022 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-25 11:19 | 2022-03-25 13:05 | 43 | 001:46 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1111-01. SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO POR SCADA. LLEVANDO EL 5% DEL 1115-05. | S22032500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-03-25 | 4558 | keep | 0 | Mar | 2022 | 0.0031044 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
UTUADO | 2022-03-25 11:26 | 2022-03-25 16:14 | 20 | 004:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22032500017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-03-25 | 5760 | keep | 0 | Mar | 2022 | 0.0039231 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-25 11:38 | 2022-03-25 12:37 | 15 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO | B22032500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-03-25 | 885 | keep | 0 | Mar | 2022 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-25 11:43 | 2022-03-25 19:37 | 1 | 007:54 | P | DESGANCHE | 1 X 65 EN RISER SE RETIRO RAMA QUE ESTABA CRUZANDO EN EL RISER | M22032500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 474 | 2022-03-25 | 474 | keep | 0 | Mar | 2022 | 0.00032284 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-25 11:49 | 2022-03-25 11:50 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 3458 | keep | 0 | Mar | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2022-03-25 12:01 | 2022-03-25 16:07 | 8 | 004:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE DIERON CONEXIONES DE VIVO/NEUTRAL EN SECUNDARIA | R22032500015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 246 | 2022-03-25 | 1968 | keep | 0 | Mar | 2022 | 0.0013404 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-25 12:07 | 2022-03-25 14:25 | 100 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-13A | B22032500051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-03-25 | 13800 | keep | 0 | Mar | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-25 12:09 | 2022-03-25 19:12 | 24 | 007:03 | P | DESGANCHE | 2 X 65 EN C/L | S22032500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2022-03-25 | 10152 | keep | 0 | Mar | 2022 | 0.0069145 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CANOVANAS | 2022-03-25 12:09 | 2022-03-25 13:37 | 60 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22032500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-03-25 | 5280 | keep | 0 | Mar | 2022 | 0.0035962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-25 12:11 | 2022-03-25 13:56 | 12 | 001:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 25KVA Y SE REMPLAZO CAJA PRIMARIA | S22032400141 | New_Event | Service Transformer Failure | Include | Include | Equipment | 105 | 2022-03-25 | 1260 | keep | 0 | Mar | 2022 | 0.00085818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-25 12:29 | 2022-03-25 13:03 | 2052 | 000:34 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO POR TRAMO ENTRA UN 20% | S22032500042 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 34 | 2022-03-25 | 69768 | keep | 0 | Mar | 2022 | 0.047519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-25 12:36 | 2022-03-25 12:37 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 2163 | keep | 0 | Mar | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
HUMACAO | 2022-03-25 12:37 | 2022-03-25 16:11 | 90 | 003:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22032500108 | New_Event |  |  | Include | Wildlife | 214 | 2022-03-25 | 19260 | keep | 0 | Mar | 2022 | 0.013118 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2022-03-25 12:42 | 2022-03-25 18:46 | 10 | 006:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | A22032500023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 364 | 2022-03-25 | 3640 | keep | 0 | Mar | 2022 | 0.0024792 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-03-25 12:50 | 2022-03-25 14:50 | 50 | 002:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P22032500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-03-25 | 6000 | keep | 0 | Mar | 2022 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-25 13:03 | 2022-03-25 13:04 | 2044 | 000:01 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO HACIA CAJAS SECAS | S22032500042 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 2044 | keep | 0 | Mar | 2022 | 0.0013922 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-25 13:04 | 2022-03-25 13:05 | 1155 | 000:01 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO HACIA VARIOS DISPOSITIVOS SOTERRADOS | S22032500042 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 1155 | keep | 0 | Mar | 2022 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
BAYAMON | 2022-03-25 13:10 | 2022-03-25 14:10 | 8 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTES Y CONEXIONES | B22032500055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-03-25 | 480 | keep | 0 | Mar | 2022 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-25 13:11 | 2022-03-25 15:44 | 93 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA PRIMARIA | S22032500085 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-03-25 | 14229 | keep | 0 | Mar | 2022 | 0.0096913 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
CANOVANAS | 2022-03-25 13:11 | 2022-03-25 13:14 | 4188 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR TRATANDO DE NORMALIZAR CARGA DEL 2404-05 | R22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-25 | 12564 | keep | 0 | Mar | 2022 | 0.0085573 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CAGUAS | 2022-03-25 13:12 | 2022-03-25 17:07 | 1 | 003:55 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZARON PORTAFUSIBLES Y TERMINACIONES QUEMADAS DEL SU8 HACIA CLIENTE | C22032500114 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 235 | 2022-03-25 | 235 | keep | 0 | Mar | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-25 13:15 | 2022-03-25 14:10 | 4 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO LINEA SECUNDARIA DEL SUELO | C22032500115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-03-25 | 220 | keep | 0 | Mar | 2022 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-03-25 13:39 | 2022-03-25 16:20 | 200 | 002:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22032500126 | New_Event | Cutout Failure | Include | Include | Equipment | 161 | 2022-03-25 | 32200 | keep | 0 | Mar | 2022 | 0.021931 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-25 13:43 | 2022-03-25 14:40 | 8 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22032400116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-03-25 | 456 | keep | 0 | Mar | 2022 | 0.00031058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-25 13:43 | 2022-03-25 18:00 | 100 | 004:17 | P | PROTECCION DEFECTUOSA | 1 X 100 EN RISER | B22032500056 | New_Event | Protection Miscoordination | Include | Include | Other | 257 | 2022-03-25 | 25700 | keep | 0 | Mar | 2022 | 0.017504 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-25 13:47 | 2022-03-25 15:01 | 8 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22032500091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2022-03-25 | 592 | keep | 0 | Mar | 2022 | 0.00040321 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-25 13:58 | 2022-03-25 19:19 | 10 | 005:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P22032500047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 321 | 2022-03-25 | 3210 | keep | 0 | Mar | 2022 | 0.0021863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-25 14:01 | 2022-03-25 15:19 | 918 | 001:18 | T | NO SE REPORTO CAUSA | DISPARO SE CERO LOCALMENTE | C22032500140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-03-25 | 71604 | keep | 0 | Mar | 2022 | 0.048769 | 0.00062525 | Sustained | FALSE | FALSE | Not_TMED_Event | 918
UTUADO | 2022-03-25 14:13 | 2022-03-25 16:40 | 30 | 002:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032500027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-03-25 | 4410 | keep | 0 | Mar | 2022 | 0.0030036 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-25 14:35 | 2022-03-25 15:34 | 100 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22032500164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-03-25 | 5900 | keep | 0 | Mar | 2022 | 0.0040185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-25 15:25 | 2022-03-25 15:26 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22032500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 4641 | keep | 0 | Mar | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
VEGA BAJA | 2022-03-25 15:36 | 2022-03-25 18:24 | 42 | 002:48 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22032500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-03-25 | 7056 | keep | 0 | Mar | 2022 | 0.0048058 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2022-03-25 15:39 | 2022-03-25 19:08 | 12 | 003:29 | P | DESGANCHE | 1 X 30 EN XMR DESGANCHE | S22032500109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-03-25 | 2508 | keep | 0 | Mar | 2022 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-25 15:49 | 2022-03-25 16:16 | 6 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONNECTORES SULFATADOS | C22032500195 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-03-25 | 162 | keep | 0 | Mar | 2022 | 0.00011034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-25 15:55 | 2022-03-25 19:18 | 200 | 003:23 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50, 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE LIMPIO CONTAMINACION EN PISTOLA | C22032500201 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 203 | 2022-03-25 | 40600 | keep | 0 | Mar | 2022 | 0.027652 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-03-25 15:58 | 2022-03-25 18:39 | 11 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BAJANTES SECUNDARIOS/SE AJUSTO BUSHING SECUNDARIO EN XMER (NO FUNDIO) | R22032500022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2022-03-25 | 1771 | keep | 0 | Mar | 2022 | 0.0012062 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-03-25 16:24 | 2022-03-25 20:07 | 12 | 003:43 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR 12 CLIENTES | S22032500084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-03-25 | 2676 | keep | 0 | Mar | 2022 | 0.0018226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-25 16:33 | 2022-03-25 16:37 | 1000 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 80% POR EL 1424-08 | S22032500116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-25 | 4000 | keep | 0 | Mar | 2022 | 0.0027244 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-03-25 16:33 | 2022-03-25 16:37 | 278 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1424-08 | S22032500116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-25 | 1112 | keep | 0 | Mar | 2022 | 0.00075738 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2022-03-25 16:33 | 2022-03-25 16:37 | 9 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 1348-07, 80% DEL 1348-06 | S22032500116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-03-25 | 36 | keep | 0 | Mar | 2022 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-03-25 16:33 | 2022-03-25 16:34 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 5062 | keep | 0 | Mar | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2022-03-25 16:47 | 2022-03-25 17:26 | 10 | 000:39 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA REPARAR BARRA DE PEDESTAL | S22032500118 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 39 | 2022-03-25 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-25 16:56 | 2022-03-25 16:57 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 527 | keep | 0 | Mar | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-03-25 16:58 | 2022-03-25 18:18 | 4 | 001:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO PARTIDO | C22032500208 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 80 | 2022-03-25 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-03-25 17:03 | 2022-03-26 08:37 | 8 | 015:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22032500209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 934 | 2022-03-25 | 7472 | keep | 0 | Mar | 2022 | 0.0050891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-25 17:11 | 2022-03-25 19:07 | 70 | 001:56 | P | OTRAS CAUSAS | 1 X 40 EN AEREO PROVISIONAL 70 CLIENTES AVERIA NUEVA T-7 @ T-8, T- 8 QUEDO FUERA 10 CLIENTES. | B22032500077 | New_Event | Other Causes | Include | Include | Other | 116 | 2022-03-25 | 8120 | keep | 0 | Mar | 2022 | 0.0055305 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-03-25 17:30 | 2022-03-25 18:07 | 36 | 000:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22032500186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-03-25 | 1332 | keep | 0 | Mar | 2022 | 0.00090722 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
UTUADO | 2022-03-25 17:37 | 2022-03-25 19:27 | 10 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | A22032500036 | New_Event |  |  | Include | Wildlife | 110 | 2022-03-25 | 1100 | keep | 0 | Mar | 2022 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-25 17:38 | 2022-03-25 18:12 | 7621 | 000:34 | T | CABLE SOTERRADO AVERIADO | SE CERRO AMARRE CONTRA ALIMENTADOR 2402-03 - CARR. PR-3 INTERSECCION CARR. PR-874 MEDIANTE SWITCHING-FORM SJ-220319-50 POR SALIDA SOTERRADA AVERIADA | R22032500025 | New_Event | UG Cable Fault | Include | Include | Equipment | 34 | 2022-03-25 | 259114 | keep | 0 | Mar | 2022 | 0.17648 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
AGUADILLA | 2022-03-25 18:42 | 2022-03-25 23:00 | 30 | 004:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032500080 | New_Event | Bad Weather | Include | Include | Weather | 258 | 2022-03-25 | 7740 | keep | 0 | Mar | 2022 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-25 18:56 | 2022-03-25 18:57 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 308 | keep | 0 | Mar | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CAGUAS | 2022-03-25 19:00 | 2022-03-26 12:28 | 45 | 017:28 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22032500219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2022-03-25 | 47160 | keep | 0 | Mar | 2022 | 0.03212 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-25 19:07 | 2022-03-26 12:00 | 10 | 016:53 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO PARA ENERGIZAR T-8 | B22032500079 | New_Event | UG Cable Fault | Include | Include | Equipment | 1013 | 2022-03-25 | 10130 | keep | 0 | Mar | 2022 | 0.0068995 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-25 19:37 | 2022-03-25 22:54 | 100 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C22032500223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-03-25 | 19700 | keep | 0 | Mar | 2022 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-25 19:52 | 2022-03-25 21:23 | 10 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA (NO FUNDIO) | R22032500069 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2022-03-25 | 910 | keep | 0 | Mar | 2022 | 0.0006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-25 20:01 | 2022-03-26 10:49 | 14 | 014:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22032500225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 888 | 2022-03-25 | 12432 | keep | 0 | Mar | 2022 | 0.0084674 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2022-03-25 21:44 | 2022-03-26 07:00 | 20 | 009:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22032500236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 556 | 2022-03-25 | 11120 | keep | 0 | Mar | 2022 | 0.0075738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-25 22:16 | 2022-03-26 08:22 | 30 | 010:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22032500072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 606 | 2022-03-25 | 18180 | keep | 0 | Mar | 2022 | 0.012382 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-25 23:15 | 2022-03-25 23:16 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1206-01 PARTE POR 1201-02. LLEVA 1206-02 | S22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-03-25 23:15 | 2022-03-25 23:16 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1206-01 LLEVA 1206-02 | S22032500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-25 | 733 | keep | 0 | Mar | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
UTUADO | 2022-03-26 05:45 | 2022-03-26 09:45 | 54 | 004:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-03-26 | 12960 | keep | 0 | Mar | 2022 | 0.008827 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
YAUCO | 2022-03-26 06:07 | 2022-03-26 06:08 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 3973 | keep | 0 | Mar | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
BAYAMON | 2022-03-26 06:22 | 2022-03-26 09:10 | 80 | 002:48 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B22032600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-03-26 | 13440 | keep | 0 | Mar | 2022 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-03-26 06:22 | 2022-03-26 08:22 | 50 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22032600002 | New_Event |  |  | Include | Wildlife | 120 | 2022-03-26 | 6000 | keep | 0 | Mar | 2022 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-26 06:55 | 2022-03-26 16:02 | 4 | 009:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2022-03-26 | 2188 | keep | 0 | Mar | 2022 | 0.0014902 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-03-26 06:56 | 2022-03-26 08:48 | 248 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22032600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-03-26 | 27776 | keep | 0 | Mar | 2022 | 0.018918 | 0.00016891 | Sustained | FALSE | FALSE | Not_TMED_Event | 248
SAN JUAN | 2022-03-26 07:39 | 2022-03-26 08:45 | 10 | 001:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO AISLADOR | R22032600002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 66 | 2022-03-26 | 660 | keep | 0 | Mar | 2022 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-26 07:43 | 2022-03-26 08:17 | 80 | 000:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22032600006 | New_Event | Cutout Failure | Include | Include | Equipment | 34 | 2022-03-26 | 2720 | keep | 0 | Mar | 2022 | 0.0018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-03-26 07:50 | 2022-03-26 10:00 | 48 | 002:10 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA DE EMERGENCIA POR POSTE EN LLAMAS. EL FUEGO APAGADO, SE CORTO PERILLA DEL POSTE Y SE CERRO CORTE DE LINEA | P22032600007 | New_Event | Defective Pole | Include | Include | Equipment | 130 | 2022-03-26 | 6240 | keep | 0 | Mar | 2022 | 0.00425 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
PONCE | 2022-03-26 07:53 | 2022-03-26 11:15 | 100 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P22032600006 | New_Event |  |  | Include | Wildlife | 202 | 2022-03-26 | 20200 | keep | 0 | Mar | 2022 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-26 07:57 | 2022-03-26 07:58 | 514 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1520-05 | S22032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 514 | keep | 0 | Mar | 2022 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-03-26 07:57 | 2022-03-26 07:58 | 752 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1520-05 | S22032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 752 | keep | 0 | Mar | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-03-26 07:57 | 2022-03-26 07:58 | 68 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S22032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 68 | keep | 0 | Mar | 2022 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2022-03-26 08:14 | 2022-03-26 08:15 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 8007-04 | A22032600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-26 08:14 | 2022-03-26 08:15 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DEL 8007-03 | A22032600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2022-03-26 08:15 | 2022-03-26 08:16 | 2228 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 8007-04 | A22032600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 2228 | keep | 0 | Mar | 2022 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2022-03-26 08:15 | 2022-03-26 08:16 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DEL 8007-03 | A22032600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 438 | keep | 0 | Mar | 2022 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
CAGUAS | 2022-03-26 08:17 | 2022-03-26 11:32 | 25 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22032600024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2022-03-26 | 4875 | keep | 0 | Mar | 2022 | 0.0033203 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-03-26 08:25 | 2022-03-26 14:48 | 25 | 006:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22032600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-03-26 | 9575 | keep | 0 | Mar | 2022 | 0.0065215 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-03-26 08:27 | 2022-03-26 11:40 | 15 | 003:13 | P | DESGANCHE | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR SE RETIRO RAMAS SOBRE TRANSFORMADOR | A22032600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-03-26 | 2895 | keep | 0 | Mar | 2022 | 0.0019718 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-26 08:34 | 2022-03-26 12:10 | 156 | 003:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO FASES A TIERRA | A22032600011 | New_Event |  |  | Include | Wildlife | 216 | 2022-03-26 | 33696 | keep | 0 | Mar | 2022 | 0.02295 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
CANOVANAS | 2022-03-26 08:40 | 2022-03-26 08:41 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R22032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 1894 | keep | 0 | Mar | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
HUMACAO | 2022-03-26 08:45 | 2022-03-26 13:04 | 8 | 004:19 | P | HERRAJE ROTO O PODRIDO | 1 X 30 EN XMR SE REEMPLAZO HERRAJE | C22032600029 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 259 | 2022-03-26 | 2072 | keep | 0 | Mar | 2022 | 0.0014112 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-03-26 08:49 | 2022-03-26 08:50 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | C22032600000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-26 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-26 08:50 | 2022-03-26 11:09 | 112 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1X 40 Y 1 X 30 EN C/L CRUCE POR AVE | C22032600034 | 1st_after_momentary |  |  | Include | Wildlife | 139 | 2022-03-26 | 15568 | keep | 0 | Mar | 2022 | 0.010603 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
SAN JUAN | 2022-03-26 08:51 | 2022-03-26 09:58 | 15 | 001:07 | P | SECUNDARIA/DESGANCHE | SE REPARO BAJANTE SECUNDARIO Y SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | S22032500102 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 67 | 2022-03-26 | 1005 | keep | 0 | Mar | 2022 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-26 08:54 | 2022-03-26 12:14 | 10 | 003:20 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO | C22032600031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 200 | 2022-03-26 | 2000 | keep | 0 | Mar | 2022 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-26 09:00 | 2022-03-26 09:35 | 10 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22032500075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-03-26 | 350 | keep | 0 | Mar | 2022 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-26 09:00 | 2022-03-26 09:40 | 15 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22032500080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-03-26 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-26 09:05 | 2022-03-26 10:45 | 120 | 001:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-03-26 | 12000 | keep | 0 | Mar | 2022 | 0.0081731 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2022-03-26 09:14 | 2022-03-26 14:35 | 25 | 005:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22032600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2022-03-26 | 8025 | keep | 0 | Mar | 2022 | 0.0054658 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-03-26 09:15 | 2022-03-26 09:16 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 5018-04 | P22032600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 752 | keep | 0 | Mar | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2022-03-26 09:15 | 2022-03-26 09:16 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 5011-04 | P22032600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 2696 | keep | 0 | Mar | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
HUMACAO | 2022-03-26 09:50 | 2022-03-26 14:39 | 60 | 004:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22032600043 | New_Event |  |  | Include | Wildlife | 289 | 2022-03-26 | 17340 | keep | 0 | Mar | 2022 | 0.01181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-03-26 09:52 | 2022-03-26 09:53 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22032600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-26 | 1382 | keep | 0 | Mar | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-03-26 09:52 | 2022-03-26 09:53 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22032600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-26 | 654 | keep | 0 | Mar | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
FAJARDO | 2022-03-26 10:25 | 2022-03-26 11:30 | 70 | 001:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | R22032600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-03-26 | 4550 | keep | 0 | Mar | 2022 | 0.003099 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-03-26 11:09 | 2022-03-26 11:10 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | C22032600000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-26 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-26 11:10 | 2022-03-26 12:25 | 112 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1X 40 Y 1 X 30 EN C/L CRUCE POR AVE | C22032600034 | 1st_after_momentary |  |  | Include | Wildlife | 75 | 2022-03-26 | 8400 | keep | 0 | Mar | 2022 | 0.0057212 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
PONCE | 2022-03-26 11:17 | 2022-03-26 16:37 | 8 | 005:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO SECUNDARIA Y SE REMPLAZARON 3 POSTES SECUNDARIOS | P22032600014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 320 | 2022-03-26 | 2560 | keep | 0 | Mar | 2022 | 0.0017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-03-26 11:17 | 2022-03-26 18:14 | 250 | 006:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2X80 EN C/L (POR AVE EN LA LINEA) | C22032600048 | New_Event |  |  | Include | Wildlife | 417 | 2022-03-26 | 104250 | keep | 0 | Mar | 2022 | 0.071004 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2022-03-26 11:32 | 2022-03-26 13:01 | 32 | 001:29 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO BAMBUA SOBRE LINEA | C22032600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-03-26 | 2848 | keep | 0 | Mar | 2022 | 0.0019398 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1924 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 3848 | keep | 0 | Mar | 2022 | 0.0026209 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 968 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 1936 | keep | 0 | Mar | 2022 | 0.0013186 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 680 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 1360 | keep | 0 | Mar | 2022 | 0.00092629 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2246 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4492 | keep | 0 | Mar | 2022 | 0.0030595 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2011 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4022 | keep | 0 | Mar | 2022 | 0.0027394 | 0.0013697 | Momentary | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 339 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 678 | keep | 0 | Mar | 2022 | 0.00046178 | 0.00023089 | Momentary | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2470 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4940 | keep | 0 | Mar | 2022 | 0.0033646 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1182 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 2364 | keep | 0 | Mar | 2022 | 0.0016101 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2340 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4680 | keep | 0 | Mar | 2022 | 0.0031875 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1637 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 3274 | keep | 0 | Mar | 2022 | 0.0022299 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1475 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700, AFECTANDO LAS SUBESTACIONES 5501, 5305, 5304, 5602, 5401, 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 2950 | keep | 0 | Mar | 2022 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 661 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700, AFECTANDO LAS SUBESTACIONES 5501, 5305, 5304, 5602, 5401, 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 1322 | keep | 0 | Mar | 2022 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 502 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 1004 | keep | 0 | Mar | 2022 | 0.00068382 | 0.00034191 | Momentary | FALSE | FALSE | Not_TMED_Event | 502
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2747 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 5494 | keep | 0 | Mar | 2022 | 0.0037419 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1587 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 3174 | keep | 0 | Mar | 2022 | 0.0021618 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2671 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 5342 | keep | 0 | Mar | 2022 | 0.0036384 | 0.0018192 | Momentary | FALSE | FALSE | Not_TMED_Event | 2671
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 3138 | keep | 0 | Mar | 2022 | 0.0021373 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2309 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4618 | keep | 0 | Mar | 2022 | 0.0031453 | 0.0015726 | Momentary | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2179 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4358 | keep | 0 | Mar | 2022 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2440 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4880 | keep | 0 | Mar | 2022 | 0.0033237 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 1352 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 2704 | keep | 0 | Mar | 2022 | 0.0018417 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 3973 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 7946 | keep | 0 | Mar | 2022 | 0.005412 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-03-26 11:34 | 2022-03-26 11:36 | 2484 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 AFECTANDO LAS SUBESTACIONES 5501 5305 5304 5602 5401 5303 Y 5302 | P22032600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 4968 | keep | 0 | Mar | 2022 | 0.0033837 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2022-03-26 11:34 | 2022-03-26 11:36 | 281 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22032500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 562 | keep | 0 | Mar | 2022 | 0.00038278 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-03-26 11:34 | 2022-03-26 11:36 | 1252 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22032500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 2504 | keep | 0 | Mar | 2022 | 0.0017055 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-03-26 11:34 | 2022-03-26 11:36 | 595 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22032500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 1190 | keep | 0 | Mar | 2022 | 0.0008105 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-03-26 11:34 | 2022-03-26 11:36 | 51 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22032500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 102 | keep | 0 | Mar | 2022 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-03-26 11:34 | 2022-03-26 11:36 | 721 | 000:02 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M22032500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-26 | 1442 | keep | 0 | Mar | 2022 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
CAGUAS | 2022-03-26 11:46 | 2022-03-26 11:47 | 2859 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | C22032600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-26 | 2859 | keep | 0 | Mar | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2022-03-26 11:47 | 2022-03-26 16:24 | 45 | 004:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X80 EN C/L & SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | C22032600064 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 277 | 2022-03-26 | 12465 | keep | 0 | Mar | 2022 | 0.0084899 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-26 11:47 | 2022-03-26 15:07 | 38 | 003:20 | P | DESGANCHE | 1X50 EN C/L | B22032600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-03-26 | 7600 | keep | 0 | Mar | 2022 | 0.0051763 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2022-03-26 11:54 | 2022-03-26 18:41 | 1 | 006:47 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | A22032600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2022-03-26 | 407 | keep | 0 | Mar | 2022 | 0.00027721 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-26 12:20 | 2022-03-26 20:48 | 25 | 008:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M22032600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 508 | 2022-03-26 | 12700 | keep | 0 | Mar | 2022 | 0.0086499 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-03-26 12:22 | 2022-03-26 13:43 | 30 | 001:21 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-03-26 | 2430 | keep | 0 | Mar | 2022 | 0.0016551 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-26 12:59 | 2022-03-26 14:26 | 100 | 001:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22032600018 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2022-03-26 | 8700 | keep | 0 | Mar | 2022 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-03-26 13:17 | 2022-03-26 13:18 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 527 | keep | 0 | Mar | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-03-26 13:30 | 2022-03-26 15:22 | 100 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22032600074 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2022-03-26 | 11200 | keep | 0 | Mar | 2022 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-26 13:32 | 2022-03-26 20:10 | 100 | 006:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22032600077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 398 | 2022-03-26 | 39800 | keep | 0 | Mar | 2022 | 0.027108 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-03-26 13:32 | 2022-03-26 15:26 | 12 | 001:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A22032600023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 114 | 2022-03-26 | 1368 | keep | 0 | Mar | 2022 | 0.00093174 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-03-26 13:33 | 2022-03-26 15:43 | 15 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR AVE CRUZO LINEAS | P22032600022 | New_Event |  |  | Include | Wildlife | 130 | 2022-03-26 | 1950 | keep | 0 | Mar | 2022 | 0.0013281 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-03-26 13:38 | 2022-03-26 15:30 | 10 | 001:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AUTO PRIVADO IMPACTO POSTE | C22032600080 | New_Event |  |  | Include | Wildlife | 112 | 2022-03-26 | 1120 | keep | 0 | Mar | 2022 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-26 13:42 | 2022-03-26 13:43 | 641 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% POR EL 1118-10 | S22032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 641 | keep | 0 | Mar | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-03-26 13:42 | 2022-03-26 13:43 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVANDO UN 20% DEL 1111-01 SE CERRO POR SCADA | S22032600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 2782 | keep | 0 | Mar | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2022-03-26 14:10 | 2022-03-26 17:49 | 150 | 003:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22032600026 | New_Event | Wire Down | Include | Include | Equipment | 219 | 2022-03-26 | 32850 | keep | 0 | Mar | 2022 | 0.022374 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-03-26 14:26 | 2022-03-26 14:30 | 3718 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA AVERIADA | P22032600029 | Additional_clients | Cutout Failure | Include | Include | Equipment | 4 | 2022-03-26 | 14872 | keep | 0 | Mar | 2022 | 0.010129 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-26 14:30 | 2022-03-26 14:43 | 100 | 000:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA CORTE DE LINEA | P22032600018 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 13 | 2022-03-26 | 1300 | keep | 0 | Mar | 2022 | 0.00088542 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-26 14:37 | 2022-03-26 14:38 | 5630 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22032600095 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-26 | 5630 | keep | 0 | Mar | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
ARECIBO | 2022-03-26 14:37 | 2022-03-26 14:38 | 199 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22032600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 199 | keep | 0 | Mar | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2022-03-26 14:37 | 2022-03-26 14:38 | 24 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22032600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 24 | keep | 0 | Mar | 2022 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2022-03-26 14:38 | 2022-03-26 16:01 | 80 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X100 EN C/L & 1X80 EN C/L (POR CRUCE DE AVE) | C22032600100 | 1st_after_momentary |  |  | Include | Wildlife | 83 | 2022-03-26 | 6640 | keep | 0 | Mar | 2022 | 0.0045225 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-26 14:55 | 2022-03-26 21:23 | 100 | 006:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M22032600030 | New_Event |  |  | Include | Wildlife | 388 | 2022-03-26 | 38800 | keep | 0 | Mar | 2022 | 0.026427 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-26 14:58 | 2022-03-26 16:54 | 72 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L Y SE REMPLAZO CAJA PRIMARIA | B22032600019 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2022-03-26 | 8352 | keep | 0 | Mar | 2022 | 0.0056885 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
FAJARDO | 2022-03-26 15:18 | 2022-03-26 18:30 | 100 | 003:12 | P | PARARRAYOS DEFECTUOSO | 2 X 80 Y 1 X 65 EN C/L SE REEMPLAZO PARARRAYOS | R22032600035 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 192 | 2022-03-26 | 19200 | keep | 0 | Mar | 2022 | 0.013077 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-26 15:44 | 2022-03-26 19:21 | 1 | 003:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN BANCO DE TRANSFORMADORES SE REEMPLAZO CAJAS QUEMADAS | C22032600105 | New_Event | Cutout Failure | Include | Include | Equipment | 217 | 2022-03-26 | 217 | keep | 0 | Mar | 2022 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-26 15:54 | 2022-03-26 18:56 | 590 | 003:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S22032600017 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2022-03-26 | 107380 | keep | 0 | Mar | 2022 | 0.073136 | 0.00040185 | Sustained | FALSE | FALSE | Not_TMED_Event | 590
MAYAGÃœEZ | 2022-03-26 16:17 | 2022-03-27 02:03 | 10 | 009:46 | P | DESGANCHE | 2 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | M22032600039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 586 | 2022-03-26 | 5860 | keep | 0 | Mar | 2022 | 0.0039912 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-03-26 16:32 | 2022-03-26 16:33 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 215 | keep | 0 | Mar | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2022-03-26 16:47 | 2022-03-26 18:18 | 78 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X65 EN C/L & SE LEVANTO ALAMBRE PRIMARIO DEL SUELO | S22032600024 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2022-03-26 | 7098 | keep | 0 | Mar | 2022 | 0.0048344 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
ARECIBO | 2022-03-26 17:07 | 2022-03-26 18:02 | 40 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTE VIENTO | A22032600033 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2022-03-26 | 2200 | keep | 0 | Mar | 2022 | 0.0014984 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-26 17:26 | 2022-03-26 17:27 | 2697 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A22032600034 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-03-26 | 2697 | keep | 0 | Mar | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-03-26 17:27 | 2022-03-26 20:00 | 300 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA DE 200AMP AVERIADA EN CORTE DE LINEA | A22032600035 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 153 | 2022-03-26 | 45900 | keep | 0 | Mar | 2022 | 0.031262 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-03-26 18:07 | 2022-03-27 10:15 | 10 | 016:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS ESTE EVENTO ES EL ORIGINAL DEL AREA, EL QUE UTILIZO CON ESTE EVENTO NO ERA DEL SECTOR | A22032600044 | New_Event | Bad Weather | Include | Include | Weather | 968 | 2022-03-26 | 9680 | keep | 0 | Mar | 2022 | 0.006593 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-26 18:07 | 2022-03-26 21:12 | 25 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR NO ENCONTRARON CAUSA PARA LOS FUSIBLES FUNDIDOS ES EVENTO NO ERA DE ESE SECTOR | A22032600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-03-26 | 4625 | keep | 0 | Mar | 2022 | 0.0031501 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-03-26 18:12 | 2022-03-26 18:13 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22032600042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 4641 | keep | 0 | Mar | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
SAN JUAN | 2022-03-26 18:56 | 2022-03-26 19:00 | 922 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DEL 1401-08 EL CUAL LLEVA LA CARGA DEL 1346-05 | S22032600017 | Additional_clients | Cutout Failure | Include | Include | Equipment | 4 | 2022-03-26 | 3688 | keep | 0 | Mar | 2022 | 0.0025119 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-26 18:56 | 2022-03-26 19:00 | 135 | 000:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1401-08 QUE LLEVA LA CARGA DEL 1346-05 POR CAJA QUEMADA EN EVENTO S22032600017 | S22032600000 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2022-03-26 | 540 | keep | 0 | Mar | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
GUAYAMA | 2022-03-26 19:04 | 2022-03-26 21:10 | 30 | 002:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22032600033 | New_Event | Cutout Failure | Include | Include | Equipment | 126 | 2022-03-26 | 3780 | keep | 0 | Mar | 2022 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-03-26 19:08 | 2022-03-26 19:09 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22032600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-26 | 464 | keep | 0 | Mar | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
SAN JUAN | 2022-03-26 19:10 | 2022-03-26 21:39 | 12 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFORMADOR | S22032600035 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2022-03-26 | 1788 | keep | 0 | Mar | 2022 | 0.0012178 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-03-26 19:16 | 2022-03-26 20:05 | 9 | 000:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO C/L | R22032600051 | New_Event | Wire Down | Include | Include | Equipment | 49 | 2022-03-26 | 441 | keep | 0 | Mar | 2022 | 0.00030036 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-03-26 19:32 | 2022-03-26 22:50 | 150 | 003:18 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22032600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-03-26 | 29700 | keep | 0 | Mar | 2022 | 0.020229 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-03-26 19:50 | 2022-03-26 20:56 | 16 | 001:06 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B22032600023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-03-26 | 1056 | keep | 0 | Mar | 2022 | 0.00071924 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-03-26 20:29 | 2022-03-27 11:31 | 7 | 015:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA LEVANTAR SECUNDARIA | C22032500231 | New_Event | Secondary Wire Down | Include | Include | Equipment | 902 | 2022-03-26 | 6314 | keep | 0 | Mar | 2022 | 0.0043004 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-26 21:32 | 2022-03-27 09:44 | 44 | 012:12 | P | TRANSFORMADOR AVERIADO | 1 X 50 Y 1 X 40 EN CORTES DE LINEA ELIMINO XMR QUEMADO DE 37.5 Y TRANSFIRIO LA CARGA A OTRO XMR | C22032600122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 732 | 2022-03-26 | 32208 | keep | 0 | Mar | 2022 | 0.021937 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
ARECIBO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1105 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 59670 | keep | 0 | Mar | 2022 | 0.040641 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2022-03-26 21:38 | 2022-03-26 23:04 | 385 | 001:26 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 86 | 2022-03-26 | 33110 | keep | 0 | Mar | 2022 | 0.022551 | 0.00026222 | Sustained | FALSE | FALSE | Not_TMED_Event | 385
ARECIBO | 2022-03-26 21:38 | 2022-03-26 23:04 | 264 | 001:26 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 86 | 2022-03-26 | 22704 | keep | 0 | Mar | 2022 | 0.015464 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1405 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 75870 | keep | 0 | Mar | 2022 | 0.051675 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 669 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 36126 | keep | 0 | Mar | 2022 | 0.024605 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1527 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 82458 | keep | 0 | Mar | 2022 | 0.056162 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1054 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 56916 | keep | 0 | Mar | 2022 | 0.038765 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 932 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 50328 | keep | 0 | Mar | 2022 | 0.034278 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1633 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 88182 | keep | 0 | Mar | 2022 | 0.06006 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1624 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 87696 | keep | 0 | Mar | 2022 | 0.059729 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 705 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 38070 | keep | 0 | Mar | 2022 | 0.025929 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 1521 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 82134 | keep | 0 | Mar | 2022 | 0.055941 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2022-03-26 21:38 | 2022-03-26 22:32 | 882 | 000:54 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL BANCO 115/38KV DE DOS BOCAS QUE ALIMENTA LA BARRA DE 38KV DE DOS BOCAS | A22032600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 54 | 2022-03-26 | 47628 | keep | 0 | Mar | 2022 | 0.032439 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
MAYAGÃœEZ | 2022-03-26 22:08 | 2022-03-27 00:15 | 3 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA LLUVIA Y VIENTO | M22032600052 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2022-03-26 | 381 | keep | 0 | Mar | 2022 | 0.0002595 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-03-26 22:16 | 2022-03-27 11:21 | 22 | 013:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L REEMPLAZO DISCO PARTIDO | C22032600123 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 785 | 2022-03-26 | 17270 | keep | 0 | Mar | 2022 | 0.011763 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2022-03-26 22:25 | 2022-03-27 12:05 | 30 | 013:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE EVENTO ES 114 DEL DIA 26 LO CERRARON SIN COMENTARIOS LE CREARON UNO EL DIA 27 A22032700005 PARA TRABAJARLO | A22032600114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 820 | 2022-03-26 | 24600 | keep | 0 | Mar | 2022 | 0.016755 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-03-26 23:05 | 2022-03-27 08:22 | 5 | 009:17 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA EVENTO CREADO POR OIC YA AL TERMNAL EL RELEVO EL EVENTO DEL CLIENTE SE ELIMINO. | A22032700002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 557 | 2022-03-26 | 2785 | keep | 0 | Mar | 2022 | 0.0018969 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-03-26 23:07 | 2022-03-27 09:00 | 24 | 009:53 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN CORTE DE LINE Y SE REEMPLAZO TERMINACION EN TRANSFORMADOR | R22032600052 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 593 | 2022-03-26 | 14232 | keep | 0 | Mar | 2022 | 0.0096934 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BARRANQUITAS | 2022-03-27 00:22 | 2022-03-27 00:23 | 2565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 2565 | keep | 0 | Mar | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
AGUADILLA | 2022-03-27 00:40 | 2022-03-27 01:54 | 14 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA Y VIENTO | M22032700001 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2022-03-27 | 1036 | keep | 0 | Mar | 2022 | 0.00070561 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-03-27 00:47 | 2022-03-27 09:26 | 30 | 008:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B22032700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 519 | 2022-03-27 | 15570 | keep | 0 | Mar | 2022 | 0.010605 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-27 02:26 | 2022-03-27 09:00 | 150 | 006:34 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22032700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-03-27 | 59100 | keep | 0 | Mar | 2022 | 0.040253 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-03-27 04:03 | 2022-03-27 07:20 | 74 | 003:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L Y 1 X 10 EN XMR REEMPLAZO CAJA QUEMADA | C22032700002 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2022-03-27 | 14578 | keep | 0 | Mar | 2022 | 0.009929 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
PONCE | 2022-03-27 04:05 | 2022-03-27 10:00 | 100 | 005:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA POSTE PRIMARIO PARTIDO POR AUTOMOVIL SE ABREN PUENTES PARA SECCIONALIZAR AVERIA | P22032700002 | New_Event |  |  | Include | Wildlife | 355 | 2022-03-27 | 35500 | keep | 0 | Mar | 2022 | 0.024179 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-27 06:25 | 2022-03-27 09:50 | 200 | 003:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22032700013 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2022-03-27 | 41000 | keep | 0 | Mar | 2022 | 0.027925 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-27 06:47 | 2022-03-27 17:37 | 20 | 010:50 | P | CABLE SOTERRADO AVERIADO | CG-220327-01 SE REEMPLAZO CABLE SOTERRADO DEL T18 AL T19 | C22032700006 | New_Event | UG Cable Fault | Include | Include | Equipment | 650 | 2022-03-27 | 13000 | keep | 0 | Mar | 2022 | 0.0088542 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-27 07:09 | 2022-03-27 09:44 | 300 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO INTERRRUPTOR PARA SECCIONALIZAR | M22032700015 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2022-03-27 | 46500 | keep | 0 | Mar | 2022 | 0.031671 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-03-27 07:14 | 2022-03-27 07:15 | 450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 450 | keep | 0 | Mar | 2022 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
HUMACAO | 2022-03-27 07:16 | 2022-03-27 09:59 | 50 | 002:43 | P | DESGANCHE | 1 X 50 EN C/L ABRIO PUENTE HACIA LINEA VACANTE | C22032700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-03-27 | 8150 | keep | 0 | Mar | 2022 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-27 07:18 | 2022-03-27 07:20 | 837 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERO SU CARGA POR 1401-07 SE PROBO QUEDO EN SERVICIO | S2203270000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 1674 | keep | 0 | Mar | 2022 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-03-27 07:18 | 2022-03-27 07:20 | 908 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERO LLEVA 1401-06 SE PROBO QUEDO EN SERVICIO | S2203270000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 1816 | keep | 0 | Mar | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2022-03-27 07:18 | 2022-03-27 10:32 | 104 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA 50% DE LA CARGA POR EL 9203-04 EL OTRO 50% POR EL 9202-04 | B22032700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-03-27 | 20176 | keep | 0 | Mar | 2022 | 0.013742 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
CANOVANAS | 2022-03-27 07:23 | 2022-03-27 07:25 | 2106 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRPTOR Y SE CERRO POR SCADA | R22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 4212 | keep | 0 | Mar | 2022 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2022-03-27 07:29 | 2022-03-27 13:45 | 100 | 006:16 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2022-03-27 | 37600 | keep | 0 | Mar | 2022 | 0.025609 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-27 07:48 | 2022-03-27 07:49 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22032700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 2067 | keep | 0 | Mar | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-03-27 08:21 | 2022-03-27 19:38 | 10 | 011:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | M22032700040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 677 | 2022-03-27 | 6770 | keep | 0 | Mar | 2022 | 0.004611 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-27 08:22 | 2022-03-27 11:50 | 200 | 003:28 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 200 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032700042 | New_Event | Bad Weather | Include | Include | Weather | 208 | 2022-03-27 | 41600 | keep | 0 | Mar | 2022 | 0.028334 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-03-27 08:38 | 2022-03-27 08:40 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1401-8 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 1844 | keep | 0 | Mar | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-27 08:38 | 2022-03-27 08:40 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO LLVEA CARGA 1346-5 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 270 | keep | 0 | Mar | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
GUAYAMA | 2022-03-27 08:47 | 2022-03-27 12:42 | 12 | 003:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | P22032700017 | New_Event |  |  | Include | Wildlife | 235 | 2022-03-27 | 2820 | keep | 0 | Mar | 2022 | 0.0019207 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-03-27 09:00 | 2022-03-27 12:40 | 65 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | R22032700007 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2022-03-27 | 14300 | keep | 0 | Mar | 2022 | 0.0097397 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-03-27 09:16 | 2022-03-27 09:17 | 817 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C22032700010 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-27 | 817 | keep | 0 | Mar | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2022-03-27 09:17 | 2022-03-27 09:51 | 175 | 000:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CG-220327-02 CONDUCTOR EN EL SUELO | C22032700020 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 34 | 2022-03-27 | 5950 | keep | 0 | Mar | 2022 | 0.0040525 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
HUMACAO | 2022-03-27 09:31 | 2022-03-27 11:55 | 30 | 002:24 | P | DESGANCHE | 1 X 50 EN C/L | C22032700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-03-27 | 4320 | keep | 0 | Mar | 2022 | 0.0029423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-03-27 09:44 | 2022-03-27 13:43 | 1943 | 003:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION DE KEVIN MERCADO PARA REPARAR LINEA ROTA. SE CERRO POR SCADA | M22032700067 | Additional_clients | Wire Down | Include | Include | Equipment | 239 | 2022-03-27 | 464377 | keep | 0 | Mar | 2022 | 0.31629 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-27 09:51 | 2022-03-27 10:19 | 817 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | A PETICION DE JOSE FUENTES SE ABRIO BKR POR CONDUCTOR VIVO EN EL SUELO | C22032700016 | Additional_clients | Wire Down | Include | Include | Equipment | 28 | 2022-03-27 | 22876 | keep | 0 | Mar | 2022 | 0.015581 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-27 09:59 | 2022-03-27 14:18 | 40 | 004:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | C22032700017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-03-27 | 10360 | keep | 0 | Mar | 2022 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-27 10:01 | 2022-03-27 10:03 | 125 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22032700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 250 | keep | 0 | Mar | 2022 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-03-27 10:04 | 2022-03-27 10:05 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | R22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 1026 | keep | 0 | Mar | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
MAYAGÃœEZ | 2022-03-27 10:15 | 2022-03-27 14:46 | 40 | 004:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032700076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-03-27 | 10840 | keep | 0 | Mar | 2022 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-27 10:19 | 2022-03-27 14:26 | 798 | 004:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CG-220327-02 SE LEVANTO CONDUCTOR DEL SUELO Y SE REEMPLAZARON MACHETES QUEMADOS | C22032700020 | New_Event | Wire Down | Include | Include | Equipment | 247 | 2022-03-27 | 197106 | keep | 0 | Mar | 2022 | 0.13425 | 0.00054351 | Sustained | FALSE | FALSE | Not_TMED_Event | 798
FAJARDO | 2022-03-27 10:56 | 2022-03-27 10:57 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 2722 | keep | 0 | Mar | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2022-03-27 10:56 | 2022-03-27 10:57 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 1234 | keep | 0 | Mar | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
SAN JUAN | 2022-03-27 11:00 | 2022-03-27 12:25 | 10 | 001:25 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR Y SE REALIZO DESGACHE DE ENREDADERA | R22032700021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 85 | 2022-03-27 | 850 | keep | 0 | Mar | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-03-27 11:09 | 2022-03-27 14:20 | 60 | 003:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22032700018 | New_Event |  |  | Include | Wildlife | 191 | 2022-03-27 | 11460 | keep | 0 | Mar | 2022 | 0.0078054 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-27 11:12 | 2022-03-27 13:34 | 100 | 002:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | R22032700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-03-27 | 14200 | keep | 0 | Mar | 2022 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-27 11:19 | 2022-03-27 12:43 | 120 | 001:24 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B22032700017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-03-27 | 10080 | keep | 0 | Mar | 2022 | 0.0068654 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-03-27 11:23 | 2022-03-27 11:24 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2132 | keep | 0 | Mar | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2022-03-27 11:23 | 2022-03-27 11:24 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2366 | keep | 0 | Mar | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2022-03-27 11:23 | 2022-03-27 11:24 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1976 | keep | 0 | Mar | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2022-03-27 11:23 | 2022-03-27 11:24 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 3688 | keep | 0 | Mar | 2022 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 3070 | keep | 0 | Mar | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2735 | keep | 0 | Mar | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1070 | keep | 0 | Mar | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1647 | keep | 0 | Mar | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 3295 | keep | 0 | Mar | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1180 | keep | 0 | Mar | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-03-27 11:23 | 2022-03-27 11:24 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | B22032700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2234 | keep | 0 | Mar | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2022-03-27 11:25 | 2022-03-27 11:26 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2132 | keep | 0 | Mar | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2022-03-27 11:25 | 2022-03-27 11:26 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2366 | keep | 0 | Mar | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2022-03-27 11:25 | 2022-03-27 11:26 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1976 | keep | 0 | Mar | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2022-03-27 11:25 | 2022-03-27 11:26 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 3688 | keep | 0 | Mar | 2022 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 3070 | keep | 0 | Mar | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2735 | keep | 0 | Mar | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1070 | keep | 0 | Mar | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1647 | keep | 0 | Mar | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 3295 | keep | 0 | Mar | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1180 | keep | 0 | Mar | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-03-27 11:25 | 2022-03-27 11:26 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22032700000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2234 | keep | 0 | Mar | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BARRANQUITAS | 2022-03-27 11:34 | 2022-03-27 15:40 | 70 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22032700028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-03-27 | 17220 | keep | 0 | Mar | 2022 | 0.011728 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-03-27 11:45 | 2022-03-27 13:37 | 15 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22032700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-03-27 | 1680 | keep | 0 | Mar | 2022 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-03-27 11:49 | 2022-03-27 14:43 | 30 | 002:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR SE RETIRO AVE MUERTA Y SE REEMPLAZO CAJA QUEMADA | C22032700030 | New_Event |  |  | Include | Wildlife | 174 | 2022-03-27 | 5220 | keep | 0 | Mar | 2022 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-03-27 11:57 | 2022-03-27 11:58 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22032700091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2022-03-27 12:23 | 2022-03-27 14:30 | 1 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN MONTURA DE TRANSFORMADORES SE RETIRO IGUANA | B22032700024 | New_Event |  |  | Include | Wildlife | 127 | 2022-03-27 | 127 | keep | 0 | Mar | 2022 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-03-27 12:24 | 2022-03-27 12:25 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22032700093 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2022-03-27 12:43 | 2022-03-27 12:44 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPRTOR | B22032700000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 3438 | keep | 0 | Mar | 2022 | 0.0023416 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-27 12:44 | 2022-03-27 13:24 | 120 | 000:40 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B22032700017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-03-27 | 4800 | keep | 0 | Mar | 2022 | 0.0032693 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-03-27 12:48 | 2022-03-27 16:45 | 770 | 003:57 | T | DESGANCHE | SE RETIRO BAMBUS SOBRE LAS LINEAS SE CERRO PUENTE PRIMARIO Y SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 7801-04 | M22032700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-03-27 | 182490 | keep | 0 | Mar | 2022 | 0.12429 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2022-03-27 12:48 | 2022-03-27 16:45 | 1772 | 003:57 | T | DESGANCHE | CARGA POR 7801-02 | M22032700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-03-27 | 419964 | keep | 0 | Mar | 2022 | 0.28604 | 0.0012069 | Sustained | FALSE | FALSE | Not_TMED_Event | 1772
ARECIBO | 2022-03-27 13:34 | 2022-03-27 16:40 | 20 | 003:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A22032700015 | New_Event | Wire Down | Include | Include | Equipment | 186 | 2022-03-27 | 3720 | keep | 0 | Mar | 2022 | 0.0025337 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-27 13:43 | 2022-03-27 15:15 | 1400 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA SE CERRO MACHETES | M22032700015 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2022-03-27 | 128800 | keep | 0 | Mar | 2022 | 0.087725 | 0.00095353 | Sustained | FALSE | FALSE | Not_TMED_Event | 1400
HUMACAO | 2022-03-27 13:47 | 2022-03-27 13:48 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22032700044 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-27 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-27 13:48 | 2022-03-27 16:20 | 40 | 002:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22032700048 | 1st_after_momentary |  |  | Include | Wildlife | 152 | 2022-03-27 | 6080 | keep | 0 | Mar | 2022 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-27 13:49 | 2022-03-27 17:16 | 70 | 003:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22032700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2022-03-27 | 14490 | keep | 0 | Mar | 2022 | 0.0098691 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-03-27 13:54 | 2022-03-27 16:11 | 100 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22032700047 | New_Event |  |  | Include | Wildlife | 137 | 2022-03-27 | 13700 | keep | 0 | Mar | 2022 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-27 14:00 | 2022-03-27 15:13 | 5 | 001:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22032700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-03-27 | 365 | keep | 0 | Mar | 2022 | 0.0002486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-03-27 14:33 | 2022-03-27 14:34 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22032700028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 527 | keep | 0 | Mar | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-03-27 15:05 | 2022-03-27 15:06 | 1378 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 1378 | keep | 0 | Mar | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
AGUADILLA | 2022-03-27 15:17 | 2022-03-27 17:16 | 1 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER AVE CRUZO RISER | M22032700131 | New_Event |  |  | Include | Wildlife | 119 | 2022-03-27 | 119 | keep | 0 | Mar | 2022 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-27 15:21 | 2022-03-27 17:19 | 30 | 001:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22032700027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-03-27 | 3540 | keep | 0 | Mar | 2022 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-03-27 15:32 | 2022-03-27 15:34 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 SE PROBO QUEDO EN SERVICIO | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 450 | keep | 0 | Mar | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-27 15:32 | 2022-03-27 15:34 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLAVA 1303-4 SE PROBO QUEDO EN SERVICIO | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 1740 | keep | 0 | Mar | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-03-27 15:53 | 2022-03-27 15:54 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1206-01 LLEVA CARGA 1206-02 PARTE DE SU CARGA POR 1201-02 POR CONVERTIDOR | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 300 | keep | 0 | Mar | 2022 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-03-27 15:53 | 2022-03-27 15:54 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-1 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 733 | keep | 0 | Mar | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
VEGA BAJA | 2022-03-27 16:02 | 2022-03-27 20:16 | 776 | 004:14 | S | DISPARO DE BARRA DE TRANSMISION | IGUANA CRUZO PT Y BARRA 38KV VEGA BAJA TC | B22032700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 254 | 2022-03-27 | 197104 | keep | 0 | Mar | 2022 | 0.13425 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2022-03-27 16:02 | 2022-03-27 20:16 | 2216 | 004:14 | S | DISPARO DE BARRA DE TRANSMISION | IGUANA CRUZO PT Y BARRA 38KV VEGA BAJA TC | B22032700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 254 | 2022-03-27 | 562864 | keep | 0 | Mar | 2022 | 0.38336 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
PONCE | 2022-03-27 16:05 | 2022-03-27 16:06 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22032700031 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 527 | keep | 0 | Mar | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
FAJARDO | 2022-03-27 16:07 | 2022-03-27 20:37 | 306 | 004:30 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R22032700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-03-27 | 82620 | keep | 0 | Mar | 2022 | 0.056272 | 0.00020842 | Sustained | FALSE | FALSE | Not_TMED_Event | 306
CAGUAS | 2022-03-27 16:24 | 2022-03-27 19:40 | 40 | 003:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22032700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-03-27 | 7840 | keep | 0 | Mar | 2022 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-27 16:31 | 2022-03-27 18:47 | 25 | 002:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A22032700019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 136 | 2022-03-27 | 3400 | keep | 0 | Mar | 2022 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-03-27 17:10 | 2022-03-27 17:12 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22032700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 4252 | keep | 0 | Mar | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
GUAYAMA | 2022-03-27 17:23 | 2022-03-27 19:06 | 2 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22032700035 | New_Event |  |  | Include | Wildlife | 103 | 2022-03-27 | 206 | keep | 0 | Mar | 2022 | 0.00014031 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-03-27 17:24 | 2022-03-28 12:43 | 15 | 019:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ROTA | M22032700148 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1159 | 2022-03-27 | 17385 | keep | 0 | Mar | 2022 | 0.011841 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-27 18:20 | 2022-03-28 11:10 | 7 | 016:50 | P | TRANSFORMADOR AVERIADO | REMPLAZAO XMR QUEMADO DE 75 KVA X 75 KVA | C22032700071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1010 | 2022-03-27 | 7070 | keep | 0 | Mar | 2022 | 0.0048153 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 574 | keep | 0 | Mar | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2493 | keep | 0 | Mar | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1415 | keep | 0 | Mar | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1428 | keep | 0 | Mar | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1036 | keep | 0 | Mar | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 382 | keep | 0 | Mar | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 39 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 39 | keep | 0 | Mar | 2022 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 2366 | keep | 0 | Mar | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2022-03-27 18:23 | 2022-03-27 18:24 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 1337 | keep | 0 | Mar | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-03-27 18:23 | 2022-03-27 18:24 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22032700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-27 | 709 | keep | 0 | Mar | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
AGUADILLA | 2022-03-27 18:27 | 2022-03-27 18:28 | 154 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR POSTE PRIMARIO PARTIDO | M22032700152 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2022-03-27 | 154 | keep | 0 | Mar | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2022-03-27 18:28 | 2022-03-27 22:13 | 5 | 003:45 | P | ESTRUCTURA AVERIADA | POSTE PRIMARIO CON TRANSFORMADOR EN TRONCAL DEL ALIMENTADOR SE ABRIO INTERRUPTOR PARA REMPLAZO | M22032700197 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 225 | 2022-03-27 | 1125 | keep | 0 | Mar | 2022 | 0.00076623 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-27 18:32 | 2022-03-27 18:34 | 1483 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO 30 % POR 1336-8 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 2966 | keep | 0 | Mar | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-27 18:32 | 2022-03-27 18:34 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO PARTE POR 1336-8 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-27 18:32 | 2022-03-27 18:34 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1336-9 LLEVA 30% DEL 1204-4 Y PARTE DE 1204-5 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 10580 | keep | 0 | Mar | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-27 18:32 | 2022-03-27 18:34 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1336-8 | S22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-27 | 414 | keep | 0 | Mar | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
HUMACAO | 2022-03-27 18:35 | 2022-03-27 18:36 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22032700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 3420 | keep | 0 | Mar | 2022 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BAYAMON | 2022-03-27 18:45 | 2022-03-27 23:21 | 50 | 004:36 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN PROVISIONAL AVERIA NUEVA DE T-520 @ T 519 Y AVERIA VIEJA DE T-517 @ T-518. 2 XMRS FUERA | B22032700138 | New_Event | UG Cable Fault | Include | Include | Equipment | 276 | 2022-03-27 | 13800 | keep | 0 | Mar | 2022 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-27 18:46 | 2022-03-27 19:55 | 16 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA EN PEDESTAL | B22032700107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2022-03-27 | 1104 | keep | 0 | Mar | 2022 | 0.00075193 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2022-03-27 19:02 | 2022-03-27 21:06 | 10 | 002:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE ABRIO CORTE DE LINEA TOTAL PARA REPARAR CAJA PRIMARIA COLGANDO EN TRANSFORMADOR | B22032700148 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2022-03-27 | 1240 | keep | 0 | Mar | 2022 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-27 19:11 | 2022-03-28 07:31 | 19 | 012:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN TRANSFORMADOR CRUCE DE FASES SECUNDARIAS POR IGUANA | P22032700037 | New_Event |  |  | Include | Wildlife | 740 | 2022-03-27 | 14060 | keep | 0 | Mar | 2022 | 0.0095762 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2022-03-27 19:42 | 2022-03-27 19:43 | 3654 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | A22032700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 3654 | keep | 0 | Mar | 2022 | 0.0024887 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
MAYAGÃœEZ | 2022-03-27 19:49 | 2022-03-27 23:25 | 100 | 003:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032700157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-03-27 | 21600 | keep | 0 | Mar | 2022 | 0.014712 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-27 20:38 | 2022-03-27 22:34 | 150 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X 100 EN SU | S22032700035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-03-27 | 17400 | keep | 0 | Mar | 2022 | 0.011851 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-03-27 20:52 | 2022-03-28 11:31 | 10 | 014:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R22032700082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 879 | 2022-03-27 | 8790 | keep | 0 | Mar | 2022 | 0.0059868 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-27 21:06 | 2022-03-27 21:35 | 88 | 000:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE ABRIO CORTE DE LINEA TOTAL PARA REPARAR CAJA PRIMARIA COLGANDO EN TRANSFORMADOR | B22032700148 | Additional_clients | Cutout Failure | Include | Include | Equipment | 29 | 2022-03-27 | 2552 | keep | 0 | Mar | 2022 | 0.0017382 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-27 21:45 | 2022-03-27 21:46 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22032700201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-27 | 312 | keep | 0 | Mar | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
AGUADILLA | 2022-03-27 22:13 | 2022-03-28 02:44 | 154 | 004:31 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA REMPLAZO DE POSTE PRIMARIO PARTIDO EN TRONCAL DEL ALIMENTADOR | M22032700214 | Additional_clients | Defective Pole | Include | Include | Equipment | 271 | 2022-03-27 | 41734 | keep | 0 | Mar | 2022 | 0.028425 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-27 22:15 | 2022-03-28 10:34 | 140 | 012:19 | P | DESGANCHE | 1 X 100 Y 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22032700015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 739 | 2022-03-27 | 103460 | keep | 0 | Mar | 2022 | 0.070466 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2022-03-27 22:27 | 2022-03-28 15:54 | 40 | 017:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | B22032700183 | New_Event |  |  | Include | Wildlife | 1047 | 2022-03-27 | 41880 | keep | 0 | Mar | 2022 | 0.028524 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-27 22:40 | 2022-03-28 03:51 | 6 | 005:11 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO SU-1 Y SE CERRO MACHETES EN ANTIGUO CONVERTIDOR | B22032700184 | New_Event | UG Cable Fault | Include | Include | Equipment | 311 | 2022-03-27 | 1866 | keep | 0 | Mar | 2022 | 0.0012709 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-27 22:41 | 2022-03-28 01:29 | 150 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 100 DE RISER @ SU-5 | S22032700061 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-03-27 | 25200 | keep | 0 | Mar | 2022 | 0.017164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-27 23:24 | 2022-03-28 09:30 | 20 | 010:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 C/L REMPLAZO AISLADOR | C22032700078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 606 | 2022-03-27 | 12120 | keep | 0 | Mar | 2022 | 0.0082549 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-03-28 01:20 | 2022-03-28 09:42 | 80 | 008:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2022-03-28 | 40160 | keep | 0 | Mar | 2022 | 0.027353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-03-28 02:44 | 2022-03-28 04:44 | 5 | 002:00 | P | ESTRUCTURA AVERIADA | SE INSTALO Y CONECTO TRANSFORMADOR A POSTE REMPLAZADO | M22032700197 | Partial_restoration | Defective Pole | Include | Include | Equipment | 120 | 2022-03-28 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-03-28 02:55 | 2022-03-28 11:35 | 20 | 008:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22032800002 | New_Event | Wire Down | Include | Include | Equipment | 520 | 2022-03-28 | 10400 | keep | 0 | Mar | 2022 | 0.0070834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-03-28 03:11 | 2022-03-28 03:12 | 172 | 000:01 | T | CABLE SOTERRADO AVERIADO | HACIENDO OPERACIONES DE AMARRE DISPARO BKR | B22032800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-28 | 172 | keep | 0 | Mar | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2022-03-28 03:51 | 2022-03-28 04:39 | 3 | 000:48 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO SU-1 Y SE CERRO MACHETES EN ANTIGUO CONVERTIDOR | B22032700184 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 48 | 2022-03-28 | 144 | keep | 0 | Mar | 2022 | 9.8078e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-28 04:39 | 2022-03-28 04:41 | 2 | 000:02 | P | CABLE SOTERRADO AVERIADO | EN OPERACIONES DISPARO 9206-09 ATRAVEZ DEL 9206-08 | B22032700184 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 2 | 2022-03-28 | 4 | keep | 0 | Mar | 2022 | 2.7244e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-28 04:41 | 2022-03-28 04:42 | 603 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO HACIENDO OPERACIONES | B22032700184 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-28 | 603 | keep | 0 | Mar | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-03-28 04:41 | 2022-03-28 04:42 | 6 | 000:01 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO Y SE CERRO 9206-08 LLEVANDO 9206-09 | B22032700184 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-28 | 6 | keep | 0 | Mar | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-03-28 04:42 | 2022-03-28 05:35 | 2 | 000:53 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO DE SU-1 @ BKR Y SE CERRO N/O EN EL SU DEL CORREO CARR. 696 | B22032700184 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 53 | 2022-03-28 | 106 | keep | 0 | Mar | 2022 | 7.2196e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-03-28 06:05 | 2022-03-28 14:28 | 180 | 008:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C22032800001 | New_Event | Wire Down | Include | Include | Equipment | 503 | 2022-03-28 | 90540 | keep | 0 | Mar | 2022 | 0.061666 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2022-03-28 06:12 | 2022-03-28 11:40 | 60 | 005:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22032800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2022-03-28 | 19680 | keep | 0 | Mar | 2022 | 0.013404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-03-28 06:30 | 2022-03-28 11:34 | 15 | 005:04 | P | DESGANCHE | 1 X 30 EN C/L | C22032800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-03-28 | 4560 | keep | 0 | Mar | 2022 | 0.0031058 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-28 06:31 | 2022-03-28 09:43 | 30 | 003:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-03-28 | 5760 | keep | 0 | Mar | 2022 | 0.0039231 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-03-28 06:39 | 2022-03-28 10:11 | 15 | 003:32 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22032800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-03-28 | 3180 | keep | 0 | Mar | 2022 | 0.0021659 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-28 07:00 | 2022-03-28 14:40 | 8 | 007:40 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR DESGANCHE SECUNDARIO TRAS PATIO Y REPARAR SECUNDARIA | S22032800005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 460 | 2022-03-28 | 3680 | keep | 0 | Mar | 2022 | 0.0025064 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-03-28 07:25 | 2022-03-28 10:04 | 100 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032800017 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2022-03-28 | 15900 | keep | 0 | Mar | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-28 07:31 | 2022-03-28 07:32 | 1818 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR SE REMPLAZO BAJANTE PRIMARIO EN MACHETE | M22032800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-28 | 1818 | keep | 0 | Mar | 2022 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
MAYAGÃœEZ | 2022-03-28 07:31 | 2022-03-28 07:32 | 4381 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22032800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-28 | 4381 | keep | 0 | Mar | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-03-28 07:32 | 2022-03-28 13:40 | 500 | 006:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M22032800037 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 368 | 2022-03-28 | 184000 | keep | 0 | Mar | 2022 | 0.12532 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-03-28 07:38 | 2022-03-28 14:54 | 24 | 007:16 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA T-519 | B22032800006 | New_Event | UG Cable Fault | Include | Include | Equipment | 436 | 2022-03-28 | 10464 | keep | 0 | Mar | 2022 | 0.007127 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2022-03-28 07:44 | 2022-03-28 07:45 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
BARRANQUITAS | 2022-03-28 07:56 | 2022-03-28 13:16 | 40 | 005:20 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y REMPLAZO 2 DISCOS ROTOS | C22032800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2022-03-28 | 12800 | keep | 0 | Mar | 2022 | 0.008718 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-28 08:02 | 2022-03-28 14:23 | 40 | 006:21 | P | DESGANCHE | 1 X 50 EN C/L | C22032800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2022-03-28 | 15240 | keep | 0 | Mar | 2022 | 0.01038 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-28 08:19 | 2022-03-28 09:24 | 1 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN C/L CRUCE X AVE | C22032800021 | New_Event |  |  | Include | Wildlife | 65 | 2022-03-28 | 65 | keep | 0 | Mar | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-28 08:28 | 2022-03-28 12:03 | 12 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22032800022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2022-03-28 | 2580 | keep | 0 | Mar | 2022 | 0.0017572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-03-28 08:31 | 2022-03-28 12:15 | 50 | 003:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22032800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-03-28 | 11200 | keep | 0 | Mar | 2022 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-28 08:40 | 2022-03-28 15:19 | 1 | 006:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C22032800032 | New_Event |  |  | Include | Wildlife | 399 | 2022-03-28 | 399 | keep | 0 | Mar | 2022 | 0.00027176 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-28 08:40 | 2022-03-28 09:35 | 7 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS AVERIADOS | P22032800008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-03-28 | 385 | keep | 0 | Mar | 2022 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-03-28 08:43 | 2022-03-28 11:06 | 1 | 002:23 | P | OTRAS CAUSAS | 1 X 30 EN RISER PROA SE DEJO EN SERVICIO PERO SE RECOMENDO A CLIENTE QUE REALIZE REPARACIONES | R22032800023 | New_Event | Other Causes | Include | Include | Other | 143 | 2022-03-28 | 143 | keep | 0 | Mar | 2022 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-28 08:52 | 2022-03-28 14:35 | 14 | 005:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN PROVISIONAL | S22032800004 | New_Event |  |  | Include | Wildlife | 343 | 2022-03-28 | 4802 | keep | 0 | Mar | 2022 | 0.0032706 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-03-28 08:55 | 2022-03-28 10:00 | 35 | 001:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22032800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-03-28 | 2275 | keep | 0 | Mar | 2022 | 0.0015495 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2022-03-28 08:55 | 2022-03-28 10:10 | 12 | 001:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO | P22032800011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 75 | 2022-03-28 | 900 | keep | 0 | Mar | 2022 | 0.00061299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-28 09:06 | 2022-03-28 10:11 | 7 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22032800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2022-03-28 | 455 | keep | 0 | Mar | 2022 | 0.0003099 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-28 09:08 | 2022-03-28 16:43 | 78 | 007:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22032800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2022-03-28 | 35490 | keep | 0 | Mar | 2022 | 0.024172 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
SAN JUAN | 2022-03-28 09:16 | 2022-03-28 15:50 | 87 | 006:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | S22032800042 | New_Event | Wire Down | Include | Include | Equipment | 394 | 2022-03-28 | 34278 | keep | 0 | Mar | 2022 | 0.023347 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
FAJARDO | 2022-03-28 09:17 | 2022-03-28 14:48 | 8 | 005:31 | P | DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE CRITICO | R22032800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-03-28 | 2648 | keep | 0 | Mar | 2022 | 0.0018035 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-03-28 09:34 | 2022-03-28 12:54 | 15 | 003:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS PARTIDAS | P22032800072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 200 | 2022-03-28 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-03-28 09:45 | 2022-03-28 12:00 | 10 | 002:15 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS | A22032800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-03-28 | 1350 | keep | 0 | Mar | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-28 09:47 | 2022-03-28 11:19 | 75 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR Y 1 X 50 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR AVE | P22032800035 | New_Event |  |  | Include | Wildlife | 92 | 2022-03-28 | 6900 | keep | 0 | Mar | 2022 | 0.0046996 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-03-28 09:57 | 2022-03-28 12:00 | 10 | 002:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIR XMR PARA REEMPLAZAR POSTE SECUNDARIO | B22032800062 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 123 | 2022-03-28 | 1230 | keep | 0 | Mar | 2022 | 0.00083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-03-28 10:02 | 2022-03-28 12:58 | 50 | 002:56 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-03-28 | 8800 | keep | 0 | Mar | 2022 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-03-28 10:07 | 2022-03-28 11:28 | 8 | 001:21 | P | OTRAS CAUSAS | SE ABRE TRANSFORMADOR POR AVERIA INTERNA EN OFICINA DE ADMINISTRACION | R22032800036 | New_Event | Other Causes | Include | Include | Other | 81 | 2022-03-28 | 648 | keep | 0 | Mar | 2022 | 0.00044135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-03-28 10:12 | 2022-03-28 10:13 | 316 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22032800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 316 | keep | 0 | Mar | 2022 | 0.00021523 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2022-03-28 10:13 | 2022-03-28 12:07 | 50 | 001:54 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA NO REPORTARON CAUSA | A22032800028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-03-28 | 5700 | keep | 0 | Mar | 2022 | 0.0038822 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-03-28 10:18 | 2022-03-28 11:56 | 8 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A22032800027 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-03-28 | 784 | keep | 0 | Mar | 2022 | 0.00053398 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-03-28 10:28 | 2022-03-28 12:18 | 65 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 50 EN CORTES DE LINEA CAMION DE RECOGIDO DE DESPERDICIOS CRUZA FASES PRIMARIAS | P22032800052 | New_Event |  |  | Include | Wildlife | 110 | 2022-03-28 | 7150 | keep | 0 | Mar | 2022 | 0.0048698 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2022-03-28 10:31 | 2022-03-28 11:25 | 40 | 000:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032800172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-03-28 | 2160 | keep | 0 | Mar | 2022 | 0.0014712 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-28 10:57 | 2022-03-28 22:53 | 100 | 011:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN AEREO PROVISIONAL | B22032800072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 716 | 2022-03-28 | 71600 | keep | 0 | Mar | 2022 | 0.048766 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-28 10:57 | 2022-03-28 10:58 | 320 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22032800000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-28 | 320 | keep | 0 | Mar | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-03-28 10:58 | 2022-03-28 17:22 | 44 | 006:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO GALLINA DE PALO DE LA LINEA | B22032800078 | 1st_after_momentary |  |  | Include | Wildlife | 384 | 2022-03-28 | 16896 | keep | 0 | Mar | 2022 | 0.011508 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BARRANQUITAS | 2022-03-28 11:00 | 2022-03-28 14:55 | 7 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA RELOCALIZAR SECUNDARIA PARA FUTURA V/L | C22032800057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2022-03-28 | 1645 | keep | 0 | Mar | 2022 | 0.0011204 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-03-28 11:03 | 2022-03-28 16:56 | 1 | 005:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X 10 EN XMR CRUCE X AVE | C22032800058 | New_Event |  |  | Include | Wildlife | 353 | 2022-03-28 | 353 | keep | 0 | Mar | 2022 | 0.00024043 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-03-28 11:05 | 2022-03-28 11:17 | 1 | 000:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22032800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-03-28 | 12 | keep | 0 | Mar | 2022 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-28 11:18 | 2022-03-28 12:10 | 1 | 000:52 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO AVERIADO | A22032800036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 52 | 2022-03-28 | 52 | keep | 0 | Mar | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-03-28 11:26 | 2022-03-28 13:20 | 100 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22032800073 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2022-03-28 | 11400 | keep | 0 | Mar | 2022 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-28 11:53 | 2022-03-28 14:19 | 1 | 002:26 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE XMRS NO CAUSA | C22032800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-03-28 | 146 | keep | 0 | Mar | 2022 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-03-28 12:23 | 2022-03-28 15:00 | 10 | 002:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR BAJANTE SECUNDARIO CRUZADO | P22032800084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 157 | 2022-03-28 | 1570 | keep | 0 | Mar | 2022 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-28 12:25 | 2022-03-28 17:13 | 4 | 004:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRA SECUNDARIA DE PM | C22032800068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 288 | 2022-03-28 | 1152 | keep | 0 | Mar | 2022 | 0.00078462 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-03-28 12:51 | 2022-03-28 15:30 | 5 | 002:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22032800049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 159 | 2022-03-28 | 795 | keep | 0 | Mar | 2022 | 0.00054147 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-03-28 12:52 | 2022-03-28 15:04 | 30 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER INFORMA FOREMAN NO IDENTIFICO CAUSA | A22032800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-03-28 | 3960 | keep | 0 | Mar | 2022 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-28 12:54 | 2022-03-28 15:22 | 10 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22032800052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2022-03-28 | 1480 | keep | 0 | Mar | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-03-28 13:13 | 2022-03-28 14:08 | 4 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SECUNDARIA | R22032800033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-03-28 | 220 | keep | 0 | Mar | 2022 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-03-28 13:16 | 2022-03-28 18:41 | 15 | 005:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN C/L ELIMINO LINEA VACANTE | C22032800072 | New_Event | Wire Down | Include | Include | Equipment | 325 | 2022-03-28 | 4875 | keep | 0 | Mar | 2022 | 0.0033203 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-28 13:37 | 2022-03-28 15:05 | 1712 | 001:28 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO MANUAL ELECTRICAMENTE SUBESTACION NO TIENE RTU | P22032800091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-03-28 | 150656 | keep | 0 | Mar | 2022 | 0.10261 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
MAYAGÃœEZ | 2022-03-28 13:45 | 2022-03-28 16:49 | 40 | 003:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032800208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-03-28 | 7360 | keep | 0 | Mar | 2022 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-28 13:50 | 2022-03-28 16:37 | 7 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN SECUNDARIA | B22032700092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2022-03-28 | 1169 | keep | 0 | Mar | 2022 | 0.0007962 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-03-28 13:55 | 2022-03-28 14:50 | 15 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22032700033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-03-28 | 825 | keep | 0 | Mar | 2022 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-28 14:05 | 2022-03-28 16:29 | 4 | 002:24 | P | SECUNDARIA/ESTRUCTURA AVERIADA | REMPLAZO PEDESTAL Y BARRAS | C22032800085 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 144 | 2022-03-28 | 576 | keep | 0 | Mar | 2022 | 0.00039231 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-03-28 14:20 | 2022-03-28 14:25 | 527 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON RR EN OFF SE VERIFICO PERSONAL FUERA DE LINEAS PRIMARIAS Y SE REALIZO PRUEBA | P22032800108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-03-28 | 2635 | keep | 0 | Mar | 2022 | 0.0017947 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-03-28 15:00 | 2022-03-29 09:51 | 9 | 018:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REEMPLAZARON CONECTORES SULFATADOS | C22032800094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1131 | 2022-03-28 | 10179 | keep | 0 | Mar | 2022 | 0.0069329 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-03-28 15:10 | 2022-03-28 18:36 | 45 | 003:26 | P | OTRAS CAUSAS | SE ABRIO TOTAL EN 3 HACIA SU-4 PARA ENCABEZAR LINEA QUE SE HABIA DEJADO DESCONECTADA POR AVERIA Y LE DA SERVICIO AL TRANSCLOSURE DE LA ESCUELA | B22032800102 | New_Event | Other Causes | Include | Include | Other | 206 | 2022-03-28 | 9270 | keep | 0 | Mar | 2022 | 0.0063138 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-03-28 15:42 | 2022-03-28 15:43 | 1180 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | B22032800106 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-28 | 1180 | keep | 0 | Mar | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
CANOVANAS | 2022-03-28 15:43 | 2022-03-28 17:19 | 130 | 001:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22032800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-03-28 | 12480 | keep | 0 | Mar | 2022 | 0.0085001 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-03-28 15:43 | 2022-03-28 17:42 | 120 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR EN EL SUELO | B22032800170 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 119 | 2022-03-28 | 14280 | keep | 0 | Mar | 2022 | 0.009726 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
YAUCO | 2022-03-28 15:45 | 2022-03-28 16:16 | 10 | 000:31 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA RETIRAR ENREDADERA QUE SE ESTABA QUEMANDO | P22032800001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 31 | 2022-03-28 | 310 | keep | 0 | Mar | 2022 | 0.00021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-28 15:45 | 2022-03-28 19:10 | 61 | 003:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22032800115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-03-28 | 12505 | keep | 0 | Mar | 2022 | 0.0085171 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2022-03-28 16:11 | 2022-03-28 18:36 | 100 | 002:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M22032800232 | New_Event |  |  | Include | Wildlife | 145 | 2022-03-28 | 14500 | keep | 0 | Mar | 2022 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-28 16:51 | 2022-03-28 18:32 | 2216 | 001:41 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR PROBO MALO SE SECCIONALIZO AISLADOR ROTO | B22032800118 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2022-03-28 | 223816 | keep | 0 | Mar | 2022 | 0.15244 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
PONCE | 2022-03-28 16:53 | 2022-03-28 16:54 | 1606 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECIERRE DE INTERRUPTOR EN OPERACION DISPARO LINEA 40300 | P22032800170 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1606 | keep | 0 | Mar | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-03-28 16:57 | 2022-03-29 02:07 | 1922 | 009:10 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZA SUBESTACION A TRAVES DEL 0160 Y SE CIERRA INTERRUPTOR POR SCADA | P22032800161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 550 | 2022-03-28 | 1057100 | keep | 0 | Mar | 2022 | 0.71999 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
PONCE | 2022-03-28 16:57 | 2022-03-29 03:55 | 2235 | 010:58 | S | LINEA DE TRANSMISION 38KV | SE AMARRO ALIMENTADOR 2 CON EL 3 A TRAVES BARRA DE INSPECCION YA QUE INTERRUPTOR 2 BOTA HUMO AL ENERGIZAR SUBESTACION | P22032900057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 658 | 2022-03-28 | 1470630 | keep | 0 | Mar | 2022 | 1.0016 | 0.0015222 | Sustained | FALSE | FALSE | Not_TMED_Event | 2235
PONCE | 2022-03-28 16:57 | 2022-03-29 02:07 | 713 | 009:10 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZA SUBESTACION A TRAVES DEL 0160 Y SE CIERRA INTERRUPTOR POR SCADA | P22032800161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 550 | 2022-03-28 | 392150 | keep | 0 | Mar | 2022 | 0.26709 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
PONCE | 2022-03-28 16:57 | 2022-03-29 02:07 | 1067 | 009:10 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZA SUBESTACION A TRAVES DEL 0160 Y SE CIERRA INTERRUPTOR POR SCADA | P22032800161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 550 | 2022-03-28 | 586850 | keep | 0 | Mar | 2022 | 0.3997 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-03-28 16:57 | 2022-03-28 23:53 | 75 | 006:56 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 4800 POR SOBRE CARGA AL NO TENER APORTACION EN LINEA 40300 QUE APORTA AL BANCO 115/38KV SANTA ISABEL TC. | P22032800166 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 416 | 2022-03-28 | 31200 | keep | 0 | Mar | 2022 | 0.02125 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-03-28 16:57 | 2022-03-28 23:53 | 449 | 006:56 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 4800 POR SOBRE CARGA AL NO TENER APORTACION EN LINEA 40300 QUE APORTA AL BANCO 115/38KV SANTA ISABEL TC. | P22032800166 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 416 | 2022-03-28 | 186784 | keep | 0 | Mar | 2022 | 0.12722 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2022-03-28 16:57 | 2022-03-28 23:49 | 1293 | 006:52 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 4800 POR SOBRE CARGA AL NO TENER APORTACION EN LINEA 40300 QUE APORTA AL BANCO 115/38KV SANTA ISABEL TC. | P22032800168 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 412 | 2022-03-28 | 532716 | keep | 0 | Mar | 2022 | 0.36283 | 0.00088066 | Sustained | FALSE | FALSE | Not_TMED_Event | 1293
PONCE | 2022-03-28 16:57 | 2022-03-28 23:49 | 426 | 006:52 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 4800 POR SOBRE CARGA AL NO TENER APORTACION EN LINEA 40300 QUE APORTA AL BANCO 115/38KV SANTA ISABEL TC. | P22032800168 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 412 | 2022-03-28 | 175512 | keep | 0 | Mar | 2022 | 0.11954 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
PONCE | 2022-03-28 16:57 | 2022-03-28 23:49 | 1556 | 006:52 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 4800 POR SOBRE CARGA AL NO TENER APORTACION EN LINEA 40300 QUE APORTA AL BANCO 115/38KV SANTA ISABEL TC. | P22032800168 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 412 | 2022-03-28 | 641072 | keep | 0 | Mar | 2022 | 0.43663 | 0.0010598 | Sustained | FALSE | FALSE | Not_TMED_Event | 1556
ARECIBO | 2022-03-28 16:58 | 2022-03-29 01:45 | 25 | 008:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA | A22032800068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 527 | 2022-03-28 | 13175 | keep | 0 | Mar | 2022 | 0.0089734 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-03-28 17:12 | 2022-03-28 21:40 | 2825 | 004:28 | T | PARARRAYOS DEFECTUOSO | SE RETIRO PARARRAYO CRUZADO SE CERRO INTERRUPTOR | M22032800245 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 268 | 2022-03-28 | 757100 | keep | 0 | Mar | 2022 | 0.51566 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
SAN JUAN | 2022-03-28 17:18 | 2022-03-29 10:24 | 40 | 017:06 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22032800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1026 | 2022-03-28 | 41040 | keep | 0 | Mar | 2022 | 0.027952 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-28 17:38 | 2022-03-28 17:39 | 20 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22032800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 20 | keep | 0 | Mar | 2022 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-28 17:42 | 2022-03-28 18:10 | 1180 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO 70% CONTINUAN CON BY-220328-01 | B22032800170 | Additional_clients | Wire Down | Include | Include | Equipment | 28 | 2022-03-28 | 33040 | keep | 0 | Mar | 2022 | 0.022503 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-28 17:49 | 2022-03-28 17:50 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22032800278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 4304 | keep | 0 | Mar | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
VEGA BAJA | 2022-03-28 18:06 | 2022-03-28 18:07 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B22032800184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 2610 | keep | 0 | Mar | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
BAYAMON | 2022-03-28 18:10 | 2022-03-28 21:58 | 398 | 003:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO CERRARON MACHETES | B22032800170 | Partial_restoration | Wire Down | Include | Include | Equipment | 228 | 2022-03-28 | 90744 | keep | 0 | Mar | 2022 | 0.061805 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-28 18:10 | 2022-03-28 18:39 | 18 | 000:29 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22032800112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-03-28 | 522 | keep | 0 | Mar | 2022 | 0.00035553 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-03-28 18:18 | 2022-03-28 18:19 | 487 | 000:01 | P | SOBRECARGA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 20% POR 1303-2 POR AVERIA SU-2 LOS TECATOS | S22032800197 | New_Event | Trip Due To Overload | Include | Include | Other | 1 | 2022-03-28 | 487 | keep | 0 | Mar | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-03-28 18:18 | 2022-03-28 18:19 | 2044 | 000:01 | P | SOBRECARGA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 20% POR 1303-2 POR AVERIA SU-2 LOS TECATOS | S22032800197 | New_Event | Trip Due To Overload | Include | Include | Other | 1 | 2022-03-28 | 2044 | keep | 0 | Mar | 2022 | 0.0013922 | 0.0013922 | Momentary | FALSE | FALSE | Not_TMED_Event | 2044
SAN JUAN | 2022-03-28 18:18 | 2022-03-28 18:19 | 2435 | 000:01 | T | SOBRECARGA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO LLEVA 20% 1204-2 Y LLEVA 20 % 1204-5 POR AVERIA SU-2 LOS TECATOS SE LE HABIA TRANSFERIDO CARGA Y NO SE HABIA NORMALIZADO | S22032800197 | New_Event | Trip Due To Overload | Include | Include | Other | 1 | 2022-03-28 | 2435 | keep | 0 | Mar | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
ARECIBO | 2022-03-28 18:21 | 2022-03-28 20:40 | 15 | 002:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22032800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-03-28 | 2085 | keep | 0 | Mar | 2022 | 0.0014201 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-28 18:24 | 2022-03-28 20:29 | 300 | 002:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M22032800261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-03-28 | 37500 | keep | 0 | Mar | 2022 | 0.025541 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-03-28 18:32 | 2022-03-28 21:26 | 339 | 002:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO SE CERRO MACHETES | B22032800202 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2022-03-28 | 58986 | keep | 0 | Mar | 2022 | 0.040175 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-28 18:34 | 2022-03-29 10:00 | 55 | 015:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA RAMAL Y 1 X 100 EN CORTE DE LINEA PRINCIPAL. SE REALIZO DESGANCHE Y SE REEPLAZO AISLADOR | S22032800172 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 926 | 2022-03-28 | 50930 | keep | 0 | Mar | 2022 | 0.034688 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2022-03-28 18:39 | 2022-03-29 08:00 | 16 | 013:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C22032800115 | New_Event |  |  | Include | Wildlife | 801 | 2022-03-28 | 12816 | keep | 0 | Mar | 2022 | 0.0087289 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-03-28 18:39 | 2022-03-28 20:07 | 3654 | 001:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE ELIMINO LINEA PRIMARIA PARTIDA QUE NO DABA SERVICIO A NADIE | A22032800075 | New_Event | Wire Down | Include | Include | Equipment | 88 | 2022-03-28 | 321552 | keep | 0 | Mar | 2022 | 0.21901 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
SAN JUAN | 2022-03-28 18:54 | 2022-03-28 19:03 | 487 | 000:09 | P | SOBRECARGA | DISPARO 20% POR 1303-2 | S22032800197 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 9 | 2022-03-28 | 4383 | keep | 0 | Mar | 2022 | 0.0029852 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-03-28 18:54 | 2022-03-28 19:03 | 2044 | 000:09 | P | SOBRECARGA | DISPARO 20% POR 1303-2 | S22032800197 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 9 | 2022-03-28 | 18396 | keep | 0 | Mar | 2022 | 0.012529 | 0.0013922 | Sustained | FALSE | FALSE | Not_TMED_Event | 2044
SAN JUAN | 2022-03-28 18:54 | 2022-03-28 19:03 | 2435 | 000:09 | T | SOBRECARGA | DISPARO LLEVA CARGA 20%1204-2 Y 20% 1204-5 POR AVERIA SU-2 LOS TECATOS | S22032800197 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 9 | 2022-03-28 | 21915 | keep | 0 | Mar | 2022 | 0.014926 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1339 | keep | 0 | Mar | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 470 | keep | 0 | Mar | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 2483 | keep | 0 | Mar | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 2190 | keep | 0 | Mar | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 3006 | keep | 0 | Mar | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 179 | keep | 0 | Mar | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 107 | keep | 0 | Mar | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1666 | keep | 0 | Mar | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 18:57 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 4387 | keep | 0 | Mar | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 21:09 | 3147 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15700 SE RETIRO CARGA DE SUBESTACION SE CERRO 15710 Y LUEGO SE RETABLECIO LA CARGA | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2022-03-28 | 418551 | keep | 0 | Mar | 2022 | 0.28507 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-03-28 18:56 | 2022-03-28 21:09 | 4304 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15700 SE RETIRO CARGA DE SUBESTACION SE CERRO 15710 Y LUEGO SE RETABLECIO LA CARGA | M22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2022-03-28 | 572432 | keep | 0 | Mar | 2022 | 0.38988 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
FAJARDO | 2022-03-28 19:05 | 2022-03-28 20:03 | 239 | 000:58 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | R22032800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-03-28 | 13862 | keep | 0 | Mar | 2022 | 0.0094413 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
SAN JUAN | 2022-03-28 19:10 | 2022-03-28 19:25 | 487 | 000:15 | P | SOBRECARGA | DISPARO POR SOBRECARGA 20% POR 1204-2 Y ABRIO VENUS GARDEN PARA BAJAR CARGA Y REMPLAZAR MACHETE | S22032800197 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 15 | 2022-03-28 | 7305 | keep | 0 | Mar | 2022 | 0.0049754 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-28 19:10 | 2022-03-28 20:11 | 2044 | 001:01 | P | SOBRECARGA | SE NORMALIZARON CARGAS POR AVERIA SU-2 LOS TECATOS | S22032800197 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 61 | 2022-03-28 | 124684 | keep | 0 | Mar | 2022 | 0.084922 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-28 19:10 | 2022-03-28 19:25 | 2435 | 000:15 | T | SOBRECARGA | DISPARO POR SOBRECARGA LLEVA 20% 1204-2 Y 20% 1204-5 SE ABRIO VENUS GARDEN PARA BAJAR CARGA Y REMPLAZAR MACHETE | S22032800197 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 15 | 2022-03-28 | 36525 | keep | 0 | Mar | 2022 | 0.024877 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-28 19:42 | 2022-03-28 19:43 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 2725 | keep | 0 | Mar | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-28 19:42 | 2022-03-28 19:43 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-28 19:42 | 2022-03-28 19:43 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1437 | keep | 0 | Mar | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-03-28 19:42 | 2022-03-28 19:43 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 2565 | keep | 0 | Mar | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-03-28 19:42 | 2022-03-28 19:43 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEAS 8500 Y 4800 | C22032800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 3565 | keep | 0 | Mar | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-03-28 19:42 | 2022-03-28 19:43 | 1606 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE INTERRUPTOR EN OPERACION DISPARO LINEA 4800 | P22032800283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1606 | keep | 0 | Mar | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BARRANQUITAS | 2022-03-28 19:43 | 2022-03-28 20:33 | 2565 | 000:50 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA TRABAJAR AVERIA DE LINEA CARGA POR EL 3502-02 | C22032800165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-03-28 | 128250 | keep | 0 | Mar | 2022 | 0.08735 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-03-28 19:43 | 2022-03-28 20:33 | 3565 | 000:50 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTORES DE SUBESTACION PARA CERRAR PUENTE ABIERTO DE LINEA 4800 LLEVANDO LA CARGA DEL 3502-01 | C22032800165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 50 | 2022-03-28 | 178250 | keep | 0 | Mar | 2022 | 0.12141 | 0.0024281 | Sustained | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 2751 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE LINEA L4800 | P22032800429 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 665742 | keep | 0 | Mar | 2022 | 0.45343 | 0.0018737 | Sustained | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 576 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE LINEA 4800 | P22032800429 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 139392 | keep | 0 | Mar | 2022 | 0.094939 | 0.00039231 | Sustained | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 2584 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE LINEA 4800 | P22032800429 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 625328 | keep | 0 | Mar | 2022 | 0.42591 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 1606 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE LINEA 4800 | P22032800429 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 388652 | keep | 0 | Mar | 2022 | 0.26471 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 29 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE | P22032800429 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 7018 | keep | 0 | Mar | 2022 | 0.0047799 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 4035 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LINEA TRANSMISION 4800 | P22032800429 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 976470 | keep | 0 | Mar | 2022 | 0.66507 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-03-28 19:43 | 2022-03-28 23:45 | 3718 | 004:02 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LINEA TRANSMISION 4800 | P22032800429 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 242 | 2022-03-28 | 899756 | keep | 0 | Mar | 2022 | 0.61282 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
FAJARDO | 2022-03-28 20:03 | 2022-03-28 20:04 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22032800090 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 2286 | keep | 0 | Mar | 2022 | 0.001557 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-03-28 20:03 | 2022-03-28 20:04 | 693 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22032800091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 693 | keep | 0 | Mar | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
FAJARDO | 2022-03-28 20:04 | 2022-03-28 20:40 | 239 | 000:36 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | R22032800064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 36 | 2022-03-28 | 8604 | keep | 0 | Mar | 2022 | 0.0058601 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
MAYAGÃœEZ | 2022-03-28 20:04 | 2022-03-29 10:45 | 25 | 014:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032800353 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2022-03-28 | 22025 | keep | 0 | Mar | 2022 | 0.015001 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-03-28 20:07 | 2022-03-28 23:08 | 120 | 003:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE ELIMINO LINEA PARTIDA FUERA DE USO | A22032800096 | Partial_restoration | Wire Down | Include | Include | Equipment | 181 | 2022-03-28 | 21720 | keep | 0 | Mar | 2022 | 0.014793 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-28 20:29 | 2022-03-28 20:30 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22032800369 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-28 | 6285 | keep | 0 | Mar | 2022 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2022-03-28 20:30 | 2022-03-29 01:00 | 300 | 004:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M22032800261 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-03-28 | 81000 | keep | 0 | Mar | 2022 | 0.055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-28 20:31 | 2022-03-29 09:21 | 40 | 012:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN C/L MAL TIEMPO LLUVIA | B22032800224 | New_Event | Bad Weather | Include | Include | Weather | 770 | 2022-03-28 | 30800 | keep | 0 | Mar | 2022 | 0.020978 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-28 20:33 | 2022-03-29 00:59 | 2565 | 004:26 | S | LINEA DE TRANSMISION 38KV | SE REPARO LINEA 4800 Y AL ENERGIZAR SE INSTALO 2 PUENTES PORTATILES EN 3502-01 (SALIDA) Y SE CERRO B/I CONTRA 3502-02 Y SE CERRO 3502-02. | C22032800165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 266 | 2022-03-28 | 682290 | keep | 0 | Mar | 2022 | 0.4647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-03-28 20:33 | 2022-03-29 00:59 | 3565 | 004:26 | S | LINEA DE TRANSMISION 38KV | SE REPARO LINEA 4800 Y AL ENERGIZAR SE INSTALO 2 PUENTES PORTATILES EN 3502-01 (SALIDA) Y SE CERRO B/I CONTRA 3502-02 Y SE CERRO 3502-02. | C22032800165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 266 | 2022-03-28 | 948290 | keep | 0 | Mar | 2022 | 0.64588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-28 20:40 | 2022-03-28 21:55 | 200 | 001:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | S22032800000 | New_Event | Wire Down | Include | Include | Equipment | 75 | 2022-03-28 | 15000 | keep | 0 | Mar | 2022 | 0.010216 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-03-28 20:44 | 2022-03-29 10:37 | 60 | 013:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22032800097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 833 | 2022-03-28 | 49980 | keep | 0 | Mar | 2022 | 0.034041 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-03-28 21:07 | 2022-03-29 05:35 | 70 | 008:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22032800174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 508 | 2022-03-28 | 35560 | keep | 0 | Mar | 2022 | 0.02422 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-03-28 21:13 | 2022-03-28 21:14 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8500 | C22032800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 2725 | keep | 0 | Mar | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-28 21:13 | 2022-03-28 21:14 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8500 | C22032800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-28 21:13 | 2022-03-28 21:14 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8500 | C22032800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-28 | 1437 | keep | 0 | Mar | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
UTUADO | 2022-03-28 21:23 | 2022-03-29 08:23 | 4 | 011:00 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22032800108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2022-03-28 | 2640 | keep | 0 | Mar | 2022 | 0.0017981 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-03-28 21:34 | 2022-03-29 01:40 | 206 | 004:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B22032800238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-03-28 | 50676 | keep | 0 | Mar | 2022 | 0.034515 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
BAYAMON | 2022-03-28 21:49 | 2022-03-29 05:55 | 20 | 008:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1 X 10 | B22032800242 | New_Event | Cutout Failure | Include | Include | Equipment | 486 | 2022-03-28 | 9720 | keep | 0 | Mar | 2022 | 0.0066202 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-03-28 22:46 | 2022-03-29 11:54 | 10 | 013:08 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | C22032800196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 788 | 2022-03-28 | 7880 | keep | 0 | Mar | 2022 | 0.005367 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-28 22:59 | 2022-03-29 00:34 | 100 | 001:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | A22032800138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-03-28 | 9500 | keep | 0 | Mar | 2022 | 0.0064704 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-03-28 23:41 | 2022-03-28 23:43 | 2725 | 000:02 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA PARA REALIZAR OPERACIONES | C22032800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-28 | 5450 | keep | 0 | Mar | 2022 | 0.003712 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-28 23:41 | 2022-03-28 23:43 | 1834 | 000:02 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA PARA REALIZAR OPERACIONES | C22032800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-28 | 3668 | keep | 0 | Mar | 2022 | 0.0024983 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-28 23:41 | 2022-03-28 23:43 | 1437 | 000:02 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA PARA REALIZAR OPERACIONES | C22032800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-28 | 2874 | keep | 0 | Mar | 2022 | 0.0019575 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BAYAMON | 2022-03-28 23:43 | 2022-03-28 23:45 | 169 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1116-05 CERRADO POR CONTROL | S22032800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-28 | 338 | keep | 0 | Mar | 2022 | 0.00023021 | 0.00011511 | Momentary | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-03-28 23:43 | 2022-03-28 23:45 | 5 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA 1116-04 Y 1117-08 CERRADO POR CONTROL | S22032800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-28 | 10 | keep | 0 | Mar | 2022 | 6.811e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-28 23:43 | 2022-03-28 23:45 | 466 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1116-05 CERRADO POR CONTROL | S22032800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-28 | 932 | keep | 0 | Mar | 2022 | 0.00063478 | 0.00031739 | Momentary | FALSE | FALSE | Not_TMED_Event | 466
CAGUAS | 2022-03-29 00:26 | 2022-03-29 00:27 | 1893 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 1893 | keep | 0 | Mar | 2022 | 0.0012893 | 0.0012893 | Momentary | FALSE | FALSE | Not_TMED_Event | 1893
VEGA BAJA | 2022-03-29 00:58 | 2022-03-29 00:59 | 603 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO LLEVA LA CARGA DEL 9206-09 | B22032900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 603 | keep | 0 | Mar | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2022-03-29 00:58 | 2022-03-29 00:59 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO CARGA P0R EL 9206-08 | B22032900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 6 | keep | 0 | Mar | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-03-29 01:09 | 2022-03-29 01:10 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B22032900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
SAN JUAN | 2022-03-29 01:59 | 2022-03-29 03:28 | 49 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22032900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-03-29 | 4361 | keep | 0 | Mar | 2022 | 0.0029703 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
ARECIBO | 2022-03-29 04:57 | 2022-03-29 07:58 | 50 | 003:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE AVERIADO | A22032900003 | New_Event | Cutout Failure | Include | Include | Equipment | 181 | 2022-03-29 | 9050 | keep | 0 | Mar | 2022 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-03-29 05:06 | 2022-03-29 05:07 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR CARGA POR EL 9902-03 | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 2280 | keep | 0 | Mar | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-03-29 05:06 | 2022-03-29 05:07 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9902-03 LLEVANDO 9902-02 | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 1617 | keep | 0 | Mar | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
PONCE | 2022-03-29 05:07 | 2022-03-29 12:29 | 2751 | 007:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 442 | 2022-03-29 | 1215942 | keep | 0 | Mar | 2022 | 0.82817 | 0.0018737 | Sustained | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2022-03-29 05:07 | 2022-03-29 11:45 | 576 | 006:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 398 | 2022-03-29 | 229248 | keep | 0 | Mar | 2022 | 0.15614 | 0.00039231 | Sustained | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2022-03-29 05:07 | 2022-03-29 12:30 | 2584 | 007:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 443 | 2022-03-29 | 1144712 | keep | 0 | Mar | 2022 | 0.77966 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-03-29 05:07 | 2022-03-29 11:45 | 4035 | 006:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 398 | 2022-03-29 | 1605930 | keep | 0 | Mar | 2022 | 1.0938 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2022-03-29 05:07 | 2022-03-29 11:45 | 3718 | 006:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 398 | 2022-03-29 | 1479764 | keep | 0 | Mar | 2022 | 1.0079 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2022-03-29 05:37 | 2022-03-29 09:39 | 30 | 004:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-03-29 | 7260 | keep | 0 | Mar | 2022 | 0.0049448 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-29 05:55 | 2022-03-29 05:56 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22032900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 3438 | keep | 0 | Mar | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2022-03-29 05:56 | 2022-03-29 10:20 | 20 | 004:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1 X 10 | B22032800242 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 264 | 2022-03-29 | 5280 | keep | 0 | Mar | 2022 | 0.0035962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-29 06:12 | 2022-03-29 08:16 | 80 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CL | B22032900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-03-29 | 9920 | keep | 0 | Mar | 2022 | 0.0067565 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-03-29 06:20 | 2022-03-29 06:21 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 Y 4800 | C2203290000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 2725 | keep | 0 | Mar | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-29 06:20 | 2022-03-29 06:21 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 Y 4800 | C2203290000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-29 06:20 | 2022-03-29 06:21 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 Y 4800 | C2203290000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 1437 | keep | 0 | Mar | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2022-03-29 06:20 | 2022-03-29 11:45 | 2565 | 005:25 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 4600 | C22032900090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-03-29 | 833625 | keep | 0 | Mar | 2022 | 0.56778 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-03-29 06:20 | 2022-03-29 11:45 | 3565 | 005:25 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 4600 | C22032900090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-03-29 | 1158625 | keep | 0 | Mar | 2022 | 0.78913 | 0.0024281 | Sustained | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 1922 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 1741332 | keep | 0 | Mar | 2022 | 1.186 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 2235 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900091 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 2024910 | keep | 0 | Mar | 2022 | 1.3792 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 713 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 645978 | keep | 0 | Mar | 2022 | 0.43997 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 1067 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 966702 | keep | 0 | Mar | 2022 | 0.65842 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2022-03-29 06:20 | 2022-03-29 13:37 | 75 | 007:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 437 | 2022-03-29 | 32775 | keep | 0 | Mar | 2022 | 0.022323 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-03-29 06:20 | 2022-03-29 13:37 | 449 | 007:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 437 | 2022-03-29 | 196213 | keep | 0 | Mar | 2022 | 0.13364 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 1293 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 1171458 | keep | 0 | Mar | 2022 | 0.79787 | 0.00088066 | Sustained | FALSE | FALSE | Not_TMED_Event | 1293
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 426 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 385956 | keep | 0 | Mar | 2022 | 0.26287 | 0.00029015 | Sustained | FALSE | FALSE | Not_TMED_Event | 426
PONCE | 2022-03-29 06:20 | 2022-03-29 21:26 | 1556 | 015:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P22032900094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 906 | 2022-03-29 | 1409736 | keep | 0 | Mar | 2022 | 0.96016 | 0.0010598 | Sustained | FALSE | FALSE | Not_TMED_Event | 1556
PONCE | 2022-03-29 06:20 | 2022-03-29 11:45 | 1606 | 005:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-03-29 | 521950 | keep | 0 | Mar | 2022 | 0.3555 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2022-03-29 06:20 | 2022-03-29 11:45 | 29 | 005:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P22032900067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-03-29 | 9425 | keep | 0 | Mar | 2022 | 0.0064193 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CAGUAS | 2022-03-29 06:23 | 2022-03-29 11:42 | 90 | 005:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22032900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2022-03-29 | 28710 | keep | 0 | Mar | 2022 | 0.019554 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-03-29 06:25 | 2022-03-29 09:35 | 100 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032900009 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2022-03-29 | 19000 | keep | 0 | Mar | 2022 | 0.012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-03-29 06:47 | 2022-03-29 10:59 | 10 | 004:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN C/L Y 1 X 15 EN XMR CRUCE X AVE | R22032900004 | New_Event |  |  | Include | Wildlife | 252 | 2022-03-29 | 2520 | keep | 0 | Mar | 2022 | 0.0017164 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-29 06:54 | 2022-03-29 12:09 | 13 | 005:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B22032900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 315 | 2022-03-29 | 4095 | keep | 0 | Mar | 2022 | 0.0027891 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2022-03-29 07:17 | 2022-03-29 11:39 | 100 | 004:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22290300029 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2022-03-29 | 26200 | keep | 0 | Mar | 2022 | 0.017845 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-03-29 07:20 | 2022-03-29 07:21 | 3701 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22032900031 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-29 | 3701 | keep | 0 | Mar | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-03-29 07:21 | 2022-03-29 10:14 | 166 | 002:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORFTE DE LINEA CRUCE CON AVE | C22032900032 | 1st_after_momentary |  |  | Include | Wildlife | 173 | 2022-03-29 | 28718 | keep | 0 | Mar | 2022 | 0.01956 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
CAGUAS | 2022-03-29 07:41 | 2022-03-29 15:24 | 18 | 007:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA EN RISER | C22032900041 | New_Event | Cutout Failure | Include | Include | Equipment | 463 | 2022-03-29 | 8334 | keep | 0 | Mar | 2022 | 0.0056762 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-03-29 07:48 | 2022-03-30 04:58 | 8 | 021:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | M22032900018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1270 | 2022-03-29 | 10160 | keep | 0 | Mar | 2022 | 0.0069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-29 07:58 | 2022-03-29 21:50 | 10 | 013:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032900021 | New_Event | Bad Weather | Include | Include | Weather | 832 | 2022-03-29 | 8320 | keep | 0 | Mar | 2022 | 0.0056667 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-03-29 07:59 | 2022-03-29 13:29 | 100 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22032900046 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2022-03-29 | 33000 | keep | 0 | Mar | 2022 | 0.022476 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-29 08:08 | 2022-03-29 12:34 | 15 | 004:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA POR ACCIDENTE VEHICULAR | M22032900026 | New_Event |  |  | Include | Wildlife | 266 | 2022-03-29 | 3990 | keep | 0 | Mar | 2022 | 0.0027176 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-03-29 08:08 | 2022-03-29 13:19 | 80 | 005:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-03-29 | 24880 | keep | 0 | Mar | 2022 | 0.016946 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-03-29 08:10 | 2022-03-29 08:11 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES DEL ALINEA 8500 | C2203290000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 2725 | keep | 0 | Mar | 2022 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-29 08:10 | 2022-03-29 08:11 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES DEL ALINEA 8500 | C2203290000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 1834 | keep | 0 | Mar | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-29 08:10 | 2022-03-29 08:11 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | OPERACIONES DEL ALINEA 8500 | C2203290000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 1437 | keep | 0 | Mar | 2022 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BAYAMON | 2022-03-29 08:19 | 2022-03-29 08:20 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 5961 | keep | 0 | Mar | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
MAYAGÃœEZ | 2022-03-29 08:30 | 2022-03-29 11:47 | 1 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032900032 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2022-03-29 | 197 | keep | 0 | Mar | 2022 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-29 08:43 | 2022-03-29 13:00 | 15 | 004:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22032900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-03-29 | 3855 | keep | 0 | Mar | 2022 | 0.0026256 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-03-29 08:43 | 2022-03-29 12:39 | 5 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 Y 2 X 25 EN TRANSFORMADORES CRUCE CON AVE | C22032900080 | New_Event |  |  | Include | Wildlife | 236 | 2022-03-29 | 1180 | keep | 0 | Mar | 2022 | 0.00080369 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-03-29 08:52 | 2022-03-29 16:56 | 40 | 008:04 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | M22032900037 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 484 | 2022-03-29 | 19360 | keep | 0 | Mar | 2022 | 0.013186 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-03-29 08:58 | 2022-03-29 12:44 | 10 | 003:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A22032900018 | New_Event | Wire Down | Include | Include | Equipment | 226 | 2022-03-29 | 2260 | keep | 0 | Mar | 2022 | 0.0015393 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-29 09:11 | 2022-03-29 15:30 | 10 | 006:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR MAL TIEMPO | A22032900020 | New_Event | Bad Weather | Include | Include | Weather | 379 | 2022-03-29 | 3790 | keep | 0 | Mar | 2022 | 0.0025814 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-29 09:23 | 2022-03-29 10:52 | 15 | 001:29 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | B22032800159 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 89 | 2022-03-29 | 1335 | keep | 0 | Mar | 2022 | 0.00090926 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-29 09:32 | 2022-03-29 14:21 | 27 | 004:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE RETIRO AVE QUE CRUZO PARARRAYO | B22032900026 | New_Event |  |  | Include | Wildlife | 289 | 2022-03-29 | 7803 | keep | 0 | Mar | 2022 | 0.0053146 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-03-29 09:33 | 2022-03-29 14:49 | 3 | 005:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTARON 2 TRAMOS PRIMARIOS Y SE REALIZO DESGANCHE | B22032900018 | New_Event | Wire Down | Include | Include | Equipment | 316 | 2022-03-29 | 948 | keep | 0 | Mar | 2022 | 0.00064568 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 1339 | keep | 0 | Mar | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 470 | keep | 0 | Mar | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 2483 | keep | 0 | Mar | 2022 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 2190 | keep | 0 | Mar | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 3006 | keep | 0 | Mar | 2022 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 179 | keep | 0 | Mar | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 107 | keep | 0 | Mar | 2022 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 1666 | keep | 0 | Mar | 2022 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 09:40 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-29 | 4387 | keep | 0 | Mar | 2022 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 11:29 | 3147 | 001:50 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES INSPECCIONO E HIZO PRUEBAS A INTERRUPTOR CERRADO POR CCE | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-03-29 | 346170 | keep | 0 | Mar | 2022 | 0.23577 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-03-29 09:39 | 2022-03-29 11:29 | 4304 | 001:50 | S | LINEA DE TRANSMISION 38KV | PERSONAL DE SUBESTACIONES INSPECCIONO E HIZO PRUEBAS A INTERRUPTOR CERRADO POR CCE | M22032900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-03-29 | 473440 | keep | 0 | Mar | 2022 | 0.32246 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
ARECIBO | 2022-03-29 09:46 | 2022-03-29 15:28 | 1 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A22032900052 | New_Event | Bad Weather | Include | Include | Weather | 342 | 2022-03-29 | 342 | keep | 0 | Mar | 2022 | 0.00023293 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-29 10:08 | 2022-03-29 10:09 | 71 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22032900119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 71 | keep | 0 | Mar | 2022 | 4.8358e-05 | 4.8358e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2022-03-29 10:14 | 2022-03-29 10:15 | 3701 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22032900122 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-29 | 3701 | keep | 0 | Mar | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-03-29 10:15 | 2022-03-29 10:39 | 166 | 000:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORFTE DE LINEA CRUCE CON AVE | C22032900032 | 1st_after_momentary |  |  | Include | Wildlife | 24 | 2022-03-29 | 3984 | keep | 0 | Mar | 2022 | 0.0027135 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
AGUADILLA | 2022-03-29 10:18 | 2022-03-29 12:30 | 12 | 002:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO DE TRANSFORMADOR | M22032900076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 132 | 2022-03-29 | 1584 | keep | 0 | Mar | 2022 | 0.0010789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-29 10:50 | 2022-03-29 16:32 | 35 | 005:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | A22032900034 | New_Event | Cutout Failure | Include | Include | Equipment | 342 | 2022-03-29 | 11970 | keep | 0 | Mar | 2022 | 0.0081527 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-03-29 11:02 | 2022-03-29 11:35 | 2 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R22032900010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-03-29 | 66 | keep | 0 | Mar | 2022 | 4.4952e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-03-29 11:10 | 2022-03-29 13:00 | 100 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETEZAR LINEAS PRIMARIAS | A22032900037 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-03-29 | 11000 | keep | 0 | Mar | 2022 | 0.007492 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-29 11:13 | 2022-03-29 19:02 | 14 | 007:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REEMPLAZARON CONECTORES SULFATADOS | C22032900060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 469 | 2022-03-29 | 6566 | keep | 0 | Mar | 2022 | 0.0044721 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2022-03-29 11:15 | 2022-03-29 11:26 | 1530 | 0:11 | P | DESGANCHE | DISPARO DEL 2604-03 LLEVANDO 65% DEL 2604-01 SE VERIFICO PERSONAL FUERA | C22032900134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 11 | 2022-03-29 | 16830 | keep | 0 | Mar | 2022 | 0.011463 | 0.0010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 1530
HUMACAO | 2022-03-29 11:15 | 2022-03-29 11:26 | 1593 | 000:11 | T | DESGANCHE | DISPARO SE VERIFICO PERSONAL FUERA | C22032900134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 11 | 2022-03-29 | 17523 | keep | 0 | Mar | 2022 | 0.011935 | 0.001085 | Sustained | FALSE | FALSE | Not_TMED_Event | 1593
CAGUAS | 2022-03-29 11:15 | 2022-03-30 17:24 | 15 | 030:09 | P | ESTRUCTURA AVERIADA | 1 X 25 EN C/L REMPLAZO POSTE PARTIDO | C22032900135 | New_Event | Defective Pole | Include | Include | Equipment | 1809 | 2022-03-29 | 27135 | keep | 0 | Mar | 2022 | 0.018482 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-29 11:22 | 2022-03-29 11:24 | 520 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 20% DE LA CARGA POR EL 1717-04 SE CERRO POR SCADA | B22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 1040 | keep | 0 | Mar | 2022 | 0.00070834 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
HUMACAO | 2022-03-29 11:26 | 2022-03-29 14:45 | 1074 | 003:19 | P | DESGANCHE | RAMA CRUZO FASES, CERRARON INTELLIRRUPTER 2604-03G | C22032900144 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-03-29 | 213726 | keep | 0 | Mar | 2022 | 0.14557 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-29 11:29 | 2022-03-29 17:20 | 30 | 005:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2022-03-29 | 10530 | keep | 0 | Mar | 2022 | 0.0071719 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-03-29 11:30 | 2022-03-29 12:06 | 19 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P22032900295 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-03-29 | 684 | keep | 0 | Mar | 2022 | 0.00046587 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-03-29 11:32 | 2022-03-29 11:33 | 4176 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22032900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-03-29 | 4176 | keep | 0 | Mar | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-03-29 11:33 | 2022-03-29 18:17 | 33 | 006:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR Y SE REALIZO DESGANCHE | B22032900039 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 404 | 2022-03-29 | 13332 | keep | 0 | Mar | 2022 | 0.0090804 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-03-29 11:35 | 2022-03-29 13:26 | 1584 | 001:51 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M22032900097 | New_Event | Wire Down | Include | Include | Equipment | 111 | 2022-03-29 | 175824 | keep | 0 | Mar | 2022 | 0.11975 | 0.0010789 | Sustained | FALSE | FALSE | Not_TMED_Event | 1584
SAN JUAN | 2022-03-29 11:42 | 2022-03-29 13:20 | 50 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22032900066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-03-29 | 4900 | keep | 0 | Mar | 2022 | 0.0033374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-29 11:42 | 2022-03-29 21:44 | 15 | 010:02 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T19 AL T20 SE CONSTRUYO AEREO PROVISIONAL EXISTENTE AL T20 | C22032900043 | New_Event | UG Cable Fault | Include | Include | Equipment | 602 | 2022-03-29 | 9030 | keep | 0 | Mar | 2022 | 0.0061503 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-03-29 11:43 | 2022-03-29 11:45 | 2725 | 000:02 | S | NO SE REPORTO CAUSA | OPERACIONES EN LA LINEA 8500 | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 5450 | keep | 0 | Mar | 2022 | 0.003712 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2022-03-29 11:43 | 2022-03-29 11:45 | 1834 | 000:02 | S | NO SE REPORTO CAUSA | OPERACIONES EN LA LINEA 8500 | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 3668 | keep | 0 | Mar | 2022 | 0.0024983 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-03-29 11:43 | 2022-03-29 11:45 | 1437 | 000:02 | S | NO SE REPORTO CAUSA | OPERACIONES EN LA LINEA 8500 | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 2874 | keep | 0 | Mar | 2022 | 0.0019575 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
CAGUAS | 2022-03-29 11:48 | 2022-03-29 13:50 | 10 | 002:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REEMPLAZO CAJA PARTIDA | C22032900147 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-03-29 | 1220 | keep | 0 | Mar | 2022 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-29 11:57 | 2022-03-29 13:30 | 451 | 001:33 | T | DESGANCHE | DISPARO SE CERRO INTERRUPTOR 1904-06 SECCIONALIZANDO 1901-03 PARA REALIZAR DESGANCHE DE ENREDADERA. 75% EN SERVICIO | S22032900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-03-29 | 41943 | keep | 0 | Mar | 2022 | 0.028567 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 1935 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 5805 | keep | 0 | Mar | 2022 | 0.0039538 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 3 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA CARGA POR EL 1707-05 | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 9 | keep | 0 | Mar | 2022 | 6.1299e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 61 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA CARGA POR EL 1707-05 | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 183 | keep | 0 | Mar | 2022 | 0.00012464 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 1501 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 4503 | keep | 0 | Mar | 2022 | 0.003067 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 546 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA LLEVA LA CARGA DEL 1707-02 Y 1707-03 | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 1638 | keep | 0 | Mar | 2022 | 0.0011156 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 959 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA CARGA POR EL 1904-07 | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 2877 | keep | 0 | Mar | 2022 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 1264 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA CARGA POR EL 1904-07 | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 3792 | keep | 0 | Mar | 2022 | 0.0025827 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2022-03-29 11:58 | 2022-03-29 12:01 | 620 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BUENA VISTA | B22032900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2022-03-29 | 1860 | keep | 0 | Mar | 2022 | 0.0012668 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2022-03-29 12:02 | 2022-03-29 12:03 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1706-03 | B22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 1382 | keep | 0 | Mar | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-03-29 12:02 | 2022-03-29 12:03 | 663 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1706-02 | B22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 663 | keep | 0 | Mar | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
CAGUAS | 2022-03-29 12:02 | 2022-03-29 19:59 | 23 | 007:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE CON AVE | C22032900156 | New_Event |  |  | Include | Wildlife | 477 | 2022-03-29 | 10971 | keep | 0 | Mar | 2022 | 0.0074723 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-03-29 12:05 | 2022-03-29 12:06 | 2435 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR CARGA POR EL 1909-08 | B22032900000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-29 | 2435 | keep | 0 | Mar | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-03-29 12:05 | 2022-03-29 12:06 | 2956 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR LLEVE LA CARGA DEL 1907-05 | B22032900000 | New_Event |  |  | Include | Wildlife | 1 | 2022-03-29 | 2956 | keep | 0 | Mar | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-03-29 12:06 | 2022-03-29 17:34 | 111 | 005:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L SE RETIRO AVE CRUZANDO LINEAS | S22032900117 | 1st_after_momentary |  |  | Include | Wildlife | 328 | 2022-03-29 | 36408 | keep | 0 | Mar | 2022 | 0.024797 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
BAYAMON | 2022-03-29 12:09 | 2022-03-29 12:10 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1720-08 | B22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 2402 | keep | 0 | Mar | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-03-29 12:09 | 2022-03-29 12:10 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1709-02 | B22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-29 12:15 | 2022-03-29 15:30 | 100 | 003:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032900128 | New_Event | Bad Weather | Include | Include | Weather | 195 | 2022-03-29 | 19500 | keep | 0 | Mar | 2022 | 0.013281 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-03-29 12:35 | 2022-03-29 16:55 | 60 | 004:20 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032900150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-03-29 | 15600 | keep | 0 | Mar | 2022 | 0.010625 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-29 12:36 | 2022-03-29 13:14 | 64 | 000:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22032900080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-03-29 | 2432 | keep | 0 | Mar | 2022 | 0.0016564 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2022-03-29 12:39 | 2022-03-29 12:40 | 533 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 533 | keep | 0 | Mar | 2022 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
CAGUAS | 2022-03-29 12:43 | 2022-03-29 17:49 | 100 | 005:06 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C22032900178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-03-29 | 30600 | keep | 0 | Mar | 2022 | 0.020842 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-03-29 12:48 | 2022-03-29 13:20 | 50 | 000:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X REPTIL | R22032900012 | New_Event |  |  | Include | Wildlife | 32 | 2022-03-29 | 1600 | keep | 0 | Mar | 2022 | 0.0010898 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-03-29 12:57 | 2022-03-30 08:47 | 6 | 019:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22032900186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1190 | 2022-03-29 | 7140 | keep | 0 | Mar | 2022 | 0.004863 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-29 13:14 | 2022-03-29 13:17 | 3460 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 Y UN 30% DEL 1204-04 | S22032900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-03-29 | 10380 | keep | 0 | Mar | 2022 | 0.0070698 | 0.0023566 | Momentary | FALSE | FALSE | Not_TMED_Event | 3460
SAN JUAN | 2022-03-29 13:14 | 2022-03-29 13:17 | 1500 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO PARTE POR 1336-8 | S22032900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-03-29 | 4500 | keep | 0 | Mar | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-29 13:14 | 2022-03-29 13:17 | 5290 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09, UN 30% DEL 1204-04 Y PARTE DEL 1204-05 | S22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-29 | 15870 | keep | 0 | Mar | 2022 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-29 13:14 | 2022-03-29 13:17 | 207 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 Y UN 30% DEL 1204-04 | S22032900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2022-03-29 | 621 | keep | 0 | Mar | 2022 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-03-29 13:17 | 2022-03-29 13:23 | 64 | 000:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22032900080 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-03-29 | 384 | keep | 0 | Mar | 2022 | 0.00026154 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-29 13:23 | 2022-03-29 13:24 | 3460 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 Y UN 30% DEL 1204-04 | S22032900000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-03-29 | 3460 | keep | 0 | Mar | 2022 | 0.0023566 | 0.0023566 | Momentary | FALSE | FALSE | Not_TMED_Event | 3460
SAN JUAN | 2022-03-29 13:23 | 2022-03-29 14:43 | 64 | 001:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S22032900080 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-03-29 | 5120 | keep | 0 | Mar | 2022 | 0.0034872 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-29 13:23 | 2022-03-29 13:24 | 1500 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO PARTE POR 1336-8 | S22032900000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-03-29 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-29 13:23 | 2022-03-29 13:24 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09, UN 30% DEL 1204-04 Y PARTE DEL 1204-05 | S22032900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 5290 | keep | 0 | Mar | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-29 13:23 | 2022-03-29 13:24 | 207 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1336-09 Y UN 30% DEL 1204-04 | S22032900000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2022-03-29 | 207 | keep | 0 | Mar | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
HUMACAO | 2022-03-29 13:23 | 2022-03-29 13:26 | 327 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-29 | 981 | keep | 0 | Mar | 2022 | 0.00066815 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
FAJARDO | 2022-03-29 13:25 | 2022-03-29 16:21 | 7 | 002:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 NX DE 10A CAMION DEMOLIENDO CASA DAÃ‘O LA TOMA | R22032900014 | New_Event |  |  | Include | Wildlife | 176 | 2022-03-29 | 1232 | keep | 0 | Mar | 2022 | 0.00083911 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-03-29 13:30 | 2022-03-29 16:34 | 113 | 003:04 | P | DESGANCHE | SE CERRO MACHETES Y SE REALIZO DESGANCHE DE ENREDADERA 100% EN SERVICIO | S22032900054 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-03-29 | 20792 | keep | 0 | Mar | 2022 | 0.014161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-29 13:34 | 2022-03-29 14:17 | 1483 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA SECCIONALIZAR NEUTRAL PARTIDO CRUZANDO 30% POR 1336-8 | S22032900225 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-03-29 | 63769 | keep | 0 | Mar | 2022 | 0.043433 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-29 13:34 | 2022-03-29 14:17 | 1500 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA SECCIONALIZAR NEUTRAL PARTIDO CRUZANDO PARTE POR 1336-8 | S22032900225 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 43 | 2022-03-29 | 64500 | keep | 0 | Mar | 2022 | 0.043931 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-29 13:34 | 2022-03-29 14:17 | 5290 | 000:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA SECCIONALIZAR NEUTRAL PARTIDO CRUZANDO FASE LLEVA 1336-9 Y 30% DEL 1204-4 Y PARTE DEL 1204-5 | S22032900225 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-03-29 | 227470 | keep | 0 | Mar | 2022 | 0.15493 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-29 13:34 | 2022-03-29 14:17 | 207 | 000:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA SECCIONALIZAR NEUTRAL PARTIDO CRUZANDO FASE SU CARGA POR 1336-8 | S22032900225 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 43 | 2022-03-29 | 8901 | keep | 0 | Mar | 2022 | 0.0060624 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2022-03-29 13:35 | 2022-03-29 16:37 | 5 | 003:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR REPARO TOMA AVERIADA POR PERSONAL DE AAA | R22032900015 | New_Event |  |  | Include | Wildlife | 182 | 2022-03-29 | 910 | keep | 0 | Mar | 2022 | 0.0006198 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-29 13:49 | 2022-03-29 16:38 | 324 | 002:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA PRINCIPAL SE DEJO CORTE DE LINEA INTERMEDIO ABIERTO PARA REALIZAR DESGANCHE. EN SERVICIO 280 CLTES | B22032900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-03-29 | 54756 | keep | 0 | Mar | 2022 | 0.037294 | 0.00022067 | Sustained | FALSE | FALSE | Not_TMED_Event | 324
PONCE | 2022-03-29 14:10 | 2022-03-29 16:59 | 15 | 002:49 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22032900335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-03-29 | 2535 | keep | 0 | Mar | 2022 | 0.0017266 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-03-29 14:16 | 2022-03-29 18:32 | 100 | 004:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA LAJAS LO ATIENDE DISTRITO DE YAUCO QUE ES LA REGION DE PONCE, PROPOSITO DEL DOC LO ATIENDE MAYAGÃœEZ | P22032900337 | New_Event | Cutout Failure | Include | Include | Equipment | 256 | 2022-03-29 | 25600 | keep | 0 | Mar | 2022 | 0.017436 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-03-29 14:17 | 2022-03-29 15:20 | 529 | 001:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL Y SE CERRO MACHETE 100% EN SERVICIO | S22032900225 | Partial_restoration | Wire Down | Include | Include | Equipment | 63 | 2022-03-29 | 33327 | keep | 0 | Mar | 2022 | 0.022699 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-29 14:44 | 2022-03-29 14:45 | 341 | 000:01 | T | CABLE SOTERRADO AVERIADO | SE ABRIO INTERRUPTOR 1717-05 PARA PODER ABRIR DE SU 6 A SU7 PARA CONECTAR AEREO PROVISIONAL HACIA CEMENTERIO NACIONAL QUE LE FALTABA 1 FASE. SU 6 Y SU 7 EN MAL ESTADO POR ESO SE DISPARO INTERRUPTOR. | B22032900094 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-03-29 | 341 | keep | 0 | Mar | 2022 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
CAGUAS | 2022-03-29 14:44 | 2022-03-31 12:37 | 15 | 045:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN C/L SE CERRO PUENTE ABIERTO DESGANCHE | C22032900219 | New_Event | Wire Down | Include | Include | Equipment | 2753 | 2022-03-29 | 41295 | keep | 0 | Mar | 2022 | 0.028126 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-29 14:45 | 2022-03-29 16:24 | 5 | 001:39 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE SU 7 A SUBESTACION CEMENTERIO NACIONAL POR AVERIA EN UNA DE SUS FASES | B22032900095 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 99 | 2022-03-29 | 495 | keep | 0 | Mar | 2022 | 0.00033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-03-29 14:57 | 2022-03-29 16:52 | 100 | 001:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22032900220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-03-29 | 11500 | keep | 0 | Mar | 2022 | 0.0078326 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-03-29 15:05 | 2022-03-29 17:21 | 200 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C22032900222 | New_Event |  |  | Include | Wildlife | 136 | 2022-03-29 | 27200 | keep | 0 | Mar | 2022 | 0.018526 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-03-29 15:11 | 2022-03-29 17:24 | 15 | 002:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER Y 1X 50 EN CORTE DE LINEA SE RETIRO AVE | B22032900102 | New_Event |  |  | Include | Wildlife | 133 | 2022-03-29 | 1995 | keep | 0 | Mar | 2022 | 0.0013588 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-29 15:37 | 2022-03-29 15:39 | 1483 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO 30% CARGA POR 1336-8 | S22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 2966 | keep | 0 | Mar | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-29 15:37 | 2022-03-29 15:39 | 1500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO PARTE POR 1336-8 | S22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-29 15:37 | 2022-03-29 15:39 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1336-9 Y 30% 1204-4 Y PARTE 1204-5 | S2203290000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 10580 | keep | 0 | Mar | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-29 15:37 | 2022-03-29 15:39 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1336-8 | S2203290000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-29 | 414 | keep | 0 | Mar | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-03-29 15:48 | 2022-03-29 16:46 | 1483 | 000:58 | P | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE CARR.65 INFANTERIA Y SE CERRO BKR. 30% POR 1336-8 | S22032900374 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-03-29 | 86014 | keep | 0 | Mar | 2022 | 0.058584 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-29 15:48 | 2022-03-29 16:46 | 1500 | 000:58 | P | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE CARR.65 INFANTERIA Y SE CERRO BKR. PARTE POR 1336-8 | S22032900374 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-03-29 | 87000 | keep | 0 | Mar | 2022 | 0.059255 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-29 15:48 | 2022-03-29 16:46 | 5290 | 000:58 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE CARR.65 INFANTERIA Y SE CERRO BKR. 90% EN SERVICIO Y 100% 1336-9 30% EN SERVICIO 1204-4 Y PARTE DEL 1204-5 | S22032900374 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-03-29 | 306820 | keep | 0 | Mar | 2022 | 0.20897 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-29 15:48 | 2022-03-29 16:46 | 207 | 000:58 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE CARR.65 INFANTERIA Y SE CERRO BKR. SU CARGA POR 1336-8 | S22032900374 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-03-29 | 12006 | keep | 0 | Mar | 2022 | 0.0081772 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-03-29 15:55 | 2022-03-29 16:21 | 9 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | B22032900077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-03-29 | 234 | keep | 0 | Mar | 2022 | 0.00015938 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2022-03-29 16:08 | 2022-03-29 17:30 | 12 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES | A22032900005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2022-03-29 | 984 | keep | 0 | Mar | 2022 | 0.0006702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-29 16:23 | 2022-03-29 18:50 | 5 | 002:27 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR PARARRAYO CRUZADO | A22032900088 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 147 | 2022-03-29 | 735 | keep | 0 | Mar | 2022 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-29 16:25 | 2022-03-29 18:12 | 232 | 001:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR PRIMARIA Y REMPLAZO DE 2 DISCOS | S22032900362 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2022-03-29 | 24824 | keep | 0 | Mar | 2022 | 0.016908 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
BAYAMON | 2022-03-29 16:38 | 2022-03-29 18:22 | 44 | 001:44 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEAINTERMEDIO SE REALIZO DESGANCHE. | B22032900078 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-03-29 | 4576 | keep | 0 | Mar | 2022 | 0.0031167 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-29 16:46 | 2022-03-29 17:35 | 529 | 000:49 | P | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO NADA Y SE CERRO MACHETE 100% EN SERVICIO | S22032900374 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-03-29 | 25921 | keep | 0 | Mar | 2022 | 0.017655 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-29 16:47 | 2022-03-29 20:00 | 25 | 003:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032900210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-03-29 | 4825 | keep | 0 | Mar | 2022 | 0.0032863 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-03-29 16:50 | 2022-03-29 19:40 | 4 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22032900235 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2022-03-29 | 680 | keep | 0 | Mar | 2022 | 0.00046314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-03-29 16:51 | 2022-03-29 16:52 | 595 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22032900394 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-29 | 595 | keep | 0 | Mar | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
PONCE | 2022-03-29 16:52 | 2022-03-29 21:53 | 140 | 005:01 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22032900521 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 301 | 2022-03-29 | 42140 | keep | 0 | Mar | 2022 | 0.028701 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2022-03-29 16:56 | 2022-03-29 18:51 | 88 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22032900146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-03-29 | 10120 | keep | 0 | Mar | 2022 | 0.0068927 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
PONCE | 2022-03-29 17:09 | 2022-03-29 18:58 | 100 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA CON POLLO | P22032900408 | New_Event |  |  | Include | Wildlife | 109 | 2022-03-29 | 10900 | keep | 0 | Mar | 2022 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-29 17:22 | 2022-03-29 17:59 | 8 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B22032900153 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-03-29 | 296 | keep | 0 | Mar | 2022 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-03-29 17:24 | 2022-03-29 20:25 | 20 | 003:01 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE ELIMINO PARARRAYO | B22032900028 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 181 | 2022-03-29 | 3620 | keep | 0 | Mar | 2022 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-29 17:53 | 2022-03-30 11:44 | 60 | 017:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22032900223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1071 | 2022-03-29 | 64260 | keep | 0 | Mar | 2022 | 0.043767 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-29 18:03 | 2022-03-29 22:41 | 11 | 004:38 | P | DESGANCHE | 1X10 EN XMR & SE LIMPIO ENRREDADERA | S22032900393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-03-29 | 3058 | keep | 0 | Mar | 2022 | 0.0020828 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2022-03-29 18:06 | 2022-03-29 20:28 | 80 | 002:22 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA PARARRAYO AVERIADO | P22032900441 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 142 | 2022-03-29 | 11360 | keep | 0 | Mar | 2022 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-03-29 18:09 | 2022-03-29 19:40 | 600 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZO DOS CAJAS PRIMARIAS EN SALIDA DE CONVERTIDOR | P22032900442 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2022-03-29 | 54600 | keep | 0 | Mar | 2022 | 0.037188 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
MAYAGÃœEZ | 2022-03-29 18:23 | 2022-03-29 19:05 | 15 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22032900230 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2022-03-29 | 630 | keep | 0 | Mar | 2022 | 0.00042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-29 18:28 | 2022-03-29 21:45 | 47 | 003:17 | P | NO SE REPORTO CAUSA | 1X80 EN RISER | S22032900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-03-29 | 9259 | keep | 0 | Mar | 2022 | 0.0063063 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-03-29 18:31 | 2022-03-29 21:34 | 25 | 003:03 | P | TRANSFORMADOR AVERIADO | 1 X 80 EN RISER Y 1 X 80 SUM-20 T-23 AVERIADO SE DEJARON 4 TRANSFORMADORES FUERA | S22032900399 | New_Event | Service Transformer Failure | Include | Include | Equipment | 183 | 2022-03-29 | 4575 | keep | 0 | Mar | 2022 | 0.003116 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-29 18:41 | 2022-03-29 20:55 | 461 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1X 65 EN CORTES DE LINEA SE RETIRO AVE | S22032900404 | New_Event |  |  | Include | Wildlife | 134 | 2022-03-29 | 61774 | keep | 0 | Mar | 2022 | 0.042074 | 0.00031399 | Sustained | FALSE | FALSE | Not_TMED_Event | 461
HUMACAO | 2022-03-29 18:48 | 2022-03-30 06:48 | 50 | 012:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22032900241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 720 | 2022-03-29 | 36000 | keep | 0 | Mar | 2022 | 0.024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-29 18:50 | 2022-03-29 21:36 | 5 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22032900164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-03-29 | 830 | keep | 0 | Mar | 2022 | 0.00056531 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-29 18:51 | 2022-03-29 20:05 | 18 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN AEREO PROVISIONAL | B22032900165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-03-29 | 1332 | keep | 0 | Mar | 2022 | 0.00090722 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-03-29 19:06 | 2022-03-30 04:29 | 22 | 009:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22032900237 | New_Event | Bad Weather | Include | Include | Weather | 563 | 2022-03-29 | 12386 | keep | 0 | Mar | 2022 | 0.008436 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2022-03-29 19:39 | 2022-03-29 22:23 | 101 | 002:44 | P | NO SE REPORTO CAUSA | 1X65 EN C/L & 1X40 EN C/L | S22032900419 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-03-29 | 16564 | keep | 0 | Mar | 2022 | 0.011282 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
PONCE | 2022-03-29 19:40 | 2022-03-29 21:24 | 2584 | 001:44 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE RETIRA CARGA A LINEA 4800 | P22032900513 | New_Event |  |  |  |  | 104 | 2022-03-29 | 268736 | keep | 0 | Mar | 2022 | 0.18303 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2022-03-29 19:44 | 2022-03-29 21:24 | 1606 | 001:40 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE RETIRA CARGA A LINEA 4800 | P22032900514 | New_Event |  |  |  |  | 100 | 2022-03-29 | 160600 | keep | 0 | Mar | 2022 | 0.10938 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
AGUADILLA | 2022-03-29 20:05 | 2022-03-30 01:20 | 40 | 005:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22032900243 | New_Event | Bad Weather | Include | Include | Weather | 315 | 2022-03-29 | 12600 | keep | 0 | Mar | 2022 | 0.0085818 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-29 20:08 | 2022-03-30 14:30 | 7 | 018:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22032900260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1102 | 2022-03-29 | 7714 | keep | 0 | Mar | 2022 | 0.005254 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-29 20:28 | 2022-03-30 03:20 | 30 | 006:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO | M22032900249 | New_Event | Bad Weather | Include | Include | Weather | 412 | 2022-03-29 | 12360 | keep | 0 | Mar | 2022 | 0.0084183 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-03-29 20:51 | 2022-03-29 23:56 | 6 | 003:05 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA ENCIMA DEL TRANSFORMADOR | A22032900104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-03-29 | 1110 | keep | 0 | Mar | 2022 | 0.00075602 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-29 21:02 | 2022-03-29 21:03 | 125 | 000:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22032900251 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-03-29 | 125 | keep | 0 | Mar | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-03-29 21:20 | 2022-03-29 23:12 | 50 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22032900106 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2022-03-29 | 5600 | keep | 0 | Mar | 2022 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-29 21:27 | 2022-03-29 21:37 | 20 | 000:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN RISER CHIRINGA CRUZO FASES | P22032900572 | New_Event |  |  | Include | Wildlife | 10 | 2022-03-29 | 200 | keep | 0 | Mar | 2022 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-03-29 21:34 | 2022-03-30 09:29 | 30 | 011:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-29 | S22032900399 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 715 | 2022-03-29 | 21450 | keep | 0 | Mar | 2022 | 0.014609 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-29 21:46 | 2022-03-30 01:57 | 2 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO DE LINEA @ CAJA (NO FUNDIO) | S22032900434 | New_Event | Wire Down | Include | Include | Equipment | 251 | 2022-03-29 | 502 | keep | 0 | Mar | 2022 | 0.00034191 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-03-29 22:29 | 2022-03-29 22:33 | 377 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22032900000 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2022-03-29 | 1508 | keep | 0 | Mar | 2022 | 0.0010271 | 0.00025677 | Momentary | FALSE | FALSE | Not_TMED_Event | 377
VEGA BAJA | 2022-03-29 22:33 | 2022-03-30 10:22 | 16 | 011:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO CAJA PRIMARIA | B22032900586 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 709 | 2022-03-29 | 11344 | keep | 0 | Mar | 2022 | 0.0077263 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2022-03-29 22:40 | 2022-03-29 23:42 | 55 | 001:02 | P | NO SE REPORTO CAUSA | 1X65 EN RISER | B22032900199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-03-29 | 3410 | keep | 0 | Mar | 2022 | 0.0023225 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2022-03-29 22:43 | 2022-03-29 22:44 | 528 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22032900260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-29 | 528 | keep | 0 | Mar | 2022 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
PONCE | 2022-03-29 22:51 | 2022-03-30 06:09 | 792 | 007:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR FUERTES LLUVIAS | P22032900592 | New_Event | Bad Weather | Include | Include | Weather | 438 | 2022-03-29 | 346896 | keep | 0 | Mar | 2022 | 0.23627 | 0.00053943 | Sustained | FALSE | FALSE | Not_TMED_Event | 792
PONCE | 2022-03-29 23:29 | 2022-03-30 04:38 | 1905 | 005:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO EN TRONCAL SE ABRIERON MACHETES Y SE CERRO INTERRUPTOR MANUALMENTE | P22032900597 | New_Event | Wire Down | Include | Include | Equipment | 309 | 2022-03-29 | 588645 | keep | 0 | Mar | 2022 | 0.40092 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
BAYAMON | 2022-03-29 23:54 | 2022-03-30 03:56 | 40 | 004:02 | P | TRANSFORMADOR AVERIADO | 1X50 EN C/L | B22032900202 | New_Event | Service Transformer Failure | Include | Include | Equipment | 242 | 2022-03-29 | 9680 | keep | 0 | Mar | 2022 | 0.006593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-03-30 00:56 | 2022-03-30 02:35 | 70 | 001:39 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S22033000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-03-30 | 6930 | keep | 0 | Mar | 2022 | 0.00472 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-03-30 01:35 | 2022-03-30 12:25 | 10 | 010:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR Y 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | S22033000004 | New_Event | Cutout Failure | Include | Include | Equipment | 650 | 2022-03-30 | 6500 | keep | 0 | Mar | 2022 | 0.0044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-30 04:10 | 2022-03-30 09:41 | 50 | 005:31 | P | DESGANCHE | 1 X 50 EN C/L | C22033000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-03-30 | 16550 | keep | 0 | Mar | 2022 | 0.011272 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-30 04:17 | 2022-03-30 11:11 | 50 | 006:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE | P22033000003 | New_Event |  |  | Include | Wildlife | 414 | 2022-03-30 | 20700 | keep | 0 | Mar | 2022 | 0.014099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-03-30 04:38 | 2022-03-30 05:05 | 1715 | 000:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO Y NO SE ENCONTRO NADA MAS SE CERRARON MACHETES Y QUEDO TODO EN SERVICIO | P22033000006 | Partial_restoration | Wire Down | Include | Include | Equipment | 27 | 2022-03-30 | 46305 | keep | 0 | Mar | 2022 | 0.031538 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 05:29 | 2022-03-30 10:35 | 25 | 005:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN AEREO PROVISIONAL SE LEVANTO CONDUCTOR | R22033000004 | New_Event | Wire Down | Include | Include | Equipment | 306 | 2022-03-30 | 7650 | keep | 0 | Mar | 2022 | 0.0052104 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-03-30 05:41 | 2022-03-30 09:00 | 50 | 003:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO PORTAFUSIBLE | R22033000012 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2022-03-30 | 9950 | keep | 0 | Mar | 2022 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-30 05:49 | 2022-03-30 12:30 | 50 | 006:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M22033000008 | New_Event | Cutout Failure | Include | Include | Equipment | 401 | 2022-03-30 | 20050 | keep | 0 | Mar | 2022 | 0.013656 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-03-30 05:51 | 2022-03-30 10:00 | 100 | 004:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22033000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-03-30 | 24900 | keep | 0 | Mar | 2022 | 0.016959 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-30 06:00 | 2022-03-30 11:10 | 40 | 005:10 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN PROVISIONAL, 1 X 80 EN SU-16, 1 X 65 EN PROVISIONAL Y1 X 100 EN SU-13 40 CLIENTES | B22033000303 | New_Event | UG Cable Fault | Include | Include | Equipment | 310 | 2022-03-30 | 12400 | keep | 0 | Mar | 2022 | 0.0084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-03-30 06:02 | 2022-03-30 12:39 | 30 | 006:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22033000010 | New_Event | Cutout Failure | Include | Include | Equipment | 397 | 2022-03-30 | 11910 | keep | 0 | Mar | 2022 | 0.0081118 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-03-30 06:15 | 2022-03-30 10:07 | 5 | 003:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R22033000015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-03-30 | 1160 | keep | 0 | Mar | 2022 | 0.00079007 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-30 06:23 | 2022-03-30 10:24 | 347 | 004:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22033000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-03-30 | 83627 | keep | 0 | Mar | 2022 | 0.056958 | 0.00023634 | Sustained | FALSE | FALSE | Not_TMED_Event | 347
PONCE | 2022-03-30 06:37 | 2022-03-30 06:38 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22033000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 3114 | keep | 0 | Mar | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2022-03-30 07:10 | 2022-03-30 10:47 | 125 | 003:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE QUE CRUZO LINEA | M22033000016 | New_Event |  |  | Include | Wildlife | 217 | 2022-03-30 | 27125 | keep | 0 | Mar | 2022 | 0.018475 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-03-30 07:11 | 2022-03-30 14:16 | 28 | 007:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA TRANSFORMADOR | S22033000025 | New_Event | Cutout Failure | Include | Include | Equipment | 425 | 2022-03-30 | 11900 | keep | 0 | Mar | 2022 | 0.008105 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2022-03-30 07:26 | 2022-03-30 08:52 | 200 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L Y 1 X 50 EN C/L MAL TIEMPO LLUVIAS | B22033000016 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2022-03-30 | 17200 | keep | 0 | Mar | 2022 | 0.011715 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-03-30 07:42 | 2022-03-30 13:18 | 34 | 005:36 | P | DESGANCHE | 1 X 50 EN C/L | C22033000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2022-03-30 | 11424 | keep | 0 | Mar | 2022 | 0.0077808 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2022-03-30 07:59 | 2022-03-30 11:53 | 130 | 003:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 80 EN C/L'S CRUCE X AVE | C22033000010 | New_Event |  |  | Include | Wildlife | 234 | 2022-03-30 | 30420 | keep | 0 | Mar | 2022 | 0.020719 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
PONCE | 2022-03-30 08:09 | 2022-03-30 11:16 | 100 | 003:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22033000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-03-30 | 18700 | keep | 0 | Mar | 2022 | 0.012736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-03-30 08:21 | 2022-03-30 10:05 | 150 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE NORMALIZO CARGA QUE ESTABA POR 1529-13 | S22033000037 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2022-03-30 | 15600 | keep | 0 | Mar | 2022 | 0.010625 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-03-30 08:21 | 2022-03-30 12:25 | 199 | 004:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE LEVANTO LINEA PRIMARIA TRONCAL 100% EN SERVICIO | S22033000037 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2022-03-30 | 48556 | keep | 0 | Mar | 2022 | 0.033071 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-03-30 08:25 | 2022-03-30 22:27 | 40 | 014:02 | P | DESGANCHE | 1X50 EN C/L SE CERRO PUENTE ABIERTO Y SE DESGANCHO | B22033000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2022-03-30 | 33680 | keep | 0 | Mar | 2022 | 0.022939 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-03-30 08:34 | 2022-03-30 08:36 | 853 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22033000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-30 | 1706 | keep | 0 | Mar | 2022 | 0.0011619 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
BAYAMON | 2022-03-30 08:36 | 2022-03-30 21:19 | 1 | 012:43 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | B22033000039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 763 | 2022-03-30 | 763 | keep | 0 | Mar | 2022 | 0.00051968 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-30 08:43 | 2022-03-30 12:30 | 45 | 003:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22033000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-03-30 | 10215 | keep | 0 | Mar | 2022 | 0.0069574 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-03-30 08:46 | 2022-03-30 11:25 | 50 | 002:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22033000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-03-30 | 7950 | keep | 0 | Mar | 2022 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-30 08:55 | 2022-03-30 22:41 | 100 | 013:46 | P | DESGANCHE | 1X80 EN C/L | B22033000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 826 | 2022-03-30 | 82600 | keep | 0 | Mar | 2022 | 0.056258 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-03-30 08:57 | 2022-03-30 12:42 | 2584 | 003:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO Y SE LEVANTO ALAMBRE SPACER PRIMARIO | P22033000019 | New_Event | Wire Down | Include | Include | Equipment | 225 | 2022-03-30 | 581400 | keep | 0 | Mar | 2022 | 0.39599 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
BAYAMON | 2022-03-30 09:00 | 2022-03-30 18:05 | 9 | 009:05 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR SECUNDARIO | B22033000049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 545 | 2022-03-30 | 4905 | keep | 0 | Mar | 2022 | 0.0033408 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-03-30 09:03 | 2022-03-30 09:06 | 1681 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-30 | 5043 | keep | 0 | Mar | 2022 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-03-30 09:03 | 2022-03-30 09:06 | 1598 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-4 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-30 | 4794 | keep | 0 | Mar | 2022 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-03-30 09:15 | 2022-03-30 12:44 | 80 | 003:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22033000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-03-30 | 16720 | keep | 0 | Mar | 2022 | 0.011388 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-03-30 09:22 | 2022-03-30 10:55 | 80 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA EN CORTE DE LINEA, SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA EN C/L Y SE REMPLAZO AISLADOR | R22033000029 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2022-03-30 | 7440 | keep | 0 | Mar | 2022 | 0.0050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-30 09:29 | 2022-03-30 09:31 | 1483 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO 30% POR 1336-8 | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-03-30 | 2966 | keep | 0 | Mar | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-30 09:29 | 2022-03-30 09:31 | 1500 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO PARTE POR 1336-8 | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-03-30 | 3000 | keep | 0 | Mar | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-30 09:29 | 2022-03-30 09:31 | 5290 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1336-9 Y 30% 1204-4 Y PARTE DEL 1204-5 SE PROBO QUEDO EN SERVICIO | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-03-30 | 10580 | keep | 0 | Mar | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-30 09:29 | 2022-03-30 09:31 | 207 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1336-8 | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-03-30 | 414 | keep | 0 | Mar | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-03-30 09:29 | 2022-03-30 13:15 | 45 | 003:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22033000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-03-30 | 10170 | keep | 0 | Mar | 2022 | 0.0069267 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-03-30 09:31 | 2022-03-30 11:02 | 30 | 001:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-29 | S22032900399 | New_Event | Service Transformer Failure | Include | Include | Equipment | 91 | 2022-03-30 | 2730 | keep | 0 | Mar | 2022 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-03-30 09:47 | 2022-03-30 09:48 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22033000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 2484 | keep | 0 | Mar | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
PONCE | 2022-03-30 09:53 | 2022-03-30 09:54 | 5063 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22033000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 5063 | keep | 0 | Mar | 2022 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
AGUADILLA | 2022-03-30 10:23 | 2022-03-30 13:28 | 26 | 003:05 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE NECESITA DESGANCHE | M22033000052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-03-30 | 4810 | keep | 0 | Mar | 2022 | 0.0032761 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-03-30 10:30 | 2022-03-30 11:58 | 10 | 001:28 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA Y SE HIZO DESGANCHE | S22033000030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 88 | 2022-03-30 | 880 | keep | 0 | Mar | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-30 10:38 | 2022-03-30 19:26 | 15 | 008:48 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN RISER SE REEMPLAZO DE XMR T-51 100KVA X 100KVA | B22033000068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 528 | 2022-03-30 | 7920 | keep | 0 | Mar | 2022 | 0.0053943 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-30 10:38 | 2022-03-30 14:14 | 25 | 003:36 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN C/L SE DEJO XMR QUEMADO T-51 FUERA PARA REEMPLAZARLO | B22033000068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 216 | 2022-03-30 | 5400 | keep | 0 | Mar | 2022 | 0.0036779 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-03-30 10:41 | 2022-03-30 11:23 | 8 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE DESGANCHO EN 2 PUNTOS DIFERENTES SE CORRIGIERON CONDICIONES EN 2 PUNTOS DIFERENTES Y SE REPARO EL BAJANTE XMR SECUNDARIO | R22032900060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-03-30 | 336 | keep | 0 | Mar | 2022 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-03-30 10:54 | 2022-03-30 16:07 | 5 | 005:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PARTIDO Y TRANSFORMADOR IMPACTADO POR CAMION | R22033000037 | New_Event |  |  | Include | Wildlife | 313 | 2022-03-30 | 1565 | keep | 0 | Mar | 2022 | 0.0010659 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-03-30 11:02 | 2022-03-30 11:03 | 1483 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO 30% POR 1336-8 | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1483 | keep | 0 | Mar | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-30 11:02 | 2022-03-30 11:03 | 1500 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1336-8 | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-30 11:02 | 2022-03-30 11:03 | 5290 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1336-9 30% DEL 1204-4 Y PARTE DEL 1204-5 SE PROBO QUEDO EN SERVICIO | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 5290 | keep | 0 | Mar | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-30 11:02 | 2022-03-30 11:03 | 207 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1336-8 | S22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 207 | keep | 0 | Mar | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-03-30 11:03 | 2022-03-30 11:16 | 30 | 000:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-29 | S22032900399 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 13 | 2022-03-30 | 390 | keep | 0 | Mar | 2022 | 0.00026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-30 11:04 | 2022-03-30 17:14 | 4 | 006:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA REPARAR PEDESTAL | S22033000127 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 370 | 2022-03-30 | 1480 | keep | 0 | Mar | 2022 | 0.001008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-03-30 11:16 | 2022-03-30 11:17 | 1483 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPASO SE PROBO QUEDO EN SERVICIO 30% POR 1204-4 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1483 | keep | 0 | Mar | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-30 11:16 | 2022-03-30 11:17 | 1500 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPASO SE PROBO QUEDO EN SERVICIO PARTE POR 1336-8 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-30 11:16 | 2022-03-30 11:17 | 5290 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPASO SE PROBO QUEDO EN SERVICIO LLEVA 1336-9 30% 1204-4 Y PARTE DEL 1204-5 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 5290 | keep | 0 | Mar | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-30 11:16 | 2022-03-30 11:17 | 207 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPASO SE PROBO QUEDO EN SERVICIO CARGA POR 1336-8 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 207 | keep | 0 | Mar | 2022 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-03-30 11:17 | 2022-03-30 11:22 | 30 | 000:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-29 | S22032900399 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 5 | 2022-03-30 | 150 | keep | 0 | Mar | 2022 | 0.00010216 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 11:22 | 2022-03-30 11:54 | 1483 | 000:32 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO MACHETE 65 INFANTERIA Y SE CERRO INTERRUPTOR SU CARGA POR 1336-8 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 32 | 2022-03-30 | 47456 | keep | 0 | Mar | 2022 | 0.032322 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-03-30 11:22 | 2022-03-30 11:54 | 1500 | 000:32 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO MACHETE 65 INFANTERIA Y SE CERRO INTERRUPTOR PARTE POR 1336-8 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 32 | 2022-03-30 | 48000 | keep | 0 | Mar | 2022 | 0.032693 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-03-30 11:22 | 2022-03-30 11:54 | 5290 | 000:32 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO MACHETE 65 INFANTERIA Y SE CERRO INTERRUPTOR 90% EN SERVICIO LLEVA 1336-9 30% DEL 1204-4 Y PARTE DEL 1204-5 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 32 | 2022-03-30 | 169280 | keep | 0 | Mar | 2022 | 0.1153 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-03-30 11:22 | 2022-03-30 11:54 | 207 | 000:32 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO MACHETE 65 INFANTERIA Y SE CERRO INTERRUPTOR SU CARGA POR 1336-8 | S22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 32 | 2022-03-30 | 6624 | keep | 0 | Mar | 2022 | 0.0045116 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2022-03-30 11:25 | 2022-03-30 16:05 | 2132 | 004:40 | S | LINEA DE TRANSMISION 115KV | EN SERVICIO LINEA 36100 | A22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 280 | 2022-03-30 | 596960 | keep | 0 | Mar | 2022 | 0.40659 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2022-03-30 11:25 | 2022-03-30 16:05 | 2366 | 004:40 | S | LINEA DE TRANSMISION 115KV | EN SERVICIO LINEA 36100 | A22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 280 | 2022-03-30 | 662480 | keep | 0 | Mar | 2022 | 0.45121 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2022-03-30 11:25 | 2022-03-30 16:05 | 1976 | 004:40 | S | LINEA DE TRANSMISION 115KV | EN SERVICIO LINEA 36100 | A22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 280 | 2022-03-30 | 553280 | keep | 0 | Mar | 2022 | 0.37684 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2022-03-30 11:25 | 2022-03-30 16:05 | 3688 | 004:40 | S | LINEA DE TRANSMISION 115KV | EN SERVICIO LINEA 36100 | A22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 280 | 2022-03-30 | 1032640 | keep | 0 | Mar | 2022 | 0.70333 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 3070 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 159640 | keep | 0 | Mar | 2022 | 0.10873 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 2735 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 142220 | keep | 0 | Mar | 2022 | 0.096865 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 1070 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 55640 | keep | 0 | Mar | 2022 | 0.037896 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 1647 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 85644 | keep | 0 | Mar | 2022 | 0.058332 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 3295 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 171340 | keep | 0 | Mar | 2022 | 0.1167 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 1180 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 61360 | keep | 0 | Mar | 2022 | 0.041792 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 320 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 16640 | keep | 0 | Mar | 2022 | 0.011333 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-03-30 11:25 | 2022-03-30 12:17 | 2234 | 000:52 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B22033000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 52 | 2022-03-30 | 116168 | keep | 0 | Mar | 2022 | 0.079121 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2022-03-30 11:35 | 2022-03-30 15:13 | 1116 | 003:38 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO 2 POSTES PARTIDOS TRAS PATIO | C22033000040 | New_Event | Defective Pole | Include | Include | Equipment | 218 | 2022-03-30 | 243288 | keep | 0 | Mar | 2022 | 0.1657 | 0.0007601 | Sustained | FALSE | FALSE | Not_TMED_Event | 1116
BARRANQUITAS | 2022-03-30 11:35 | 2022-03-30 12:54 | 40 | 001:19 | P | HERRAJE ROTO O PODRIDO | REMPLAZO HOT CLAMP Y FIJO PUENTE | C22033000039 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 79 | 2022-03-30 | 3160 | keep | 0 | Mar | 2022 | 0.0021523 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-03-30 11:36 | 2022-03-30 12:56 | 45 | 001:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE QUEMADO | R22033000040 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2022-03-30 | 3600 | keep | 0 | Mar | 2022 | 0.0024519 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2022-03-30 11:37 | 2022-03-30 13:52 | 1 | 002:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X AVE | C22033000042 | New_Event |  |  | Include | Wildlife | 135 | 2022-03-30 | 135 | keep | 0 | Mar | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-03-30 11:37 | 2022-03-30 11:38 | 1310 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22033000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1310 | keep | 0 | Mar | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
FAJARDO | 2022-03-30 11:41 | 2022-03-30 12:51 | 14 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER SE RETIRO AVE CRUZANDO LINEA | R22033000041 | New_Event |  |  | Include | Wildlife | 70 | 2022-03-30 | 980 | keep | 0 | Mar | 2022 | 0.00066747 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-03-30 11:42 | 2022-03-30 14:25 | 4 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22033000036 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2022-03-30 | 652 | keep | 0 | Mar | 2022 | 0.00044407 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-03-30 11:54 | 2022-03-30 12:13 | 529 | 000:19 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE ECNONTRO MACHETE QUEMADO Y AISLADOR PARTIDO RES. RAMOS ANTONINI | S22033000219 | Partial_restoration | Switch Failure | Include | Include | Equipment | 19 | 2022-03-30 | 10051 | keep | 0 | Mar | 2022 | 0.0068457 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 11:54 | 2022-03-30 12:13 | 30 | 000:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-29 | S22032900399 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 19 | 2022-03-30 | 570 | keep | 0 | Mar | 2022 | 0.00038822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-03-30 12:01 | 2022-03-30 12:02 | 1310 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1310 | keep | 0 | Mar | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
YAUCO | 2022-03-30 12:05 | 2022-03-30 13:03 | 133 | 000:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22033000056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-03-30 | 7714 | keep | 0 | Mar | 2022 | 0.005254 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
SAN JUAN | 2022-03-30 12:07 | 2022-03-30 18:02 | 12 | 005:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S22033000216 | New_Event | Secondary Wire Down | Include | Include | Equipment | 355 | 2022-03-30 | 4260 | keep | 0 | Mar | 2022 | 0.0029015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-03-30 12:09 | 2022-03-30 12:10 | 1310 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-03-30 | 1310 | keep | 0 | Mar | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-03-30 12:13 | 2022-03-30 14:11 | 1483 | 001:58 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE TRANSFIRIO AL 1206-3 PARA REPARAR MACHETE Y AISLADOR PARTIDO 1336-08 | S22033000219 | Partial_restoration | Switch Failure | Include | Include | Equipment | 118 | 2022-03-30 | 174994 | keep | 0 | Mar | 2022 | 0.11919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 12:13 | 2022-03-30 14:11 | 1500 | 001:58 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE TRANSFIRIO AL 1303-02 PARA REPARAR MACHETE Y AISLADOR PARTIDO 1336-08 | S22033000219 | Partial_restoration | Switch Failure | Include | Include | Equipment | 118 | 2022-03-30 | 177000 | keep | 0 | Mar | 2022 | 0.12055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 12:13 | 2022-03-30 16:02 | 5290 | 003:49 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ENCONTRO MACHETE QUEMADO Y AISLADOR PARTIDO DETRAS RES. RAMOS ANTONINI | S22033000000 | Additional_clients | Switch Failure | Include | Include | Equipment | 229 | 2022-03-30 | 1211410 | keep | 0 | Mar | 2022 | 0.82509 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 12:13 | 2022-03-30 16:02 | 207 | 003:49 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ENCONTRO MACHETE QUEMADO Y AISLADOR PARTIDO DETRAS RES. RAMOS ANTONINI SU CARGA POR 1336-8 | S22033000000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 229 | 2022-03-30 | 47403 | keep | 0 | Mar | 2022 | 0.032286 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-03-30 12:14 | 2022-03-31 10:56 | 129 | 022:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L Y 1 X 15 EN XMR CRUCE POR AVE | C22033000054 | New_Event |  |  | Include | Wildlife | 1362 | 2022-03-30 | 175698 | keep | 0 | Mar | 2022 | 0.11967 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
VEGA BAJA | 2022-03-30 12:14 | 2022-03-30 14:00 | 1310 | 001:46 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE SECCIONALIZO 70% EN SERVICIO | B22033000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 106 | 2022-03-30 | 138860 | keep | 0 | Mar | 2022 | 0.094577 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
GUAYAMA | 2022-03-30 12:15 | 2022-03-30 15:19 | 12 | 003:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA A 2.4 KV | P22033000059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 184 | 2022-03-30 | 2208 | keep | 0 | Mar | 2022 | 0.0015039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-03-30 12:16 | 2022-03-30 17:45 | 20 | 005:29 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22033000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 329 | 2022-03-30 | 6580 | keep | 0 | Mar | 2022 | 0.0044816 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-30 12:31 | 2022-03-30 14:25 | 450 | 001:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22033000240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-03-30 | 51300 | keep | 0 | Mar | 2022 | 0.03494 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
CANOVANAS | 2022-03-30 12:31 | 2022-03-30 15:24 | 3 | 002:53 | P | ESTRUCTURA AVERIADA | SE RELOCALIZO SECUNDARIA A POSTE EXISTENTE POR POSTE PARTIDO | R22033000045 | New_Event | Defective Pole | Include | Include | Equipment | 173 | 2022-03-30 | 519 | keep | 0 | Mar | 2022 | 0.00035349 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-30 12:40 | 2022-03-30 14:45 | 100 | 002:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22033000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-03-30 | 12500 | keep | 0 | Mar | 2022 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-03-30 13:20 | 2022-03-30 17:37 | 44 | 004:17 | P | DESGANCHE | 1 X 50 EN C/L | C22033000062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-03-30 | 11308 | keep | 0 | Mar | 2022 | 0.0077018 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2022-03-30 13:23 | 2022-03-30 13:57 | 7 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y NEUTRAL | B22033000188 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2022-03-30 | 238 | keep | 0 | Mar | 2022 | 0.0001621 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-03-30 13:38 | 2022-03-30 15:45 | 80 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS POR VEHICULO | A22033000115 | New_Event |  |  | Include | Wildlife | 127 | 2022-03-30 | 10160 | keep | 0 | Mar | 2022 | 0.0069199 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-30 13:49 | 2022-03-30 17:14 | 1 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN RISER POR MAL TIEMPO | M22033000092 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2022-03-30 | 205 | keep | 0 | Mar | 2022 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-03-30 13:50 | 2022-03-31 10:26 | 20 | 020:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22033000093 | New_Event | Bad Weather | Include | Include | Weather | 1236 | 2022-03-30 | 24720 | keep | 0 | Mar | 2022 | 0.016837 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-30 14:00 | 2022-03-30 18:29 | 50 | 004:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR CAMION IMPACTO POSTE | M22033000095 | New_Event |  |  | Include | Wildlife | 269 | 2022-03-30 | 13450 | keep | 0 | Mar | 2022 | 0.0091607 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-03-30 14:00 | 2022-03-30 16:47 | 393 | 002:47 | P | DESCONECTIVO DEFECTUOSO | SE RETIRO PALMA SOBRE LA LINEA Y SE CERRARON MACHETES PROBO MALO | B22033000000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 167 | 2022-03-30 | 65631 | keep | 0 | Mar | 2022 | 0.044701 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 14:03 | 2022-03-30 14:07 | 3838 | 000:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22033000049 | New_Event |  |  | Include | Wildlife | 4 | 2022-03-30 | 15352 | keep | 0 | Mar | 2022 | 0.010456 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
SAN JUAN | 2022-03-30 14:04 | 2022-03-30 14:05 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO QUEDO ABIERTO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 922 | keep | 0 | Mar | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-30 14:04 | 2022-03-30 14:05 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO QUEDO ABIERTO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 135 | keep | 0 | Mar | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
PONCE | 2022-03-30 14:06 | 2022-03-30 14:53 | 65 | 000:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22033000065 | New_Event |  |  | Include | Wildlife | 47 | 2022-03-30 | 3055 | keep | 0 | Mar | 2022 | 0.0020807 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-03-30 14:07 | 2022-03-30 20:41 | 6 | 006:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA EXCAVADORA DEL MUNICIPIO CRUZO LINEAS | R22033000072 | 1st_after_momentary |  |  | Include | Wildlife | 394 | 2022-03-30 | 2364 | keep | 0 | Mar | 2022 | 0.0016101 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-03-30 14:15 | 2022-03-30 17:45 | 10 | 003:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA POR 50 KVA | A22033000113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2022-03-30 | 2100 | keep | 0 | Mar | 2022 | 0.0014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-30 14:19 | 2022-03-30 18:06 | 30 | 003:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCR POR AVE | B22033000198 | New_Event |  |  | Include | Wildlife | 227 | 2022-03-30 | 6810 | keep | 0 | Mar | 2022 | 0.0046383 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-03-30 14:31 | 2022-03-30 17:30 | 6 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22033000101 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2022-03-30 | 1074 | keep | 0 | Mar | 2022 | 0.0007315 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-03-30 14:45 | 2022-03-30 15:00 | 5 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22033000146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-03-30 | 75 | keep | 0 | Mar | 2022 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-30 14:45 | 2022-03-30 15:44 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B22033000207 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-03-30 | 708 | keep | 0 | Mar | 2022 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-03-30 15:07 | 2022-03-30 17:59 | 40 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22033000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2022-03-30 | 6880 | keep | 0 | Mar | 2022 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-03-30 15:09 | 2022-03-30 15:10 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 3332 | keep | 0 | Mar | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
CAGUAS | 2022-03-30 15:13 | 2022-03-30 23:58 | 481 | 008:45 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO 2 POSTES PARTIDOS TRASPATIO ABRIENDO PUENTE EN DOS PUNTOS SE CONTINUARA TRABAJANDO CON GOI CG-220330-01 | C22033000091 | Partial_restoration | Defective Pole | Include | Include | Equipment | 525 | 2022-03-30 | 252525 | keep | 0 | Mar | 2022 | 0.17199 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-30 15:15 | 2022-03-30 16:50 | 8 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIO | A22033000165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2022-03-30 | 760 | keep | 0 | Mar | 2022 | 0.00051763 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-30 15:21 | 2022-03-30 16:42 | 60 | 001:21 | P | DESGANCHE | 1 X 50 EN RISER SE RETIRO BEJUCOS | M22033000108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-03-30 | 4860 | keep | 0 | Mar | 2022 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-03-30 15:26 | 2022-03-30 20:07 | 23 | 004:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA NO FUNDIO | B22033000216 | New_Event | Wire Down | Include | Include | Equipment | 281 | 2022-03-30 | 6463 | keep | 0 | Mar | 2022 | 0.0044019 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
GUAYAMA | 2022-03-30 15:29 | 2022-03-30 17:45 | 10 | 002:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | P22033000068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 136 | 2022-03-30 | 1360 | keep | 0 | Mar | 2022 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-30 15:50 | 2022-03-30 15:51 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C2203300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 1879 | keep | 0 | Mar | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
SAN JUAN | 2022-03-30 16:02 | 2022-03-30 21:37 | 100 | 005:35 | P | TRANSFORMADOR AVERIADO | SE DEJO T-29 FUERA HAY QUE REMPLAZARLO. SE CAMBIO T-23 2 X 100 EN RISER Y 2 X 40 EN SU-2 SE REMPLAZO PISTOLA UN EMPALME 100 CLIENTES | S22032900399 | New_Event | Service Transformer Failure | Include | Include | Equipment | 335 | 2022-03-30 | 33500 | keep | 0 | Mar | 2022 | 0.022817 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-30 16:07 | 2022-03-30 19:44 | 60 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22033000226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-03-30 | 13020 | keep | 0 | Mar | 2022 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-03-30 16:44 | 2022-03-30 23:20 | 150 | 006:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22033000128 | New_Event | Wire Down | Include | Include | Equipment | 396 | 2022-03-30 | 59400 | keep | 0 | Mar | 2022 | 0.040457 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-03-30 16:47 | 2022-03-30 16:54 | 1310 | 000:07 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE CERRO POR SCADA 70% EN SERVICIO | B22033000000 | Additional_clients | Switch Failure | Include | Include | Equipment | 7 | 2022-03-30 | 9170 | keep | 0 | Mar | 2022 | 0.0062456 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-30 16:50 | 2022-03-30 19:24 | 30 | 002:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CORTES DE LINEA POR MAL TIEMPO | M22033000131 | New_Event | Bad Weather | Include | Include | Weather | 154 | 2022-03-30 | 4620 | keep | 0 | Mar | 2022 | 0.0031467 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-03-30 16:54 | 2022-03-30 20:50 | 393 | 003:56 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y SE CERRARON MACHETES 100% EN SERVICIO | B22033000000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 236 | 2022-03-30 | 92748 | keep | 0 | Mar | 2022 | 0.06317 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-03-30 17:12 | 2022-03-30 17:49 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | R22033000060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-03-30 | 370 | keep | 0 | Mar | 2022 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-30 17:13 | 2022-03-30 18:45 | 72 | 001:32 | P | ESTRUCTURA AVERIADA | 1 X 50 EN C/L SECCIONALIZO POSTE PARTIDO | C22033000103 | New_Event | Defective Pole | Include | Include | Equipment | 92 | 2022-03-30 | 6624 | keep | 0 | Mar | 2022 | 0.0045116 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2022-03-30 17:17 | 2022-03-30 20:19 | 23 | 003:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA | S22033000368 | New_Event | Secondary Wire Down | Include | Include | Equipment | 182 | 2022-03-30 | 4186 | keep | 0 | Mar | 2022 | 0.0028511 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
VEGA BAJA | 2022-03-30 17:18 | 2022-03-30 19:45 | 15 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | B22033000252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-03-30 | 2205 | keep | 0 | Mar | 2022 | 0.0015018 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-30 17:20 | 2022-03-30 17:21 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-05 LLEVANDO PARTE DE LA CARGA 1206-03 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 1500 | keep | 0 | Mar | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-03-30 17:20 | 2022-03-30 21:05 | 141 | 003:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22033000369 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2022-03-30 | 31725 | keep | 0 | Mar | 2022 | 0.021608 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
SAN JUAN | 2022-03-30 17:20 | 2022-03-30 17:21 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-05 LLEVANDO PARTE DE LA CARGA 1206-03 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-30 | 1615 | keep | 0 | Mar | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2022-03-30 17:40 | 2022-03-30 19:35 | 150 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | GOI PC-220328-01A PARA REPLAZAR 2 POSTES PRIMARIOS PARTIDOS POR VEHCULO DE MOTOR SE ABRIO CORTE DE LINEA PARA CERRAR PUENTES PRIMARIOS EN AMBOS EXTREMOS | P22033000046 | New_Event |  |  | Include | Wildlife | 115 | 2022-03-30 | 17250 | keep | 0 | Mar | 2022 | 0.011749 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-03-30 17:46 | 2022-03-30 21:32 | 15 | 003:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA Y SE LEVANTARON 3 TRAMOS DE CONDUCTOR PRIMARIO | R22033000063 | New_Event | Wire Down | Include | Include | Equipment | 226 | 2022-03-30 | 3390 | keep | 0 | Mar | 2022 | 0.0023089 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-30 18:15 | 2022-03-30 21:44 | 50 | 003:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22033000388 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2022-03-30 | 10450 | keep | 0 | Mar | 2022 | 0.0071174 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-03-30 18:35 | 2022-03-31 09:28 | 41 | 014:53 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN AEREO PROVISIONAL HACIA SU3. AVERIA NUEVA DE SU3 A SU4 FASE A. 1 CLIENTE FUERA ESCUELA | B22033000271 | New_Event | UG Cable Fault | Include | Include | Equipment | 893 | 2022-03-30 | 36613 | keep | 0 | Mar | 2022 | 0.024937 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
SAN JUAN | 2022-03-30 18:37 | 2022-03-31 13:16 | 13 | 018:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MONTURA PARA CERRAR PUENTE DE LINEA A CAJA TRANSFORMADOR | S22033000394 | New_Event | Wire Down | Include | Include | Equipment | 1119 | 2022-03-30 | 14547 | keep | 0 | Mar | 2022 | 0.0099079 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-03-30 18:40 | 2022-03-30 19:55 | 8 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22033000229 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-03-30 | 600 | keep | 0 | Mar | 2022 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-03-30 18:45 | 2022-03-31 23:40 | 40 | 028:55 | P | ESTRUCTURA AVERIADA | 1 X 50 Y 1 X 30 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO Y TRANSFORMADOR DE 50 KVA POR ARBOL QUE CAYO | C22033000066 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1735 | 2022-03-30 | 69400 | keep | 0 | Mar | 2022 | 0.047268 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-30 19:16 | 2022-03-31 04:55 | 1 | 009:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22033000137 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 579 | 2022-03-30 | 579 | keep | 0 | Mar | 2022 | 0.00039435 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-30 19:40 | 2022-03-30 20:55 | 9 | 001:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22033000226 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 75 | 2022-03-30 | 675 | keep | 0 | Mar | 2022 | 0.00045974 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-03-30 19:41 | 2022-03-31 09:40 | 10 | 013:59 | P | OTRAS CAUSAS | 1 X 15 EN MONTURA DE TRANSFORMADOR FUSIBLE CORROIDO POR EL SALITRE | P22033000099 | New_Event | Other Causes | Include | Include | Other | 839 | 2022-03-30 | 8390 | keep | 0 | Mar | 2022 | 0.0057144 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-30 19:48 | 2022-03-31 00:59 | 3 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR LLUVIA Y VIENTO | A22033000233 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2022-03-30 | 933 | keep | 0 | Mar | 2022 | 0.00063546 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-03-30 19:53 | 2022-03-30 21:47 | 60 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | M22033000138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-03-30 | 6840 | keep | 0 | Mar | 2022 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-30 20:01 | 2022-03-30 21:26 | 80 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22033000403 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-03-30 | 6800 | keep | 0 | Mar | 2022 | 0.0046314 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-03-30 20:36 | 2022-03-31 03:40 | 1 | 007:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22033000241 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 424 | 2022-03-30 | 424 | keep | 0 | Mar | 2022 | 0.00028878 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-03-30 21:30 | 2022-03-31 09:47 | 1 | 012:17 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22033000242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 737 | 2022-03-30 | 737 | keep | 0 | Mar | 2022 | 0.00050197 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-30 21:37 | 2022-03-31 12:24 | 30 | 014:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-29 | S22032900399 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 887 | 2022-03-30 | 26610 | keep | 0 | Mar | 2022 | 0.018124 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-30 21:45 | 2022-03-31 09:40 | 20 | 011:55 | P | DESGANCHE | 1 X 65N EN CORTE DE LINEA | S22033000417 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2022-03-30 | 14300 | keep | 0 | Mar | 2022 | 0.0097397 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-03-30 23:12 | 2022-03-31 11:14 | 40 | 012:02 | P | DESGANCHE | 1 X 40 EN C/L | R22033000075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 722 | 2022-03-30 | 28880 | keep | 0 | Mar | 2022 | 0.01967 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-30 23:38 | 2022-03-31 07:38 | 23 | 008:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR 1 X 25 EN C/L CRUCE POR AVE | C22033000169 | New_Event |  |  | Include | Wildlife | 480 | 2022-03-30 | 11040 | keep | 0 | Mar | 2022 | 0.0075193 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2022-03-30 23:58 | 2022-03-31 00:24 | 43 | 000:26 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO 2 POSTES PARTIDOS TRASPATIO ABRIENDO PUENTE EN DOS PUNTOS SE CONTINUARA TRABAJANDO CON GOI CG-220330-01 | C22033000091 | Partial_restoration | Defective Pole | Include | Include | Equipment | 26 | 2022-03-30 | 1118 | keep | 0 | Mar | 2022 | 0.00076146 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-31 00:20 | 2022-03-31 00:21 | 87 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 20% DE LA CARGA POR EL 1658-14 CERRADO POR CONTROL | R22033100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 87 | keep | 0 | Mar | 2022 | 5.9255e-05 | 5.9255e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2022-03-31 00:20 | 2022-03-31 00:21 | 2245 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1658-14 CERRADO POR CONTROL | R22033100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 2245 | keep | 0 | Mar | 2022 | 0.0015291 | 0.0015291 | Momentary | FALSE | FALSE | Not_TMED_Event | 2245
SAN JUAN | 2022-03-31 00:20 | 2022-03-31 00:21 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1658-13 Y 20% DEL 1657-02 CERRADO POR CONTROL | R22033100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 1 | keep | 0 | Mar | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-31 00:51 | 2022-03-31 00:52 | 3896 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 3896 | keep | 0 | Mar | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
CAGUAS | 2022-03-31 01:16 | 2022-03-31 09:18 | 100 | 008:02 | P | DESGANCHE | 1 X 140 EN C/L Y DESGANCHE | C22033100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2022-03-31 | 48200 | keep | 0 | Mar | 2022 | 0.032829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-31 01:25 | 2022-03-31 12:37 | 15 | 011:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | B22033100001 | New_Event |  |  | Include | Wildlife | 672 | 2022-03-31 | 10080 | keep | 0 | Mar | 2022 | 0.0068654 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-03-31 01:55 | 2022-03-31 09:35 | 25 | 007:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22033100002 | New_Event | Wire Down | Include | Include | Equipment | 460 | 2022-03-31 | 11500 | keep | 0 | Mar | 2022 | 0.0078326 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-03-31 02:12 | 2022-03-31 02:13 | 2524 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 2524 | keep | 0 | Mar | 2022 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
SAN JUAN | 2022-03-31 02:17 | 2022-03-31 07:20 | 17 | 005:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA SECUNDARIA EN EL PISO Y SE EMPLAMO 40PIES 3/0 | S22033100002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 303 | 2022-03-31 | 5151 | keep | 0 | Mar | 2022 | 0.0035083 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2022-03-31 02:25 | 2022-03-31 02:26 | 1084 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22033100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 1084 | keep | 0 | Mar | 2022 | 0.00073831 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
BAYAMON | 2022-03-31 02:50 | 2022-03-31 02:52 | 1935 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-31 | 3870 | keep | 0 | Mar | 2022 | 0.0026358 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-03-31 02:50 | 2022-03-31 02:52 | 3 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-31 | 6 | keep | 0 | Mar | 2022 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-31 02:50 | 2022-03-31 02:52 | 61 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-31 | 122 | keep | 0 | Mar | 2022 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-03-31 02:50 | 2022-03-31 02:52 | 1501 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-31 | 3002 | keep | 0 | Mar | 2022 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-03-31 02:50 | 2022-03-31 02:52 | 546 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-03-31 | 1092 | keep | 0 | Mar | 2022 | 0.00074376 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
MAYAGÃœEZ | 2022-03-31 03:11 | 2022-03-31 06:23 | 10 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22033100004 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2022-03-31 | 1920 | keep | 0 | Mar | 2022 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-03-31 03:18 | 2022-03-31 09:38 | 50 | 006:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA | R22033100003 | New_Event | Cutout Failure | Include | Include | Equipment | 380 | 2022-03-31 | 19000 | keep | 0 | Mar | 2022 | 0.012941 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-03-31 03:26 | 2022-03-31 03:32 | 225 | 000:06 | T | DESGANCHE | DISPARO DE INTERRUPTOR CARGA TRANSFERIDA AL 1303-05 | S22033100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-03-31 | 1350 | keep | 0 | Mar | 2022 | 0.00091948 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-03-31 03:26 | 2022-03-31 03:32 | 870 | 000:06 | T | DESGANCHE | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1303-04 | S22033100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-03-31 | 5220 | keep | 0 | Mar | 2022 | 0.0035553 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-03-31 03:32 | 2022-03-31 11:05 | 250 | 007:33 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE DESGANCHO Y SE REMPLAZO PORTAFUSIBLE | S22033100027 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 453 | 2022-03-31 | 113250 | keep | 0 | Mar | 2022 | 0.077134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-31 03:36 | 2022-03-31 03:42 | 1825 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-03-31 | 10950 | keep | 0 | Mar | 2022 | 0.007458 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-03-31 03:36 | 2022-03-31 03:42 | 47 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-03-31 | 282 | keep | 0 | Mar | 2022 | 0.00019207 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-03-31 03:36 | 2022-03-31 03:42 | 315 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-03-31 | 1890 | keep | 0 | Mar | 2022 | 0.0012873 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-03-31 03:36 | 2022-03-31 03:42 | 2 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-03-31 | 12 | keep | 0 | Mar | 2022 | 8.1731e-06 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-03-31 03:36 | 2022-03-31 03:42 | 2391 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-03-31 | 14346 | keep | 0 | Mar | 2022 | 0.009771 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2022-03-31 03:36 | 2022-03-31 08:47 | 175 | 005:11 | P | DESGANCHE | 2 X 100 EN C/L | R22033100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-03-31 | 54425 | keep | 0 | Mar | 2022 | 0.037069 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CAGUAS | 2022-03-31 03:36 | 2022-03-31 08:55 | 2276 | 005:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 319 | 2022-03-31 | 726044 | keep | 0 | Mar | 2022 | 0.49451 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-03-31 03:36 | 2022-03-31 08:55 | 777 | 005:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 319 | 2022-03-31 | 247863 | keep | 0 | Mar | 2022 | 0.16882 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-03-31 03:36 | 2022-03-31 08:55 | 12 | 005:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 319 | 2022-03-31 | 3828 | keep | 0 | Mar | 2022 | 0.0026072 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-03-31 03:36 | 2022-03-31 08:55 | 1290 | 005:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 319 | 2022-03-31 | 411510 | keep | 0 | Mar | 2022 | 0.28028 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
MAYAGÃœEZ | 2022-03-31 03:44 | 2022-03-31 06:30 | 30 | 002:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22033100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-03-31 | 4980 | keep | 0 | Mar | 2022 | 0.0033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-03-31 03:48 | 2022-03-31 18:06 | 262 | 014:18 | P | ESTRUCTURA AVERIADA | 3 X 40 EN C/L Y SE REEMPLAZARON 3 AISLADORES Y POSTE PARTIDO | C22033100035 | New_Event | Defective Pole | Include | Include | Equipment | 858 | 2022-03-31 | 224796 | keep | 0 | Mar | 2022 | 0.15311 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
BAYAMON | 2022-03-31 04:09 | 2022-03-31 06:36 | 20 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER HACIA T 35 | B22033100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-03-31 | 2940 | keep | 0 | Mar | 2022 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-03-31 04:10 | 2022-03-31 11:40 | 6 | 007:30 | P | DESGANCHE | SE REEMPLAZO PARARRAYO, AISLADOR Y SE REALIZO DESGANCHE | C22033100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 450 | 2022-03-31 | 2700 | keep | 0 | Mar | 2022 | 0.001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-03-31 05:22 | 2022-03-31 09:49 | 80 | 004:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA | R22033100007 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2022-03-31 | 21360 | keep | 0 | Mar | 2022 | 0.014548 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-31 05:33 | 2022-03-31 11:14 | 75 | 005:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | B22033100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2022-03-31 | 25575 | keep | 0 | Mar | 2022 | 0.017419 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-03-31 06:03 | 2022-03-31 09:01 | 30 | 002:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22033100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2022-03-31 | 5340 | keep | 0 | Mar | 2022 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-03-31 06:03 | 2022-03-31 09:06 | 1647 | 003:03 | T | DESGANCHE | SE REALIZO DESGANCHE CON VARETA DE RAMA CRUZANDO LINEAS Y SE CERRO POR SCADA | B22033100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-03-31 | 301401 | keep | 0 | Mar | 2022 | 0.20528 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
VEGA BAJA | 2022-03-31 06:19 | 2022-03-31 08:08 | 150 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22033100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-03-31 | 16350 | keep | 0 | Mar | 2022 | 0.011136 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-03-31 06:26 | 2022-03-31 09:55 | 100 | 003:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P22033100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-03-31 | 20900 | keep | 0 | Mar | 2022 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-03-31 06:32 | 2022-03-31 11:37 | 400 | 005:05 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22033100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-03-31 | 122000 | keep | 0 | Mar | 2022 | 0.083094 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-03-31 06:41 | 2022-03-31 12:05 | 84 | 005:24 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22033100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-03-31 | 27216 | keep | 0 | Mar | 2022 | 0.018537 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
CAGUAS | 2022-03-31 06:44 | 2022-03-31 10:01 | 40 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22033000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-03-31 | 7880 | keep | 0 | Mar | 2022 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-03-31 06:50 | 2022-03-31 14:23 | 10 | 007:33 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | C22033100067 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 453 | 2022-03-31 | 4530 | keep | 0 | Mar | 2022 | 0.0030854 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-03-31 07:05 | 2022-03-31 07:07 | 1746 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B22033100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-31 | 3492 | keep | 0 | Mar | 2022 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
HUMACAO | 2022-03-31 07:07 | 2022-03-31 07:10 | 676 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5300 | C22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-31 | 2028 | keep | 0 | Mar | 2022 | 0.0013813 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-03-31 07:07 | 2022-03-31 07:10 | 2873 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5300 | C22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-31 | 8619 | keep | 0 | Mar | 2022 | 0.0058704 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2022-03-31 07:07 | 2022-03-31 07:10 | 3902 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5300 | C22032100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-03-31 | 11706 | keep | 0 | Mar | 2022 | 0.0079729 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
BAYAMON | 2022-03-31 07:33 | 2022-03-31 11:18 | 3 | 003:45 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y SE REALIZO DESGANCHE SECUNDARIO | B22033100046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 225 | 2022-03-31 | 675 | keep | 0 | Mar | 2022 | 0.00045974 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-03-31 07:56 | 2022-03-31 08:50 | 75 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P22033100003 | New_Event |  |  | Include | Wildlife | 54 | 2022-03-31 | 4050 | keep | 0 | Mar | 2022 | 0.0027584 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-03-31 08:11 | 2022-03-31 08:12 | 6244 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22033100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 6244 | keep | 0 | Mar | 2022 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
FAJARDO | 2022-03-31 08:16 | 2022-03-31 08:17 | 3003 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22033100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 3003 | keep | 0 | Mar | 2022 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-03-31 08:16 | 2022-03-31 08:17 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22033100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 1234 | keep | 0 | Mar | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
CANOVANAS | 2022-03-31 08:16 | 2022-03-31 08:19 | 3012 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-31 | 9036 | keep | 0 | Mar | 2022 | 0.0061544 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
VEGA BAJA | 2022-03-31 08:35 | 2022-03-31 13:08 | 24 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA FUERTE | B22033100062 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2022-03-31 | 6552 | keep | 0 | Mar | 2022 | 0.0044625 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2022-03-31 08:38 | 2022-03-31 17:15 | 120 | 008:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22033100107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 517 | 2022-03-31 | 62040 | keep | 0 | Mar | 2022 | 0.042255 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-03-31 08:41 | 2022-03-31 13:43 | 20 | 005:02 | P | DESGANCHE | 1 X 30 EN C/L Y 1 10 EN XMR | R22033100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-03-31 | 6040 | keep | 0 | Mar | 2022 | 0.0041138 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-03-31 08:41 | 2022-03-31 13:10 | 3 | 004:29 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M22033100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2022-03-31 | 807 | keep | 0 | Mar | 2022 | 0.00054964 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-03-31 08:42 | 2022-03-31 10:15 | 41 | 001:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22033100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-03-31 | 3813 | keep | 0 | Mar | 2022 | 0.002597 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CANOVANAS | 2022-03-31 08:53 | 2022-03-31 15:03 | 8 | 006:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X AVE | R22033100038 | New_Event |  |  | Include | Wildlife | 370 | 2022-03-31 | 2960 | keep | 0 | Mar | 2022 | 0.002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-31 09:00 | 2022-03-31 12:00 | 30 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO 100 PIES SECUNDARIA | S22033100046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-03-31 | 5400 | keep | 0 | Mar | 2022 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-03-31 09:06 | 2022-03-31 09:07 | 3896 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 3896 | keep | 0 | Mar | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
BAYAMON | 2022-03-31 09:28 | 2022-04-01 18:24 | 2 | 032:56 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL PARA COMPLETAR FASE ABIERTA HACIA SU-4 | B22033100078 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1976 | 2022-03-31 | 3952 | keep | 0 | Mar | 2022 | 0.0026917 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-31 09:29 | 2022-03-31 12:37 | 6 | 003:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | M22033100021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 188 | 2022-03-31 | 1128 | keep | 0 | Mar | 2022 | 0.00076828 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-03-31 09:30 | 2022-03-31 13:31 | 8 | 004:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZAR CONECTOR SECUNDARIA | S22033100066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 241 | 2022-03-31 | 1928 | keep | 0 | Mar | 2022 | 0.0013132 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-03-31 09:34 | 2022-03-31 11:21 | 7 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR SE REPARO SECUNDARIA | C22033100131 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2022-03-31 | 749 | keep | 0 | Mar | 2022 | 0.00051014 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-03-31 09:53 | 2022-03-31 10:51 | 8 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B22033100047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-03-31 | 464 | keep | 0 | Mar | 2022 | 0.00031603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-03-31 09:58 | 2022-03-31 18:02 | 1 | 008:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE ZAFADO NO FUNDIO | R22033100048 | New_Event | Wire Down | Include | Include | Equipment | 484 | 2022-03-31 | 484 | keep | 0 | Mar | 2022 | 0.00032965 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-03-31 10:02 | 2022-03-31 10:03 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22033100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 2379 | keep | 0 | Mar | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CANOVANAS | 2022-03-31 10:05 | 2022-03-31 18:59 | 1 | 008:54 | P | DESGANCHE | 1 X 30 EN C/L | R22033100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 534 | 2022-03-31 | 534 | keep | 0 | Mar | 2022 | 0.0003637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-03-31 10:06 | 2022-03-31 21:30 | 50 | 011:24 | P | DESGANCHE | 3 X 30 EN C/L Y 40 EN C/L DESGANCHE | C22033100142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 684 | 2022-03-31 | 34200 | keep | 0 | Mar | 2022 | 0.023293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-03-31 10:10 | 2022-03-31 12:26 | 5 | 002:16 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR PEDESTAL QUEMADO | M22033100024 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 136 | 2022-03-31 | 680 | keep | 0 | Mar | 2022 | 0.00046314 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-03-31 10:16 | 2022-03-31 17:23 | 15 | 007:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22033100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 427 | 2022-03-31 | 6405 | keep | 0 | Mar | 2022 | 0.0043624 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-03-31 10:22 | 2022-03-31 12:11 | 10 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22033100145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-03-31 | 1090 | keep | 0 | Mar | 2022 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-03-31 10:23 | 2022-03-31 14:50 | 40 | 004:27 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS | A22033100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2022-03-31 | 10680 | keep | 0 | Mar | 2022 | 0.0072741 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-03-31 10:25 | 2022-03-31 13:02 | 30 | 002:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS POR IMPACTO DE CAMION | A22033100015 | New_Event |  |  | Include | Wildlife | 157 | 2022-03-31 | 4710 | keep | 0 | Mar | 2022 | 0.003208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-03-31 10:26 | 2022-03-31 12:05 | 84 | 001:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P22033100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-03-31 | 8316 | keep | 0 | Mar | 2022 | 0.005664 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
CANOVANAS | 2022-03-31 10:46 | 2022-03-31 15:22 | 95 | 004:36 | P | DESGANCHE | 2 X 50 EN C/L | R22033100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-03-31 | 26220 | keep | 0 | Mar | 2022 | 0.017858 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
HUMACAO | 2022-03-31 10:48 | 2022-03-31 14:21 | 1 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22033100157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-03-31 | 213 | keep | 0 | Mar | 2022 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-03-31 10:48 | 2022-03-31 13:48 | 17 | 003:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22033100195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-03-31 | 3060 | keep | 0 | Mar | 2022 | 0.0020842 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2022-03-31 10:53 | 2022-03-31 13:28 | 1 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22033100105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-03-31 | 155 | keep | 0 | Mar | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-03-31 11:00 | 2022-03-31 15:30 | 10 | 004:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M22033100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 270 | 2022-03-31 | 2700 | keep | 0 | Mar | 2022 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-31 11:02 | 2022-03-31 19:27 | 300 | 008:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIR C/L PARA CERRAR PUENTES ABIERTOS | C22033100160 | New_Event | Wire Down | Include | Include | Equipment | 505 | 2022-03-31 | 151500 | keep | 0 | Mar | 2022 | 0.10319 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-03-31 11:09 | 2022-03-31 16:12 | 60 | 005:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | S22033100079 | New_Event | Cutout Failure | Include | Include | Equipment | 303 | 2022-03-31 | 18180 | keep | 0 | Mar | 2022 | 0.012382 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-03-31 11:24 | 2022-03-31 13:43 | 80 | 002:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L SE REEMPLAZO ALAMBRE EN EL PISO | C22033100168 | New_Event | Wire Down | Include | Include | Equipment | 139 | 2022-03-31 | 11120 | keep | 0 | Mar | 2022 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-31 11:44 | 2022-03-31 19:20 | 128 | 007:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X10 EN TRANSFORMADOR | B22033100116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 456 | 2022-03-31 | 58368 | keep | 0 | Mar | 2022 | 0.039754 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BAYAMON | 2022-03-31 12:01 | 2022-03-31 14:47 | 1984 | 002:46 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1529-12 LLEVANDO CARGA 1911-07. SE SECCIONALIZO EN URB GARDEN HILLS Y SE CERRO POR SCADA. 100% 1911-07 Y 95% 1529-12 EN SERVICIO | S22033100107 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 166 | 2022-03-31 | 329344 | keep | 0 | Mar | 2022 | 0.22431 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-03-31 12:01 | 2022-03-31 14:47 | 577 | 002:46 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1529-12 LLEVANDO CARGA 1911-07. SE SECCIONALIZO POSTE PARTIDO EN URB GARDEN HILLS Y SE CERRO POR SCADA. 100% 1911-07 | S22033100107 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 166 | 2022-03-31 | 95782 | keep | 0 | Mar | 2022 | 0.065237 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
HUMACAO | 2022-03-31 12:15 | 2022-03-31 12:21 | 327 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 2603-07 | C22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-03-31 | 1962 | keep | 0 | Mar | 2022 | 0.0013363 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
CAGUAS | 2022-03-31 12:15 | 2022-03-31 17:31 | 80 | 005:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22033100179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 316 | 2022-03-31 | 25280 | keep | 0 | Mar | 2022 | 0.017218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-03-31 12:35 | 2022-03-31 16:22 | 125 | 003:47 | P | NO SE REPORTO CAUSA | 1 X65 EN C/L | C22033100183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-03-31 | 28375 | keep | 0 | Mar | 2022 | 0.019326 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2022-03-31 12:38 | 2022-03-31 14:06 | 6 | 001:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA AVERIADA | R22033100069 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2022-03-31 | 528 | keep | 0 | Mar | 2022 | 0.00035962 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-03-31 12:43 | 2022-03-31 16:20 | 50 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22033100185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-03-31 | 10850 | keep | 0 | Mar | 2022 | 0.0073899 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-03-31 12:47 | 2022-03-31 13:15 | 1 | 000:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X REPTIL | R22033100071 | New_Event |  |  | Include | Wildlife | 28 | 2022-03-31 | 28 | keep | 0 | Mar | 2022 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-03-31 12:49 | 2022-03-31 14:34 | 7 | 001:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22033100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-03-31 | 735 | keep | 0 | Mar | 2022 | 0.00050061 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-03-31 13:06 | 2022-03-31 13:07 | 2299 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 2299 | keep | 0 | Mar | 2022 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
ARECIBO | 2022-03-31 13:14 | 2022-03-31 14:40 | 20 | 001:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | A22033100023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 86 | 2022-03-31 | 1720 | keep | 0 | Mar | 2022 | 0.0011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-03-31 13:17 | 2022-03-31 16:00 | 80 | 002:43 | P | ESTRUCTURA AVERIADA | 3 X 50 EN CORTE DE LINEA SE ABRIO PUENTES PARA REMPLAZO DE POSTE PRIMARIO | M22033100045 | New_Event | Defective Pole | Include | Include | Equipment | 163 | 2022-03-31 | 13040 | keep | 0 | Mar | 2022 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-03-31 13:22 | 2022-04-01 15:21 | 5 | 025:59 | P | CABLE SOTERRADO AVERIADO | SE REPARO LINEA SOTERRADA | M22033100047 | New_Event | UG Cable Fault | Include | Include | Equipment | 1559 | 2022-03-31 | 7795 | keep | 0 | Mar | 2022 | 0.0053091 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-03-31 13:26 | 2022-03-31 13:34 | 4431 | 000:08 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-03-31 | 35448 | keep | 0 | Mar | 2022 | 0.024143 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
MAYAGÃœEZ | 2022-03-31 13:26 | 2022-03-31 13:27 | 2825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 2825 | keep | 0 | Mar | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
BAYAMON | 2022-03-31 13:32 | 2022-03-31 18:04 | 110 | 004:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L PRINCIPAL 1 X 80 EN C/L INTERMEDIO Y 1 X 10 EN XMR AVE CRUZO CAJA PRIMARIA Y LINEA | B22033100138 | New_Event |  |  | Include | Wildlife | 272 | 2022-03-31 | 29920 | keep | 0 | Mar | 2022 | 0.020378 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BAYAMON | 2022-03-31 13:34 | 2022-03-31 17:44 | 102 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER HACIA SU 1 | B22033100173 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 250 | 2022-03-31 | 25500 | keep | 0 | Mar | 2022 | 0.017368 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-03-31 13:36 | 2022-03-31 16:40 | 15 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22033100051 | New_Event |  |  | Include | Wildlife | 184 | 2022-03-31 | 2760 | keep | 0 | Mar | 2022 | 0.0018798 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-31 13:36 | 2022-03-31 15:29 | 8 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22033100144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-03-31 | 904 | keep | 0 | Mar | 2022 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-03-31 13:43 | 2022-03-31 14:29 | 476 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-03-31 | 21896 | keep | 0 | Mar | 2022 | 0.014913 | 0.0003242 | Sustained | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-03-31 13:43 | 2022-03-31 14:29 | 1655 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-03-31 | 76130 | keep | 0 | Mar | 2022 | 0.051852 | 0.0011272 | Sustained | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-03-31 13:43 | 2022-03-31 14:29 | 361 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-03-31 | 16606 | keep | 0 | Mar | 2022 | 0.01131 | 0.00024588 | Sustained | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-03-31 13:43 | 2022-03-31 14:29 | 2842 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-03-31 | 130732 | keep | 0 | Mar | 2022 | 0.089041 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-03-31 13:43 | 2022-03-31 14:29 | 1702 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-03-31 | 78292 | keep | 0 | Mar | 2022 | 0.053324 | 0.0011592 | Sustained | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-03-31 13:43 | 2022-03-31 14:29 | 918 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-03-31 | 42228 | keep | 0 | Mar | 2022 | 0.028761 | 0.00062525 | Sustained | FALSE | FALSE | Not_TMED_Event | 918
ARECIBO | 2022-03-31 13:43 | 2022-03-31 16:16 | 40 | 002:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A22033100027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 153 | 2022-03-31 | 6120 | keep | 0 | Mar | 2022 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-03-31 14:04 | 2022-03-31 15:53 | 67 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO PB - 10 @ MH - 4 PARA VACIARLO POR AVERIA DE AAA | R22033100084 | New_Event |  |  | Include | Wildlife | 109 | 2022-03-31 | 7303 | keep | 0 | Mar | 2022 | 0.004974 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
AGUADILLA | 2022-03-31 14:05 | 2022-03-31 14:15 | 10 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M22033100049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2022-03-31 | 100 | keep | 0 | Mar | 2022 | 6.811e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-03-31 14:10 | 2022-03-31 15:59 | 1662 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZO PARA LEVANTAR NEUTRAL DEL SUELO | C22033100186 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2022-03-31 | 181158 | keep | 0 | Mar | 2022 | 0.12339 | 0.001132 | Sustained | FALSE | FALSE | Not_TMED_Event | 1662
PONCE | 2022-03-31 14:18 | 2022-03-31 17:40 | 15 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P22033100031 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2022-03-31 | 3030 | keep | 0 | Mar | 2022 | 0.0020637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-03-31 14:20 | 2022-03-31 14:45 | 7 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA. | P22033100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-03-31 | 175 | keep | 0 | Mar | 2022 | 0.00011919 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-03-31 14:27 | 2022-03-31 22:05 | 537 | 007:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22033100059 | New_Event | Wire Down | Include | Include | Equipment | 458 | 2022-03-31 | 245946 | keep | 0 | Mar | 2022 | 0.16751 | 0.00036575 | Sustained | FALSE | FALSE | Not_TMED_Event | 537
CAGUAS | 2022-03-31 14:29 | 2022-03-31 18:44 | 80 | 004:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L SE REEMPLAZO ALAMBRE EN EL PISO | C22033100168 | Partial_restoration | Wire Down | Include | Include | Equipment | 255 | 2022-03-31 | 20400 | keep | 0 | Mar | 2022 | 0.013894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-03-31 14:42 | 2022-03-31 18:58 | 1 | 004:16 | P | SECUNDARIA/DESGANCHE | 2 X 8 EN BANCO DE XMRS DESGANCHE | R22033100087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 256 | 2022-03-31 | 256 | keep | 0 | Mar | 2022 | 0.00017436 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-03-31 14:43 | 2022-04-01 13:39 | 15 | 022:56 | P | DESGANCHE | 2 X 50 EN C/L | S22033100141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1376 | 2022-03-31 | 20640 | keep | 0 | Mar | 2022 | 0.014058 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-31 14:47 | 2022-03-31 18:59 | 99 | 004:12 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | ALIMENTADOR SECCIONALIZADO | S22033100149 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 252 | 2022-03-31 | 24948 | keep | 0 | Mar | 2022 | 0.016992 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-31 14:54 | 2022-03-31 17:35 | 18 | 002:41 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22033100155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-03-31 | 2898 | keep | 0 | Mar | 2022 | 0.0019738 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-03-31 14:59 | 2022-04-01 08:40 | 7 | 017:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22033100156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1061 | 2022-03-31 | 7427 | keep | 0 | Mar | 2022 | 0.0050585 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-03-31 15:04 | 2022-03-31 17:47 | 10 | 002:43 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R22033100089 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 163 | 2022-03-31 | 1630 | keep | 0 | Mar | 2022 | 0.0011102 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-03-31 15:05 | 2022-04-01 11:05 | 15 | 020:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA TENSOR CRUZO LINEAS PRIMARIAS | M22033100062 | New_Event | Wire Down | Include | Include | Equipment | 1200 | 2022-03-31 | 18000 | keep | 0 | Mar | 2022 | 0.01226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-03-31 15:07 | 2022-03-31 15:10 | 922 | 000:03 | T | NO SE REPORTO CAUSA | RECERRO QUEDO ABIERTO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S22033000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-31 | 2766 | keep | 0 | Mar | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-03-31 15:07 | 2022-03-31 15:10 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-31 | 405 | keep | 0 | Mar | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
ARECIBO | 2022-03-31 15:11 | 2022-03-31 18:33 | 1644 | 003:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA EN TRONCAL DE ALIMENTADOR Y SE CERRO INTERRUPTOR | A22033100032 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-03-31 | 332088 | keep | 0 | Mar | 2022 | 0.22618 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
BAYAMON | 2022-03-31 15:15 | 2022-03-31 15:17 | 2617 | 000:02 | T | NO SE REPORTO CAUSA | DISOPARO DE INTERRUPTOR SE CERRO POR SCADA | B22033100158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-03-31 | 5234 | keep | 0 | Mar | 2022 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
PONCE | 2022-03-31 15:19 | 2022-04-01 13:10 | 10 | 021:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA A 4160KV POR UNO DE LA MISMA CAPACIDAD | P22033100035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1311 | 2022-03-31 | 13110 | keep | 0 | Mar | 2022 | 0.0089292 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-03-31 15:43 | 2022-03-31 15:44 | 1262 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22033100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 1262 | keep | 0 | Mar | 2022 | 0.00085954 | 0.00085954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2022-03-31 15:49 | 2022-04-01 06:11 | 50 | 014:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | P22033100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 862 | 2022-03-31 | 43100 | keep | 0 | Mar | 2022 | 0.029355 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-31 15:55 | 2022-03-31 18:42 | 18 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR FUERTES VIENTOS | A22033100041 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2022-03-31 | 3006 | keep | 0 | Mar | 2022 | 0.0020474 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-03-31 16:00 | 2022-03-31 16:30 | 1 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU-1 | S22033100172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-03-31 | 30 | keep | 0 | Mar | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-03-31 16:00 | 2022-04-01 01:09 | 40 | 009:09 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONLIZAR LA AVERIA | M22033100045 | Partial_restoration | Defective Pole | Include | Include | Equipment | 549 | 2022-03-31 | 21960 | keep | 0 | Mar | 2022 | 0.014957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-03-31 16:00 | 2022-03-31 21:21 | 1 | 005:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA FUERTE VIENTO | A22033100043 | New_Event | Bad Weather | Include | Include | Weather | 321 | 2022-03-31 | 321 | keep | 0 | Mar | 2022 | 0.00021863 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-03-31 16:01 | 2022-03-31 17:10 | 12 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO CONEXIONES | A22033100021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2022-03-31 | 828 | keep | 0 | Mar | 2022 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-03-31 16:09 | 2022-03-31 18:05 | 80 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN C/L | S22033100160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-03-31 | 9280 | keep | 0 | Mar | 2022 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-03-31 16:09 | 2022-03-31 16:10 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 12600 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 2450 | keep | 0 | Mar | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-03-31 16:09 | 2022-03-31 16:10 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 12600 | C22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 640 | keep | 0 | Mar | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-03-31 16:12 | 2022-03-31 19:36 | 513 | 003:24 | P | NO SE REPORTO CAUSA | 20% DE LA CARGA TRANSFERIDA AL 1118-10 DISPARO Y SE CERRO POR CONTROL LUEGO DE PATRULLAR | S22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-03-31 | 104652 | keep | 0 | Mar | 2022 | 0.071278 | 0.0003494 | Sustained | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-03-31 16:12 | 2022-03-31 19:36 | 2782 | 003:24 | T | NO SE REPORTO CAUSA | SE PATRULLO Y SE CERRO POR CONTROL LLEVA 20% 1111-01 | S22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-03-31 | 567528 | keep | 0 | Mar | 2022 | 0.38654 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
ARECIBO | 2022-03-31 16:25 | 2022-04-01 01:10 | 50 | 008:45 | P | ESTRUCTURA AVERIADA | 3 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO PARTIDO Y TRANSFORMADOR QUE SE AVERIO AL PARTIRCE EL POSTE DE 25KVA POR UNO DE 37.5KVA | A22033100047 | New_Event | Defective Pole | Include | Include | Equipment | 525 | 2022-03-31 | 26250 | keep | 0 | Mar | 2022 | 0.017879 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-03-31 16:36 | 2022-03-31 16:46 | 2132 | 000:10 | T | HERRAJE ROTO O PODRIDO | SE ABRIO INTERRUPTOR Y SE SECCIONALIZO AVERIA DE CRUCETA QUEMANDOSE | A22033100083 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 10 | 2022-03-31 | 21320 | keep | 0 | Mar | 2022 | 0.014521 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
CANOVANAS | 2022-03-31 16:39 | 2022-03-31 17:54 | 60 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | R22033100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-03-31 | 4500 | keep | 0 | Mar | 2022 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-03-31 16:40 | 2022-03-31 17:55 | 10 | 001:15 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | R22033100095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2022-03-31 | 750 | keep | 0 | Mar | 2022 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-03-31 16:46 | 2022-03-31 21:06 | 1599 | 004:20 | P | HERRAJE ROTO O PODRIDO | SE REPARO CRUCETA Y SE CERRO MACHETES | A22033100083 | Partial_restoration | Broken / Rusty Hardware | Include | Include | Equipment | 260 | 2022-03-31 | 415740 | keep | 0 | Mar | 2022 | 0.28316 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-03-31 16:50 | 2022-03-31 18:41 | 4 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BARRAS EN PEDESTAL | C22033100388 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2022-03-31 | 444 | keep | 0 | Mar | 2022 | 0.00030241 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-03-31 16:58 | 2022-03-31 18:48 | 42 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO MS LIK REFERENCIA 8101356 | P22033100044 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-03-31 | 4620 | keep | 0 | Mar | 2022 | 0.0031467 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2022-03-31 17:08 | 2022-03-31 18:22 | 15 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22033100169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-03-31 | 1110 | keep | 0 | Mar | 2022 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-03-31 17:19 | 2022-03-31 19:04 | 10 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22033100170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-03-31 | 1050 | keep | 0 | Mar | 2022 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-03-31 17:24 | 2022-03-31 20:55 | 25 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | B22033100172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-03-31 | 5275 | keep | 0 | Mar | 2022 | 0.0035928 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-03-31 17:36 | 2022-03-31 19:39 | 8 | 002:03 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | B22033100174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-03-31 | 984 | keep | 0 | Mar | 2022 | 0.0006702 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-03-31 17:43 | 2022-03-31 18:54 | 2 | 001:11 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22033100176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-03-31 | 142 | keep | 0 | Mar | 2022 | 9.6716e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-03-31 18:27 | 2022-03-31 18:28 | 824 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 65% DE SU CARGA POR 2604-03 | C22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 824 | keep | 0 | Mar | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
CAGUAS | 2022-03-31 18:29 | 2022-03-31 19:50 | 8 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22033100447 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-03-31 | 648 | keep | 0 | Mar | 2022 | 0.00044135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-03-31 18:41 | 2022-03-31 22:25 | 1253 | 003:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 SE TRANSFIRIO LA SUBESTACION A LA LINEA 2000 | M22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 224 | 2022-03-31 | 280672 | keep | 0 | Mar | 2022 | 0.19116 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-03-31 18:41 | 2022-03-31 22:25 | 1266 | 003:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 SE TRANSFIRIO LA SUBESTACION A LA LINEA 2000 | M22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 224 | 2022-03-31 | 283584 | keep | 0 | Mar | 2022 | 0.19315 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-03-31 18:41 | 2022-03-31 22:25 | 411 | 003:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 SE TRANSFIRIO LA SUBESTACION A LA LINEA 2000 | M22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 224 | 2022-03-31 | 92064 | keep | 0 | Mar | 2022 | 0.062704 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-03-31 18:41 | 2022-04-01 10:59 | 108 | 016:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1500 | M22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 978 | 2022-03-31 | 105624 | keep | 0 | Mar | 2022 | 0.07194 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2022-03-31 18:51 | 2022-03-31 21:43 | 80 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL AEREO | S22033100271 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2022-03-31 | 13760 | keep | 0 | Mar | 2022 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-03-31 18:59 | 2022-03-31 19:01 | 1984 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1911-07 | S22033100000 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2022-03-31 | 3968 | keep | 0 | Mar | 2022 | 0.0027026 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-31 18:59 | 2022-03-31 19:01 | 577 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | CARGA TRANSFERIDA AL 1529-12 DISPARO Y SE CERRO POR CONTROL | S22033100000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2022-03-31 | 1154 | keep | 0 | Mar | 2022 | 0.00078598 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2022-03-31 19:01 | 2022-03-31 19:37 | 99 | 000:36 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | ALIMENTADOR SECCIONALIZADO | S22033100149 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 36 | 2022-03-31 | 3564 | keep | 0 | Mar | 2022 | 0.0024274 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
PONCE | 2022-03-31 19:02 | 2022-03-31 21:31 | 20 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA RATON CRUZO FASE | P22033100058 | New_Event |  |  | Include | Wildlife | 149 | 2022-03-31 | 2980 | keep | 0 | Mar | 2022 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-03-31 19:14 | 2022-03-31 19:15 | 1935 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 APAGANDOSE LA BARRA GUARAGUAO 38 KV | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 1935 | keep | 0 | Mar | 2022 | 0.0013179 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-03-31 19:14 | 2022-03-31 19:15 | 3 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 APAGANDOSE LA BARRA GUARAGUAO 38 KV | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 3 | keep | 0 | Mar | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-03-31 19:14 | 2022-03-31 19:15 | 61 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 APAGANDOSE LA BARRA GUARAGUAO 38 KV | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 61 | keep | 0 | Mar | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-03-31 19:14 | 2022-03-31 19:15 | 1501 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 APAGANDOSE LA BARRA GUARAGUAO 38 KV | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 1501 | keep | 0 | Mar | 2022 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-03-31 19:14 | 2022-03-31 19:15 | 546 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 APAGANDOSE LA BARRA GUARAGUAO 38 KV | B22033100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-03-31 | 546 | keep | 0 | Mar | 2022 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
CAGUAS | 2022-03-31 19:14 | 2022-03-31 19:15 | 554 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 554 | keep | 0 | Mar | 2022 | 0.00037733 | 0.00037733 | Momentary | FALSE | FALSE | Not_TMED_Event | 554
MAYAGÃœEZ | 2022-03-31 19:14 | 2022-04-01 07:09 | 150 | 011:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22033100160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2022-03-31 | 107250 | keep | 0 | Mar | 2022 | 0.073047 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-03-31 19:15 | 2022-03-31 21:44 | 1 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | C22033100515 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-03-31 | 149 | keep | 0 | Mar | 2022 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-03-31 19:15 | 2022-04-01 04:22 | 6 | 009:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22033100161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 547 | 2022-03-31 | 3282 | keep | 0 | Mar | 2022 | 0.0022354 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-03-31 19:19 | 2022-03-31 20:19 | 80 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A22033100093 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2022-03-31 | 4800 | keep | 0 | Mar | 2022 | 0.0032693 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-03-31 19:21 | 2022-04-01 14:00 | 40 | 018:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S22033100316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1119 | 2022-03-31 | 44760 | keep | 0 | Mar | 2022 | 0.030486 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-03-31 19:21 | 2022-04-01 07:39 | 120 | 012:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22033100486 | New_Event | Vegetation Contact | Include | Include | Vegetation | 738 | 2022-03-31 | 88560 | keep | 0 | Mar | 2022 | 0.060318 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-03-31 19:25 | 2022-03-31 19:28 | 553 | 000:03 | P | NO SE REPORTO CAUSA | 30% DE SU CARGA TRANSFERIDO AL 1529-15 DISPARO Y SE CERRO POR CONTROL | S22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-31 | 1659 | keep | 0 | Mar | 2022 | 0.0011299 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-03-31 19:25 | 2022-03-31 19:28 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 30% DEL 1346-02 | S22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-03-31 | 5406 | keep | 0 | Mar | 2022 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-03-31 19:37 | 2022-03-31 21:13 | 1984 | 001:36 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO INTERRUPTOR 1529-12 LLEVANDO CARGA 1911-07 SECCIONALIZANDO ALIIMENTADOR 1529-12. 20% 1529-12 EN SERVICIO | B22033100286 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 96 | 2022-03-31 | 190464 | keep | 0 | Mar | 2022 | 0.12972 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-03-31 19:37 | 2022-03-31 22:33 | 577 | 002:56 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO EN RISER FRENTE A GASOLINERA TOTAL - AVE. LUIS VIGOREAUX PARA SECCIONALIZAR AVERIA DEL 1529-12 QUE LLEVA TRANSFERIDA LA CARGA DEL 1911-07 | S22033100085 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 176 | 2022-03-31 | 101552 | keep | 0 | Mar | 2022 | 0.069167 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
ARECIBO | 2022-03-31 19:55 | 2022-03-31 21:17 | 300 | 001:22 | P | SOBRECARGA | 1 X 200 EN CORTE DE LINEA POR CARGA | A22033100097 | New_Event | Trip Due To Overload | Include | Include | Other | 82 | 2022-03-31 | 24600 | keep | 0 | Mar | 2022 | 0.016755 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-03-31 20:02 | 2022-03-31 20:03 | 1860 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S22033100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-03-31 | 1860 | keep | 0 | Mar | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2022-03-31 20:09 | 2022-03-31 23:00 | 6 | 002:51 | P | CABLE SOTERRADO AVERIADO | 1X20 EN RISER AVERIA NUEVA: T-14 @ T-15, AVERIA VIEJA: T-16 @ T-17, FUERA DE SERVICIO: T-15 & T-16, SE LE REFIRIO AL DISTRITO | B22033100213 | New_Event | UG Cable Fault | Include | Include | Equipment | 171 | 2022-03-31 | 1026 | keep | 0 | Mar | 2022 | 0.0006988 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-03-31 20:09 | 2022-04-01 15:55 | 12 | 019:46 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA DE CABLE SOTERRADO DE T-14 @ T-15 | B22033100213 | New_Event | UG Cable Fault | Include | Include | Equipment | 1186 | 2022-03-31 | 14232 | keep | 0 | Mar | 2022 | 0.0096934 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-03-31 20:10 | 2022-04-01 10:13 | 100 | 014:03 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22033100214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 843 | 2022-03-31 | 84300 | keep | 0 | Mar | 2022 | 0.057416 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100